## NCR Data
Contract | Site Area | PTR Number | Type | Subject | Originator | Organisation | Organisation Code | Project Area | Location | Required Close Out Date | Closed Out Date | Days Late | Date Initiated | Discipline | Estimated_Cost_of_NCR | FCD Classification | NCR Classification, eB_Proposed_Disposition AS [Proposed_Disposition | Final_Disposition | Category | Status | Root Cause | Stage | Initiator | Detailed Description | Current Actioner
| 06TD - Technical (Design) | Cxxx-NCR-000018 | NCR | Auto-Transformer Impedance |  | Contr |  | ZAW - Asset Wide (All Locations) (Technical (Design)) |  | 2011-04-22 | 2011-09-02 11:10 | 133 | 2011-03-31 | Systems - Traction Power Systems | 500 |  | Design | Reject |  | Complete |  | Completed |  | The incorrect value of auto-transformer impedance has been used in Cxxx studies
| 06TD - Technical (Design) | Cxxx-NCR-000034 | NCR | Superseded specification not withdrawn from use |  | Contr |  | PAD - Paddington Station (Technical (Design)) |  | 2011-03-02 | 2012-05-30 09:28 | 455 | 2011-02-02 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Repair |  | Complete |  | Completed |  | Front sheet of specification C131-MMD-C2-RSP-B071-00002 Rev 2.0 states that it was formerly C131-MMD-C2-COM-B071-00002 and therefore supersedes the former document. This former document has not been issued as superseded resulting in two current and different versions of specifications for energy piles in the eB EDMS
| 06TD - Technical (Design) | Cxxx-NCR-000035 | NCR | Two Different Drawing Registers in eB Listing the Same Drawings with Discrepencies |  | Contr |  | PAD - Paddington Station (Technical (Design)) |  | 2011-05-20 | 2011-09-30 08:28 | 133 | 2011-04-19 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | Two registers listing the same drawings are stored and available in eB with no indication of which is the definitive current register. Both C131-MMD-Z-LRG-B071-00006 Rev 9.0 and C131-MMD-Z-LRG-B071-00009 Rev 5.0 are lists of RIBA F drawings. Examination of 70 drawings listed on both registers showed that seven of the drawings had discrepancies in their revision status (eg C131-MMD-S-DDB-B071_Z-13009 is listed at Rev C01 in C131-MMD-Z-LRG-B071-00006 Rev 9.0 and at Rev C02 in C131-MMD-Z-LRG-B071-00009 Rev 5.0. In addition, one drawing, C131-MMD-S-DDD-B071_Z-15042 is listed in C131-MMD-Z-LRG-B071-00009 Rev 5.0 but not listed in C131-MMD-Z-LRG-B071-00006 Rev 9.0. .
| 06TD - Technical (Design) | Cxxx-NCR-000038 | NCR | Missing Technical Reference |  | Contr |  | PAD - Paddington Station (Technical (Design)) |  | 2012-05-02 | 2012-07-23 12:27 | 82 | 2012-04-18 | Architectural - Roofing & Exterior Treatment | 500 |  | Design | Rework |  | Complete |  | Completed |  | Technical Reference Sheet, C131-MMD-A-RSP-B071-00004, does not include the specification reference for tag STR-08
| 06TD - Technical (Design) | Cxxx-NCR-000294 | NCR | WTH Stair 3 Headroom - Remedial |  | Crossrail | PDP | BOS - Bond Street Station (Technical (Design)) |  | 2013-09-27 | 2013-10-04 17:33 | 7 | 2013-09-13 11:22 | Architectural - General | 5000 |  | Design | Repair | 3 (3-6k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | Headroom is not sufficient at the ground floor landing of stair 3
| 06TD - Technical (Design) | Cxxx-NCR-000105 | NCR | No evidence that design continues to QMS in line with ISO 9001. |  | Crossrail | XRL | PML - Pudding Mill Lane Portal (Technical (Design)) |  | 2015-10-16 | 2015-12-03 12:01 | 48 | 2015-08-17 09:13 | Civil - Civil Engineering General | 0 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | No information was provided for surveillance QS152-01 by Cxxx with respect to their quality management system.
| 06TD - Technical (Design) | Cxxx-NCR-000106 | NCR | EIP Blockwork Cracks |  | Crossrail | XRL | PML - Pudding Mill Lane Portal (Technical (Design)) |  | 2019-08-27 12:22 | 2019-05-29 12:55 | -90 | 2019-04-25 08:57 | Architectural - Brickworks/Blockworks | 22000 |  | Design | Use As-Is | 2 (6-60k) | Complete | Design Problem - Inadequate or defective design | Completed |  | Further to Cxxx-NCR-002458 and Cxxx-NCR-002480 regarding blockwork cracks observed in the EIP building on 30/05/2017 additional cracks were noted subsequently at the ground and first floors when the Framework Design Consultant (Cxxx __) carried out a survey on 13/11/2018. The Designer compiled a report recording crack dimensions, locations and required remedial works – ‘Design Assurance Statement EIP Blockwork at Surface Level and Level 01’ (Cxxx-SWN-S-__-CR094_PT002-50004 Rev 2) (refer Att 01). The Designer has specified that cracks with a width of greater than 0.3mm shall be chased out to a width of 15mm and depth of 10mm and then firestopped using a fire-resistant silicone sealant (refer Att 01). Crack repair number 7 in CER 1/740 and Switch Room 1/662 is inaccessible because of MEP equipment and CMS fixed to the wall. A meeting was held on 19/02/2019 with RfL, __ and CRL to discuss the remedial work. All present agreed that the remedial proposed was acceptable and that the 2 areas where the cracks are not accessible could be ‘use as-is’ (refer Att 02 Item 2.10). A follow up email was sent on 4/03/2019 to the attendees of the meeting (RfL, __ and CRL) confirming acceptance of ‘use as-is’ for repair number 7 (refer Att 03) The Contractor managed to carry out the remedial work on the upper level repair number 3.
| 06TD - Technical (Design) | Cxxx-NCR-000009 | NCR | Duplicate Copies of Drawings with Different Drawing Numbers |  | Contr |  | WEP - Westbourne Park (Technical (Design)) |  | 2011-08-03 | 2013-08-29 13:32 | 757 | 2011-07-13 | Shafts - Linings | 500 |  | Supervision/Management | Repair |  | Complete |  | Completed |  | Superseded documents in eB have not been identified as “superseded” in eB and the replacement documents have not been registered and stored in eB. See attachment for full details
| 02SL - Stations (LUL) | Cxxx-NCR-000009 | NCR | Doument Approvals |  | Contr |  | BOS - Bond Street Station (West) |  | 2010-10-14 | 2011-03-07 10:15 | 144 | 2010-10-07 | Civil - Civil Engineering General | 500 |  |  | Rework |  | Complete |  | Completed |  | Documents including quality plan and ITP without contractor signatures and/or PDP decal code 1 or 2 acceptance.
| 02SL - Stations (LUL) | Cxxx-NCR-000015 | NCR | Concrete Retention works installation in Gilbert street |  | Contr |  | BOS - Bond Street Station (West) |  | 2011-02-15 | 2012-03-07 15:50 | 386 | 2011-02-07 | Civil - Demolition/Site Clearance | 500 |  | System Defect | Use As-Is |  | Complete |  | Completed |  | The new concrete retention as per the issued as built, via eB with a Transmittal No :C207-CRL-0000004/TR002 on 20/01/2011 shows that it is constructed at an offset distance of 410mm from outside of the proposed walling. Which actually should have constructed at 1.5m offset from the proposed walling as per the issued drawing.
| 02SL - Stations (LUL) | Cxxx-NCR-000016 | NCR | 19 Hanover Square brick repair |  | Contr |  | BOS - Bond Street Station (West) |  | 2011-03-11 | 2012-03-27 10:23 | 382 | 2011-03-03 | Civil - Demolition/Site Clearance | 500 |  | Supervision/Management | Rework |  | Complete |  | Completed |  | In order to rebuild a section of the 19 Hanover Square party wall at level five on the front elevation, a strip of poor quality brickwork was removed to allow rebuild. The section of brickwork removed was in excess of the agreed area to be removed.
| 02SL - Stations (LUL) | Cxxx-NCR-000017 | NCR | Installation of Stage 1 Sheet Piles at the corner of Gilbert St and St Anselms Place |  | Contr |  | BOS - Bond Street Station (West) |  | 2011-03-25 | 2012-03-07 15:51 | 348 | 2011-03-15 | Civil - Demolition/Site Clearance | 500 |  | Workmanship | Rework |  | Complete |  | Completed |  | To enable installation of stage 1 sheet piles, the nearside kerbline has been removed adjacent to the hoarding line. Additional sheet piles were installed at the corner of Gilbert St and St Anselms Place which were not on the design drawing. During excavation for installation of the box frame, the depth of dig was in excess of the design depth. A crack has formed in the pavement during these works.
| 02SL - Stations (LUL) | Cxxx-NCR-000019 | NCR | WTH Basement Retention Removal - Installation of Sheet Piles |  | Contr |  | BOS - Bond Street Station (West) |  | 2011-03-25 | 2012-03-07 15:53 | 348 | 2011-03-25 | Civil - Demolition/Site Clearance | 500 |  | Workmanship | Rework |  | Complete |  | Completed |  | Sheet piles are not interlocked, and have been installed with the backside (flat section) on the far side of the frame. This limits the amount of welding to the frame to thickness of the sheet pile, instead of the full width. No sheet piles installed on sides of the trench as detailed in the MS and TWD. Excavation carried out is not battered to 45 degrees as per MS (some sections are vertical). The length of the frame is 7.5m instead of 11.5m.
| 02SL - Stations (LUL) | Cxxx-NCR-000022 | NCR | Temporary Wind Barrier __ledge |  | Contr |  | BOS - Bond Street Station (West) |  | 2011-05-16 | 2011-07-29 14:42 | 74 | 2011-05-13 | Civil - Demolition/Site Clearance | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | Pre-cast kentledge blocks have been used as a substitute for in-situ cast blocks to accelerate the programme.
| 02SL - Stations (LUL) | Cxxx-NCR-000043 | NCR | Non-logging of Field Changes |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2010-10-26 | 2010-10-13 08:23 | -13 | 2010-10-12 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | The structural beams installed by the contractor do not use M16 Lindapter girder clamps as specified in the fixing details. The Contractor has been reminded several times that all deviations from the design need to be either pre-approved or captured post installation by the correct Field Change procedure. Failure to log this change is a non-conformance against the process.
| 02SL - Stations (LUL) | Cxxx-NCR-000048 | NCR | Lack of Pull test on CMS fixings |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2010-11-01 | 2011-07-20 12:37 | 261 | 2010-10-18 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | during site surveillance on 14/10/10 there was no evidence of pull test records on the newly installed CMS fixings
| 02SL - Stations (LUL) | Cxxx-NCR-000072 | NCR | Installation of New Single Fire Door (for CER 1/951 Fire Rated Hoarding) |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2010-11-05 | 2010-11-29 19:16 | 24 | 2010-11-02 | Fire - Compartmentation | 500 |  | Workmanship | Rework |  | Complete |  | Completed |  | The door installed is not a __ Door as per approved design. In addition, the door could not be opened fully due to a clash with an existing asset (50 x 50mm trunking mounted on existing ceiling) and the door frame was subject to movement meaning the door could not be easily secured/locked.
| 02SL - Stations (LUL) | Cxxx-NCR-000091 | NCR | Cutting, Drilling and Fixing Log |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2010-12-06 | 2010-11-29 11:51 | -7 | 2010-11-15 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Rework |  | Complete |  | Completed |  | Although signed records of penetrations had been kept, these were not in the correct template as required in the standard. The cutting, drilling and fixing log is an important piece of assurance evidence and will need to sent to LUL upon completion of the project.
| 02SL - Stations (LUL) | Cxxx-NCR-000093 | NCR | Non-machine cut blockwork |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2010-11-23 | 2010-11-26 16:20 | 3 | 2010-11-16 | Architectural - Brickworks/Blockworks | 500 |  | Workmanship | Reject |  | Complete |  | Completed |  | As can be seen in the attached picture the blocks on the Left Hand Side have not been machine cut.
| 02SL - Stations (LUL) | Cxxx-NCR-000094 | NCR | Formwork - Composition of Sacrificial Shutter |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2010-11-19 | 2010-11-26 23:21 | 7 | 2010-11-16 | Civil - Civil Engineering General | 500 |  | Material | Reject |  | Complete |  | Completed |  | Following installation of the formwork during the weekend of 13November, it is evident that the class 0 ply installed in this area is to be a sacrificial shutter. This was not outlined in the sketch and timber cannot be left in situ without a concession against LUL standards.
| 02SL - Stations (LUL) | Cxxx-NCR-000099 | NCR | Serrated washers on post route |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2010-12-01 | 2010-11-26 16:19 | -5 | 2010-11-17 | Electrical - Cable Management | 500 |  | Damaged | Rework |  | Complete |  | Completed |  | The serrated washers installed are not of sufficient size to cover the manufactured holes in the PFC's, good practice would have been to install a suitable penny washer so that the serrated washer is seated correctly against the mating surfaces. As it is, the majority of washers have been damaged and these would need to be revisited regardless of any further requirements.
| 02SL - Stations (LUL) | Cxxx-NCR-000100 | NCR | Level of Structural L Beams along gridline G - H |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2010-12-02 | 2011-07-20 12:39 | 230 | 2010-11-18 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | The installed beams do not appear to be level.
| 02SL - Stations (LUL) | Cxxx-NCR-000101 | NCR | Defective Fixing on Structural Beam |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2010-11-21 | 2010-11-25 08:44 | 4 | 2010-11-18 | Civil - Civil Engineering General | 500 |  | Material | Reject |  | Complete |  | Completed |  | The underside of the clamp is manufactured incorrectly causing the connecting bolts to be skewed.
| 02SL - Stations (LUL) | Cxxx-NCR-000104 | NCR | Corners not bonded |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2010-11-25 | 2010-11-25 14:18 | 0 | 2010-11-23 | Architectural - Brickworks/Blockworks | 500 |  | Workmanship | Rework |  | Complete |  | Completed |  | 2 No corners not bonded. Movement joints installed instead.
| 02SL - Stations (LUL) | Cxxx-NCR-000131 | NCR | Defective Blockwork |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2010-12-16 | 2011-01-12 14:06 | 27 | 2010-12-09 | Architectural - Brickworks/Blockworks | 500 |  | Workmanship | Rework |  | Complete |  | Completed |  | Poor workmanship was the reason of the deficiency in the blockwork, the blockwork has subsequently been removed and is currently being constructed to the satisfactory standard.
| 02SL - Stations (LUL) | Cxxx-NCR-000132 | NCR | Powder Coated Trunking |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2010-12-10 | 2011-01-12 14:11 | 33 | 2010-12-09 | Electrical - Cable Management | 500 |  | Design | Reject |  | Complete |  | Completed |  | The powder coated trunking delivered to site on the 07th December 2010 was the incorrect design, the deficiency in the trunking was due to the inadequate dividers in the trunking, which were 100mm in length, the length of the dividers in the design is 150mm. The powder coated trunking has subsequently been redelivered to the desirable requirements and will be installed during the engineering hours shift on the 10th December 2010.
| 02SL - Stations (LUL) | Cxxx-NCR-000178 | NCR | In complete Powder Coated Trunking Platform 2 |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2011-03-03 | 2011-08-23 21:51 | 173 | 2011-02-25 | Electrical - Cable Management | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | The powder coated trunking currently terminates when alternating from horizontal to vertical sections, the vertical section also requires installation in Powder Coated Finish due to the level of the PPC Panels at this location
| 02SL - Stations (LUL) | Cxxx-NCR-000209 | NCR | UPS Manufacturer |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2011-04-08 | 2011-08-01 15:59 | 115 | 2011-03-31 | Electrical - LV Equipment | 500 |  | Material | Reject |  | Complete |  | Completed |  | It is now apparent that the UPS currently in the process of being installed in the CER room is not from Chloride Ltd as specified in the electrical specifications. This change from design has not be requested by the Contractor.
| 02SL - Stations (LUL) | Cxxx-NCR-000213 | NCR | M&E asset locations in CER |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2011-04-17 | 2011-08-01 16:05 | 106 | 2011-04-13 | Mechanical - Mechanical Engineering General | 500 |  | Supervision/Management | Rework |  | Complete |  | Completed |  | Various M&E assets have been installed which will obstruct the installation of these assets as planned.
| 02SL - Stations (LUL) | Cxxx-NCR-000003 | NCR | Commencement of Works prior to ITP Approval at Code 1/2 |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2011-05-19 | 2011-05-26 10:23 | 7 | 2011-05-19 | Civil - Utilities Engineering | 500 |  | Planning | Repair |  | Complete |  | Completed |  | Trial hole and excavation works for the C216 utilities diversions started on site prior to recieving Code 1/2 approval of ITP's.
| 02SL - Stations (LUL) | Cxxx-NCR-000017 | NCR | Concrete acceptance for Moorfields TBS |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2011-07-19 | 2011-09-15 16:20 | 58 | 2011-07-13 | Utilities Engineering - Electricity | 500 |  | Material | Rework |  | Complete |  | Completed |  | Cubes were not taken for the 3m x 3m x 300mm deep TBS base slab on the Moorfields pedestrianised area. Cube results are required by Crossrail to provide verification of the concrete strength to __.
| 02SL - Stations (LUL) | Cxxx-NCR-000029 | NCR | Non Conformant Gas Main location within utility corridor |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2011-08-25 | 2011-09-15 16:46 | 21 | 2011-08-18 | Utilities Engineering - Gas | 500 |  | System Defect | Rework |  | Complete |  | Completed |  | The new 125mm LP gas main has been installed nestled within the telecoms bank, preventing access to NGG for new connections and maintenance. NGG's site representative (Nigel Watts) confirmed at a site meeting on 17/8/11 that the current configuration is unnacceptable and must be re-laid within a clear route as per their requirements.
| 02SL - Stations (LUL) | Cxxx-NCR-000032 | NCR | Duct Testing Non Conformances |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2011-09-06 | 2012-02-22 16:36 | 169 | 2011-08-30 | Utilities Engineering - Telecomms | 500 |  | Workmanship | Rework |  | Complete |  | Completed |  | No ducts to date have been tested in accordance with the above specifications or the approved ITP plan for C216. Inserting a rope with a rod does not contitute a full test and should not be presented a such.
| 02SL - Stations (LUL) | Cxxx-NCR-000036 | NCR | Telecom Chamber Defects |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2011-09-30 | 2012-02-22 16:12 | 145 | 2011-09-16 | Utilities Engineering - Telecomms | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | Chamber defects as listed in attached document - created during inspection walkover of chambers on 15/9/11 with LoR and CRL.
| 02SL - Stations (LUL) | Cxxx-NCR-000022 | NCR | Steelwork Fabrication |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2011-03-25 | 2011-08-05 14:05 | 133 | 2011-03-09 | Civil - Structural Engineering | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | Works information ( Bolume 1 -General ) CRL1-PDP-W-XW1-CRG03-00025 version 2 item 5.7 specifies: '' the contractor shal prepare and submit an ITP , the contractor shall not commence the works until the project manager has accepted it
| 02SL - Stations (LUL) | Cxxx-NCR-000086 | NCR | Grout for Patching Up Existing Lining Removed From Bolt Cutting |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2011-12-12 | 2011-12-01 15:19 | -11 | 2011-11-28 | Civil - Civil Engineering General | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | The mortar was deliveried to site to met originial program requirements with a production date of 14.6.2011. Due to delays in revising safe system of work and weather the mortar the 3 months has expired. Please note none of the material has been used in the works. The issuie has been nnoticed proir to the material be in required
| 02SL - Stations (LUL) | Cxxx-NCR-000093 | NCR | Incorrect Bay Sizes, Main Shaft heading North |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2012-01-18 | 2012-02-08 09:05 | 21 | 2012-01-04 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | From north of the main saft bays have been formed incorrectly with 6no 4.264m bays and 9no 8.528m. This means overall conrete lining from the centre of the shaft north is 102.336m and not as design of 106.6m. In addition the last bay has had the movement joint formed. To extend the concrete lining the correct distance would mean the emergerncy egress at Swanlea School will need to be incoporated into the works.
| 02SL - Stations (LUL) | Cxxx-NCR-000094 | NCR | Scaffolding clip in the concrete mix |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2012-02-24 | 2012-03-28 11:03 | 33 | 2012-02-17 | Civil - Civil Engineering General | 500 |  |  | Use As-Is |  | Complete |  | Completed |  | Scaffolding clip was found in the concrete mix while poring concrete into the sewer was taken place. The scaffold clip was retrieved from the concrete during placement of the concrete
| 02SL - Stations (LUL) | Cxxx-NCR-000095 | NCR | D9 - Void |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2012-03-13 | 2012-03-28 11:14 | 15 | 2012-02-28 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | D9 was poured on the 27th Feb 2012. On cormencement of stripping the shutters on the crown. There is a void in the crown where the shutter has not been filled. During the concrete pour the air hole on the stopped was closed once concrete started to come out of it
| 02SL - Stations (LUL) | Cxxx-NCR-000098 | NCR | Joint Between D12/D11 |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2012-03-13 | 2012-03-28 11:26 | 15 | 2012-03-06 | Civil - Civil Engineering General | 500 |  |  | Repair |  | Complete |  | Completed |  | The joint fill at the invert has lifted during the concrete pour. Therefore there is not a uniform joint located at the joint of the cast ioron segement
| 02SL - Stations (LUL) | Cxxx-NCR-000099 | NCR | Concrete Finish D17 to d11 |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2012-03-13 | 2012-03-28 11:38 | 15 | 2012-03-06 | Civil - Civil Engineering General | 500 |  |  | Repair |  | Complete |  | Completed |  | Due to the bend in the existng sewer and forming the bay with 1m straight shutter panels. Joint between the shutter panels oin placeces have opened up. This has caused remial woeks required. D12, D14 and D15 are the worst effected bays please see attached photos. Photo D16 show the minotr repair required for the joints
| 02SL - Stations (LUL) | Cxxx-NCR-000105 | NCR | Extensometer SB804-C-EX Location Bay 6/7 4 o'clock |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2012-07-12 | 2012-07-05 13:29 | -7 | 2012-06-28 | Surveying - Instrumentation and Monitoring | 500 |  | Equipment Breakdown | Repair |  | Complete |  | Completed |  | all works where completed and all instruments test once per day for 5 days with a hand helded vibrating wire reader. On completing the installation of the control cabinets and wiring. The extensometer located at 4 oclock southbound between bay 6/7 was not recording. Instrument was discounted from the control panel and manually tested. On reading could be obtian. Either the instrument or cable is defective. As the completion of the control panel was after the shaft fit out. Cable was cut at the base of the shaft and tested. On signal could be obtianed from the instrument. Therefore entre into the sewer is required
| 01CV - Civils | Cxxx-NCR-000042 | NCR | Non UKAS accredited Technician |  | Contr |  | WEP - Westbourne Park (West) |  | 2010-11-04 | 2011-03-01 16:37 | 117 | 2010-10-29 | Structural Engineering - Testing | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | The contractor did not have a trained operative / technician in accordance with the specification i.e. UKAS accredited, to carry out the sampling and testing of concrete to be used on site.
| 01CV - Civils | Cxxx-NCR-000043 | NCR | Concrete Mix Design |  | Contr |  | WEP - Westbourne Park (West) |  | 2010-11-01 | 2011-01-18 13:27 | 78 | 2010-11-01 | Geotechnical Engineering - Concrete - Bored Pile | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | Concrete mix used for piling was not an Approved Mix Design
| 01CV - Civils | Cxxx-NCR-000061 | NCR | Piles Construction 260 to 341 |  | Contr |  | WEP - Westbourne Park (West) |  | 2010-12-13 | 2011-01-18 13:30 | 36 | 2010-12-06 | Civil - Excavation | 500 |  |  | Repair |  | Complete |  | Completed |  | We confirm that we have constructed piles 260 to 341 approximately 75mm low. We propose to cast the Capping Beam 75mm low to compensate, providing the designed reinforcement and pile projection within it. We would increase the depth of the capping beam to maintain the finished level. An anti-crack mesh would be used in the wide section of the capping beam and the links extended for the projecting nib that the fence fixes to
| 01CV - Civils | Cxxx-NCR-000066 | NCR | C230~Top of Pile Reinforcement Low |  | Contr |  | WEP - Westbourne Park (West) |  | 2010-12-22 | 2011-01-18 13:35 | 27 | 2010-12-08 | Civil - Excavation | 500 |  | Design | Repair |  | Complete |  | Completed |  | We confirm that piles 272, 322 and 336 pile reinforcment have been constructed low which would result in an embedment within the pile cap of 220, 191 & 290mm respectively, compared to a design embedment of 375mm (see schedule of levels attached).
| 01CV - Civils | Cxxx-NCR-000070 | NCR | Overbreak of the piles when cutting and trimming off to specified level |  | Contr |  | WEP - Westbourne Park (West) |  | 2010-12-17 | 2011-01-18 13:39 | 32 | 2010-12-14 | Structural Engineering - Concrete Member | 500 |  | Damaged | Repair |  | Complete |  | Completed |  | A number of piles have been over broke caused from cutting and trimming the piles to cut off level
| 01CV - Civils | Cxxx-NCR-000071 | NCR | Low Piles No. 207, 231, 251 & 258 |  | Contr |  | WEP - Westbourne Park (West) |  | 2010-12-24 | 2011-02-14 12:44 | 52 | 2010-12-21 | Geotechnical Engineering - Concrete - Bored Pile | 500 |  | Supervision/Management | Repair |  | Complete |  | Completed |  | Pile No.s 207, 231, 251 & 258 have been constructed low.
| 01CV - Civils | Cxxx-NCR-000077 | NCR | SR30 Piling Rig |  | Contr |  | WEP - Westbourne Park (West) |  | 2011-01-20 | 2011-02-14 12:46 | 25 | 2011-01-13 | Structural Engineering - Structural Engineering - General | 500 |  | Design | Repair |  | Complete |  | Completed |  | SR30 Piling rig was working at high level constructing piles. this is not in accordance with the WPP
| 01CV - Civils | Cxxx-NCR-000078 | NCR | Low Piles No. 204, 221 and 226 |  | Contr |  | WEP - Westbourne Park (West) |  | 2011-01-21 | 2011-02-14 12:48 | 24 | 2011-01-17 | Geotechnical Engineering - Concrete - Bored Pile | 500 |  | Workmanship | Reject |  | Complete |  | Completed |  | Piles low - out of tolerance. Pile No. 204 = 213, 221 = 227 & 226 = 245
| 01CV - Civils | Cxxx-NCR-000088 | NCR | Pile No. 207 |  | Contr |  | WEP - Westbourne Park (West) |  | 2011-02-09 | 2011-03-21 14:54 | 40 | 2011-02-02 | Geotechnical Engineering - Concrete - Bored Pile | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | Pile No. 207 has been cast 335mm low with 15No. BM10 & BM14 H40 bars protruding into the pilecap as opposed to a total number of 16 as per design. See attached photo.
| 01CV - Civils | Cxxx-NCR-000091 | NCR | Pile No. 250 Low Steel |  | Contr |  | WEP - Westbourne Park (West) |  | 2011-02-09 | 2011-03-15 13:38 | 34 | 2011-02-07 | Geotechnical Engineering - Concrete - Bored Pile | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | Pile No. 250 has been cast low. The projection steel is approximately 100 - 120 mm low.
| 01CV - Civils | Cxxx-NCR-000093 | NCR | Incorrect Steel to Pile No. 160 |  | Contr |  | WEP - Westbourne Park (West) |  | 2011-02-11 | 2011-03-30 09:15 | 47 | 2011-02-07 | Geotechnical Engineering - Concrete - Bored Pile | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | We confirm that the incorrect steel has been installed into pile 160. The design details 14 H40 bars connected to 14 H25 bars for the upper two cages. We installed the following:- 8 x H32, 8xH25, lapped to 8H20 coupled (top cage) 8 x H32 , 8xH20 (second cage) 16xH40 (for the lower sections)
| 01CV - Civils | Cxxx-NCR-000105 | NCR | Inadequate protection to strain gauges to Pile No. 141 |  | Contr |  | WEP - Westbourne Park (West) |  | 2011-02-25 | 2011-04-01 10:44 | 35 | 2011-02-18 | Geotechnical Engineering - Concrete - Bored Pile | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | There was inadequate protection to the strain gauges when installing Pile No. 141. This resulted in partial lengths of the strain gauge cables being embedded into the concrete at the top of the pile. The WPP has not been followed.
| 01CV - Civils | Cxxx-NCR-000106 | NCR | Damaged strain gauge to Pile No. 198 |  | Contr |  | WEP - Westbourne Park (West) |  | 2011-02-25 | 2011-03-30 09:13 | 33 | 2011-02-18 | Geotechnical Engineering - Concrete - Bored Pile | 500 |  | Damaged | Use As-Is |  | Complete |  | Completed |  | 1 No. strain gauge has been damaged when installing the pile cage.
| 01CV - Civils | Cxxx-NCR-000111 | NCR | Low Piles |  | Contr |  | WEP - Westbourne Park (West) |  | 2011-02-25 | 2011-04-01 10:45 | 35 | 2011-02-22 | Geotechnical Engineering - Concrete - Bored Pile | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | 5 No. Piles have been cast low and are out of tolerance. Pile No. mm low 125 123 132 125 137 310 138 140 139 160
| 01CV - Civils | Cxxx-NCR-000112 | NCR | Incorrect steel to pile cages |  | Contr |  | WEP - Westbourne Park (West) |  | 2011-03-01 | 2011-05-13 08:17 | 73 | 2011-02-22 | Geotechnical Engineering - Concrete - Bored Pile | 500 |  | Planning | Use As-Is |  | Complete |  | Completed |  | Pile No.s 164, 166, 168 & 176 have been cast reinforcement cages not as per the design. The design drawings show vertical reinforcement bars being a combination of H20, H25 & H32 bars. The pile cages installed have H40 bars running the full length of the pile.
| 01CV - Civils | Cxxx-NCR-000132 | NCR | Damaged Strain Gauges and Inclinometer Tube |  | Contr |  | WEP - Westbourne Park (West) |  | 2011-03-14 | 2011-03-30 09:14 | 16 | 2011-03-07 | Geotechnical Engineering - Concrete - Bored Pile | 500 |  | Damaged | Use As-Is |  | Complete |  | Completed |  | The attached report shows 3No. permanently damaged strain gauges to Pile No. 141, 4No. permanently damaged strain gauges to Pile No. 147 and 2No. permanently damaged strain gauges to Pile No. 198. The upper 6m length of inclinometer tube is also damaged.
| 01CV - Civils | Cxxx-NCR-000146 | NCR | Re-forming broken existing retaining wall |  | Contr |  | WEP - Westbourne Park (West) |  | 2011-03-30 | 2011-04-01 10:46 | 2 | 2011-03-28 | Civil - Excavation | 500 |  | Damaged | Repair |  | Complete |  | Completed |  | A small section of wall was broken when excavating for the pile cap due to a construction joint not being of adequate strength.
| 01CV - Civils | Cxxx-NCR-000147 | NCR | Eliptical drainage between piles and brick/ blockwork |  | Contr |  | WEP - Westbourne Park (West) |  | 2011-04-22 | 2011-04-01 10:54 | -21 | 2011-03-31 | Civil - Drainage | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | The Shotcrete over the top of the mesh is protruding into the cavity between the piles and the brickwork. As a result the cavity has been reduced in width and there is not a sufficient amount of room to install the designed 110mm diameter half pipe eliptical drainage.
| 01CV - Civils | Cxxx-NCR-000148 | NCR | Drainage channel clashing with blockwork |  | Contr |  | WEP - Westbourne Park (West) |  | 2011-04-22 | 2011-04-01 10:49 | -21 | 2011-03-29 | Civil - Drainage | 500 |  | Design | Use As-Is |  | Complete |  | Completed |  | If the some piles are to the edge of their designed tolerance in position (75mm), when the drainage is attached, this will clash by 43mm with the blockwork. There are a few positions so far where the piles are within tolerance, but the blockwork clashes by 20mm with 1m long sections of blockwork.
| 01CV - Civils | Cxxx-NCR-000152 | NCR | 28/15 Channel between piles no.s 245 & 246 |  | Contr |  | WEP - Westbourne Park (West) |  | 2011-05-13 | 2011-05-06 11:11 | -7 | 2011-05-03 | Structural Engineering - Structural Engineering - General | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | One of the 28/15 channel's between pile no.s 245 & 246 (closest to pile no. 245) has only been fitted to the top 2.5m of wall as opposed to the full height (4m).
| 01CV - Civils | Cxxx-NCR-000154 | NCR | Reduced cavity at pile 183 location |  | Contr |  | WEP - Westbourne Park (West) |  | 2011-05-20 | 2011-05-24 13:16 | 4 | 2011-05-10 | Structural Engineering - Structural Engineering - General | 500 |  | System Defect | Use As-Is |  | Complete |  | Completed |  | Due to the location of the pile (within tolerance) and the overspill of the concrete from the casing and loose material around the top of the pile a cavity of approx 50mm provided.
| 01CV - Civils | Cxxx-NCR-000156 | NCR | foundations to have been removed |  | Contr |  | WEP - Westbourne Park (West) |  | 2011-11-25 | 2012-05-18 10:47 | 175 | 2011-10-28 | Civil - Excavation | 500 |  |  | Rework |  | Complete |  | Completed |  | During the excavation of a trench which runs through the footprint of the old Great Western Studios, the Contractor came across obstructions that were not expected to be present. The obstructions have been identified as being the remnants of the Great Western Studios foundations.
|  | Cxxx-NCR-000003 | NCR | C Crimp Incorrectly Crimped for 120mm Expansion Joint Earth Links Westbound Platform |  | Contr | COF | BOS - Bond Street Station (West) |  | 2020-09-15 | 2020-09-01 15:47 | -14 | 2020-09-01 12:16 | Electrical - Earthing & Bonding | 0 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The expansion joint C-Crimp for link 28 on the 120mm 1c Earth cable in PES header on Westbound Platform between SEB-W-B5-13 to SEB-E-B5-15 is crimped 3 times. The 3rd crimp is crimped at an angle and at the end of the C-Crimp.
|  | Cxxx-NCR-000004 | NCR | PES EB & WB Platform Earthing Expansion Joint Connections - Incorrect 'C' Crimping |  | Contr | COF | BOS - Bond Street Station (West) |  | 2020-11-30 | 2020-09-25 15:08 | -66 | 2020-09-21 06:28 | Electrical - Earthing & Bonding | 7000 |  | Workmanship | Rework | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | 120mm 1C earth cables are installed between Eastbound Platform earth bars SEB-E-B5-14 & SEB-W-B5-12 and Westbound Platform earth bars SEB-E-B5-15 & SEB-W-B5-13. Upon inspection of the 120mm 1C 'tap-off's' to the expansion joints, a number of c-crimp defects were found as the 3rd crimp has not crimped the 120mm 'tap-off' cables. The locations found are as follows: Eastbound Platform: Links 6, 8, 15, 16, 17, 22 & 31. Westbound Platform: Links 5, 8, 9, 11, 25, 28 & 29. New links HAVE been installed as follows: Eastbound Platform: Links 6, 8, 15, 16, 17, 22 & 31. Westbound Platform: Links 25, 28 & 29. New Links TO be installed during November '20 Construction Window: Westbound Platform: 5, 8, 9 & 11. NOTE: Links 1 & 2 on the Eastbound and Links 21 & 22 on the Westbound. this will be carried out during the November construction window and is captured under Cxxx-PWK-00070.
|  | Cxxx-NCR-000005 | NCR | Master / Master PLC |  | Contr | COF | BOS - Bond Street Station (West) |  | 2020-11-30 | 2021-03-10 19:01 | 100 | 2020-09-21 08:21 | Communications and Control Systems - SCADA/Central Management System | 20000 |  | Design | Rework | 2 (6-60k) | Complete | Design Problem - Other | Completed |  | Clarifications Guide of LV Panel Operational Modes and SCADA Interface CRL1-XRL-R3-GUI-CR001-50001 requires that each LV Panel (A&B) can work independent of each other should one Panel suffer a fault or decommissioning of PLC failure. For this requirement both LV Panels must be fitted with a Master PLC. Presently the LV B Panels in the WTH and Eth have been fitted with Slave PLCs that are controlled via PLC A therefore a single point of failure (LV Panel A PLC) is present.
|  | Cxxx-NCR-000006 | NCR | SCADA Control Cables |  | Contr | COF | BOS - Bond Street Station (West) |  | 2020-11-30 | 2021-04-08 12:05 | 129 | 2020-09-21 08:33 | Communications and Control Systems - SCADA/Central Management System | 5000 |  | Incomplete Works | Rework | 3 (3-6k) | Complete | Discipline/Workmanship - Not Defined | Completed |  | The SCADA control cables (Field Cabling) between LV Panels which are listed below and their relevant battery chargers have not been installed prior to commencing Phase 2.3 SCADA testing. Supplied From: Equipment Supplied ID: BOS/LV/E/A LV Switchboard battery charger Isolator BOS/LV/E/B LV Switchboard battery charger Isolator BOS/LV/W/A LV Switchboard battery charger Isolator BOS/LV/W/B LV Switchboard battery charger Isolator
|  | Cxxx-NCR-000008 | NCR | Cable Sheath Damage to 120mm 1c Earth Cable in WTH Riser 6/787 |  | Contr | COF | BOS - Bond Street Station (West) |  | 2020-12-02 | 2020-10-16 15:29 | -47 | 2020-09-29 13:48 | Electrical - Earthing & Bonding | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The cable sheath of the 120mm 1c cable earth for the earth ring link between earth bars SEB-W-B5-03 & SEB-W-B5-13 within Riser 6/787 has been damaged at high level where cable peels of CMS.
|  | Cxxx-NCR-000009 | NCR | Radio installation deviates from __ design - 4 Western Ticket Hall |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2020-10-20 | 2021-04-21 10:03 | 183 | 2020-10-06 13:16 | Communications and Control Systems - Radio | 0 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Not Defined | Completed |  | T1 Installed radio feeder cables and equipment differ in routing and location from __ design. Drawings and email chain are attached showing deviation and details.
|  | Cxxx-NCR-000010 | NCR | Damaged GSMR cables ETH |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2020-11-06 | 2020-12-15 14:31 | 39 | 2020-10-07 08:38 | Communications and Control Systems - Radio | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | It was found on a night shift by __ that the GSMR cabling at Bond Street station Eastern Ticket Hall had sustained some damage and also equipment had been tampered with putting stress on the splitter and couplers mounted. The damage looks as though it had been caused by another contractor on site whilst installing steel work near and around the radio cable tray Eastern ticket hall -5. Photos and email chain attached.
|  | Cxxx-NCR-000011 | NCR | Damage to station asset |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2020-11-06 | 2021-03-05 16:16 | 119 | 2020-10-09 07:56 | Communications and Control Systems - Public Address Systems | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Horn speaker Z33-B30 in WTH -1 has been found damaged and will need replacing
|  | Cxxx-NCR-000012 | NCR | Damaged 110v Cable ( Brown Core ) |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2020-10-26 | 2021-02-26 16:49 | 123 | 2020-10-12 01:56 | Electrical - General | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Damaged cable insulation through to copper. Circuit E-LVB02/3 Location: ETH 0 (See mark up attached).
|  | Cxxx-NCR-000013 | NCR | Frame 1 steel connector plate modification |  | Contr | COF | BOS - Bond Street Station (West) |  | 2020-10-19 | 2020-11-10 11:55 | 22 | 2020-10-12 15:39 | Structural Engineering - Steel Member | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | At Frame 1 (WTH EB) enclosure wall we have restricted access to install the PES glazing steel frame. The site installation team required to cut a section of the connecting plate to allow the lift of the main frame to be undertaken. The structural designer has confirmed that this could be spliced and a steel splice connection plate be installed at this location, including fixing details. Note that this only applies to one out of the three connection plates on this Frame, see attached 'Frame 1 splice location' and 'Location Map'.
|  | Cxxx-NCR-000014 | NCR | Defected cable |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2021-03-26 | 2021-03-03 16:35 | -23 | 2020-10-13 07:28 | Communications and Control Systems - Radio | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Not Defined | Completed |  | __ tested feeder cable FD071 which failed the installation test
|  | Cxxx-NCR-000015 | NCR | Defected installed PMR radio cable |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2020-11-02 | 2021-03-04 16:10 | 122 | 2020-10-19 11:22 | Communications and Control Systems - Radio | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | __ carried out and installation test on the radio cable before terminating ends.
|  | Cxxx-NCR-000017 | NCR | Torquing of bolts in AP2/AP3 |  | Contr | COF | BOS - Bond Street Station (West) |  | 2020-10-22 | 2020-10-30 12:30 | 8 | 2020-10-20 09:26 | Structural Engineering - Bolted Connections | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Design Problem - Approval of Design Change Notice (FCN/FCR) in CTI excessive | Completed |  | Torque inspection was undertaken with CRL/ as per ITP requirements. The procedure is to marked all fixings that have been adequately torqued. Upon spot check of marked fixings, it was witnessed that one location took multiple turns (5-6 turns) to reach the desired torqued of 180Nm. CRL/ then inspected another already marked as completed fixing and found it also took 2 turns to reach 180Nm.
|  | Cxxx-NCR-000018 | NCR | Incorrect Connection of 300mm 1c Earth Cables (Earth Ring) to ETH MEB-E-B4-02 |  | Contr | COF | BOS - Bond Street Station (West) |  | 2020-11-09 | 2021-05-28 07:57 | 200 | 2020-10-26 14:45 | Electrical - Earthing & Bonding | 5000 |  | Incorrect Installation | Rework | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Following an inspection on earth bar MEB-E-B4-02, it was raised that the termination sequence was not installed as per specification (Cxxx-SKC-M-RSP-Cxxx-50037) preventing the ability to disconnect the 300mm² ring for testing purposes.
|  | Cxxx-NCR-000019 | NCR | Square Plate Washer Not Installed on Services Support Brackets |  | Contr | COF | BOS - Bond Street Station (West) |  | 2020-11-05 | 2020-12-17 17:31 | 42 | 2020-10-22 14:53 | Electrical - Cable Management | 0 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Insufficient information made available to the worker. | Completed |  | The contractor has identified on various areas throughout the site that the subcontractor has failed to install square plate washers to the underside of __ supports. The __ tests for fire conditions and loading tests include the use of a square plate washer to the underside of the __ and following a discussion with the __ representative Richard Goode these are required to fall in line with the test data provided by __, used in the __ Bracket Calculations. It is noted that the majority of the installation has been installed with the open channel facing upwards with a square plate installed only on the top of the channel; this is typically the case for all electrical and other cabled services and for ventilation ductwork. For piped services typically the support channel has been installed with the open channel facing down with a square plate installed across the open channel on the underside of the channel. Refer to IMG_3149.
|  | Cxxx-NCR-000020 | NCR | Earth bonding from the local Earth bar not directly connected to the dedicated earthing terminal of the ATS's and MCC Panels |  | Contr | COF | BOS - Bond Street Station (West) |  | 2020-11-06 | 2021-04-17 15:43 | 162 | 2020-10-23 14:11 | Electrical - Earthing & Bonding | 5000 |  | Incorrect Installation | Rework | 3 (3-6k) | Complete | Design Problem - Change to drawings not provided on time | Completed |  | The Earth bonding from the local Earth bar is not directly connected to the dedicated earthing terminal of the ATS's and MCC Panels, some have been cross bonded to the copper banjo CPC connection of the SWA cables as they entre the panels. ATS & MCCs affected: Chiller Plant No. 1 ATS E029/E087 & MCC-E-01 Chiller Plant No. 2 ATS E015/E083 & MCC-E-02 Fan 1 ATS E018/E058 & MCC-E-04 PFR 1 ATS E014/E063 & MCC-E-05 PSE E035/E082 ATS & MCC-E-06 PFR 3 ATS E024/E067 & MCC-E-09 Chiller Plant Nos. 1 & 2 ATS W016/W080 & MCC-W-01 Chiller Plant Nos. 3 & 4 ATS W023/W085 & MCC-W-02 HVAC ATS W020/W058 & MCC-W-04 Stair Pressurisation Fans ATS W015/W019 & MCC-W-05 Plant Smoke Extract ATS W032/W057 & MCC-W-06 Ancillary AHU MCC-E-03 ETH Critical Surface Water sump Pump MCC ETH SPR MCC AAF MCC-W-03 WTH F__ No. 1 MCC
|  | Cxxx-NCR-000021 | NCR | Incorrect Installation of 300m² Earth Cable to Earth Links on MEB-E-B4-01 |  | Contr | COF | BOS - Bond Street Station (West) |  | 2021-02-19 | 2021-05-27 15:16 | 97 | 2020-10-26 14:33 | Electrical - General | 2000 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Following an inspection on earth bar MEB-E-B4-01, it was raised that the termination sequence was not installed as per specification (Cxxx-SKC-M-RSP-Cxxx-50037) preventing the ability to disconnect the 300mm² ring for testing purposes.
|  | Cxxx-NCR-000022 | NCR | Incorrect Connection of 300mm 1c Earth Cables (Earth Ring) to WTH MEB-W-B5-01 |  | Contr | COF | BOS - Bond Street Station (West) |  | 2020-11-09 | 2021-03-19 12:38 | 130 | 2020-10-26 14:36 | Electrical - General | 5000 |  | Incorrect Installation | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Following an inspection on earth bar MEB-W-B5-01, it was raised that the termination sequence was not installed as per specification (Cxxx-SKC-M-RSP-Cxxx-50037) preventing the ability to disconnect the 300mm² ring for testing purposes.
|  | Cxxx-NCR-000023 | NCR | Cxxx Record Pack Closeout - WTH L-3 NLB Wall - PMI 1270 |  | Contr | COF | BOS - Bond Street Station (West) |  | 2020-12-18 | 2021-05-07 11:16 | 140 | 2020-10-27 18:05 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Repair | 4 (0.5-3k) | Complete | Management Problem - Other management problem | Completed |  | Following the review of Record pack 50005 for the WTH L-3 NLB Walls - PMI 1270 it has been found that inadequate records have been kept and presented for the closeout and sign off for the record pack. Through discussions with __ this NCR is now covering the closeout of this pack to allow for a code 1 signature. Attached is a schedule of comments which identifies the walls at L-3 and the various stages they were poured. This schedule also shows the extent of missing records with comments provided by Matt Peddie. Pre-Inspection Records - 4no pre pours are missing, it is proposed these are now left as is as a pre pour is not actionable after the pour. In-Process Sheet - There are 10no in process sheets missing. 6 of these pours do have a 28 day cube result so this ensures that the quality of the concrete was sufficient, for the 4 pours where no cube result has been found a Schmidt hammer test is proposed. Post Pour Inspection - 6no post pours are missing but due to the concrete walls now being inaccessible due to either MEP installations or GFRC Panel Installation only 2 are accessible, these 2 will be carried out. 28 Day Cube Result - 8no Cube results are missing and cannot be located. Its is proposed to carry out Schmidt hammer testing on the locations that are still accessible, this is only 3no locations. Comments provided by __ on the initial record pack submission detail a that on all cube results that have been supplied the Spec Strength is listed as "Unknown" The spec strength of this concrete is C32/40 as designated within Code 1 MCR Cxxx-SKC-C-LRC-Cxxx-50016. The cube result certs cannot be amended at this stage so the closeout is to leave as is. Cxxx-FCD-000050 has been raised to the Architectural team to confirm the reduction of the concrete finish.
|  | Cxxx-NCR-000024 | NCR | WTH - L0 RC Upstands |  | Contr | COF | BOS - Bond Street Station (West) |  | 2021-01-29 | 2021-07-06 09:38 | 158 | 2020-10-29 08:42 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Repair | 4 (0.5-3k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | WTH L0 RC upstands were completed by / Cxxx. Pre + post pour inspections for several sections were incomplete at the time of construction. As construction has continued, many of the L0 RC upstands are now built into permanent works. Some of these are therefore unable to be inspected, and hence have the pre + post pour inspections completed in full. The sections of RC upstand which are effected are listed below, with the incomplete check sheet item noted in brackets: • GL 4/ C-G (post pour) • GL 1/ C-L (post pour) • GL 4/ E-F Upper (pre pour) • GL 4/ E-G Upper (post pour) • GL A / 2-3 (pre + post pour)
|  | Cxxx-NCR-000025 | NCR | Submain Cable W024 - Minor Damage to Outer Insulation |  | Contr | COF | BOS - Bond Street Station (West) |  | 2020-11-12 | 2020-11-03 14:55 | -9 | 2020-10-29 11:27 | Electrical - General | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Minor damage to the fire resistant outer insulation on Submain Cable W024 has been reported within LV Switch Room III (6/671), WTH Level -5. Further investigation has shown that the damage has most likely been caused whilst wiring additional earthing cables on the shared CMS route. The site team have confirmed that the damage occurs on the outer insulation only and does not affect the inner insulation.
|  | Cxxx-NCR-000026 | NCR | PAVA Zone 17 & Zone 18 Platform corners |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2020-11-24 | 2021-01-22 16:40 | 59 | 2020-11-03 13:28 | Communications and Control Systems - Public Address Systems | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | Speaker locations for Zone 17 & 18 A1 are not in the correct location according to __ design drawings. The circuits first speakers seem to have been installed further along the platform. This is a deviation from the PAVA __ drawings. Please see attached marked up drawings with red arrow indicating the deviation of location on each platform A1 speaker.
|  | Cxxx-NCR-000027 | NCR | Submain Cable W060 - Incorrect Model of Protective Device Installed |  | Contr | COF | BOS - Bond Street Station (West) |  | 2020-11-19 | 2020-11-29 13:13 | 10 | 2020-11-05 09:13 | Electrical - General | 1000 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During an inspection on Submain Cable W060, it was highlighted that an incorrect model of protective device was installed within BOS/LV/W/B. A __ 2.2 (Io / Isd / Ir) has been installed where as the LV Protection Settings document (Cxxx-SKC-E-RGN-Cxxx-50030) requires a __ 2.2M (Ir / Isd / Class 5) to be installed.
|  | Cxxx-NCR-000028 | NCR | Cable Sheath Damage to CPC on Circuit DB-E-EL08 3L1 |  | Contr | COF | BOS - Bond Street Station (West) |  | 2020-11-13 | 2020-11-19 17:45 | 6 | 2020-11-09 10:05 | Electrical - General | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During inspection of lighting circuit DB-E-EL08 3L1 it was found that the insulation/cable sheath has been damaged. The location of the damaged cable is within NPP 6/918.
|  | Cxxx-NCR-000029 | NCR | Faulty Isolator in CER1 WTH -5 Feeding Critical Cxxx Cab BOS-05-CAB6731U6 |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2020-11-23 | 2020-11-11 14:19 | -12 | 2020-11-09 10:19 | Electrical - Switchgear | 500 |  | Equipment Breakdown | Rework | 4 (0.5-3k) | Complete | Design Problem - Error in equipment or material selection | Completed |  | **For the attention of the Electrical Team** Temporary Isolator no.6 in CER 1 WTH is faulty and isn’t functioning correctly. It is fed from the temporary DB outside of the CER from circuit 2L3. It requires changing urgently as Cxxx have an isolation booked for the 12th November for testing of Cab BOS-05-CAB6731U6 in line with their programme. Attached is a photo of the isolator. A separate instruction will be issued to the electrical team for this work.
|  | Cxxx-NCR-000030 | NCR | Damaged Neutral Cable on Circuit DB-W-EL06/2L3 (Now wired on Circuit DB-W-EL06/2L2) |  | Contr | COF | BOS - Bond Street Station (West) |  | 2020-12-01 | 2020-11-21 11:32 | -10 | 2020-11-12 13:05 | Electrical - Lighting | 1000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During inspection of lighting circuit DB-W-EL06/2L3 it was found that the insulation/cable sheath to the neutral has been damaged. NOTE: This circuit has been de-scoped and the light fittings have been included within DB-W-EL06/2L2. See Cxxx-FCD-001484. The location of the damaged cable is with NPP WTH L-5 MNS 17 (6/594).
|  | Cxxx-NCR-000031 | NCR | Damaged CPC of Circuit DB-W-LVA05/1 Supplying 110V Socket Outlet |  | Contr | COF | BOS - Bond Street Station (West) |  | 2021-01-04 | 2021-11-04 12:21 | 304 | 2020-12-21 14:44 | Electrical - General | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During inspection of 110V circuit DB-W-LVA05/1 it was found that the insulation/cable sheath to the CPC has been damaged. The location of the damaged cable is with NPP WTH L-5 PLA-T (6/910).
|  | Cxxx-NCR-000033 | NCR | WTH façade stones |  | Contr | COF | BOS - Bond Street Station (West) |  | 2022-09-04 | 2022-10-20 12:21 | 46 | 2020-11-16 | Architectural - General | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Design Problem - Not Defined | Completed |  | There are a number of instances of the WTH façade stones that were replaced by __ have started spalling at the location of the fixings. The stones identified have been marked up on the attachments North and East Facade Markup - Nov 20.pdf and South and West Facade Markup - Nov 20.pdf. An example of the spalling can be found in the attachment Spalling Example Photo.jpg.
|  | Cxxx-NCR-000034 | NCR | Distribution Board DB-E-A04 Installed with Insufficient Number of Ways as Per Approved Design |  | Contr | COF | BOS - Bond Street Station (West) |  | 2020-12-02 | 2021-02-04 17:46 | 64 | 2020-11-18 15:18 | Electrical - LV Equipment | 0 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Error in equipment or material selection | Completed |  | As per 'ETH and WTH Distribution Board Schedules (L-4 and above) - Cxxx-SKC-E-XCL-Cxxx-50003', distribution board DB-E-A04 states that an 18 way TP&N is to be installed. Following an IRF inspection held on 18/11/20, it was noted that a 16 way TP&N distribution board has been installed.
|  | Cxxx-NCR-000035 | NCR | WTH OSD - RC Post Pours Incomplete & Inaccessible |  | Contr | COF | BOS - Bond Street Station (West) |  | 2020-12-03 | 2020-12-23 17:44 | 20 | 2020-11-19 09:04 | Civil - Civil Engineering General | 500 |  | Incomplete Works | Repair | 4 (0.5-3k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | This NCR concerns two PWK items open for missing post pour inspections within the WTH OSD demise (Cxxx-PWK-00485 and part of Cxxx-PWK-00714). A visual survey has been undertaken by L Mayle (CRL) and J Hyde (Cxxx) from L-1 level and through the hatch openings on the stair core. No major structural damage was observed, however there were some incomplete works such as dividag holes and drill holes not infilled. As per the attached photograph (OSD Riser) there is very limited space available. The installation of a scaffold, is not possible without exposing workers to significant work at heights - due to the confined space and constraints of the pipework. Given the incomplete works are not structural (and not easily observed) we do not deem the risks involved as tolerable. Instead, attempts will be made to infill all holes as best as possible using a paddle from L-1 or through the hatches, however we cannot guarantee the quality of this remedial work nor can we guarantee that all holes will be infilled using this method. Please note that the eastern face of W-W-21 (Cxxx-PWK-00714) can be accessed via scaffold / alloy tower and is therefore not part of this NCR - see attached Cxxx-SKC-S-DWG-Cxxx-50493 mark up.
|  | Cxxx-NCR-000036 | NCR | Swarf within ETH & WTH 'Master / Master' multi-compartment trunking with cables installed |  | Contr | COF | BOS - Bond Street Station (West) |  | 2020-12-01 | 2021-01-29 16:41 | 59 | 2020-11-24 11:46 | Electrical - Cable Management | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Verification Problems - Inspection points not adequate | Completed |  | Upon inspection of the multi-compartment trunking installed (as listed below) it was found that cables have been installed before the trunking was cleared of any swarf and debris. This contradicts JY60.3206 - Cleaning before wiring. ETH LVA Switchpanel Marshalling __le (5/668) & ETH LVB Switchpanel Marshalling __le (5/669) WTH LVA Switchpanel Marshalling __le (6/664) & WTH LVB Switchpanel Marshalling __le (6/673)
|  | Cxxx-NCR-000037 | NCR | Debris within Primary CMS containing circuits supplied from DB-E-A04 & DB-E-B04 |  | Contr | COF | BOS - Bond Street Station (West) |  | 2020-12-01 | 2021-02-06 15:47 | 67 | 2020-11-24 12:13 | Electrical - General | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Verification Problems - Inspection points not adequate | Completed |  | Upon inspection of the Primary CMS routes containing circuits for DB-E-A04 & DB-E-B04 debris was found within the CMS alongside installed cables. This contradicts JY60.3206 - Cleaning before wiring. The location being ETH Level -2 PFR 3/904
|  | Cxxx-NCR-000038 | NCR | Damaged 110V Phase Cable of DB-W-LVB-06/8 within WTH L-5 6/676 |  | Contr | COF | BOS - Bond Street Station (West) |  | 2020-12-01 | 2021-11-02 15:09 | 336 | 2020-11-24 13:14 | Electrical - General | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Upon inspection of DB-W-LCB-06/8 within Switchroom WTH L-5 6/676 it was found that the insulation has been damaged and stripped down to the bare copper.
|  | Cxxx-NCR-000039 | NCR | Failed SR3 certification for __ (__) double doors (6no.) |  | Contr | COF | BOS - Bond Street Station (West) |  | 2020-12-09 | 2021-08-06 14:15 | 240 | 2020-11-25 11:42 | Architectural - Doors | 10000 |  | Design | Repair | 2 (6-60k) | Complete | Design Problem - Conflicting information on drawings | Completed |  | The 6no. __ Doors listed below do not achieve SR3 certification. Installed doors: E-01-75-D01 E-01-75-D02 Not installed: W-01-631-D01 W-01-632-D01 E-01-902-D01 (may achieve SR3 certification due to effectively having two doors in one structural opening) E-01-902-D02 (see note above)
|  | Cxxx-NCR-000040 | NCR | Damaged Temporary Radio antenna |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2020-12-16 | 2021-01-21 15:11 | 36 | 2020-12-02 08:57 | Communications and Control Systems - Radio | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | External Phenomenon - Theft, tampering, sabotage, or vandalism | Completed |  | damage to the temporary radio antenna was reported by the C & C team on their routine checks
|  | Cxxx-NCR-000041 | NCR | __ (__) single doors missing SR3 certificates |  | Contr | COF | BOS - Bond Street Station (West) |  | 2021-04-20 | 2021-08-03 08:19 | 105 | 2020-12-02 09:55 | Architectural - Doors | 500 |  | Documentation and Records | Repair | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | __ (__) have not provided SR3 certificates for their single doors. Although __ claims the doors do meet SR3, is yet to receive a formal certificates from __. The doors in question are: E-01-74-D03 E-01-756-D02 E-01-76-D01
|  | Cxxx-NCR-000042 | NCR | WTH ESS-5 Primary CMS (Trunking) Drilled to Accomdate Lid Installation |  | Contr | COF | BOS - Bond Street Station (West) |  | 2020-12-16 | 2021-02-26 14:16 | 72 | 2020-12-02 15:45 | Electrical - Cable Management | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Within ESS-5 the contractor has drilled the trunking and installed a 'fish plate' captive nut and bolt system to accommodate the installation of variable lengths of lid, due to not matching up trunking to the correct length of lid.
|  | Cxxx-NCR-000043 | NCR | ETH TVS Cavity Drainage Core Holes |  | Contr | COF | BOS - Bond Street Station (West) |  | 2021-01-08 | 2021-04-23 15:39 | 105 | 2020-12-02 16:55 | Civil - Civil Engineering General | 5000 |  | Supervision/Management | Repair | 3 (3-6k) | Complete | Design Problem - Inadequate or defective design | Completed |  | 1) Following on from Cxxx-NCR-1129, it has been found that Core Holes Ref 1, 2 and 5 were carried out without a pre core inspection which means the ITP process has not been followed. These core holes have since been inspected by __, M Peddie and C Oosthuizen It has been found that no structural reinforcement bars have been cut during the cores. Infill steel from the previous cast in has been cut which will be painted with __. Clashes with the previously cast in upstand have been found with 4no core holes within the ETH TVS Cavity Drainage System. Items 2 and 3 below. 2) MH291 and MH290 were both required to be broken out to ensure that the cast in sleeve could be placed accurately. As you can see from the attached photos these upstands have been adequately broken back to allow for the installation of the sleeves and will be recast in their original positions. 3) Core Holes Ref 1 and Ref 2 as seen on the photos are cast within the footprint of the original upstand position. Proposal here is to modify the shape of the upstand so as not to impede the drainage gulley. The upstand will be recessed back with the reinforcing steel following suit so as to accommodate the design location of the gulley meaning the width of the upstand will be reduced. The attached upstands steel plan details the change in layout. All recast drainage upstands will utilise the attached Upstand Reinforcement Details which has been taken from the Cxxx-NCR-001129 detail. 4) Addition to this NCR to ensure its capture is the cast in of the drainage channel stop end down pipes which can be seen attached and are to be positioned where the channel changes levels. Following a teams call between Matt Peddie and __ on 08/12/20 it has been agreed to cast the pipes in using grout (Five Star Grout linked below) as opposed to C32/40 concrete to ensure the grout will spread through the cast in. U Bars will also be installed around the pipe.
|  | Cxxx-NCR-000044 | NCR | ETH EB Gates to TLPP Cabinets |  | Contr | COF | BOS - Bond Street Station (West) |  | 2021-01-25 | 2021-01-14 09:51 | -11 | 2021-01-11 17:45 | Architectural - Handrail | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Change to drawings not provided on time | Completed |  | During the installation of the of the ETH Eastbound gates in front of the TLPP cabinets, it was noted that the height of the gates were 50mm higher than the existing handrails.
|  | Cxxx-NCR-000045 | NCR | WTH Eastbound Non-Conductive Handrail |  | Contr | COF | BOS - Bond Street Station (West) |  | 2021-01-25 | 2021-01-14 16:02 | -11 | 2021-01-11 18:42 | Architectural - Handrail | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Change to drawings not provided on time | Completed |  | Following the removal of the temporary hoarding at the WTH Eastbound non-public platform end, it was identified that there was a deviation between the area where the non-conductive handrails were to be installed and the length of the non-conductive handrails. The handrails were manufactured longer than the available area.
|  | Cxxx-NCR-000048 | NCR | Commissioning of LV Switchboards |  | Contr | COF | BOS - Bond Street Station (West) |  | 2021-01-04 | 2021-03-19 12:25 | 74 | 2020-12-21 09:47 | Electrical - LV Equipment | 500 |  | Testing and Commissioning | Rework | 4 (0.5-3k) | Complete | Personnel Error - Not Defined | Completed |  | During the testing & Commissioning of the LV switchboards the wrong setting were selected on the Phase Failure relays (Undervoltage), this resulted in loss of power to the LV Switchboards and affected the Dynamic testing
|  | Cxxx-NCR-000049 | NCR | DB-E-A08 5L3 Circuit Damaged When Lidding of Trunking Installed |  | Contr | COF | BOS - Bond Street Station (West) |  | 2020-12-19 | 2021-02-03 11:19 | 46 | 2020-12-15 09:01 | Electrical - General | 3000 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | When dead testing of circuit DB-E-A08 5L3 for the IRF inspection a dead short between L-E was found. Upon investigation the fault was found within a section of trunking within ETH E/B NPP where the cables crossed from the normal section of the trunking into the emergency section. Therefore, when the lid was installed the cables where trapped and pinched. Please see attached report of cables trapped.
|  | Cxxx-NCR-000050 | NCR | WTH TVS Balustrade Paint Damage |  | Contr | COF | BOS - Bond Street Station (West) |  | 2021-08-07 | 2021-08-02 11:46 | -5 | 2021-04-30 08:13 | Architectural - Balustrade | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Following a review of the balustrades that were installed under the Cxxx contract it has been found that there are multiple areas of cosmetic damage to the powder coated finish as a result of multiple trades using the staircase for the completion of various works packages. Attached is the selection of photos of the various damage.
|  | Cxxx-NCR-000051 | NCR | Leaking water/waste pipe has caused corrosion to CMS in WTH L-2 Lobby 3/086 |  | Contr | COF | BOS - Bond Street Station (West) |  | 2020-01-31 | 2021-01-31 16:05 | 366 | 2020-12-18 13:17 | Electrical - Cable Management | 3000 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | Approx. 3m of 150 x 50mm 3-compartment trunking has corrosive damage caused by a leaking water/waste pipe within WTH L-2 Lobby 3/086.
|  | Cxxx-NCR-000052 | NCR | E-06-91-D02 Fire Mastic Completion |  | Contr | COF | BOS - Bond Street Station (West) |  | 2021-01-27 | 2021-11-17 15:32 | 294 | 2020-12-18 16:56 | Architectural - Doors | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Door installed in this structural opening have resulted in areas where gaps between door frame and RC are less than 3mm. JJS fire detail specifies doors should be installed with a gap not smaller than 3mm and not greater than 20mm. Doorset at this location to be removed and the structural opening reduced/shaven to increase width at problem areas. Structural opening to be surveyed by JJS to confirm sufficient clearance has been achieved prior to reinstating the doorset.
|  | Cxxx-NCR-000053 | NCR | Transformer Braids are Excessive in Length |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2021-03-16 | 2021-03-08 10:17 | -8 | 2020-12-18 17:22 | Electrical - Transformers | 10000 |  | Design | Rework | 2 (6-60k) | Complete | Design Problem - Other | Completed |  | Further to Cxxx-NCR-000721, the braids installed at the transformer bushings are found to be in excessive lengths (see photo). This applies to all four transformers and will require replacing.
|  | Cxxx-NCR-000056 | NCR | SC1 phones removed from WTH BOS-00-TEL-10004 & BOS-00-TEL-10005 |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2021-01-28 | 2021-03-05 16:09 | 36 | 2021-01-06 12:57 | Communications and Control Systems - Telephony | 500 |  | Incomplete Works | Rework | 4 (0.5-3k) | Complete | Design Problem - Not Defined | Completed |  | SC1 phones BOS-00-TEL-10004 & BOS-00-TEL-10005 have been through the IRN process and have been accepted by __/Cxxx CRL to T&C. However the phones have since been removed from installed locations and have yet to be re instated. Drawing attached for clarity.
|  | Cxxx-NCR-000057 | NCR | LFEPA Radio system damage to cables |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2021-01-21 | 2021-04-22 06:03 | 91 | 2021-01-07 10:51 | Communications and Control Systems - Radio | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Not Defined | Completed |  | Whilst a routine inspection was carried out by ____ he discovered damage to the temporary radio cables running up staircase 8 level 0, although it appears the damage is minor and the system seems to be working Brentwood radios are required to attend site and investigate further and report their findings.
|  | Cxxx-NCR-000058 | NCR | Incorrect finish colour of 4no. __ __ Bronze Doorsets - E-01-92-D01, W-01-411-D01, W-01-633-D01, W-04-85-D01 |  | Contr | COF | BOS - Bond Street Station (West) |  | 2021-02-17 | 2021-02-12 06:45 | -5 | 2021-02-03 09:14 | Architectural - Doors | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Not Defined | Completed |  | 4no. __ __ Bronze Doorsets listed below have been finished with the incorrect colour. E-01-92-D01 W-01-411-D01 W-01-633-D01 W-04-85-D01 The C01 drawings showed the finish colour as "PPC Anodic Bronze Y2214F" whereas the correct colour should have been “Bronze PPC - D1036 SW268JR”.
|  | Cxxx-NCR-000059 | NCR | P&T - Excessive Gap & Mis-Alignment between PES End Access Door Frame and Wall Structure (Frame 1 WTH EB) |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2021-05-28 | 2021-10-28 14:42 | 153 | 2021-02-10 12:28 | Architectural - Walls | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Design Problem - Not Defined | Completed |  | Raised by J Doyle The sequence of works for the construction of each of the PES End Wall including Track Access Door on LEVEL -5 was as follows: installation of primary steelwork followed by the install of the secondary steelwork including access door support structure and wall sheeting with the access frame and door the final element to be installed. Following the installation of the access door and frame during the Nov 2020 blockade, an excessive gap of varying width was noted between the door frame and the adjacent support angle previously installed. A survey undertaken following the installation of the door frame, revealed that this support angle was not installed vertically resulting in an inconsistent gap between the door frame and the support angle of between approx 10mm at the top and 3mm at the bottom. This excessive gap needed to be temporarily filled prior to the handback of the Non Public Platforms to seal the wall during train movements. There is NO gap detailed on any of the related drawings between the support angle and the door frame.
|  | Cxxx-NCR-000060 | NCR | Slight damage to TEL 30301 WTH -4 |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2021-04-05 | 2021-03-30 15:29 | -6 | 2021-03-22 11:50 | Communications and Control Systems - Telephony | 0 |  | Damaged | Use As-Is | 4 (0.5-3k) | Complete | Subcontractor Problems - Insufficient surveillance of subcontractors | Completed |  | It was found by Cxxx that a cover had fallen of a telephone the had bee IRN'd causing dust and a few scratches appear on the phone
|  | Cxxx-NCR-000061 | NCR | Earth bonding from the local Earth bar not directly connected to the dedicated earthing terminal of the ATS's and MCC Panels |  | Contr | COF | BOS - Bond Street Station (West) |  | 2021-04-25 | 2021-06-22 10:22 | 58 | 2021-03-26 15:34 | Electrical - Earthing & Bonding | 2000 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | The Earth bonding from the local Earth bar is not directly connected to the dedicated earthing terminal of the ATS's and MCC Panels, some have been cross bonded to the copper banjo CPC connection of the SWA cables as they entre the panels. ATS & MCCs affected: Chiller Plant No. 1 ATS E029/E087 & MCC-E-01 Chiller Plant No. 2 ATS E015/E083 & MCC-E-02 PFR 1 ATS E014/E063 & MCC-E-05 Chiller Plant Nos. 1 & 2 ATS W016/W080 & MCC-W-01 Chiller Plant Nos. 3 & 4 ATS W023/W085 & MCC-W-02 ETH Critical Surface Water sump Pump MCC ETH SPR MCC AAF MCC-W-03 WTH F__ No. 1 MCC
|  | Cxxx-NCR-000062 | NCR | DISIMILAR METALS STAINLESS STEEL SUMP PUMP PANELS, EQUIPMENT AND ACCESSORIES INSTALLED ON GALVANISED (HDG) CHANNEL BRACKETS |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2022-01-25 | 2022-01-13 17:56 | -12 | 2021-08-11 15:18 | Mechanical - Pumps | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | DISIMILAR METALS STAINLESS STEEL SUMP PUMP PANELS, EQUIPMENT AND ACCESSORIES INSTALLED ON GALVANISED (HDG) CHANNEL BRACKETS WITHIN ALL THE SUMP PUMP ROOMS. THERE COULD BE A CHEMICAL REACTION BETWEEN THE STAINLESS STEEL EQUIPMENTS, ACCESSORIES AND THE HDG CHANNEL BRACKETS IN THE DAMP AREAS WHERE THE SUMP PUMP EQUIPMENTS ARE INSTALLED. BS 7671:2018 REGULATION 522.5.2, 522.5.3 EXPLAINS THESE FURTHER. LOCATIONS: INVERTS ETH/EB/WB AND WTH/WB/EB.
|  | Cxxx-NCR-000063 | NCR | WTH L-4 UPE Plenum II 5/792 Screed Ramp Alternative Construction |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2021-04-20 | 2021-07-01 07:50 | 72 | 2021-04-06 09:53 | Architectural - Flooring | 500 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Conflicting information on drawings | Completed |  | The ramp in the WTH on L-4 in room 5/792 between grid line 4B and 4C has been installed and extends the full width of the corridor as per sketch SKC-S-PC-502 (attached), provided by __ Structural Team. In the floor finishes drawing Cxxx-SKCA-DDE-Cxxx-27640 & Cxxx-SKC-A-DDD-Cxxx-40202 the ramp does not extend full width of the corridor. This is due to limitations in loading the L-4 slab below. As detailed in Cxxx-RFI-005876, an extension of this ramp to full width was proposed, as it would negate the requirement for a handrail; and would also mean the ramp is more suitable for transporting of materials in and out of the 5/792 corridor. To satisfy limitations in loading the L-4 slab below, void former (Filcor) was used to form the bulk of the structure with a layer of screed on top as a surface finish. Subsequent information included in response to Cxxx-RFI-005876 from Jamie Boyd, states that "The Filcor MCR listed has been accepted on the basis that the concrete encapsulation is a minimum of 300mm - the proposal in this instance states a minimum 50mm of screed." In terms of fire compliance the void former (Filcor) within the ramp is surrounded on both sides and below by reinforced concrete walls and slab. The top face of the Filcor, within the ramp, has a minimum 50mm depth screed covering. It's also worth considering that the ramp is located in a draught relief area containing minimal services/plant, which would suggest it be deemed a relatively low fire risk area. Due to the fact that this ramp has already been installed, the relatively low fire risk in this location, and that any significant re-work would have significant cost implications (and necessitate the installation of a handrail(s)), we propose to "Use As-Is". Previously in response to Cxxx-NCR-000047 Jamie Boyd requested MCR details for SCR-118 screed installed. I've detailed the constituents of the screed mix with reference to applicable MCRs which are also attached. The screed mix is 1:1:3:0.25 of 6mm Agg, Portland Cement, Sharp Sand and Isopol SBR. Also in response to another query from Jamie Boyd, I can confirm there is no screed cover to Filcor 45 on the vertical faces/sides of the ramp. Installation of intumescent sealant, non-combustible mastic or silicone based mastic in these locations would be the preferable solution here. Can CRL please confirm proposal to install __ Firepro Fire Rated Silicone Sealant is acceptable here. ******UPDATE 14-06-2021******* Through discussions with John Uddoh (email trail included as an attachment) it has been agreed that the screed ramp can be left in place provided the SBR Content is below 5 percent and the screed covering the Filcor is not exposed. The 5mm thick Yelefon foam that is used as the movement joint between the screed and RC wall will be trimmed back to below the level of screed and Rockwoll LUL Intumescent Sealant will be applied. Now the ramp is full width there is no longer a need to have a handrail fixed as in Cxxx-SKC-A-DDD-Cxxx-40202 to the top of the screed penetrating the cover to the Filcor. SBR Calculations taken from attached Flowcrete Isopol SBR SBR Content Calculation 1 Isopol SBR @ 2.25kg/m2 (25 mm thick screed) Heavy screed density is 2300kg/m3 For 25mm thick = 25mm/1000mm x 2300kg/m3 = 57.5kg/m2 SBR Content percentage = 2.25kg/m2 / 57.5kg/m2 x 100 = 3.9% < 5.0% therefore acceptable. SBR Content Calculation 2 Typical mix design; Portland Cement 50kg, Sand 150kg, Granite 50kg, Isopol SBR 10kg, Water (approx.) 11kg. Total weight is 271kg SBR Content percentage = 11kg / 271kg x 100 = 3.7% < 5.0% therefore acceptable.
|  | Cxxx-NCR-000064 | NCR | WTH Cycle Friendly Gully Lids |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2022-02-11 | 2022-06-15 07:04 | 124 | 2022-01-28 08:36 | Civil - Drainage | 500 |  | Supervision/Management | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The gully lids installed by the urban realm contractor do not meet the required specification as they are not the “cycle friendly” type. Please see markup 1 and 2 for the affected locations. As stated in Cxxx-SKC-D-DDJ-Cxxx-10400_P04_IFC the gullys should be reversible hinged cycle friendly gully gratings class D400 to BS EN 124-1 by Durey Castings or similar (http://www.dureycastings.co.uk/uploads/DOCS/durey-castings-catalogue.pdf).
|  | Cxxx-NCR-000065 | NCR | Non Approved Pipework for Water Management Installed at High LEVEL in WTH AP2 |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2021-08-31 | 2021-09-17 16:17 | 17 | 2021-04-08 12:54 | Mechanical - Public Health Engineering | 2000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | NCR raised by __. A solution was proposed to solve the issue of water coming off the western edge of the drip tray located in the AP2 gutter. The detail outlined in a FCD involved the installation of copper pipework which would be soldered together and tested upon completion. The sub contractor that was instructed to undertake these additional works did not follow the agreed solution outlined in the FCD and installed the incorrect type of pipework. However the sub-contractor did not install what was agreed in the FCD and installed PUSH FIT pipework which has been rejected by the client.
|  | Cxxx-NCR-000066 | NCR | DB-E-A02, DB-E-B02, & DB-E-EL02 Colonnade Lighting |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2021-05-19 | 2022-01-25 14:20 | 251 | 2021-04-19 12:01 | Electrical - Lighting | 5000 |  | Incorrect Installation | Rework | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | DB-E-EL02 Lighting circuits which serve the Eastern Ticket Hall Colonnade lighting have not followed the NIPHAN bench mark Cxxx-COF-E-LRC-Cxxx-50048 for 2.5mm or greater circuits to __s. DB-E-EL02 7L3, 8L1, 9L1 & 9L2 are wired as per the __ and DB schedules in 4mm Direct to the NIPHAN and should follow the __ Bench Mark in retro fit adaptable boxes with ceramic block connectors. O&M stategy approval for the maintenance protocol for all the circuits listed below. DB's DB-E-A02 9L1, 9L2 & 9L3 - Lighting (Southern Colonnade) 1/78 15L1, 15L2 & 15L3 - Lighting (Southern Colonnade) 1/78 DB-E-B02 9L2, 9L3 & 10L1 - Lighting (Southern Colonnade) 1/78 13L2, 13L3 & 14L1 - Lighting (Southern Colonnade) 1/78 DB-E-EL02 7L3, 8L1, 8L2, 8L3, 9L1 & 9L2 - Lighting (Southern Colonnade) 1/79
|  | Cxxx-NCR-000067 | NCR | Cxxx-RFI-000024; Incorrect coring location. Cut slab biscuit reinforcement remedials to be determined |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2021-05-04 | 2021-05-07 12:29 | 3 | 2021-04-20 09:26 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | 2no. 100mm cores ('Western' & 'Eastern' Cores) were approved at locations within Cxxx-RFI-000024. Requirements on location to minimise risk of cutting diagonal bars. Sub-contractor cored at incorrect location although avoided diagonals (as per Cxxx-NCR-000067 CUT BARS.pdf). Cut bars being; Eastern: 1no. B16 E/W, Bottom Mat Western: 1no. Lapped N/S B12 T1 & 1no. E/W B12 T2 1no. Lapped N/S B12 B2 & 1no. E/W B12 B1 CRL delivery seek advice on any cut reinforcement remedials required beyond original RFI. Propose to leave as is, and treat cut bars with zinga paint and flexcrete or __ __ ST05.
|  | Cxxx-NCR-000069 | NCR | Submain Cable E031 - Minor Damage to Outer Insulation |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2021-05-05 | 2021-04-22 15:07 | -13 | 2021-04-21 14:35 | Electrical - Power Distribution | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Minor damage to the fire resistant outer insulation on Submain Cable E031 has been reported within Switch Room (4/665), ETH. The damage occurred during recent installation. The site team have confirmed that the damage occurs on the outer insulation only and does not affect the inner insulation. Please refer to 'issue 8' on the attached SAP report.
|  | Cxxx-NCR-000070 | NCR | Broken glass - Emergency Way out sign (Behind door of 5/085) |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2021-05-07 | 2021-11-19 12:01 | 196 | 2021-04-23 12:51 | Electrical - Lighting | 1000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Improper preservation of material after installation | Completed |  | On a routine surveillance walk I noticed that the emergency way out sign glass has been smashed. As this asset is at high level above doors I am unsure of the route cause. However, I would suggest this was done by carry conduit or trunking.
|  | Cxxx-NCR-000071 | NCR | P&T - Excessive Gap between Door Frame & Adj. Architectural Stainless Panel AP 2 & 3 on LEVEL -5 |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2021-06-07 | 2021-11-24 11:27 | 170 | 2021-05-10 16:45 | Architectural - Doors | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | Following the installation of the first stainless steel wall panel by the cladding sub contractor at one of the doors in the AP3 lift corridor, an excessive gap of approx. 20mm was noted between the panel edge and the adjacent door frame. The design only shows a 3mm gap between these items. This excessive gap exceeds the minimum gap allowed under LU standards so will need to be filled with an approved material.
|  | Cxxx-NCR-000072 | NCR | Urban Realm - Gilbert Street MH01 Connection into Sewer |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2021-05-18 | 2021-12-06 12:18 | 202 | 2021-05-04 16:24 | Civil - Drainage | 1000 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | It was realised during installation of MH01 that the proposed design (Cxxx-SKC-D-DDD-Cxxx-00350) for the __ connection to the existing sewer main did not fit as the TW sewer was found to be closer to the manhole than expected. To allow the manhole to be installed it was necessary for the rocker to be omitted. It was also realised upon discussion with the supplier of the saddle connections that this connection method would not be possible for the site conditions due to the thickness of the wall of the sewer. These discoveries were made on a Saturday shift with an open sewer connection. At this point OCS should have stopped works and raised the issue with the CRL Package Manager. However, they proceeded to install to industry best practice with materials that do not have a Code 1 MCR and without an approved design change. OCS informed the CRL Package Manager first thing Monday morning of their progress and issues raised. The CRL Package Manager reviewed the issues on site on Monday and raised concerns that the design was not followed, and this has been raised formally with OCS via an EWN The CRL Package Manager informed __ of the issues on Tuesday morning 27/04/21 and arranged a site visit to review the design issues on site.
|  | Cxxx-NCR-000073 | NCR | ETH - Waterproofing of Earthing Pits, Colonnade Columns and Winch Point Pits |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2021-05-18 | 2022-01-25 15:50 | 252 | 2021-05-04 16:36 | Architectural - General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Lack of records, testing and quality assurance to complete redlines, sub certs and record packs for ETH waterproofing of earthing pits, colonnade columns and winch point pits. Please refer to attached 'Winch & Earthing Pits QA - Overview' for an overview of the
|  | Cxxx-NCR-000074 | NCR | WTH – Waterproofing Capping Beam and L-0 |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2021-05-18 | 2022-02-09 13:38 | 267 | 2021-05-04 16:33 | Architectural - General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Not Defined | Completed |  | WTH – Waterproofing Capping Beam and L-0 Lack of records, testing and quality assurance to complete record packs for WTH waterproofing of capping beam and L0
|  | Cxxx-NCR-000075 | NCR | Earth bonding from the local Earth bar not directly connected to the dedicated earthing terminal of the ATS's and MCC Panels |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2021-05-24 | 2022-05-19 07:41 | 360 | 2021-05-10 07:56 | Electrical - Earthing & Bonding | 5000 |  | Incorrect Installation | Rework | 3 (3-6k) | Complete | Discipline/Workmanship - Other | Completed |  | The Earth bonding from the local Earth bar is not directly connected to the dedicated earthing terminal of the ATS's and MCC Panels, some have been cross bonded to the copper banjo CPC connection of the SWA cables as they entre the panels. ATS & MCCs affected: Chiller Plant No. 1 ATS E029/E087 & MCC-E-01 Chiller Plant No. 2 ATS E015/E083 & MCC-E-02 Chiller Plant Nos. 1 & 2 ATS W016/W080 & MCC-W-01 Chiller Plant Nos. 3 & 4 ATS W023/W085 & MCC-W-02 ETH Critical Surface Water sump Pump MCC ETH SPR MCC AAF MCC-W-03 WTH F__ No. 1 MCC
|  | Cxxx-NCR-000076 | NCR | Damaged Insulation of 110v cable, Circuit DB/W/LVA05/1 |  | Contr | COF | BOS - Bond Street Station (West) |  | 2021-06-10 | 2021-06-10 14:49 | 0 | 2021-05-27 12:32 | Electrical - LV Equipment | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Upon inspection of 110v circuits installed historically by another sub contractor, it has been noted that the insulation on a live conductor has been damaged. There is no damage to the copper itself. (please see photo attached)
|  | Cxxx-NCR-000077 | NCR | Cxxx-XRL-E-NOX-Cxxx-50093 Earthing and Bondng Pack 11- Site cut stud installed for unistut fixing, room A/932. |  | Contr | COF | BOS - Bond Street Station (West) |  | 2021-06-11 | 2021-06-16 14:30 | 5 | 2021-05-28 07:48 | Electrical - General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | A 10mm cut stud has been used to fix a __ bracket to a block work wall. In this instance a __ factory cut stud should be used.
|  | Cxxx-NCR-000078 | NCR | PES End Wall Signs for AP3 NOT Manufactured as Per Approved Drawings (__ ) |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2021-08-14 | 2021-06-22 11:39 | -53 | 2021-06-08 14:45 | Architectural - Signage | 500 |  | Manufacturing Defect | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | When the PES End Wall Signs USN 545 & 746 were delivered to site in late May 2021 it was noted that they were not in accordance with the approved drawing Cxxx-SKC-A-DWG-Cxxx-53855 Rev P03 so they could not be installed. The PES End Wall signs in AP3 are different to AP2 as they don't have the 20mm trim on the top edge which the signs in AP2 do have. This is to accommodate the metal section in the AP3 PES End Walls which is deeper than the glazing sections above the signs in AP2.
|  | Cxxx-NCR-000079 | NCR | Incorrect Graphic's Installed for Curved Glazing Signage SGN 205 Eastbound & Westbound Platforms (__) |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2021-09-30 | 2021-09-24 07:55 | -6 | 2021-06-19 14:56 | Architectural - Signage | 500 |  | Manufacturing Defect | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During an inspection of the SGN 205 Curved Glazed Signage on site it was noted that the graphics on the following sign references was incorrect - USN 701, 704 - Directional WAY OUT Signage. USN 522, 735 - EXIT Signage and not as per the approved wayfinding schedule. The graphics will need to be replaced with the correct text layout.
|  | Cxxx-NCR-000080 | NCR | Fire performance of WTH Shaft Roof Waterproofing __ 900 |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2021-08-17 | 2021-11-03 09:26 | 78 | 2021-06-22 16:32 | Architectural - Roofing & Exterior Treatment | 500 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Not Defined | Completed |  | Roofing materials within 6m of the relevant boundary are required to meet minimum fire performance criteria specified in Building Regulations Approved Document B (included in Crossrail New Works Standards Baseline). Relative to the OSD, most of the roof of the vent shaft is included in this requirement. The __ 900HA product intended for use on the vent shaft roof has a Euroclass E rating, under which the material is expected to produce flaming droplets or particles with substantial amounts of smoke being produced. There is no accepted MCR for the __ 900HA product.
|  | Cxxx-NCR-000081 | NCR | Reporting Procedure failure against Trial Operations Communication Protocol and C&C Plan |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2021-08-05 | 2022-01-26 12:52 | 174 | 2021-06-24 12:00 | Electrical - LV Equipment | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Other | Completed |  | In the event of LV System, Switchboard or UPS failure should ensure procedures in place are implemented in the event of an incident. ie all incidents are to be reported to the Enactment Duty Manager BOS on: 07816 088216 or via dedicated radio - channel 10 Enactment Duty Manager notifies Traffic Manager. Site Operative notifies Enactment Duty Manager. Contact unable to be made -Enactment Duty Manager notifies RTIM. Enactment Duty Manager Notifies Crossrail RCC Coordinator Enactment Duty Manager Notifies Crossrail Project Manager (or delegate) Communication Protocol. A request for support may be required following the incident. Following a UPS incident in the WTH Emergency switch room resulting in failure of the above the procedures werenot implemented
|  | Cxxx-NCR-000084 | NCR | Water Damage within WTH Draft Relief / Vent Shafts |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2021-08-07 | 2021-10-14 15:07 | 68 | 2021-06-26 19:35 | Electrical - General | 3000 |  | Material | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | Water ingress into WTH Draft Relief / Vent Shafts was identified some time ago by the FAE team, which resulted in damage to CMS, mainly staining to the galvanised finish of the CMS ( Cable Trunking and Conduit System) and remedial work has already taken place. There was also damage to a number of lights fixtures caused mainly by inadequately terminated cable entries. The original plug and socket connector serving the light fixtures have been replaced by water resistant __ connectors, the light fixtures cleaned and touch-up paint applied as necessary. See attached reports. The purpose of this NCR is to mitigate the remedial work and ensure the source of the water ingress has been removed and or the CMS and light fixtures are adequately protected and suitable for bringing into service. Areas involved and (attached file names) are as follows: 1. Water Damage WTH Level -2 West Bound Draft Relief Shaft 3/780 and 3/779. Served by Distribution Boards DB-W-A03, B03 and EL03 (westbounddraughtrelief3780andeastbounddraughtrelief3779.pdf, WTH Item 6.pdf and WTH Item 7.pdf) 2. Water Damage WTH Level -4 Vent Shaft 5/795 (ventshaft5795.pdf and WTH Item 8.pdf) 3. Water Damage WTH Level -5 6/797 Distribution Boards DB-W-A07, B07,EL07 and SC1 6/798 DB's DB-W-A07, B07 and EL07 (6797.pdf) 4. Water Damage KD7 and KD8 Level 0 CMS (KD7 and 8 water damage - kd8.pdf and kd8 level 0.pdf) and Level 3 CMS (kd8 level 3.pdf) 5. Water damage level +6 (Water damage level plus 6 WTH.pdf) 6. Water damage ground floor / level +4 8. As CMS tracker (Excel file) water affecting MEP Rev 2. 9. Item numbers 9, 10 & 20 in report have no available images 10. Water Damage to CMS in Eastbound Plenum 6/798 (WTH) CRL-OBS-35242
|  | Cxxx-NCR-000086 | NCR | Upstand deviating from design levels WTH GL4/A |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2021-08-02 | 2021-08-12 11:12 | 10 | 2021-07-19 10:17 | Civil - Structural Engineering | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | It has been found that an upstand poured by a previous contract has been installed to incorrect levels. The upstand TOC is higher than the design level of +120.700 and is therefor encroaching on the granite tile finishes build up. The full details of the defect can be found in Cxxx-RFI-000184.
|  | Cxxx-NCR-000088 | NCR | P&T - AP2 Bullet door incorrect service opeing size |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2021-08-24 | 2021-10-25 06:21 | 62 | 2021-08-10 15:34 | Architectural - Walls | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Upon completion of the AP2 bullet door bulkhead it was discovered that the service opening was installed at 800x300mm instead of the designed 850 x 500mm as a result fire stopping compliance cannot be met as the required 50mm clearance around installed services and trays has not been achieved.
|  | Cxxx-NCR-000089 | NCR | UPS Damage Incurred from Maintenance Activities |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2021-08-18 | 2021-08-26 10:13 | 8 | 2021-08-13 07:49 | Electrical - Power Distribution | 30000 |  | Damaged | Repair | 2 (6-60k) | Complete | Personnel Error - Not Defined | Completed |  | During Planned Maintenance of the WTH Comms UPS there was a short circuit created between the Live (L1) Terminal and Neutral (N) terminal causing a short circuit resulting in the activation via fault protection of the upstream MCCB's within the LV Switchboard. The fault current generated damaged internal components within the UPS and the Main LV Switchboard MCCB's.
|  | Cxxx-NCR-000091 | NCR | Weigh House Street Paving - Yorkstone Discrepancy |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2022-07-21 | 2022-06-28 11:21 | -23 | 2022-06-23 10:13 | Architectural - Urban Realm | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | As seen in attached photo the Yorkstone Paving Slabs along Weighhouse Street have been installed in an irregular pattern outside of the Westminster Council Specifications. BOS Specification JQ25 Cxxx-SKC-A-RSP-Cxxx-50042 Rev 12.0 Clause JQ25.1206 d)iii states only a nominal size but no specific deviation for cuts. Westminster Council requires the minimum of 600 x 400 for the slabs. Propose to Use as Is pending acceptance from Westminster Council.
|  | Cxxx-NCR-000092 | NCR | Oliver Connells - Material Compliance Records |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2021-10-14 | 2021-12-08 09:52 | 55 | 2021-08-31 12:01 | Materials - Approval | 0 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | The contract has not followed the Crossrail procedure for the management of Material Compliance. See Linked docs 'Demonstration of Materials Compliance Procedure,' 'Management and Acceptance of Field Documentation Procedure' and 'Works Information Volume 2B.' Materials required for the OC contract are covered in the attached spreadsheet, (WCC - Bond Street WTH UR Register) which lists the applicable drawings and specifications for the OC contract. Bond street's Lead Field Assurance Civil Engineer __, (LM) has tried to help by discussing these requirements with OC's site foremen and raising 5 missing MCR's retrospectively, after OC had already installed the materials on site. However, 4 out of the 5 materials that were advised to LM by OC's PM were not actually installed on site. This has wasted a lot of LM's time and puts the SC2 deliverable Sub-Construction Certificate for the Gilbert street MH - sewer connection at risk, (Cxxx-COF-D-CER-Cxxx-50002). Also, OC's are still ordering materials to site and installing them without first having Material Complaince Records in place or making Crossrail's delivery team aware of the materials. Here are the specific details of this NCR that LM is aware of: 1. LM raised Material Compliance Record for - Tensar TriAx Stabilisation Geogrid TX150. This is now Code 1 in eB and linked to this NCR. 2. LM raised Material Compliance Record for - Ladder for Urban Realm Manhole. This is now Code 1 in eB and linked to this NCR. The material specified for this ladder is galvanised mild steel, (see drawing Cxxx-SKC-D-DDD-Cxxx-00350) but this MCR does not cover a galvanised mild steel ladder. However, LM still managed to get this product agreed with __ and Westminster City Council, (WCC). Since raising this MCR LM has discovered that OC's site operatives rejected the delivery of this ladder and a ladder is still not installed in the Gilbert street manhole. This issue is also covered under linked Cxxx-NCR-000072. So do OC's now intend to order a different product? This ladder needs to be installed before SC2. 3. LM raised Material Compliance Record for - __Swell S-2 swellable sealant. This was advised as installed by OC's PM, (see email attachment EMAIL - RE OC TQ 05 regarding sewer connection). However, LM has since found out that this product was not used on site. LM had completed putting the MCR document together for this, (see attachment __Swell S-2 swellable sealant.zip) but has not issued for review as he now knows this product was not used on site. OC's PM has now advised an alternative product was used on site, (see attachment EMAIL - Data Sheet for __ flex Pro 3). 4. LM raised Material Compliance Record for - __ Below Ground Cast Iron Pipe. This was advised as installed by OC's PM, (see email attachment EMAIL - RE OC TQ 05 regarding sewer connection). However, LM has since found out that this was not used on site. On 26/08/21, OC's site foreman advised LM that a Timesaver pipe was used for the Gilbert street MH01 - sewer connection. LM had completed putting the MCR document together for this, (see attachment __ Below Ground Cast Iron Pipe.zip) but has not issued for review as he has been told that this product was not used on site. 5. LM started to raise a Material Compliance Record for - Cast Iron Soil Ductile Couplings. This was advised as installed by OC's PM, (see email attachment EMAIL - RE OC TQ 05 regarding sewer connection). However, LM has since found out that this product is not acceptable for underground use and also, OC's PM is now advising that these were not used on site, (see attachment EMAIL - RE QA for Cast Iron Soil Ductile Couplings with Continuity 150mm). 6. Further to point 5 above, a change coupler from clay - metal pipe was installed between the Gilbert street MH01 and the WTH building. Does OC's have a MCR in place for this? 7. See attachment 'ANOTHER EMAIL - RE 3xCxxx MCR Placeholders needed.' OC's PM has advised that '...the __ drainage pipe was used on all of the connections on Gilbert street due to the thickness of the Sewer there was not a saddle connection that would suit.' This covers the Gilbert street MH01 - sewer and all of the gully - sewer connections in Gilbert street. This would have required a change coupler from clay - metal pipe. Does OC's have a MCR in place for this? 8. On 21/08/21 LM asked OC's site foreman what type of coupler was installed between Blu-3's pipe left buried in the ground, (see page 6 of C446 Record Pack: WTH - Drainage on Davies Street (North)) and their clay pipe. This is for the PG20 - EG19 drainage connection as covered in Cxxx-FCD-001354. OC's site foreman described a rubber coupler. Does this does have a MCR in place? This drainage run has since passed a successful air test. 9. See photo attachments of the materials used for the drainage run between PG22-EG21 in Davies street. This confirms that black Timesaver pipes and couplers were installed for this drainage run. Do these have a MCR in place? 10. See photo attachment 'WTH UR, Davies st progress - Pic 1.' This is a photo of the pipe installed between Davies street gullies PG21-PG22. This pipe is red. Both the __ pipe that LM was incorrectly informed was installed and the Timesaver pipe advised in point 9 above are black. So what is this material? Is there a MCR in place for this? 11. The change of Gilbert street MH01 - sewer connection: As OC's have advised Crossrail incorrect information, LM has had to rework Cxxx-FCD-000112 back to initiate stage as all 3 of the materials OC's stated were used for the Gilbert Street MH01 - Sewer connection are incorrect. Until correct information is confirmed this FCD can not progress. Also, this affects the __, (TW) agreement for discharging DS6011637 as we have advised TW the same incorrect information. So as a result of getting incorrect information from OC's - the Gilbert street MH01 - sewer connection has still not been agreed. 12. OC's to clarify all of the materials that were used for the gully - sewer connections in Gilbert street and that saddle connection materials were not used.
|  | Cxxx-NCR-000094 | NCR | Oliver Connell - Concrete use in Davies street bollards |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2021-11-04 | 2021-11-30 14:18 | 26 | 2021-09-09 11:41 | Civil - Concrete Pavement | 0 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Other management problem | Completed |  | 1. An Urban Realm Surveillance was carried out by, (CRL's Quality Verification Manager) on 23/08/2021. Here is his observation: 'During the surveillance I witnessed concrete encasement of Bollards in Davis Street, I received the check sheet post surveillance (attached), the check sheet references S4 concrete mix being placed. On checking the approved MCR ‘Urban Realm Bollard Encasement Concrete’ Cxxx-SKC-C-MCR-Cxxx-50075 (rev 1). S3 concrete mix is referenced in line with the Westminster council specification. Can you please confirm that S4 is approved for use in the encasement of Bollards and provide evidence.' It has since been established that the delivery docket confirms the S3 mix, but the check sheet shows the slump at 200 which is compliant for S4 mix, S3 slump requirements: slump range 100-150 with a deviation of -20 +30 which makes the mix non-compliant. So the issues are - the on site checksheet has been complete incorrectly and the concrete delivered was out of spec and should have been rejected. 2. On putting this NCR together I have found that the applicable ITP is not Code 1.
|  | Cxxx-NCR-000095 | NCR | ETH - Blu-3 Incomplete QA for UR drainage, (replaces C446-NCR-000002) |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2023-03-18 |  | -40 | 2021-10-13 11:46 | Civil - Drainage | 500 |  | Documentation and Records | Repair | 4 (0.5-3k) | Open | Management Problem - Work organization/planning deficiency | IMPLEMENTATION |  | This NCR has been raised to replace C446-NCR-000002 which is to be cancelled in eB. ************************************************************** During compilation of the information for the record packs for the ETH Station Drainage it has been noted that there isn't conclusive evidence that CRL has witnessed and approved certain elements along with additional works required as listed below; 1. C446-BLT-D-LRC-Cxxx-50001 - ETH MH01 & MH02 water test - there wasn't conclusive evidence that the water test was viewed by CRL 2. C446-BLT-D-LRC-Cxxx-50002 - CRL Site Manager signed Gully QA check sheets rather than CRL Field Assurance 3. C446-BLT-D-LRC-Cxxx-50002 - Thames water certificate of completion not included in Gully record pack 4. C446-BLT-D-RGN-Cxxx-50001 - Confirmation of the drain stopper/plug have been removed and provide evidence 5. C446-BLT-D-RGN-Cxxx-50002 - Video doesn't show invert of outlet to main sewer 6. C446-BLT-D-RGN-Cxxx-50002 - Pipe material changes at MH02 connection point 7. C446-BLT-D-RGN-Cxxx-50002 - Incomplete installation at starting point of video 8. C446-BLT-D-RGN-Cxxx-50003 - Please remove Settled deposits and re CCTV ************************************************************** __, (CRL) 16/02/22: On putting together a spreadsheet to capture all of the outstanding Civil Drainage works at Bond street I found another omission to Blu-3's UR drainage at the ETH. There is no CCTV survey from new MH01 in to the building line. This CCTV survey should be carried out.
|  | Cxxx-NCR-000096 | NCR | WTH - Blu-3 Carriageway Construction Incomplete Works and QA, (replaces C446-NCR-000003) |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2021-11-30 | 2021-11-23 14:37 | -7 | 2021-11-16 16:52 | Civil - Concrete Pavement | 500 |  | Incomplete Works | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | This NCR has been raised to replace C446-NCR-000003 which is to be cancelled in eB. Blu-3 were removed from the project and not allowed back to action anything found during the ITP Record Pack reviews. Therefore, the only way to get the Blu-3 ITP Record Packs to Code 1 status was to capture all shortfalls in NCR's and instruct the content of those NCR's to another Tier 2 Contractor at a later date. Linked to this NCR are the ITP Record Packs and comment sheets that referenced C446-NCR-000003. The issues identified during those document reviews are recorded here: 1. C446-BLT-D-LRC-Cxxx-50014 - C446 Record Pack: WTH - Carriageway and Footway on South Molton Lane and 75 Davies Street - Page 8 and 9 missing CRL signature. - Page 70. Where’s the paving checksheet for areas 14, 15 and 16? - Very little evidence of CRL inspection signatures. 2. C446-BLT-D-LRC-Cxxx-50015 - C446 Record Pack: WTH - Street furniture on South Molton Lane and 75 Davies Street - No CRL witness signature on check sheets. Raise NCR (Arrange for CRL inspection) 3. C446-BLT-D-LRC-Cxxx-50017 - C446 Record Pack: WTH - Carriageway and Footway on Weighhouse Street from Grid line A to G - Very little evidence of CRL inspection signatures - Kerb installations are Hold Points for the Contractor. Contractor signature missing from boxes 4.8 and 4.9. - Footway inspections are Hold Points for the Contractor. Contractor ITP Hold Point signature missing from boxes 5.1, 5.2 and 5.4. - Cxxx-SKC-A-DWG-Cxxx-52779 P01 version of this drawing in eB only. P03 to be uploaded to eB and sent to the Architects For Acceptance. 4. C446-BLT-D-LRC-Cxxx-50020 - C446 Record Pack: WTH - Carriageway and Footway on Weighhouse Street from Grid line G to J - Missing 50009-D paperwork for the north section of footpath. This needs to be found and included. - CRL’s signature missing from pages 8 and 9. 5. C446-BLT-D-LRC-Cxxx-50026 - C446 Record Pack: WTH - Carriageway and Footway on Davies Street (North) - Page 12 - The kerb boxes have been left blank. - Page 7 & 8 - Missing CRL signatures. - Page 36 - Footway Construction and All Finishes for both Carriageway and Footway to be Completed by others
|  | Cxxx-NCR-000097 | NCR | WTH - Blu-3 Incomplete works and QA for UR drainage, (replaces C446-NCR-000004) |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2022-09-04 | 2022-11-16 10:07 | 73 | 2021-11-05 14:48 | Civil - Drainage | 500 |  | Documentation and Records | Repair | 4 (0.5-3k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | This NCR has been raised to replace C446-NCR-000004 which is to be cancelled in eB. Blu-3 were removed from the project and not allowed back to action anything found during the ITP Record Pack and CCTV Survey reviews. Therefore, the only way to get the Blu-3 ITP Record Packs and CCTV Surveys to Code 1 status was to capture all shortfalls in NCR's and instruct the content of those NCR's to another Tier 2 Contractor at a later date. Linked to this NCR are the ITP Record Packs and CCTV Surveys that referenced C446-NCR-000004. The issues identified during those document reviews are recorded here: 1. C446-BLT-D-LRC-Cxxx-50008 - C446 Record Pack: WTH – Weighhouse Street - Station Drainage, Sewer / Gully Connections, Flood Chamber & Sleeve Extensions: - MH02. MH testing is a hold point for Crossrail, but was not Witnessed by them. - MH02. No CCTV Survey of the west rodding eye. - MH02. No CCTV Survey or pipe test in to the building. - PG02 drainage run. Contractor inspection for the fill surround line item is a Hold point for the Contractor, but was not witnessed. - Flood Chamber MH. Non-return valve not installed. - Flood Chamber MH. MH testing is a hold point for Crossrail, but was not Witnessed by them. - Flood Chamber - Missing FCMH – East gully spur drainage paperwork. - Flood Chamber - Missing CCTV survey of east gully spur. - Flood Chamber - No CCTV Survey or pipe test in to the building. 2. C446-BLT-D-LRC-Cxxx-50013 - C446 Record Pack: WTH - Drainage on South Molton Lane and 75 Davies Street: - PG10 - Issues now dealt with in C446-NCR-000007/Cxxx-NCR-000099, C446-FCD-000004. NCR's and FCD now closed out. - PG11 - Issues now dealt with in C446-BLT-D-LRC-Cxxx-50008 and Cxxx-FCD-001233. Issues clarified in C446-BLT-D-LRC-Cxxx-50008. 3. C446-BLT-D-RGN-Cxxx-50004 - C446 WTH Urban Realm FCMH Drainage CCTV Report: - Flood Chamber - CCTV Report doesn’t show evidence that the non-return valve has been installed at the flood chamber as required by drawing Cxxx-SKC-D-DDD-Cxxx-00352. 4. C446-BLT-D-RGN-Cxxx-50012 - C466 Blu-3 - CCTV Report : WTH - PG13-PG12 drainage run CCTV survey: - PG12. Please confirm PG12 has been cleaned out. - PG12/13. Looks like catch pits have not been installed – just ply boxes. ************************************************************************************************* __ Update (04/03/22): 5. C446-BLT-D-LRC-Cxxx-50038 1.0 Placeholder Clint Herbst - C446 Record Pack: WTH - Blu-3 - St Anselm's Place- Drainage - Blu-3 did not deliver any Quality Assurance paperwork for drainage that they installed in St.Anselm's Place. That being gullies PG17, PG18 and PG19 as can be seen in drawing Cxxx-SKC-D-DDA-Cxxx-10403 P05. - See Cxxx-RFI-005824 and C446-BLT-D-RGN-Cxxx-50014
|  | Cxxx-NCR-000098 | NCR | WTH - Blu-3 Weighhouse Street Carriageway Failed and Missing Cubes, (replaces C446-NCR-000006) |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2021-11-30 | 2021-11-25 09:19 | -5 | 2021-11-16 17:35 | Civil - Concrete Pavement | 0 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Training Deficiency - Not Defined | Completed |  | This NCR has been raised to replace C446-NCR-000006 which is to be cancelled in eB. Blu-3 were removed from the project and not allowed back to action anything found during the ITP Record Pack reviews. Therefore, the only way to get the Blu-3 ITP Record Packs to Code 1 status was to capture all shortfalls in NCR's and instruct the content of those NCR's to another Tier 2 Contractor at a later date. Linked to this NCR are the ITP Record Packs and comment sheets that referenced C446-NCR-000006 The issues identified during those document reviews are recorded here: 1. C446-BLT-D-LRC-Cxxx-50014 - C446 Record Pack: WTH - Carriageway and Footway on South Molton Lane and 75 Davies Street - Cube results for slab 14 unavailable. 2. C446-BLT-D-LRC-Cxxx-50020 - C446 Record Pack: WTH - Carriageway and Footway on Weighhouse Street from Grid line G to J - Pages 27-29 - 2 out of 3 concrete cube results have failed. The one that passed, passed marginally. Therefore not convinced this concrete is up to spec. 3. C446-BLT-D-LRC-Cxxx-50026 - C446 Record Pack: WTH - Carriageway and Footway on Davies Street (North) - Pages 15-17 - 3 out of 4 concrete cube results have failed. The one that passed, passed marginally. Therefore not convinced this concrete is up to spec.
|  | Cxxx-NCR-000099 | NCR | WTH - Blu-3 Urban Realm PG09 & PG10 Gully Configuration, (replaces C446-NCR-000007) |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2021-10-25 | 2021-10-22 10:01 | -3 | 2021-10-11 14:00 | Civil - Drainage | 0 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | This NCR has been raised to replace C446-NCR-000007 which is to be cancelled in eB due to Blu-3 leaving the project.. See email attachment 'EMAIL - -GC-054739 Re WTH - PG09 oncrete culvert clashing.' This indicates that gullies PG09 and PG10 were agreed to be moved with Blu-3. However, no agreement with WCC or record of this can be found in eB. Cxxx-FCD-000952 records a change in this regard. However, gully PG10 is a further north than this FCD agrees, (see pics attached). Also, the email attachment date is after this FCD was closed, so an updated FCD needs to be raised to record these changes. This change to gully locations needs to be agreed with WCC then recorded in a FCD to be sent to __ for acceptance. When this FCD is complete and closed out this NCR can be closed.
|  | Cxxx-NCR-000100 | NCR | WTH - Blu-3 Level 0, Incorrect Earth Pit Construction at GL. C/1 and J/1, (replaces C446-NCR-000008) |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2021-10-27 | 2022-01-21 15:38 | 86 | 2021-10-13 10:22 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | This NCR has been raised to replace C446-NCR-000008 which is to be cancelled in eB. Oliver Connells confirmed to __ on site on 20/10/21 that Blu-3 constructed the earth pits at GL. C/1 and J/1. The earth pit construction at GL. C/1, (earth pit 2) has a drainage hole, but the water doesn't flow away. The earth pit construction at GL. J/1, (earth pit 5) does not have a core drainage hole required as shown in linked drawing Cxxx-SKC-L-DDD-Cxxx-50620 P02.
|  | Cxxx-NCR-000101 | NCR | WTH - Blu-3 Weighhouse street kerb tolerance, (replaces C446-NCR-000010) |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2022-03-30 | 2022-03-24 12:37 | -6 | 2022-03-16 09:18 | Architectural - Urban Realm | 0 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | This NCR has been raised to replace C446-NCR-000010 which is to be cancelled in eB. Blu-3 installed the kerb from GL 1/A-G south of Weighhouse Street. As per the ITP (Cxxx-COF-C-ITP-Cxxx-50001) the kerb level must not exceed +/- 6mm and no section of kerb shorter than 300mm. Following the as built (Cxxx-SKC-D-DDA-Cxxx-10621 P02_IFC kerb asbuilt) conducted by J. Hyde, the kerb falls outside of these tolerances. Due to the carriageway being completed proposal is to leave as is. South side of Weighhouse Street does not look to be holding water during any significant rain event which shows it gradient is sufficient.
|  | Cxxx-NCR-000102 | NCR | WTH - Blu-3 Weighhouse St - Bollard 01 Level, (replaces C446-NCR-000011) |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2022-09-04 | 2022-06-16 10:27 | -80 | 2021-12-10 09:26 | Civil - Street Furniture | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | This NCR has been raised to replace C446-NCR-000011 which is to be cancelled in eB. The b (biscuit) of Bollard 01 on Weighhouse St has been installed too low. Remedial works are required so that the bollard is at the correct level. The bollard array has already been concreted into position so remedial works need to consider this.
|  | Cxxx-NCR-000103 | NCR | WTH Urban Realm - Check Sheets Incorrectly Signed |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2021-10-04 | 2021-11-01 16:04 | 28 | 2021-09-20 13:13 | Civil - Drainage | 500 |  | Documentation and Records | Repair | 4 (0.5-3k) | Complete | Management Problem - No evidence of program review from Contractor's Quality Manager or Management | Completed |  | The Record Pack for Gilbert St Drainage (Cxxx-COF-D-LRC-Cxxx-50002) contains several check sheets that have been signed without the activities taking place or without the correct documentation/evidence. These have been noted on the comments sheet (Cxxx-COF-D-XCS-Cxxx-50006) and have resulted in the Record Pack being returned as Code 2. The list below has been taken from the Comment Sheet: - Page 9, 11, 13, 24, 27, 38, 40, 51, 54, 56, 58 and 60 - MCR's on check sheet signed off but MCR's were not in place (and still not in place) - Page 12, 25, 39, 54 and 59 - air test signed when activity was not done - Page 13, 27, 40 and 56 - signed for saddle joint installation when this was not done - Page 51 - water test signed but test not carried out
|  | Cxxx-NCR-000104 | NCR | Contractor unable to provide evidence of Benchmarking for Urban Realm Works |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2021-10-31 | 2021-11-03 08:20 | 3 | 2021-09-21 15:09 | Architectural - Landscape Architectural | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | During a planned Urban Realm Surveillance, the Contractor was asked to provide evidence for Benchmarking in line with Architectural specification Cxxx-SKC-A-RSP-Cxxx-50042: JQ10.2105 Benchmark Requirements: “The first 3m of kerb completely installed with a completed corner”. JQ25.2107: The first completed area of each type of the works as agreed and accepted by the Project Manager. The Contractor was unable to provide the evidence.
|  | Cxxx-NCR-000105 | NCR | AHP-151 Lightning Pits (WTH) - Incorrect Material |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2021-10-05 | 2021-11-25 10:04 | 51 | 2021-09-21 14:59 | Civil - Streets & Highways | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Use of unapproved materials | Completed |  | The AHP-151 lightning pit covers at the WTH (refer to Cxxx-SKC-L-DDD-Cxxx-50620 and specification Cxxx-SKC-A-RSP-Cxxx-50020 clause JL22. 1226) should have an internal tray depth of 105mm. The manufacturer (Jones of Oswestry) have various options available and the internal depth of pit covers installed is 75mm. All other requirements of the specification have been met.
|  | Cxxx-NCR-000106 | NCR | Gilbert St Carriageway - Surface Course |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2021-10-05 | 2021-10-28 07:21 | 23 | 2021-09-21 15:32 | Civil - Wearing Course | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | Asphalt surface course on Gilbert St, St Anselm's Pl and Davies St does not have a strip adjacent to kerb without precoated chips.
|  | Cxxx-NCR-000107 | NCR | WTH - Davies St - Incorrect Formation of Lightning Pits |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2021-10-06 | 2022-01-21 15:25 | 107 | 2021-09-22 19:23 | Civil - Streets & Highways | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | The lightning pit details shown on the referenced drawing Cxxx-SKC-L-DDD-Cxxx-50620 detail 1 and 2 was not followed at two locations on Davies St (lightning pits located at approximately Grid Line 3 and 4). At each location the following was not constructed to design: - a 100mm diameter sump was not formed in the base of the lightning pit - the walls of the pit were not constructed with RC as specified. Instead engineering bricks were used (see attached picture) Original text by J. Stirzaker ------------------------------------------------------------------------------------------------------- Follow up inspection with J. Hyde and __ revealed the following for all WTH lightning pits surrounding the station. As per comments below, MCR (engineering bricks used) is to be raised (CODE1) and works to be completed then re-inspected to see if closing out of NCR is applicable. Photos with __ which can be uploaded to NCR if required. WTH Urban Realm Earthing Pit inspection 07/10/21 Earthing Pit Reference Drained Issues Captured in NCR? 1 No Brick surround Cxxx-NCR-000107 - Incomplete works 2 No Brick surround Bigger pit size (400x400*) Rubber seals missing Cover not grouted Cxxx-NCR-000107 - Incomplete works and need MCR 3 No Cover not grouted Cxxx-NCR-000107 - Incomplete works 4 Yes Brick surround Cxxx-NCR-000107 - Incomplete works 5 No Requires core hole Shingle infill Cxxx-NCR-000100 (Blu-3 item) 6 Yes Brick surround Cxxx-NCR-000107 - Incomplete works 7 No Brick surround Cxxx-NCR-000107 - Incomplete works 8 No Brick surround Cxxx-NCR-000107 - Incomplete works 9 No Access Mutiplex container To be inspected located over pit 10 No Not drilled pit located on the edge of crane base Cxxx-NCR-00107 - Incomplete works 11 - No access ply sheets Stacked on top of pit To be inspected 12 Yes Acceptable 13 Yes Acceptable 14 Yes Bigger pit size (400x400*) Cxxx-NCR-000107 - Incomplete works and need MCR Rubber seals missing 15 - No access __ work area To be inspected 16 Yes Bigger pit size (400x400*) Cxxx-NCR-000107 - Incomplete works and need MCR Rubber seals missing
|  | Cxxx-NCR-000108 | NCR | WTH - L0 and Capping Beam - Waterproofing - Missing Check Sheets |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2021-10-03 | 2021-11-09 13:25 | 37 | 2021-09-26 04:14 | Architectural - General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Not Defined | Completed |  | WTH - L0 and Capping Beam - Waterproofing - Missing Check Sheets Waterproofing inspection check sheets are missing for the following areas; WTH - Capping Beam - GL 2-4/A Gilbert Street - GL 1-4/L Davies Street WTH - L0 - to add
|  | Cxxx-NCR-000109 | NCR | WTH - L+1/ L+3/ L+5/ L+6 - Waterproofing - Missing Check Sheets |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2021-10-03 | 2021-11-05 14:48 | 33 | 2021-09-26 04:28 | Architectural - General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Not Defined | Completed |  | WTH - L+1/ L+3/ L+5/ L+6 - Waterproofing - Missing Check Sheets Waterproofing inspection check sheets are missing for the following areas; WTH - L+1 to add if insufficient records appear WTH - L+3 to add if insufficient records appear
|  | Cxxx-NCR-000110 | NCR | Lin - P&T - GIR111b - Top Plates - Deviation from __ design guidance |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2021-10-15 | 2022-03-22 09:32 | 158 | 2021-10-01 10:44 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Insufficient information made available to the worker. | Completed |  | Potential rebar clashes; drilled a series of unnecessary holes in the of L-5 soffit Slab that can’t be utilised because of minimum 130mm spacing required by __ design data for anchors. In order to minimise the amount of trail drilling carried out, have carried out a ferro scan. The trail drilling was the last resort in order to ensure the specified anchors meet the necessary embedment depth.
|  | Cxxx-NCR-000111 | NCR | P&T - Unable to Install Remaining Large GFRC Panel in AP2 due to it being OverSized () |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2021-12-24 | 2021-11-24 11:24 | -30 | 2021-10-29 14:30 | Architectural - Walls | 500 |  | Manufacturing Defect | Reject | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | During the install of the GFRC panels in AP2 it was noted that 2 of the large GFRC panels on the curved corner were the incorrect length. These 2 large GFRC panels were remanufactured by the sub-contractor and delivered to site earlier this month but it was noted during install that the straight GFRC panel was the incorrect size again and couldn't be installed.
|  | Cxxx-NCR-000112 | NCR | P&T - Clash between AP2 Corridor Sub Structure Steelwork and Ceiling Edge Rails at Various Locations () |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2021-11-30 | 2021-12-21 08:35 | 21 | 2021-10-27 08:55 | Architectural - Ceilings & Soffits | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Design Problem - Not Defined | Completed |  | During the final adjustment of a section of edge ceiling rail along the main AP2 corridor into its final position, it was noted that the horizontal sub structure steel member above was preventing the rail from being installed to the correct level (see photo below for clarity). A solution was discussed, carried out on site and offered up to the CRL Lead Architect for review and comments. The solution involved cutting the edge rail either side of the steel member so it could be installed to the correct level but this resulted in a gap in the rail and exposing the steel member. To resolve this issue, a small length of ceiling cover strip was installed to cover the exposed section of steel beam. This ceiling strip ran approx. 500mm either side of the gap to blend in with the existing ceiling rail. The CRL architect accepted the strip solution in principle but insisted that the strip would need to be the same length as the corresponding ceiling edge rail so that the ends of the additional cover strip fell in line with the joints of the edge rail, minimising the number joints visible. The approved solution outlined above was accepted in principle by CRL. Can CRL please confirm formal acceptance of the above detail which was agreed on site?
|  | Cxxx-NCR-000113 | NCR | Low level steelwork clash with PES end ceiling |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2021-11-08 | 2022-02-04 15:15 | 88 | 2021-10-25 14:23 | Architectural - Ceilings & Soffits | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The PES end steelwork at Frames 3 & 4 has been installed too low and out of design tolerance, causing a clash with the PES end ceiling install. With installing the primary steelwork out of tolerance, it is now preventing from installing the secondary ceiling structure as per design in the same location(s) without modifying the ceiling design.
|  | Cxxx-NCR-000114 | NCR | WTH - Gilbert St - Footway Asphalt |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2022-01-17 | 2022-02-04 13:52 | 18 | 2021-10-29 13:21 | Architectural - General | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Design Problem - Not Defined | Completed |  | The WTH Gilbert St footway outside ESS1 and ESS2 (GL 1-2) was initially set too low. This created a trip hazard when the granite doorway / threshold was installed. OCS subsequently saw cut the asphalt and placed new asphalt. The finish of this is poor - it does not appear to be the same spec material or to be properly compacted.
|  | Cxxx-NCR-000115 | NCR | WTH - Weighhouse St - Road Marking |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2021-11-16 | 2022-04-22 10:25 | 157 | 2021-11-02 14:31 | Architectural - Landscape Architectural | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Design Problem - Not Defined | Completed |  | Road markings of the WTH should have been completed as per Cxxx-SKC-D-DDA-Cxxx-10360. The attached 70029257-03-TMO-01 shows arrows for 'direction of traffic flow'. One arrow on Weighhouse St was painted on the carriageway surface. # These should not be applied to the surface and are only shown on the TMO for the purpose of indicating traffic flow.
|  | Cxxx-NCR-000116 | NCR | WTH Stone Kerbs (mortar joints) |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2021-11-17 | 2021-11-30 08:08 | 13 | 2021-11-03 16:08 | Civil - Streets & Highways | 500 |  | Incomplete Works | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Not Defined | Completed |  | Mortar joints between stone kerbs installed at WTH do not have mortar in the joints
|  | Cxxx-NCR-000117 | NCR | WTH L-5 - Remedial works commenced to replace damaged winch point anchors located in W-06-72-H04 without prior agreement with Cxxx |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2021-11-20 | 2021-12-15 14:56 | 25 | 2021-11-06 10:02 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | Winch point located in W-06-72-H04 (WTH L-5 Circulation Area 6/072) has been removed due to anchors being damaged. These anchors were removed by over coring the concrete. These remedial works (over coring works) commenced without prior agreement with Cxxx. Due to the increased size of the resultant holes (24mm diameter), M16 __ HST3 metal expansion anchors are no longer suitable. It's also worth noting that during coring works some rebar has been exposed but not damaged.
|  | Cxxx-NCR-000118 | NCR | P&T Steel Work & GFRC Cladding - Installation not witnessed by CRL Architectural Assurance Team |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2022-01-11 | 2022-04-07 07:51 | 86 | 2021-12-21 13:15 | Archaeology - General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Over the course of GFRC cladding installation (2016 to 2020) in: Platforms, Access Passages, Cross Passages, Concourse Areas and Escalator Barrels a number of Steel Work elements & GFRC Cladding were not presented for inspection by Cxxx engineers to CRL Architectural Assurance Team, as indicated in Cxxx-SKC-O4-ITP-Cxxx-50071 (Rev 3.0 to 7.0). Particular attention needs to be given to items: 5.1.6 Torque testing of anchors and 5.1.7 Pull Out Test of anchors or the aforementioned Cxxx-SKC-O4-ITP-Cxxx-50071 (Rev 7.0) in particular Although various joint (CRL and Cxxx) site inspection were carried out over the years, however it is our understanding the inspection sheets were never formalised and issued to eB; with documentation being lost or misplaced over the years.
|  | Cxxx-NCR-000119 | NCR | WTH Urban Realm - Unknown Drainage Pipe Material |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2021-12-04 | 2022-01-17 12:32 | 44 | 2021-11-20 08:02 | Civil - Drainage | 500 |  | Material | Repair | 4 (0.5-3k) | Complete | Design Problem - Error in equipment or material selection | Completed |  | Within the WTH urban realm area there are several buried drainage pipes that have been installed, but the pipe material is unknown. The check sheets and PTRs (raised for the change in drainage route/connections) identify the pipe material as cast iron or ductile iron, but don't identify the product type or manufacturer. The pipe is identifiable because the outside is red in colour and there are no MCRs for underground drainage pipes that are red. As the pipes are buried and there is no records of the product it is not possible to identify what product has been installed. The locations are identified on the attached pdf (WTH Unknown Drainage Material).
|  | Cxxx-NCR-000120 | NCR | AP2/AP3 Ceiling Panel Damage & Workmanship |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2022-07-07 | 2022-07-15 14:39 | 8 | 2022-06-23 09:04 | Architectural - General | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Design Problem - Not Defined | Completed |  | Site inspections of the AP2 and AP3 ceiling installation have raised concerns re the quality of the works undertaken to date. Whilst it is fully recognised that the installation has not been offered to Crossrail for inspection, a number of observations are raised as per the attached summary that identifies the works are not in line with the agreed benchmark. We raise this NCR defect notice to highlight our concerns and that unless the quality is addressed as the works proceed then a disproportionate amount of rework will be required to rectify the installation in due course. It is noted that the works to AP2 appear to be of a higher standard to those in AP3. The issues identified are but not limited to: damage to ceiling panels, small nicks, dents, scratches, dents and scratches to ceiling trims, paint chips, trims not being cut accurately, trims/panels misaligned, trims missing and dirty finger prints over new white ceiling panels.
|  | Cxxx-NCR-000121 | NCR | WTH - Urban Realm - South Molton Lane Kerbs |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2022-04-24 | 2022-06-09 14:40 | 46 | 2021-11-25 15:40 | Architectural - Landscape Architectural | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Subcontractor Problems - Not Defined | Completed |  | Several straight kerbs have been used on South Molton lane instead of radius kerbs. This has been identified by Westminster City Council (WCC) and needs to be rectified.
|  | Cxxx-NCR-000122 | NCR | WTH - Urban Realm - Weighhouse St Kerbs |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2022-04-24 | 2022-03-03 13:27 | -52 | 2021-11-25 15:54 | Architectural - Landscape Architectural | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Subcontractor Problems - Other | Completed |  | Several straight kerbs have been used at the western end of Weighhouse St instead of radius kerbs. This has been identified by Westminster City Council (WCC) and needs to be rectified.
|  | Cxxx-NCR-000123 | NCR | P&T - MEP Electrical Completing Works Prior to Seeking Permission from Architectural Team (MEP Electrical Team) |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2022-03-03 | 2022-02-18 15:26 | -13 | 2022-02-17 14:45 | Architectural - Walls | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | During the installation of the stainless steel 110v socket outlet frame & door in AP1 on the Overbridge section, MEP Electrical had installed there containment to a point and were requested by not to complete the install until had completed the access door frame. Unfortunately for some reason, MEP continued and completed the install of the 110v unit prior to completing the door frame install. The 110v socket unit requires removal to enable to complete the install of the frame and door.
|  | Cxxx-NCR-000124 | NCR | NPP Cages ETH EB Remedial Works and Concrete Repair |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2022-02-02 | 2022-04-07 12:22 | 64 | 2022-01-19 08:44 | Civil - Structural Engineering | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | Following the installation of the NPP Cages Posts at the ETH East bound platform, a hairline crack was identified (see attached pictures and marked drawing Cxxx-COF-A-DWG-Cxxx-50352).
|  | Cxxx-NCR-000125 | NCR | Missing materials for project preventing completion of work areas |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2022-09-04 | 2022-07-08 14:54 | -58 | 2022-01-25 17:23 | Architectural - Ceilings & Soffits | 500 |  | Incomplete Works | Rework | 4 (0.5-3k) | Complete | Design Problem - Not Defined | Completed |  | The subcontractor has failed to adequately supply the project with the required materials to allow the sub contractor to complete their works. The Subcontractor has not installed all materials and therefore the installation of the following areas is incomplete: AP1, AP2, AP3, PES End ceilings and PES end glazing walls in zones 1,11,12,22 and lift sip sop panels for lift 5 & lift 7 in AP2 & AP3.
|  | Cxxx-NCR-000126 | NCR | Inadequate PES End U-Channel Installation |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2022-09-04 | 2022-07-06 09:21 | -60 | 2022-01-19 16:39 | Architectural - Finishes | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | The installation and workmanship of the 4no. stainless steel PES End U-Channels by The Subcontractor () is not up to the required standard and does not meet the required design intent. The 4no. areas affected are: Frame 1, Frame 2, Frame 3 & Frame 4 PES U-channels. This NCR is raised due to the following issues: - Dimples in the finished steel trim causing inconsistent finish - Gaps between adjacent pieces of trim - Mitre joints not lining up - Butt joints not lining up - Generally poor, uneven cuts and finishes at all joints - Excessive gaps between steel trim and door, glass, PES grilles and other stainless steel elements - Excessive and inconsistent gaps between trim and flooring - Inconsistent alignment and out of design position of trim against PED frame (i.e frame 3 trim is behind door frame, frame 4 trim is in front of door frame) - Short and incorrect pieces of trim which are required to be remade not allowing works to be completed - Missing elements of the trim not allowing works to be completed - Excessive gap at frame 4 between the horizontal PES trim and the PES end ceiling trim. This gap is approx. 30mm at frame 4 vs 10mm at frame 2 - Overall design, fabrication and installation does not meet design intent and is not accepted by The Employer.
|  | Cxxx-NCR-000128 | NCR | P&T - Platform Cabinet Fire Main Doors NOT Opening 180 Deg () |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2022-02-10 | 2022-02-11 12:26 | 1 | 2022-01-27 10:35 | Architectural - Doors | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | It was noted during an inspection that the glazed door to the Fire Main Compartment of the platform cabinets on the Eastbound & Westbound platforms do not open 180 degrees as highlighted on the approved drawing. These doors need to open by 180 degrees so this will need to be rectified for all remaining cabinets.
|  | Cxxx-NCR-000129 | NCR | AP2 Door W-06-406-D01 Stainless Steel Panel Out of Tolerence |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2022-02-14 | 2022-04-22 13:03 | 67 | 2022-01-31 20:07 | Architectural - Finishes | 500 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | The subcontractor () have installed 2no. stainless steel panels at door W-06-406-D01 in AP2 WTH level -5 without completing the required design and have failed to take into account the as current site conditions at the point of contract. The stainless steel panels have manufactured & installed are 21mm out of tolerance and do not line up with the edge of the door opening. Failure by to immediately address this matter may directly lead to a delay in the completion of the Works.
|  | Cxxx-NCR-000130 | NCR | The lights and associated brackets obstruct access to air release smoke control damper AAR-W-SD007 WTH Level 2 Circulation Area 2/074 |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2022-09-04 | 2022-10-03 15:09 | 29 | 2022-02-07 15:06 | Electrical - Lighting | 3000 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Design Problem - Not Defined | Completed |  | The luminaire and is associated brackets obstruct access to air release system smoke control damper 'AAR-W-SD007' located in WTH Level 2 Circulation Area 2/074. 'AAR-W-SD007' forms part of the life safety system and requires clear access via MEWP or a tower for routine maintenance and for quick access for any failures.
|  | Cxxx-NCR-000131 | NCR | Out of Sequence Installation of 1200no. ceiling tile lanyards |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2022-02-23 | 2022-04-13 12:15 | 49 | 2022-02-09 10:34 | Architectural - Ceilings & Soffits | 500 |  | Incomplete Works | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Not Defined | Completed |  | The Subcontractor () has not installed approximately 1200no. ceiling tile lanyards across the AP1, AP2 & AP3 ceilings as per design. This will need to be completed, however this out of sequence installation results in significant rework and require each ceiling panel to be removed and reinstated. For the AP2 & AP3 areas now under SC2 Enactment as of 17/01/22, these works are required to be carried out during nightshift engineering hours.
|  | Cxxx-NCR-000132 | NCR | Incorrectly Manufactured Lift 5 & 7 Sip Sop Glazing panels |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2022-07-07 | 2022-07-12 13:47 | 5 | 2022-06-23 09:05 | Architectural - Glazing | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | The Subcontractor () has incorrectly manufactured 4no. total sip sop glazing panels for the Lift 5 & Lift 7 lift fronts. The Subcontractor has failed to adequately survey the as built site conditions as required per clause 2.15 of the Subcontract. This will result in either a remake of panels or modification to other works to rectify.
|  | Cxxx-NCR-000133 | NCR | The lights and associated brackets obstruct access to air release smoke control damper AAR-W-SD003 WTH Level 5 Circulation Area 5/071 |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2022-09-04 | 2022-07-26 11:54 | -40 | 2022-02-10 16:22 | Electrical - Lighting | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | The luminaire and is associated brackets obstruct access to air release system smoke control damper 'AAR-W-SD003' located in WTH Level 5 Circulation Area 5/071. 'AAR-W-SD003' forms part of the life safety system and requires clear access via MEWP or a tower for routine maintenance and for quick access for any failures. A step ladder could be used as a last option. The luminaire and is associated brackets need to be shifted.
|  | Cxxx-NCR-000134 | NCR | The lights and associated brackets obstruct access to fire dampers AS-W-FD093 and GE-W-FD093 WTH Circ Area 3/240 |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2022-09-04 | 2022-11-29 10:17 | 86 | 2022-02-10 16:41 | Electrical - Lighting | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | The luminaires and is associated brackets obstruct access to fire dampers AS-W-FD093 and GE-W-FD093 WTH Circ Area 3/240. These fire dampers require clear access via MEWP or a tower for routine maintenance and for quick access for any failures. A step ladder can be used as last option. The luminaires and its associated brackets need to be moved.
|  | Cxxx-NCR-000135 | NCR | Delatim - Bostwick Gate - Top Track Alignment |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2022-03-02 | 2022-04-29 12:49 | 58 | 2022-02-16 08:10 | Architectural - Doors | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Not Defined | Completed |  | Top track of the AP1 Bostwick Gate has not been installed in alignment. This is affecting the surrounding cladding.
|  | Cxxx-NCR-000136 | NCR | Missing infill trims between PES end ceilings and glazing |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2022-03-03 | 2022-04-22 13:05 | 50 | 2022-02-17 06:41 | Architectural - Ceilings & Soffits | 500 |  | Incomplete Works | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | The Subcontractor () did not install the required trims to be installed between the PES end ceilings and the PES glazing at frames 1, 2, 3 & 4 on the East and Westbound platforms level -5. As a result, out of sequence rework is required to be undertaken to complete the works in the areas.
|  | Cxxx-NCR-000137 | NCR | Missing ceiling infill trims adjacent to GFRC and DAL boom lighting |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2022-03-03 | 2022-05-13 08:00 | 71 | 2022-02-17 07:45 | Architectural - Ceilings & Soffits | 500 |  | Incomplete Works | Rework | 4 (0.5-3k) | Complete | Management Problem - Not Defined | Completed |  | The Subcontractor () did not install all of the required trims between the ceiling panels and GFRC panels and the ceiling panels and DAL boom lighting throughout multiple locations in AP1 on level -3 WTH, AP2 & AP3 on level -5. As a result, out of sequence rework is required to be undertaken by the Subcontractor to complete the works in these areas.
|  | Cxxx-NCR-000138 | NCR | WTH - L0 - GLAP Clash With Existing RC Plinth |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2022-03-03 | 2022-05-06 11:10 | 64 | 2022-02-17 08:46 | Architectural - Glazing | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Not Defined | Completed |  | The WTH L0 GLAP Unit clashes with an existing RC Plinth on the L0 slab. It appears the design of the GLAP unit has not correctly been coordinated with the existing RC plinth - which is installed as per existing design information. Drawing ref: Cxxx-SKC-A-DDD-Cxxx-35003.
|  | Cxxx-NCR-000139 | NCR | Missing movement joints in AP2 & AP3 ceilings |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2022-03-03 | 2022-04-29 12:47 | 57 | 2022-02-17 08:27 | Architectural - Ceilings & Soffits | 500 |  | Incomplete Works | Rework | 4 (0.5-3k) | Complete | Design Problem - Not Defined | Completed |  | The Subcontractor () did not install the required movement joints in the ceilings of AP2 & AP3 on level -5. As a result, out of sequence rework is required to be undertaken by the Subcontractor during engineering hours to complete the works in these areas.
|  | Cxxx-NCR-000141 | NCR | - Escalators 11-13 Trim Gaps |  | Contr | COF | BOS - Bond Street Station (West) |  | 2022-09-04 | 2022-07-07 07:49 | -59 | 2022-03-01 13:04 | Architectural - Finishes | 500 |  | Manufacturing Defect | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | A number of the stainless steel flared decking strips on Escalators 11-13 require remanufacturing as there are gaps - as shown on the attached photographs between the stainless strip and GFRC panels, which are not acceptable.
|  | Cxxx-NCR-000142 | NCR | ETH Chiller room 1/776 intake plenum - man access duct hatches obstructed by Electrical __ supports and lighting |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2022-05-01 | 2022-03-21 10:02 | -41 | 2022-03-02 09:40 | Electrical - General | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | ETH Chiller room 1/776 intake plenum man access duct hatches are obstructed by Electrical __ supports and lighting (see attached: Uni-Strut items to be moved - Obstructing the plenum access hatches.docx). If the supports are moved then this will allow access into the plenums for inspection and cleaning. A site visit between the CRL representative S Turley (mechanical engineer), and representative Vincent Ingram (Electrical Supervisor) concluded that the electrical support brackets and lighting will be moved to provide sufficient access to the hatches (described in the attached email).
|  | Cxxx-NCR-000143 | NCR | L&E Escalators 11-13 & 17-19 Hatch Finger Traps |  | Contr | COF | BOS - Bond Street Station (West) |  | 2022-09-04 | 2022-07-01 13:32 | -65 | 2022-03-03 15:58 | Architectural - Finishes | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Regarding the access hatches on escalators 11-13 and 17-19. CEG’s L&E representatives have raised concerns over the gaps around the access hatches as there is a potential risk of finger entrapment. The Escalators Cat 1 standard which forms part of the F45 requirements which need to be achieved to allow the escalators to be signed off. Also attached are photos taken from Esc 11-13 during a joint site inspection between CRL, CRL Architect, and on 24.02.22
|  | Cxxx-NCR-000144 | NCR | Emergency Exit Signs - Cxxx-PWK-00769 |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2022-09-04 | 2022-07-12 14:32 | -54 | 2022-03-07 10:26 | Electrical - General | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | DB-W-EL08 - SC3 Circuits; 1L1 - Emergency exit sign has incorrect direction arrow installed within C/776 3L3 - Emergency exit sign has incorrect direction arrow installed within B/081 3L3 - Emergency exit sign missing direction arrow cover within C/081
|  | Cxxx-NCR-000145 | NCR | Western Ticket Hall (WTH) - Exit Signs Require Relocating |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2022-03-21 | 2022-06-16 14:53 | 87 | 2022-03-07 15:49 | Architectural - Signage | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | As: Cxxx-PWK-00776 1no. exit sign within B/081 & 1no. exit sign within C/081 installed behind CAT ladder requires relocating to the left side of the ladder to allow safe access and maintenance.
|  | Cxxx-NCR-000148 | NCR | SCC 50116 - AP1 - Glavanised steel - Installation - missing / no checksheets and torque testing / works not witnessed by CRL Assurance |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2022-04-21 | 2022-04-29 13:30 | 8 | 2022-04-07 13:04 | Architectural - Balustrade | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | The non-conformance is for missing / no checksheets and torque testing / works not witnessed by CRL for the Installation Glavanised Steel in AP1 Lu Link Passage ( SCC 50116)
|  | Cxxx-NCR-000149 | NCR | Damaged leaves requiring replacement (E-02-092-D01 and E-03-091-D01) |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2022-09-04 | 2022-08-11 13:41 | -24 | 2022-04-09 13:38 | Architectural - Doors | 3000 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | The leaves for E-02-092-D01 and E-03-091-D01 have been damaged beyond repair.
|  | Cxxx-NCR-000150 | NCR | WTH - L0 GLAP - RC Floor Slab Bracketry Installed Out of Sequence |  | Contr | COF | BOS - Bond Street Station (West) |  | 2022-04-26 | 2022-05-06 11:08 | 10 | 2022-04-12 15:31 | Architectural - Glazing | 500 |  | Planning | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Not Defined | Completed |  | It is evident that have installed the GLAP structure (notably the bracketry which is fixed to the L0 Structural Floor Slab) out of sequence. As this was not completed with the rest of the GLAP structure which is fixed to the L0 Floor slab, the tiling and screed is required to be broken out by others to enable these brackets to be installed, and then re-laid following completion of 's bracket install.
|  | Cxxx-NCR-000151 | NCR | P&T - CP5 GFRC Incorrect Panel On Site |  | Contr | COF | BOS - Bond Street Station (West) |  | 2022-09-04 | 2022-07-06 09:48 | -60 | 2022-04-14 12:26 | Architectural - General | 500 |  | Incomplete Works | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Incomplete installation of GFRC panels on L-5 in CP5. Following concerns regarding the whereabouts of panel CP-5-16 the CRL team identified a panel labelled accordingly on a rack at level -5. However a subsequent check by has identified that despite this panel having been labelled up for this location it in fact does not fit the opening. Indeed the stock check undertaken by in December 2021 noted that panel CP-5-16 (or CP-X-16 as originally denoted) was present, further demonstrating that the survey had not accurately reflected the site requirements. It would appear that the survey undertaken by and incorrect labelling has resulted in GFRC panel CP-5-16 not currently being available.
|  | Cxxx-NCR-000152 | NCR | P&T - CP5 - GFRC Panel Damaged During Reinstallation |  | Contr | COF | BOS - Bond Street Station (West) |  | 2022-09-04 | 2022-08-25 12:43 | -10 | 2022-04-14 14:36 | Architectural - General | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | GFRC Panel CP-5-14 was damaged (chipped) during removal and reinstallation.
|  | Cxxx-NCR-000153 | NCR | Luminaire and associated supports obstructing access to fire damper GE-W-FD121 in WTH Circulation Area 2/074 |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2022-09-04 | 2022-11-29 10:21 | 86 | 2022-04-18 15:40 | Electrical - Lighting | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | Luminaire and associated __ supports are obstructing access to fire damper GE-W-FD121 in WTH Circulation Area 2/074. As part of CRL specification JA.6402, clause c, Crossrail will need to demonstrate to LUL that all fire dampers can be accessed safely for routine test and inspection and without the need to remove other contractors equipment. The luminaire and associated __ supports should be reworked (moved to the wall?) to allow access to the fire damper via a ladder, MEWP or podium. See attached email for photos and drawing;<RE Circulation area Fire Damper - 2074.msg >.
|  | Cxxx-NCR-000154 | NCR | CMS and associated supports obstructing access to fire damper AS-E-FD042 in ETH level 3 Circulation Area 3/073 |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2022-09-04 | 2022-07-21 14:28 | -45 | 2022-04-18 16:00 | Electrical - Cable Management | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Not Defined | Completed |  | The cable Management System (CMS) and associated supports (__ and drop rods) are obstructing access to fire damper AS-E-FD042 in ETH level 3 Circulation Area 3/073. As part of CRL specification JA.6402, clause c, Crossrail will need to demonstrate to LUL that all fire dampers can be accessed safely for routine test and inspection and without the need to remove other contractors equipment. The CMS and supports should be adjusted to allow access to the fire damper via a ladder, MEWP or podium. See attached email for photos and drawing; ETH Level -3 - circulation area fire damper AS-E-FD042 .
|  | Cxxx-NCR-000155 | NCR | Fire rated duct insulation 'cut away' to avoid clash with lighting connection - in ETH escape lobby 6/091 |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2022-09-04 | 2022-07-20 10:23 | -46 | 2022-04-18 16:21 | Electrical - Lighting | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Supervision - Insufficient supervision | Completed |  | The fire rated duct insulation has been 'cut away' by the lighting installer to avoid clash with the lighting connection and the duct system. The non-compliance has occurred in ETH escape lobby 6/091. The lighting should be moved away from the duct so that there is no clash between the duct insulation and lighting connection. In theory, during a fire incident in an adjacent room, heat could be radiated out from the duct onto the lighting connection in the escape corridor. Lighting could be affected. Moving the light connection and re-instating the insulation mitigates this risk. See attached email for photos: 'Fire rated insulation cut out in escape lobby - by lighting installer'.
|  | Cxxx-NCR-000156 | NCR | WTH - L0 GLAP - Bronze Panels Damaged |  | Contr | COF | BOS - Bond Street Station (West) |  | 2022-09-04 | 2022-07-06 10:17 | -60 | 2022-04-27 16:37 | Architectural - General | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | On 27.04.2022 it has been noted that the WTH L0 GLAP bronze panels have been damaged upon installation.
|  | Cxxx-NCR-000157 | NCR | Clash between Bostwick Gate shoot bolt top keep and the panel |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2022-09-04 | 2022-07-22 14:42 | -44 | 2022-04-29 16:12 | Architectural - Doors | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Not Defined | Completed |  | No allowance has been made in the panel adjacent to the Bostwick gate top track for the gate shoot bolt top keep.
|  | Cxxx-NCR-000159 | NCR | APs - Gaps at End of Boom Lighting |  | Contr | COF | BOS - Bond Street Station (West) |  | 2022-09-04 | 2022-07-01 13:18 | -65 | 2022-05-09 17:01 | Architectural - Finishes | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | There are gaps at the end of the Boom lighting units within AP1, AP2, and AP3 which are excessive and out of tolerance.
|  | Cxxx-NCR-000160 | NCR | AP1 - GFRC Panel Holes Not Covered |  | Contr | COF | BOS - Bond Street Station (West) |  | 2022-09-04 | 2022-06-29 07:38 | -67 | 2022-05-09 17:14 | Architectural - Walls | 500 |  | Incomplete Works | Rework | 4 (0.5-3k) | Complete | Design Problem - Not Defined | Completed |  | GFRC panel bolt holes were due to be filled with GFRC or a SS cap.
|  | Cxxx-NCR-000161 | NCR | AP1 - Stainless Steel Trim Finish Not Acceptable |  | Contr | COF | BOS - Bond Street Station (West) |  | 2022-09-04 | 2022-07-06 10:20 | -60 | 2022-05-09 17:21 | Architectural - Finishes | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The stainless steel trim finishes (as photo'd) in AP1 is not acceptable this appears to not be as per design, and leaves and exposed hole in the stainless steel.
|  | Cxxx-NCR-000162 | NCR | P&T - AP3 SIP/SOP - Damaged Glazing Panel |  | Contr | COF | BOS - Bond Street Station (West) |  | 2022-09-04 | 2022-07-08 15:00 | -58 | 2022-05-16 16:29 | Architectural - Glazing | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | External Phenomenon - Not Defined | Completed |  | The glazing panel recently installed in the top right hand corner of the AP3 SIP/SOP is damaged - the secondary layer of glazing appears to have shattered completely.
|  | Cxxx-NCR-000163 | NCR | L-5 PES Grill Anti Lift Cleats - Fixings Not Removable |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2022-09-04 | 2022-06-24 14:15 | -72 | 2022-05-18 08:52 | Architectural - General | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Not Defined | Completed |  | As per Cxxx-NCR-000255 - It has been identified that the some of the fixings which secure the anti-lift cleats above the architectural grills at each end of the platforms are unable to be removed. The M5 button head fixings are spinning when attempts are made to remove them. As such the grills are unable to be removed - currently there are various trades who need to access behind these grills to undertake surveys to progress design on other works. Please refer to the attached drawings and photographs of the grills in question.
|  | Cxxx-NCR-000164 | NCR | Competency records for pull out testing and pressure test are missing |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2022-09-04 | 2022-07-21 14:34 | -45 | 2022-05-18 09:00 | Mechanical - Public Health Engineering | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Not Defined | Completed |  | Competency records for pull out testing and pressure test are missing in package listing for WTH - Level 0.5 OSD Central Core Openings and Drainage Connection (Cxxx-COF-C-CER-Cxxx-50012).
|  | Cxxx-NCR-000165 | NCR | ETH - L0 - Poor Quality of Mastic to ETH GLAP Door |  | Contr | COF | BOS - Bond Street Station (West) |  | 2022-09-04 | 2022-06-29 07:40 | -67 | 2022-05-25 11:17 | Architectural - Finishes | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Not Defined | Completed |  | Poor quality of Mastic to ETH GLAP door. Finish of mastic to both the leading and trailing edges of the ETH GLAP door is non-compliant.
|  | Cxxx-NCR-000166 | NCR | WTH - L0 - Paid Tech Wall Bronze Finish |  | Contr | COF | BOS - Bond Street Station (West) |  | 2022-09-04 | 2022-07-07 07:51 | -59 | 2022-05-30 07:22 | Architectural - Finishes | 500 |  | Manufacturing Defect | Repair | 4 (0.5-3k) | Complete | External Phenomenon - Other | Completed |  | Blotches & impurities on bronze cladding to Tech Wall.
|  | Cxxx-NCR-000167 | NCR | WTH - L0 - GLAP Missing Trim |  | Contr | COF | BOS - Bond Street Station (West) |  | 2022-09-04 | 2022-07-01 14:56 | -65 | 2022-05-30 07:31 | Architectural - Finishes | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | External Phenomenon - Not Defined | Completed |  | WTH L0 GLAP structure has a bronze trim missing, this should be located internally above the access door (see attached photos).
|  | Cxxx-NCR-000168 | NCR | WTH - Clear Glazing - No Approved MCR |  | Contr | COF | BOS - Bond Street Station (West) |  | 2022-06-13 | 2022-06-10 09:30 | -3 | 2022-05-30 08:33 | Architectural - Glazing | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Not Defined | Completed |  | There does not appear to be an approved MCR in place for the WTH clear glazing.
|  | Cxxx-NCR-000170 | NCR | AP2 & AP3 Tether Installation |  | Contr | COF | BOS - Bond Street Station (West) |  | 2022-09-04 | 2022-08-26 09:47 | -9 | 2022-06-09 09:39 | Architectural - Ceilings & Soffits | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Cable ties have been used instead of metal clips with some of the tethers not even wrapped around the steel beams above. Meaning if they become loose, they will drop to the floor. This has been encountered in various areas of AP2 & AP3. This is both a non-conformance on install and a safety hazard within an area which is due to be open to the public once the station opens and is unacceptable.
|  | Cxxx-NCR-000171 | NCR | P&T - Escalators 11-13 & 17-19 - Non Compliant Fixings Installed |  | Contr | COF | BOS - Bond Street Station (West) |  | 2022-08-01 | 2022-09-20 03:44 | 50 | 2022-06-13 16:38 | Architectural - Security | 1000 |  | Material | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Contamination | Completed |  | The fixings installed on the hatches to Escalators 11-13 & 17-19 are non-compliant. As per 's contract with Cxxx/ - see Schedule 2, Section 3 - 7.7 Works Info Vol 2C Part 2 - 100 Architectural Component Design - Cxxx-ATK-N2-RSP-CR002-000001 Rev 12.0, JZ20.1101 - page 486. Fixings in public areas are required to be anti-tamper.
|  | Cxxx-NCR-000172 | NCR | WTH - Unpaid Tech Wall Glazing Panels Out of Tolerance |  | Contr | COF | BOS - Bond Street Station (West) |  | 2022-09-04 | 2022-07-01 11:53 | -65 | 2022-06-14 08:02 | Architectural - Glazing | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The WTH Tech Unpaid Wall Glazing Panels are installed out of the allowable tolerances.
|  | Cxxx-NCR-000173 | NCR | AP2 & AP3 - Ceiling Panel Hinges Defective Install |  | Contr | COF | BOS - Bond Street Station (West) |  | 2022-07-18 | 2022-08-26 09:49 | 39 | 2022-07-04 11:33 | Architectural - Ceilings & Soffits | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The installation of the hinges for the AP2 & AP3 ceilings panels have found to be defective – causing issues with opening and closing the panels, and in one location leading to failure of the hinges.
|  | Cxxx-NCR-000174 | NCR | P&T - AP2 Door Gaskets Defective |  | Contr | COF | BOS - Bond Street Station (West) |  | 2022-07-20 | 2022-08-04 15:50 | 15 | 2022-07-06 16:11 | Architectural - Finishes | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Design Problem - Not Defined | Completed |  | It has become apparent that the AP2 & AP3 Door Gaskets (as per Cxxx-NCR-00071) are still defective and too loose, becoming repeatedly dislodged. Whilst it is noted that the previous proposal was accepted by CRL for application, the responsibility for both the design, install, and assurance for the gaskets to be sufficient is 's responsibility.
|  | Cxxx-NCR-000177 | NCR | WTH & ETH GLAP Glazing Kite Marks |  | Contr | COF | BOS - Bond Street Station (West) |  | 2022-08-04 | 2022-08-26 09:55 | 22 | 2022-07-21 10:51 | Architectural - Glazing | 500 |  | Manufacturing Defect | Rework | 4 (0.5-3k) | Complete | External Phenomenon - Other | Completed |  | Following inspection with CRL's Architect it was noted that there are panels for the ETH & WTH GLAP Glazing that do not have the required Kite Markings stamps.
|  | Cxxx-NCR-000178 | NCR | No Proof and Witnessing of Bolt Pull Tests and Bolt Torque tests for WTH - Tile Support Brackets and Grout Trays installed by Mabey Bridge. |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2022-08-22 | 2022-09-13 12:34 | 22 | 2022-08-08 15:57 | Archaeology - General | 500 |  | Testing and Commissioning | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | No Proof and Witnessing of Bolt Pull Tests and Bolt Torque tests for WTH - Tile Support Brackets and Grout Trays installed by Bridge. Checksheets only signed by Bridge and not Engineer or CRL Assurance. See Record Pack Cxxx-COF-A-LRC-Cxxx-50044 and Sub-cert Cxxx-COF-A-CER-Cxxx-50035.
|  | Cxxx-NCR-000179 | NCR | Flood Control International MCR's not produced or issued for review. |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2023-01-31 |  | 6 | 2022-11-02 09:33 | Architectural - General | 500 |  | Documentation and Records |  |  | Open |  | PROPOSE ACTION |  | Flood Control International sent draft MCR's to Package Manager on 09/04/2019 for review. These MCR's were not given new MCR eB numbers and as a result never completed and issued to CRL for review.
|  | Cxxx-NCR-000180 | NCR | Escalator 11-13 & Escalators 17-19 Finger Traps |  | Contr | COF | BOS - Bond Street Station (West) |  | 2022-08-23 | 2022-09-15 04:19 | 23 | 2022-08-09 12:23 | Architectural - Finishes | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Escalator 11-13 and 17-19 hatch finger traps have been further highlighted as a non-conformance by CRL & LU. The initial rectification was accepted by CRL, however later, more robust inspections have found the rectification to be insufficient. The responsibility for both the design, install, and assurance for the hatches to be sufficient is 's responsibility.
|  | Cxxx-NCR-000181 | NCR | NPP Westbound & Eastbound NPP gates not locking correctly |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2022-09-14 | 2022-10-07 09:16 | 23 | 2022-08-31 14:38 | Architectural - Doors | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | It was identified that the Westbound, East NPP doors were not locking correctly.
|  | Cxxx-NCR-000182 | NCR | Escalator Inverts Sump Waterproofing Failing (ETH & WTH L-6) |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2023-06-30 |  | -144 | 2022-10-10 08:03 | Civil - Civil Engineering General | 1500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Open |  | ENGINEERING RESPONSE |  | It has been noted that the cementitious waterproofing layer to both escalator sump pits is spalling/peeling away from the concrete surface, as such it is unlikely to be watertight. Please see attached photographs for details on the type/extent of the defective waterproofing.
|  | Cxxx-NCR-000183 | NCR | WTH/ETH GLAP Doors sharp edges |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2022-11-09 | 2022-11-10 17:41 | 1 | 2022-10-26 14:17 | Architectural - Doors | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Not Defined | Completed |  | Sharp edges between the GLAP door frame and glazing, were identified to the WTH and ETH GLAP doors (see attached pictures 1&2 for the WTH). In addition, one of the stainless steel plate is protruding beyond the frame and is also a potential safety hazard (see attached picture 3)
|  | Cxxx-NCR-000184 | NCR | Outstanding site and testing records for Oliver Connell Sub-cert 50003 - Record Packs 50004 and 50014. |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2022-12-16 | 2022-12-06 10:54 | -10 | 2022-11-02 09:34 | Civil - Streets & Highways | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Record Pack 50004 – WTH – OCS – Weighhouse Street – Street Furniture After reviewing the record pack against the deliverables listed in ITP Cxxx-COF-C-ITP-Cxxx-50014 Rev 2.0 – Cxxx WTH – Street Furniture – Bond Street WTH & ETH, the following deliverable records are incomplete or missing: ITP 3.6: Only one Delivery Ticket found for Bollards 37, 38 & 39 ITP 3.7: Concrete Cube Tests report for Bollards does not specifically have the all the Bollard numbers in location description so unable to confirm if all the Bollard base pours are in the report. No PAS68 Cert for Bollards. Record Pack 50014 – WTH – OCS – Weighhouse Street – Footway – GL A to B After reviewing the record pack against the deliverables listed in ITP Cxxx-COF-C-ITP-Cxxx-50012 Rev 1.0 – Cxxx WTH – Carriageway and Footway Construction, the following deliverable records are incomplete or missing: ITP 3.1 – 3.3: Checksheet CS 50009-B ITP 3.3: Missing CBR Testing records ITP 4.3: -Compaction of Type 1 – Missing CBR Testing records ITP 4.6: Missing Concrete Delivery Notes ITP 4.7: Concrete Cube Test Report provided does not mention ‘Weighhouse Street Footway’. ITP 8.1: As-built Records
|  | Cxxx-NCR-000185 | NCR | Outstanding deliverable records for OSC Record pack Cxxx-COF-D-LRC-Cxxx-50006 - WTH - OCS - Davies Street - Carriageway and Footway. |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2022-11-22 | 2022-12-02 08:31 | 10 | 2022-11-08 09:08 | Civil - Roadworks Formation | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | After reviewing the record pack against the deliverables listed in ITP Cxxx-COF-C-ITP-Cxxx-50012 Rev 1.0 – Cxxx WTH – Carriageway and Footway Construction, the following deliverable records are incomplete or missing in record pack Cxxx-COF-D-LRC-Cxxx-50006 - WTH - OCS - Davies Street - Carriageway and Footway: ITP 4.6: Missing Concrete Delivery Notes ITP 4.7: Concrete Cube Test Reports ITP 8.1: As-built Records
|  | Cxxx-NCR-000186 | NCR | Outstanding Concrete Cube Records for Record Pack Cxxx-COF-D-LRC-Cxxx-50011 - WTH - OCS - Gilbert Street - Carriageway and Footway |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2022-11-22 | 2022-12-02 08:28 | 10 | 2022-11-08 11:02 | Civil - Streets & Highways | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Outstanding Concrete Cube Records for Record Pack Cxxx-COF-D-LRC-Cxxx-50011 - WTH - OCS - Gilbert Street - Carriageway and Footway.
|  | Cxxx-NCR-000187 | NCR | Outstanding Concrete Cube Records for Record Pack Cxxx-COF-D-LRC-Cxxx-50017 - WTH - OCS - St Anselm's Place - Carriageway Works |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2022-11-24 | 2022-12-02 08:29 | 8 | 2022-11-10 10:04 | Civil - Roadworks Formation | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Outstanding Concrete Cube Records for Record Pack Cxxx-COF-D-LRC-Cxxx-50017 - WTH - OCS - St Anselm's Place - Carriageway Works.
| 01CV - Civils | Cxxx-NCR-000081 | NCR | Review of ITP Code Status |  | Contr |  | NOW - North Woolwich Portal (East) |  | 2011-08-22 | 2011-09-19 16:16 | 28 | 2011-08-08 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Rework |  | Complete |  | Completed |  | ITPs for __ Shafts and Thames potable water PE pipes are not at the required code status (Code 01).
| 01CV - Civils | Cxxx-NCR-000083 | NCR | Notification of Requests for Inspection |  | Contr |  | NOW - North Woolwich Portal (East) |  | 2011-08-22 | 2011-09-19 16:19 | 28 | 2011-08-08 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Rework |  | Complete |  | Completed |  | No formal notification has been provided.
| 01CV - Civils | Cxxx-NCR-000084 | NCR | ITP verification documents |  | Contr |  | NOW - North Woolwich Portal (East) |  | 2011-08-22 | 2011-09-19 16:18 | 28 | 2011-08-08 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Rework |  | Complete |  | Completed |  | TP verification records were not readily available during a surveillance.
| 01CV - Civils | Cxxx-NCR-000130 | NCR | Documents not returned after the 28day review period |  | Contr |  | NOW - North Woolwich Portal (East) |  | 2011-03-10 | 2011-10-10 11:05 | 214 | 2011-09-20 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Rework |  | Complete |  | Completed |  | Works are proceding on site with documents unapproved by CRL, these documents have been with crossrail for review for longer than 28 days, see attached excel document
| 01CV - Civils | Cxxx-NCR-000144 | NCR | Incorrect Top "T" Fitting used |  | Contr |  | NOW - North Woolwich Portal (East) |  | 2011-10-19 | 2011-11-09 11:57 | 21 | 2011-10-14 | Civil - Sewage/Water services | 500 |  | Material | Rework |  | Complete |  | Completed |  | The top "T" procured was not as specified. A standard one was puchased and it should have been to the Protector pipe grade. This was highlighted during testing of the main when the fitting leaked.
| 01CV - Civils | Cxxx-NCR-000179 | NCR | Movement on the elliptical sewer |  | Contr |  | NOW - North Woolwich Portal (East) |  | 2011-11-24 | 2011-11-25 10:53 | 1 | 2011-11-10 | Utilities Engineering - Water | 500 |  | Design | Use As-Is |  | Complete |  | Completed |  | Settlement of the eliptical pipe does not conform to Thames water Specification requirements.
| 01CV - Civils | Cxxx-NCR-000186 | NCR | Failure of 250mm Electro Fusion Couplings |  | Contr |  | NOW - North Woolwich Portal (East) |  | 2012-02-09 | 2012-02-22 15:28 | 13 | 2012-01-20 | Utilities Engineering - Water | 500 |  | Material | Repair |  | Complete |  | Completed |  | Failure of the 250 mm EF couplers on Factory Road. After unsucessful Pressure testing of the 250mm main on Factory Rd a number of EF couplers were re-excavated and leaks were found. After investigation a number of these EF couplings failed destructive testing.
| 01CV - Civils | Cxxx-NCR-000262 | NCR | Accidental damage of 450mm Sluice Valve |  | Contr |  | NOW - North Woolwich Portal (East) |  | 2012-08-14 | 2012-08-17 14:08 | 3 | 2012-04-26 | Utilities Engineering - Water | 500 |  | Material | Repair |  | Complete |  | Completed |  | 450mm Sluice Valve is accidentally damaged in Victoria Dock Road in the Eastern Trunk Main connection.
| 01CV - Civils | Cxxx-NCR-000294 | NCR | BLOCKAGE IN NEWLY LAID DATA CABLE DUCT |  | Contr |  | NOW - North Woolwich Portal (East) |  | 2012-07-31 | 2012-09-14 15:05 | 45 | 2012-07-31 | Utilities Engineering - Telecomms | 500 |  | Damaged | Repair |  | Complete |  | Completed |  | __ DUCT PARTIALLY BLOCKED BY LEAN MIX WET CONCRETE SEEPING THROUGH DUCT JOINT DURING BACKFILL
| 12LP - Land and Property | Cxxx-NCR-000001 | NCR | Failure of Contractor to undertake adequate inspection of works prior to inviting CRL to witness tests |  | Crossrail | XRL | CWS - Canary Wharf Station |  | 2018-09-30 | 2018-08-31 16:07 | -30 | 2016-09-28 15:49 | Electrical - LV Equipment | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | The Contractor failed to meet his obligations under clause 20.9 of service information 2b in relation to inspection carried out on new A & B power supplies to feed Signalling Equipment in Signalling Equipment Room (SER) on 21/09/16 - Refer to Cxxx-NCR-000002 which details evidence of non conformances within the works when presented to Crossrail
| 12LP - Land and Property | Cxxx-NCR-000002 | NCR | Installation of Power Supplies to __R non-compliant with BS 7671 |  | Crossrail | XRL | CWS - Canary Wharf Station |  | 2016-10-28 | 2017-02-23 18:58 | 118 | 2016-09-28 15:56 | Electrical - LV Equipment | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Following an inspection request CRL MEP Field Engineer attended site to witness live electrical testing. Upon arrival on site it was evident that dead testing had not been undertaken and witnessed by . Being concerned that the ITP was not being followed and the contractor did not seem to be managed, I elected to begin a visual inspection of the installation whereby I found the following: 1. Cables had not been clipped using steel ties in the LV switch room 2. Cables were not clipped at adequate clipping distances prescribed by BS 7671 3. Along the route between the LV Switch Rooms, cable had simply been placed on top of the tray and had not been dressed in neatly or clipped at distances as prescribed by BS 7671 4. In the SSER cables were unsupported beneath the isolators 5. The Isolators were at different heights with one not being level 6. Cores had not been dressed in or terminated neatly within the isolators 7. Fire stopping had been breached and not made good 8, Cables had not been labelled The above are Non Conformances with BS7671 and BS8000 and LU 1-085
| 12LP - Land and Property | Cxxx-NCR-000004 | NCR | Cxxx-WO-00163 Lift bench |  | Contr | COF | CWS - Canary Wharf Station |  | 2021-04-30 | 2021-04-14 15:55 | -16 | 2020-07-27 13:45 | Architectural - Finishes | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Management Problem - Misunderstand the definition of the requirement | Completed |  | On relocating benches Sub contractor has removed the incorrect tiles on level minus 4, this is now being rectified and tiles being replaced by weekend 24/07/20, on completion Crossrail will be invite to witness the rectification works.
| 12LP - Land and Property | Cxxx-NCR-000006 | NCR | Cxxx-WO-00147 – L-4 Handrail Replacement, Prototype Inspection Issues |  | Contr | COF | CWS - Canary Wharf Station |  | 2020-09-09 | 2020-09-03 13:19 | -6 | 2020-08-26 06:57 | Civil - Civil Engineering General | 500 |  | Manufacturing Defect | Reject | 4 (0.5-3k) | Complete | Subcontractor Problems - Insufficient surveillance of subcontractors | Completed |  | Upon inspection of the L-4 balustrade stainless steel handrail prototype with CRL on 21.08.2020, the following issues were found: 1. The welds on one end of the handrail are too large – when butted up to another section they will cause a gap in the joint, it is also not an acceptable finish for an end piece of the handrail. 2. The thickness of the handrail at the bend/radius is notably thinner than the rest of the handrail section – it should be homogenous. These comments have also been raised to the SC and we are awaiting responses. Please see attached images.
| 12LP - Land and Property | Cxxx-NCR-000009 | NCR | Cxxx-WO-00194 – Floor Abrasion Main Works - ITP Hold Point Not Signed Off |  | Contr | COF | CWS - Canary Wharf Station |  | 2020-11-13 | 2020-10-30 11:11 | -14 | 2020-10-08 08:18 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Repair | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | /__ have proceeded to point 8.2 of the Floor Abrasion Works ITP (Cxxx-COF-C-ITP-CR143-50011) without the ITP sections preceding it being physically signed by the Client’s representative. CRL were invited to inspect the benchmark area following the 60 Grit Dixon Abrasion, it is understood that an inspection took place (needs to be confirmed – the SC state that it was visually inspected at the stage) but no official sign off occurred. The ITP is physically signed by __ and up to section 6 of the check sheets, CRL agreed verbally to proceed at this point to section 7 but did not sufficiently follow through with getting the physical signature. From section 7 to section 8.1 it is reported that CRL inspected the works area, but no official confirmation or physical signature was sufficiently sought out by and the SC had proceeded upon verbal instruction from .
| 12LP - Land and Property | Cxxx-NCR-000010 | NCR | Blockwork Blowout - L-2 LV Switch Room/HV Transformer Room |  | Contr | COF | CWS - Canary Wharf Station |  | 2021-03-19 | 2021-03-15 16:10 | -4 | 2020-12-11 13:24 | Health & Safety General | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During installation of new LV CMS in Canary Wharf L-2 LV Switch Room (2/661), operatives were drilling and fixing bolts into the existing blockwork wall. During the process of drilling into the blockwork wall the drill bit was pushed too deep into the wall, possibly with more force than is optimal – thus causing the blockwork wall to spall (blowout) on the opposite side. The blowout side of the drilling occurred into the HV Transformer Room 2 (2/783).
| 12LP - Land and Property | Cxxx-NCR-000011 | NCR | Cxxx-WO-00143 – Bin and MEWP Storage - Storage Room Durbar Plates Installed with Code 3 Design/Fabrication Drawings and Snags |  | Contr | COF | CWS - Canary Wharf Station |  | 2021-07-09 | 2021-10-07 12:58 | 90 | 2021-02-18 14:26 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Regarding WO-143, the storage room durbar plates have been installed with the design/fabrication drawings at code 3. The durbar plates have also been installed with the below snags: 1. Loose fixings 2. Fixtures too close to panel edges, and not uniform 3. Inconsistent and projecting fixings 4. Poor quality countersinking detail 5. Loose/projecting fixings 6. Uneven panels (circa 15mm max) 7. Sharp corners on durbar panels
| 12LP - Land and Property | Cxxx-NCR-000012 | NCR | Contractor has not submitted Assurance in line with the Works Information |  | Crossrail | XRL | CWS - Canary Wharf Station |  | 2021-05-28 | 2021-05-06 21:20 | -22 | 2021-02-26 12:57 | Electrical - General | 500 |  | Documentation and Records | Repair | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | During the quality meeting with (Cxxx) on 9th and 10th February 2021, it was noted that assurance documents required for certificate Record Package listing (Part 2) were submitted prior to the submission of the certificate. This results in rejection of IRNs and delay in assurance process. For work order (Cxxx-WO-00184) related to CAW PtC MEP051 - Replacement of CAW LV Battery Chargers: West & East LV-B LV Battery Charger, four FAT reports (Cxxx-COF-E-RGN-CR143-50063, Cxxx-COF-E-RGN-CR143-50064, Cxxx-COF-E-RGN-CR143-50065 and Cxxx-COF-E-RGN-CR143-50066) should be accepted prior to the installation release (IRN Cxxx-COF-E-NOX-CR143-50024). However, only three FAT reports were issued on eb, with submission dates after the installation inspection. The FAT test completed dated was 06/10/2020 and all four FAT reports were issued on 09/02/2021. The redline drawings (Cxxx-COF-E-DWG-CR143-50024, Cxxx-COF-E-DWG-CR143-50028, Cxxx-COF-E-DWG-CR143-50029 and Cxxx-COF-E-DWG-CR143-50030) related to this work order (Cxxx-WO-00184) were issued on eb date: 21/01/2021 with revision X01. From the work order (Cxxx-WO-00137) Modification to Escape Stair Pressurisation Ductwork, it is noted that ITP deliverable records (Cxxx-COF-M-LRC-CR143-50008) shows handover date to care and custody contract was on 08/12/2020. However, related redline drawings (Cxxx-COF-M-DWG-CR143-50005 and Cxxx-COF-M-DWG-CR143-50006) were submitted on 18/01/2021 revision X01. Similarly, ITP deliverable records and certifications associated with this element of work were not submitted and accepted at the date of handover.
| 12LP - Land and Property | Cxxx-NCR-000013 | NCR | The Contractor was unable to provide a Competency Matrix |  | Crossrail | XRL | CWS - Canary Wharf Station |  | 2021-04-30 | 2021-05-06 21:09 | 6 | 2021-02-26 15:39 | Electrical - General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | During the quality meeting with (Cxxx) on 9th and 10th February 2021, it is noted that work order (Cxxx-WO-00184) related to Cxxx-WO-00184 CAW PtC MEP051 - Replacement of CAW LV Battery Chargers: West & East LV-B LV Battery Charger has expired calibration certificate for equipment Earth Bond Tester (serial no. 12A-0203) when testing and commissioning was carried out for batteries. This certificate was used in all three FAT reports (Cxxx-COF-E-RGN-CR143-50064, Cxxx-COF-E-RGN-CR143-50065, Cxxx-COF-E-RGN-CR143-50066). This does not meet the Inspection and Testing procedure as per CRL Works Information Volume 2B (CRL1-XRL-V3-XWI-CR001-50035), Part 20 – Quality Management, section 20.8 Inspection and Testing, section 28.3 Testing and Commissioning Documentation and section 28.4 Measurements. It is also noted that there was no competency matrix submitted for Cxxx Project.
| 12LP - Land and Property | Cxxx-NCR-000014 | NCR | Cxxx-WO-00196 - Operational and Statutory Signage Scope - Removal of call point signs, incorrect material & sign locations |  | Contr | OVE | CWS - Canary Wharf Station |  | 2021-05-07 | 2021-06-21 14:37 | 45 | 2021-03-29 15:15 | Architectural - Signage | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Management Problem - Misunderstand the definition of the requirement | Completed |  | 1. When installing fire action notices, the existing fire call point signs have been removed. This is not requested in the work order. These signs are still required. 2. Fire call points removed to the FOH at platform level -5. These signs are still required. 3. A refuge point sign at Platform Level -5 has been installed in the incorrect location, meaning that it is not visible when entering the lift lobby through the emergency escape doors.
| 12LP - Land and Property | Cxxx-NCR-000015 | NCR | Blockwork Blowout at various locations |  | Crossrail | XRL | CWS - Canary Wharf Station |  | 2021-07-02 | 2021-06-25 14:58 | -7 | 2021-04-26 14:58 | Health & Safety General | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During installation of new CMS, unistrut sections and cable route penetrations in Canary Wharf Station at various locations, (namely identified during site inspections), locations identified - 2/663, 2/782, 2/665, operatives appear to have been drilling and fixing bolts into the existing blockwork wall. During the process of drilling into the blockwork wall the drill bit was pushed too deep into the wall, possibly with more force than is optimal – thus causing the blockwork wall to spall (blowout) on the opposite side. The blowout side of the drilling has occurred into the locations identified. Photos have been attached. In addition there are also redundant holes that have been made and not fully filled or left and this could contribute to breach in standards. The locations of these as inspected / identified 2/236 passage way outside 2/782 and 2/761, where holes behind unistrut have been left.
| 12LP - Land and Property | Cxxx-NCR-000017 | NCR | WO-00297, AIMS Character Count Exceeded for Interface Unit Naming |  | Contr | COF | CWS - Canary Wharf Station |  | 2022-05-08 | 2022-04-29 08:54 | -9 | 2022-04-20 12:51 | Information Management - Asset Information | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | The character count limit for ‘Interface units - L75541’ referenced in the ADCS name in AIMS is currently set at 3 (largest allowable being INTERFACE UNIT 999). This communication is to confirm that character count of 4 is allowable.
| 12LP - Land and Property | Cxxx-NCR-000018 | NCR | WO-00297, AIMS Cable Labelling Requirement |  | Contr | COF | CWS - Canary Wharf Station |  | 2022-05-08 | 2022-04-29 08:48 | -9 | 2022-04-20 12:56 | Information Management - Asset Information | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Previous Construction - Other | Completed |  | Cxxx-FCD-000300 outlines the current AIMS labelling requirement for cables at Canary Wharf Station. This communication is to reaffirm the agreement set in Cxxx-FCD-000300, that cables will not require AIMS labels on site and the ADCS schedule columns ‘Asset Label Required’ will be updated to ‘No’, and no further works are necessary to correct this non-conformance.
| 03SR - Stations (RfL) | Cxxx-NCR-000001 | NCR | No Pull Out testing being carried out on site |  | Crossrail | XRL | CWS - Canary Wharf Station |  | 2017-10-05 | 2017-10-18 15:36 | 13 | 2017-07-07 12:28 | Electrical - Earthing & Bonding | 0 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Surveillance on Earthing & Bonding was carried out at Canary Wharf Station. We visited two Surface Water Areas located Level -6 East Zone 4 where 100mm tray and both 70mm and 10mm Green/Yellow earth bonding cables had been installed. The Contractor was asked for Pull out Tests records and load calculations for the 100mm tray installation which had been fixed to the concrete soffit via __ HUS 3 fixings and via wood screws to blockwork. No evidence was provided as the Contractor was not aware he had to produce pull out records. Post site visit ITP C841-LEL-E-ITP-CR143-50001 Rev 1.0 was checked and no reference to pull testing could be found.
| 03SR - Stations (RfL) | Cxxx-NCR-000003 | NCR | C522 Newham Wall |  | Contr | DML | CWS - Canary Wharf Station |  | 2019-05-31 | 2019-08-21 13:39 | 82 | 2017-11-16 14:41 | Civil - Civil Engineering General | 500 |  | Incomplete Works | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | The small wall extensions to the left hand side of the columns at Custom House Station, are approx. 50-80mm short of the columns. The coping stones above meet the columns.
| 03SR - Stations (RfL) | Cxxx-NCR-000004 | NCR | Grout Tube Leaking |  | Crossrail | PDP | CWS - Canary Wharf Station |  | 2018-06-13 | 2018-06-22 11:30 | 9 | 2017-11-16 16:39 | Civil - Tunnelling | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Design Problem - Not Defined | Completed |  | The Contractor failed to inspect the completed works after 2 weeks as required in the approved ITP C850-SSL-C-ITP-CR143-50001 and the Design Cxxx-OVE-C4-RGN-CR143-50001 Rev 2.0. Subsequently many of the grouted tubes have be witnessed to be leaking.
| 03SR - Stations (RfL) | Cxxx-NCR-000005 | NCR | C844 - PRV Installation |  | Crossrail | PDP | CWS - Canary Wharf Station |  | 2018-12-14 | 2018-11-14 12:24 | -30 | 2018-01-08 13:18 | Fire - Suppression | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | Further to C844-SVI-00001 , it was discovered on 6th January that the PRV valves on -5 that had previously failed the flow tests were manufactured by JD Fire - which is contrary to the MCR raised CRL-MCR-005071. When tested - these valves failed to achieve the necessary flow rates, which were witnessed from the approved Rapiddrop Valves as per the accepted MCR.
| 03SR - Stations (RfL) | Cxxx-NCR-000006 | NCR | C854 - Lack of NICEIC Accreditation |  | Crossrail | PDP | CWS - Canary Wharf Station |  | 2018-07-31 | 2018-06-22 09:47 | -39 | 2018-01-08 14:18 | Electrical - General | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Not Defined | Completed |  | Under the C854 contract, under JY81 Testing and Commissioning of Electrical Services Crossrail M&W Specification CRL1-XRL-M-RSP-CR001-50087 Version 1.0 JY81 - 5a) The Contractor shall employ a specialist NICEIC approved company to undertake and manage the testing and commissioning of the electrical systems to the satisfaction of the Project Manager. CRL have been made aware that are ECA accredited, not NICEIC accredited.
| 03SR - Stations (RfL) | Cxxx-NCR-000009 | NCR | NCR for Tile Installation on Gateline Level -4 |  | Contr | DML | CWS - Canary Wharf Station |  | 2018-06-14 | 2018-05-31 14:33 | -14 | 2018-02-14 13:57 | Architectural - Flooring | 0 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Not Defined | Completed |  | Tiles have been installed to Gateline -4, without an approval MCR.
| 03SR - Stations (RfL) | Cxxx-NCR-000010 | NCR | NCR for SOR Door Level -4 |  | Contr | DML | CWS - Canary Wharf Station |  | 2018-04-12 | 2018-05-04 10:15 | 22 | 2018-02-14 14:02 | Architectural - Doors | 0 |  | Documentation and Records | Repair | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | There has been additional requirement to apply mastic to the SOR Door and MCR was not completed for this.
| 03SR - Stations (RfL) | Cxxx-NCR-000012 | NCR | MCR for SOR Door |  | Contr | DML | CWS - Canary Wharf Station |  | 2018-04-30 | 2018-05-04 09:49 | 4 | 2018-02-15 15:31 | Architectural - Doors | 0 |  | Incomplete Works | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | SOR Door was installed on site prior to MCR being formally accepted by CRL.
| 03SR - Stations (RfL) | Cxxx-NCR-000013 | NCR | C522 - Cracks to coping stones |  | Contr | DML | CWS - Canary Wharf Station |  | 2018-06-29 | 2018-07-21 11:45 | 22 | 2018-03-20 14:22 | Civil - Civil Engineering General | 10000 |  | Damaged | Repair | 2 (6-60k) | Complete | Design Problem - Other | Completed |  | During the walk along the wall C522 Delatim Project Manager (Robert Pooley) has observed some cracks on top of the coping stones. After full survey of the wall there is 6 locations where cracks have been observed. Please see attached photos on the letter. During initial investigation with __ (coping stone manufacturers) and based on the cracks patterns and location it is very unlikely of manufacturer defect. Confirmation letter from __ attached.
| 03SR - Stations (RfL) | Cxxx-NCR-000014 | NCR | 4x PED Doors (Platform End Doors) |  | Crossrail | XRL | CWS - Canary Wharf Station |  | 2018-05-20 | 2018-06-22 12:45 | 33 | 2018-04-21 11:34 | Architectural - Doors | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | 4x PED doors on Level -5, manufactured and installed on site at Level -5 without Employer acceptance. Contractor proceeded manufacturing of the doors without approval of the manufacturing drawings as per issued instruction. C857-PMI-00006 clearly states that "The Contractor shall survey the platform ends and produce a RIBA Stage F2 design for Employer's acceptance. The Contractor shall not commence fabrication of the PEDs until fabrication drawings are accepted. Any design or construction interface with Cxxx, Cxxx, Cxxx or any other interfacing contract is included in Contractor scope of work. consequences are; -there is a difference between clear structural opening and newly manufactured doors. Doors are too wide (150mm-200mm) -Door push bar clashes with RC concrete wall -Telephone cabinet and surrounding claddings impacted.
| 03SR - Stations (RfL) | Cxxx-NCR-000015 | NCR | Missing Washers on PES Grill Bracket installtion Works ~ Level -5 |  | Crossrail | XRL | CWS - Canary Wharf Station |  | 2018-05-07 | 2018-07-16 16:25 | 70 | 2018-04-23 12:46 | Structural Engineering - Bolted Connections | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | PES Grill Hanging Brackets installed to unistrut frames without standard washers. Lock washers seems had installed incorrectly. CRL believes installation doesn't meet the requirements.
| 03SR - Stations (RfL) | Cxxx-NCR-000016 | NCR | C857 - No MCR raised against Bostwick Gates Secondary Steel Sofit fixings |  | Contr | DML | CWS - Canary Wharf Station |  | 2018-10-18 | 2018-08-16 09:17 | -63 | 2018-05-21 14:54 | Architectural - General | 500 |  | Documentation and Records | Repair | 4 (0.5-3k) | Complete | Procedure Problem - Lack of procedure | Completed |  | During verification of site files the Contractor realised that sofit fixings installed as per design drawing C857-DML-A-DWG-CR143-50020 have been installed without valid MCR. In addition the ITP C857-DML-A-ITP-CR143-50006 refers to chemical anchore, which is incorrect and needs updating.
| 03SR - Stations (RfL) | Cxxx-NCR-000017 | NCR | C853 FAT/FAC ‘draft’ and ‘not approved’ for PFC and HF Units which have been installed in the works |  | Crossrail | XRL | CWS - Canary Wharf Station |  | 2018-06-08 | 2018-06-11 15:20 | 3 | 2018-05-29 10:17 | Electrical - LV Equipment | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Lack of procedure | Completed |  | A planned Crossrail surveillance was undertaken on 11th May which looked at C853 ’s Electrical installation. This included the installation of PFC and HF units in Switch Rooms at Level -2 (LV West A and B). A request was made for the Factory Acceptance Testing/Factory Acceptance Certificate for the installed PFC and HF units, as required by Works Information Part 28.2.2.1 Phase 1 – Factory Acceptance Tests which states; “Factory acceptance tests (FATs) shall be satisfactorily completed by the Contractor before shipment to Site and/or the Working Areas of any item of Plant and Materials in order to verify that it and its components are fit for its or their intended use and otherwise comply with the Works Information.” The Contractor made available submission; Factory Test Certificate - PFC & HFC units (WP32b and WP32d) C853-DRN-E-LRC-CR143-50044 at Rev 1, which on review was at ‘Draft’ and ‘Not Approved’ status. The units were delivered March 18 and have been installed without confirmation of acceptance which induces a risk to the project (until accepted) and does not meet the Contract requirements. Moreover, the ITP for this installation (50003) does not include FAT as a pre construction activity, which would typically include a Hold Point prior to installation.
| 03SR - Stations (RfL) | Cxxx-NCR-000018 | NCR | C853 No CRL Hold Point intervention for PFC and HF installation as required by the ITP |  | Crossrail | XRL | CWS - Canary Wharf Station |  | 2018-06-26 | 2018-06-22 09:53 | -4 | 2018-05-29 10:23 | Electrical - LV Equipment | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Lack of procedure | Completed |  | A planned Crossrail surveillance was undertaken on 11th May which looked at C853 ’s Electrical installation. This included the installation of PFC and HF units in Switch Rooms at Level -2 (LV West A and B). ’s provided completed check sheets CS006, CS001 and CS005 which covered installation of CMS, cables and PFC and HF units defined in ITP Power factor correction & Harmonic filtration ITP C853-DRN-E-ITP-CR143-50003 at Rev1. On checking the ITP, it was found that Inspection Numbers 12-14 included a Hold Point for both ’s and CRL. On review the check sheets completed only included ’s sign off; no CRL intervention had been recorded. A Hold Point is a mandatory intervention and is defined as ‘a point beyond which the Contractor’s work shall not proceed without attendance of the designated organisation as identified in the ITP’. It should be discussed how these Hold Points can be captured post installation; including how future Hold Points will be notified/met for other works.
| 03SR - Stations (RfL) | Cxxx-NCR-000019 | NCR | MAP Fire / Smoke damper |  | Crossrail | XRL | CWS - Canary Wharf Station |  | 2019-01-31 | 2019-01-29 09:05 | -2 | 2018-07-26 14:02 | Fire - Compartmentation | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | No Installation drawings available to site team, MAP dampers are not being installed on L-4 to manufacturers installation requirements
| 03SR - Stations (RfL) | Cxxx-NCR-000020 | NCR | CMS |  | Crossrail | XRL | CWS - Canary Wharf Station |  | 2019-01-31 | 2019-03-22 12:28 | 50 | 2018-07-26 14:16 | Communications and Control Systems - SCADA/Central Management System | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Not Defined | Completed |  | Conduit installed, __ galvanizing protection omitted on joints, bare threads and bends / double sets Studding hangers have been left too long and too short in all areas, along with cuts ends again without __ galvanized protection. __ requires protection as well. The site survey was to confirm scaffolds on L-4 & 5 could be dismantled for , the survey was stopped after inspecting works above 3 scaffolds as all the snagging was the same, contractor to inspect all installations where scaffold was enabled to confirm snags are complete before CRL return to confirm.
| 03SR - Stations (RfL) | Cxxx-NCR-000021 | NCR | Installation of non-compliant cable for signage |  | Contr | MSL | CWS - Canary Wharf Station |  | 2018-08-31 | 2018-08-07 09:06 | -24 | 2018-06-12 08:59 | Architectural - Signage | 500 |  | Material | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Use of unapproved materials | Completed |  | We have installed Niltox-319 cable on site to carry power from the spur positions to the sign positions. We have also used Niltox-319 cable in the production of our signs (internal wiring). We have been advised that this cable is non-compliant and needs to be changed for a suitable alternative. Please note that the cable has not been connected to the spurs at this point in time.
| 03SR - Stations (RfL) | Cxxx-NCR-000022 | NCR | C857 - NCR Installation of Stainless Steel Trim to Curve Column Cladding Level -5 |  | Contr | DML | CWS - Canary Wharf Station |  | 2018-07-31 | 2018-07-31 10:40 | 0 | 2018-06-14 11:52 | Architectural - General | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Procedure Problem - Lack of procedure | Completed |  | NCR raised for the installation of stainless steel trims to the curve column cladding on level -5. The site operatives undertaking the installation did not have a hard copy of the ITP on their person when undertaking the installation. The works were stopped by CRL until ITP could be issued to them for their inspection.
| 03SR - Stations (RfL) | Cxxx-NCR-000024 | NCR | The Contractor was unable to supply evidence of Signage Benchmarks acceptance. |  | Crossrail | XRL | CWS - Canary Wharf Station |  | 2018-08-17 | 2018-08-09 12:54 | -8 | 2018-06-28 10:36 | Architectural - Signage | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Lack of procedure | Completed |  | A planned Crossrail surveillance was undertaken on 27th June 2018 at Cxxx Canary Wharf Station to look at the installation of Signage. On request the Contractor unable to produce evidence of acceptance for Station Signage Quality Benchmarks as such it could not be verified that any Quality Benchmarks has been completed.
| 03SR - Stations (RfL) | Cxxx-NCR-000025 | NCR | The Contractor was unable to supply evidence of Signage Prototype acceptance |  | Crossrail | XRL | CWS - Canary Wharf Station |  | 2018-07-26 | 2018-07-23 15:07 | -3 | 2018-06-28 10:41 | Architectural - Signage | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Procedure Problem - Other | Completed |  | A planned Crossrail surveillance was undertaken on 27th June2018 at Cxxx Canary Wharf Station to look at the installation of Signage. On request the Contractor unable to produce evidence of acceptance for Station Signage Prototypes, as such it could not be verified that acceptance was in place.
| 03SR - Stations (RfL) | Cxxx-NCR-000026 | NCR | Contractors has not installed anti vibration washers as shown on signage design drawing |  | Crossrail | XRL | CWS - Canary Wharf Station |  | 2018-11-30 | 2018-10-16 09:27 | -45 | 2018-07-02 07:05 | Architectural - Signage | 1000 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | A planned Crossrail surveillance was undertaken on 27th June2018 at Cxxx Canary Wharf Station to look at the installation of Signage. On checking information obtained during the surveillance it was found that Help Point sign number 16 had not been installed inline with drawing C849-MSL-A-DWG-CR143-50339. The bracket connection to the wall is shown to have M12 bolts with M12 Nordlock anti vibration washers, it was witnessed that M12 bolts with ordinary washers had been installed. As the surveillance was based on a sample, other signs should be checked and confirmed as part of closure to this NCR.
| 03SR - Stations (RfL) | Cxxx-NCR-000027 | NCR | Cable Management Systems (CMS) Not Fire-Stopped to Tube Line Specification |  | Contr | FSL | CWS - Canary Wharf Station |  | 2018-06-29 | 2019-04-29 10:33 | 304 | 2018-07-09 12:08 | Fire - Compartmentation | 1000 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Design Problem - Not Defined | Completed |  | Cable Management Systems (CMS) with no lids in place through penetrations have been fire-stopped with __ compound direct on to the cables. This is not Tube Line specification.
| 03SR - Stations (RfL) | Cxxx-NCR-000028 | NCR | Contractor was unable to supply Offsite Manufacturing records |  | Crossrail | XRL | CWS - Canary Wharf Station |  | 2019-01-31 | 2019-07-26 13:06 | 176 | 2018-07-10 13:44 | Architectural - Signage | 500 |  | Documentation and Records | Repair | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | On request the Contractor was unable to supply Offsite Manufacturing records; Weld Procedure Specification (WPS), Welder Qualification Record inline with the WPS and Galvanising information regarding the thickness to be applied and the Certificate of Conformity (CoC) from the galvanising sub contractor stating the thickness applied. In addition the Contractor was requested to confirm if any signs have steel elements classed as structural to confirm compliance against BS EN 1090 and the Construction Products Regulations (for CE Marking). If steelwork is classified as ‘structural’ a design Execution Class (EXC) to BS EN 1090 will be required. Moreover the __s Factory Production Control (FPC) Certificate (produced by Notified Body), Responsible Weld Coordinator (RWC) Certificate and evidence that a Declaration of Performance (DoP) would be required. The Contractor is to confirm with CRL/Cxxx whether any steel as part of the signage design is classed as ‘structural’ as part of closure to this NCR. If confirmed, documentation as noted should be presented to provide the level of assurance required. It should be noted that Cxxx Specification JN15 sections JN15.1227, JN15.1228, JN15.1232, JN15.1233, JN15.1234 and JN15.1235 detail elements as structural.
| 03SR - Stations (RfL) | Cxxx-NCR-000029 | NCR | HV Cables Require Sleeve Through Penetrations |  | Contr | FSL | CWS - Canary Wharf Station |  | 2018-12-21 | 2019-02-05 17:21 | 46 | 2018-07-11 10:50 | Fire - Compartmentation | 1000 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | HV cables have been installed without a sleeve or trunking around them through penetrations. Fire stopping the cables with compound direct, is not Tube Line specification compliant. The addition of some form of sleeve or boxing will be required prior to fire-stopping works proceeding.
| 03SR - Stations (RfL) | Cxxx-NCR-000030 | NCR | Pull Testing is being completed without evidence of competance |  | Crossrail | XRL | CWS - Canary Wharf Station |  | 2018-08-10 | 2018-08-07 09:17 | -3 | 2018-07-13 13:45 | Architectural - Signage | 500 |  | Testing and Commissioning | Rework | 4 (0.5-3k) | Complete | Training Deficiency - No training provided | Completed |  | A planned Crossrail surveillance was undertaken on 27th June2018 at Cxxx Canary Wharf Station to look at the installation of Signage. At the time of the surveillance the Contractor is unable to provide evidence of the competency of the operative that has carried out pull testing on signage fixings.
| 03SR - Stations (RfL) | Cxxx-NCR-000032 | NCR | C857 - Stainless Steel Head Detail to Ticket Vending Machines on Level -4 |  | Contr | DML | CWS - Canary Wharf Station |  | 2018-12-21 | 2018-11-09 10:07 | -42 | 2018-08-06 09:10 | Architectural - General | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Delatim has manufactured and installed Stainless Steel Head Detail panels to Ticket Vending Machines on Level -4 in accordance with code 1 C857-DML-A-DWG-CR143-50008 P03. Due to site conditions panels are to big and do not achieve Cxxx design intent (10 mm shadow gap is compromised) Cxxx-OVE-A-DDD-CR143_5-00269 and Cxxx-OVE-A-DDD-CR143_5-00279. A RFI Cxxx-RFI-000573 have been raised. The outcome is that the panels need to be re-manufactured and re-installed.
| 03SR - Stations (RfL) | Cxxx-NCR-000033 | NCR | C857 - Over-torque fixings to Bostwick secondary steel supports |  | Contr | DML | CWS - Canary Wharf Station |  | 2018-12-21 | 2018-11-14 12:42 | -37 | 2018-08-15 14:03 | Architectural - General | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Not Defined | Completed |  | 1 of 4 fixing at each connection location between RC ceiling and Secondary Steele has been torqued to 140 Nm value, as per attached report from date 21-07-2018. __ recommendation for __ HST-HCR M16 fixings is 110 Nm. Remaining 3 fixings have been torque to value 110 Nm as per attached torque report dated 09-08-2018, and witnessed by Mehmet Keles (CRL package manager). __ made additional calculations, attached, which states that there is enough capacity to transfer the loads on three fixings, making one over-torque redundant, subject to exchange the washers and apply chemical resin to washers.
| 03SR - Stations (RfL) | Cxxx-NCR-000034 | NCR | Incorrect Wieland Plug & Play connectors installed in signage |  | Contr | MSL | CWS - Canary Wharf Station |  | 2018-12-21 | 2018-11-15 13:18 | -36 | 2018-08-15 17:17 | Architectural - Signage | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The “plug and play” fittings (Wieland plugs) on the illuminated signage have been identified as non compliant to BS 6761. The plug that is connected to the 240v mains supply has exposed pins, meaning that someone could possibly remove the plug, touch the pins and give themselves a shock. Even though this arrangement was present in the prototypes accepted by Cxxx and that our O&M will detail that all signs are to be isolated from the supply before any works are undertaken, it doesn’t change the fact that the current arrangement is in breach of BS 7671. These plug and play connectors are therefore not considered not fit for purpose and need to be changed.
| 03SR - Stations (RfL) | Cxxx-NCR-000035 | NCR | C851 Unfinished Drywall In Electrical Cupboards 5216 & 5416 |  | Contr | FSL | CWS - Canary Wharf Station |  | 2019-05-31 | 2019-07-18 09:31 | 48 | 2019-01-15 14:32 | Fire - Compartmentation | 0 |  | Incomplete Works | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Examples of green plasterboard with no finishing coatings identified at various locations. Photo's uploaded at T.Afloabi's request.
| 03SR - Stations (RfL) | Cxxx-NCR-000036 | NCR | C857 - PED door VE cladding adhesive failure |  | Contr | DML | CWS - Canary Wharf Station |  | 2019-03-29 | 2019-05-28 10:43 | 60 | 2018-08-22 14:53 | Architectural - General | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The Contractor, approx. 4 weeks ago has installed VE cladding to PED (Platform End Doors) using Bostik Evo-Stik Adhesive, C857-DML-A-MCR-CR143-50025. During recent site inspection we observed that VE panels start peeling off from PED doors. The Contractor is proposing to remove VE cladding and use __Tack-Panel System instead of existing adhesive. __Tack-Panel System has been used and accepted on Custom House Station, MCR attached
| 03SR - Stations (RfL) | Cxxx-NCR-000037 | NCR | MCRs not approved prior to installation on site |  | Crossrail | XRL | CWS - Canary Wharf Station |  | 2019-01-18 | 2019-03-26 10:55 | 67 | 2018-09-10 12:14 | Mechanical - Piping | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Other | Completed |  | During a Crossrail surveillance at Canary Wharf station on Eton Fire installation MCRs were checked. It was found that CRL-MCR-006812 for PE100 Gapping Pipe and CRL-MCR-006731 Delta Type Pressure Regulating Valve were not approved. The material was installed on site at the time of the surveillance. Therefore as materials have been installed without prior approval of the MCR there has been a breakdown in the ITP procedure; MCR approval is a hold point preceding site installation.
| 03SR - Stations (RfL) | Cxxx-NCR-000038 | NCR | Short Radius Pipe Bends installed on site |  | Crossrail | XRL | CWS - Canary Wharf Station |  | 2019-05-31 | 2019-07-19 13:42 | 49 | 2018-09-10 12:59 | Mechanical - Public Health Engineering | 10000 |  | Incorrect Installation | Use As-Is | 2 (6-60k) | Complete | Design Problem - Other | Completed |  | During a Crossrail surveillance at Canary Wharf station on Eton Fire installation Pipe Bends were checked outside Level -3 room 3462A. It was found that short bend radius fittings had been installed. This contravenes Material and Workmanship Specification for Wet and Dry Risers/Falling Fire mains JS61.1301: “l) All bends shall be of long radius type”. Therefore in its current state, the installation is non-compliant.
| 03SR - Stations (RfL) | Cxxx-NCR-000039 | NCR | Air Release Valves not on Drawing |  | Crossrail | XRL | CWS - Canary Wharf Station |  | 2018-12-21 | 2019-04-23 14:17 | 123 | 2018-09-10 13:48 | Mechanical - Public Health Engineering | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | During a Crossrail surveillance at Canary Wharf station on Eton Fire installation fire hydrants were checked. The most current drawing for the installation is Cxxx-OVE-P-DDE-CR147_Z-43100. On the drawing the hydrants do not show ARVs however they are installed on site on top of the hydrants. As this change has not been captured through the FCD process there has been a breakdown in the control of drawings.
| 03SR - Stations (RfL) | Cxxx-NCR-000040 | NCR | Fire Dampers Installed Incorrectly |  | Crossrail | XRL | CWS - Canary Wharf Station |  | 2019-01-25 | 2019-01-29 09:19 | 4 | 2018-09-24 11:40 | Fire - Detection | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Following site survey carried out with CRL, a number fire dampers installed on level -4 have not been installed against the wall as per instruction given by CRL. Crossrail have provided the manufacturers installation details for Fire Dampers which needs to be implemented.
| 03SR - Stations (RfL) | Cxxx-NCR-000041 | NCR | Wrong Installation on Site for LV Board A |  | Crossrail | XRL | CWS - Canary Wharf Station |  | 2019-03-29 | 2019-07-26 06:52 | 119 | 2018-09-27 09:01 | Electrical - LV Equipment | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Information not detailed | Completed |  | During the FAT testing carried out by __, we noticed an instance on LV Board A where the MCCB status’s from cubicle 18 has been wired into the wrong terminals in the BMS Marshalling Box section of the LV Board.
| 03SR - Stations (RfL) | Cxxx-NCR-000042 | NCR | LV Panel Switch Defects |  | Crossrail | XRL | CWS - Canary Wharf Station |  | 2019-03-29 | 2019-07-28 13:15 | 121 | 2018-09-28 15:39 | Electrical - LV Equipment | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Following site installation carried out on LV panel switch, a number of defects have been identified which includes the following: - Insufficient internal CMS to din rail connections - Cabling not dressed neat & tidy/obscuring terminations - Modbus cabling screens not sleeved - Plastic cable ties & cabling accessories (non CRL complaint) - Cable indents missing
| 03SR - Stations (RfL) | Cxxx-NCR-000044 | NCR | C855 - ITP not in place prior to works commencing |  | Contr | SCH | CWS - Canary Wharf Station |  | 2018-12-21 | 2019-03-22 18:47 | 91 | 2018-10-24 14:11 | Mechanical - Escalators | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Procedure Problem - Lack of procedure | Completed |  | Schindler have proceeded to start works on site without a code 1 ITP being put in place
| 03SR - Stations (RfL) | Cxxx-NCR-000045 | NCR | C855 - Works proceeding on Escalator anti fall barriers without approved design |  | Contr | SCH | CWS - Canary Wharf Station |  | 2018-12-21 | 2019-03-22 10:19 | 91 | 2018-10-24 14:40 | Mechanical - Escalators | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Procedure Problem - Lack of procedure | Completed |  | Works are underway to manufacture and install anti-fall barriers on the escalators, however the design has not been accepted as yet.
| 03SR - Stations (RfL) | Cxxx-NCR-000046 | NCR | C855 - Works proceeding ahead of MCR acceptance |  | Contr | SCH | CWS - Canary Wharf Station |  | 2018-12-21 | 2019-03-22 10:45 | 91 | 2018-10-24 14:45 | Mechanical - Escalators | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Procedure Problem - Lack of procedure | Completed |  | Works have proceeded with the manufacture and installation of a new anti-fall barrier on the escalators without MCRs being in place and accepted by Crossrail.
| 03SR - Stations (RfL) | Cxxx-NCR-000047 | NCR | Incorrect allignement of Infill panels above EDNE/Fascia signs Level -1 |  | Crossrail | XRL | CWS - Canary Wharf Station |  | 2019-04-30 | 2019-04-05 12:23 | -25 | 2018-10-30 14:00 | Architectural - Ceilings & Soffits | 500 |  | Design | Repair | 4 (0.5-3k) | Complete | Procedure Problem - Other | Completed |  | Following site inspections with the signage installation contractor, CRL realised that new manufactured infill panels above the EDNE/Fascia signs and the inside face of Bostwick Gates installed by Delatim, do not appear to align with the existing larger panels on the outside of Bostwick Gates ceiling end panels / soffits, that Delatim have just reinstalled.
| 03SR - Stations (RfL) | Cxxx-NCR-000048 | NCR | CMS Access Stepovers on Level -6 signage |  | Contr | VLK | CWS - Canary Wharf Station |  | 2019-08-08 | 2019-08-07 15:15 | -1 | 2018-11-01 11:19 | Architectural - General | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | C853 have installed access stepovers for walking over services installed at floor level. This is on West level -6. During the site inspection with Suhail Younis it was confirmed that appropriate signage should be installed to warn users of services at head height and steps. Requirement of signage was not included within design document: Cxxx-OVE-A-RGN-CR143-50005 WP61. Signage should be installed by an experienced architectural contractor on site. Please refer to redline drawing: C853-DRN-A-DWG-CR143-50001 X01 And inspection record: C853-DRN-A-LRC-CR143-50001
| 03SR - Stations (RfL) | Cxxx-NCR-000049 | NCR | Holes drilled onto new installed SOR Door at Lev -4 (Room 4460A) |  | Crossrail | XRL | CWS - Canary Wharf Station |  | 2018-03-30 | 2019-07-26 12:27 | 483 | 2018-10-31 17:25 | Architectural - Doors | 15000 |  | Damaged | Rework | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Delatim installed SR3 Security rated and 60 minutes Fire rated CRL compliant door in SOR Room at Lev-4. it was observed by site team that MEP contractor "" have drilled into door to install a cable for the release mechanism on the door. Further from investigations and Paul Doyle`s report via email, 2x 5mm dia. holes drilled into door for conduit brackets fixing with 20mm penetration into door body. CRL hesitates that this will compromise and invalidate the certification of the door.
| 03SR - Stations (RfL) | Cxxx-NCR-000050 | NCR | Shadow Gap devaition on Columns Level -5 (Platfrom Level) |  | Crossrail | XRL | CWS - Canary Wharf Station |  | 2019-05-31 | 2019-07-01 12:07 | 31 | 2018-11-08 15:56 | Architectural - Finishes | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Stainless Steel (SS) cladding installation around square column S4 was checked. The roundel had been installed (by others) and upper and lower SS panels installed by Delatim. The panels had been fixed to the column concrete using existing supports. On inspection, it was found that the joint distance between the roundel and cladding panel appeared to be inconsistent from left side to right side, in some areas approx... 9mm. On checking drawing ‘Platform Level -5 Signage and Wayfinding’ Cxxx-OVE-A-DDD-CR143_6-00211 (P02) it was found that the joint should be a 3mm shadow gap with no +/- tolerance. Furthermore, drawing C857-DML-A-DWG-CR143-50002 (P02) at Code 2 also defines a 3mm gap
| 03SR - Stations (RfL) | Cxxx-NCR-000051 | NCR | BMS labelling & identification |  | Crossrail | XRL | CWS - Canary Wharf Station |  | 2019-03-29 | 2019-01-30 12:41 | -58 | 2018-11-09 16:14 | Communications and Control Systems - General | 500 |  | Incomplete Works | Rework | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | BMS CMS, cabling & equipment not labeled in accordance with Crossrail Specification CRL1-XRL-M-RSP-CR001-50088
| 03SR - Stations (RfL) | Cxxx-NCR-000058 | NCR | Identification JY 82 |  | Crossrail | XRL | CWS - Canary Wharf Station |  | 2018-12-11 | 2019-01-29 09:46 | 49 | 2018-11-27 15:24 | Fire - Detection | 500 |  | Incomplete Works | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Assets installed by inspected IRN walk down 23.11.18 not labeled in accordance with CRL1-XRL-M-RSP-CR001-50088 JY 82. including no Permanente or temporary labeling to equipment locations 3206, 3210, 3462, 3403, 3510
| 03SR - Stations (RfL) | Cxxx-NCR-000059 | NCR | Fire Systems - Identification non compliant to JY 82 CRL1-XRL-M-RSP-CR001-50088 |  | Crossrail | XRL | CWS - Canary Wharf Station |  | 2018-12-11 | 2019-03-22 12:35 | 101 | 2018-11-27 15:36 | Fire - Detection | 500 |  | Incomplete Works | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Fire Systems CMS, cabling and equipment inspected during formal IRN walkdown 23.11.18 not labeled in accordance with JY 82 CRL1-XRL-M-RSP-CR001-50088
| 03SR - Stations (RfL) | Cxxx-NCR-000060 | NCR | CMS not designed & installed in accordance with CRL JY63 & JY90 |  | Crossrail | XRL | CWS - Canary Wharf Station |  | 2019-02-28 | 2019-07-18 09:25 | 140 | 2018-11-27 15:58 | Electrical - Cable Management | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Fire detection & LV power CMS & support systems forming part of IRN walk down 23.11.18 locations 3206, 3210, 3462 & 3403 not designs & installed in accordance with CRL specs CRL1-XRL-M-RSP-CR001-50089 JY 90 & CRL1-XRL-M-RSP-CR001-50081 JY63; Load calculations and proposed support systems shall be submitted for approval before installation commences - Outstanding No fire stopping or details of fire stopping added to CWS fire stopping register. Insufficient brackets. Fixings loading details matrix O/S
| 03SR - Stations (RfL) | Cxxx-NCR-000061 | NCR | Fire Damper Control Panels |  | Crossrail | XRL | CWS - Canary Wharf Station |  | 2019-02-28 | 2019-03-22 12:47 | 22 | 2018-11-29 09:05 | Fire - Compartmentation | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Procedure Problem - Other | Completed |  | installation of fire damper control panels has utilized porcelain connector blocks not fixed identified during IRN site walk down 23.11.18. state fixed din rail connectors to be installed to rectify this issue however these are not as per approved fire damper panel FAT/MCR. to update & submit relevant MCR/FCD for approval.
| 03SR - Stations (RfL) | Cxxx-NCR-000062 | NCR | Lighting not Installed as per Design |  | Crossrail | XRL | CWS - Canary Wharf Station |  | 2019-01-31 | 2019-06-24 08:00 | 144 | 2018-11-30 10:13 | Electrical - Lighting | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Following an inspection carried out on level -2 TVF plant room we discovered an installation issue. The rear of the TVF fans at level -2 is very narrow and could not be lit in the same way as level -4. This narrow area requires the provision of spot lights which were envisaged to be mounted below the CMS at 2.5m AFFL according to the notes at either end of the linear fittings and setup so light is thrown parallel to the wall. These fittings are currently mounted 4.5m+ AFFL. They are only 16W fittings and will not provide the required light levels at the increased mounting height and light cannot be directed parallel to the wall without overshadowing from the installed CMS
| 03SR - Stations (RfL) | Cxxx-NCR-000063 | NCR | Fire Systems CTP NOT APPROVED |  | Crossrail | XRL | CWS - Canary Wharf Station |  | 2018-12-17 | 2019-01-29 12:07 | 43 | 2018-12-03 12:01 | Fire - Detection | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Other | Completed |  | fire systems test & commissioning plan C854-SEP-E1-STP-CR143-50001 (3.0) is currently code 3 not approved have been progressing test & commissioning fire systems without an approved document.
| 03SR - Stations (RfL) | Cxxx-NCR-000064 | NCR | TVS 110v power CMS |  | Crossrail | XRL | CWS - Canary Wharf Station |  | 2018-12-18 | 2019-03-22 12:58 | 94 | 2018-12-04 07:52 | Electrical - General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Room 1206 & 1211 50mm x 50mm CMS serving TVS 110v socket outlets incorrectly installed, poor workmanship; Lid missing Bends lid missing Gaps on connections exceeding 1mm End cap missing & CMS not cut square
| 03SR - Stations (RfL) | Cxxx-NCR-000065 | NCR | Surface Water Pump Panels |  | Crossrail | XRL | CWS - Canary Wharf Station |  | 2018-12-21 | 2019-03-22 12:49 | 91 | 2018-12-07 09:26 | Electrical - Cable Management | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | CMS (conduits & __) glands not installed in accordance with CRL JY60 CRL1-XRL-M-RSP-CR001-50079, poor workmanship including loose glands, loose conduits & conduit boxes not adequately fixed, general swarf & debris left inside surface water pump panels.
| 03SR - Stations (RfL) | Cxxx-NCR-000066 | NCR | __ Surface Water Pump Panels |  | Crossrail | XRL | CWS - Canary Wharf Station |  | 2019-03-29 | 2019-03-09 09:34 | -20 | 2018-12-07 09:37 | Communications and Control Systems | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | __ BMS __ glands not installed correctly, BMS control cables within panels untidy, PVC tape markers on cores, require corrective actions
| 03SR - Stations (RfL) | Cxxx-NCR-000068 | NCR | EDNE Signs |  | Crossrail | XRL | CWS - Canary Wharf Station |  | 2018-12-28 | 2019-01-29 11:13 | 32 | 2018-12-14 14:27 | Fire - Fire Systems & General | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | signs installation & coordination with Signs.
| 03SR - Stations (RfL) | Cxxx-NCR-000069 | NCR | C857 - Benches brush finish |  | Contr | DML | CWS - Canary Wharf Station |  | 2019-01-31 | 2019-02-25 15:21 | 25 | 2018-12-14 14:39 | Architectural - Finishes | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Brush finish on benches is top-bottom rather that left-right as detailed on accepted drawing C857-DML-A-DWG-CR143-50035
| 03SR - Stations (RfL) | Cxxx-NCR-000070 | NCR | Map Fire Dampers |  | Crossrail | XRL | CWS - Canary Wharf Station |  | 2019-04-30 | 2019-06-07 15:23 | 38 | 2019-01-23 08:10 | Fire - Compartmentation | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Damper re-installed by contractors with new shim plate but using non - compliant wall duct, bolts to shim plate fitted wrong way around generally the damper has been re-installed, which does not comply to manufacturers installation detail
| 03SR - Stations (RfL) | Cxxx-NCR-000071 | NCR | Power supply for __ server |  | Crossrail | XRL | CWS - Canary Wharf Station |  | 2019-03-29 | 2019-01-30 07:54 | -58 | 2019-01-23 18:41 | Electrical - LV Equipment | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Not Defined | Completed |  | have progress through with installation of 13 amp fused connection unit for __ server without an approved design
| 03SR - Stations (RfL) | Cxxx-NCR-000073 | NCR | Hydrant valve leaking |  | Crossrail | XRL | CWS - Canary Wharf Station |  | 2019-05-31 | 2019-08-19 06:36 | 80 | 2019-02-05 15:26 | Fire - Fire Systems & General | 500 |  | Manufacturing Defect | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | L-5 LV 10 hydrant valve leaks when the valve is turned on, leak comes from connection between valve handle spindle and valve body ( (not the stuffing gland)
| 03SR - Stations (RfL) | Cxxx-NCR-000074 | NCR | JD Fire hydrant valve housings have been drilled out to accept new hydarnt valve |  | Crossrail | XRL | CWS - Canary Wharf Station |  | 2019-05-31 | 2019-09-27 15:28 | 119 | 2019-02-05 16:03 | Fire - Fire Systems & General | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Improper preservation of material after installation | Completed |  | Fire rated hydrant housings have been drilled out at the bottom of the cabinet this has now breeched the integrity of the fire rated cabinets
| 03SR - Stations (RfL) | Cxxx-NCR-000076 | NCR | Surface Water Pump Panel non conformance to CRL Specification |  | Contr | SEP | CWS - Canary Wharf Station |  | 2019-04-30 | 2019-05-07 11:25 | 7 | 2019-02-21 12:14 | Electrical - General | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Surface Water Pump Panels installed in Canary Wharf Station does not fully comply to CRL Specification CRL1-XRL-M-RSP-CR001-50116. Review events are detailed in MCR CRL-MCR-005772.
| 03SR - Stations (RfL) | Cxxx-NCR-000079 | NCR | Approved ITP and Design for CMS Works |  | Crossrail | XRL | CWS - Canary Wharf Station |  | 2019-07-25 | 2019-07-19 07:36 | -6 | 2019-02-27 08:59 | Electrical - Cable Management | 0 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Trial activity being carried out on site as part of CMS support works. The design for this work is yet to be approved by CEG however the work has progressed as part of a trial. ITP for these works needs to be updated to reflect design intent particularly for mechanical fixings to be used.
| 03SR - Stations (RfL) | Cxxx-NCR-000081 | NCR | STation Hydrant break tanks |  | Crossrail | XRL | CWS - Canary Wharf Station |  | 2019-05-31 | 2019-07-26 16:05 | 56 | 2019-03-05 15:50 | Fire - Suppression | 500 |  | Incomplete Works | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Drawing 61101-6510-00119 indicates Insulation to Hydrant Break tanks, this has not been carried out
| 03SR - Stations (RfL) | Cxxx-NCR-000083 | NCR | Commencement of work wih out an approved ITP |  | Crossrail | XRL | CWS - Canary Wharf Station |  | 2019-04-11 | 2019-07-25 07:40 | 105 | 2019-03-14 14:12 | Electrical - Power Distribution | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | During a planned surveillance of the installation by , it was noted on review of the ITP C853-DRN-E-ITP-CR143-50011 Rev 2.0 that the document was at Code 3. Work was being competed without an approved ITP. Section 20.4 of Works Information Volume 2B states that “Contractor shall not start any activity on any part of the works for which the Contract Quality Plan, applicable QSP’s or ITP’s are not accepted by the Project Manager. …”
| 03SR - Stations (RfL) | Cxxx-NCR-000084 | NCR | LV Switch Panels Functionality |  | Crossrail | XRL | CWS - Canary Wharf Station |  | 2019-05-07 | 2019-07-23 12:58 | 77 | 2019-04-23 11:09 | Electrical - Switchgear | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | When SCADA commands LV switch panels A & B East & West automatic bus couplers to open the manual bus coupler opens as well, this shouldn’t happen. The operation of the Incoming ACB’s is correct.
| 03SR - Stations (RfL) | Cxxx-NCR-000085 | NCR | C857 - Incorrect fixings used for CMS support system |  | Contr | DML | CWS - Canary Wharf Station |  | 2019-08-07 | 2019-07-19 11:02 | -19 | 2019-04-29 14:01 | Architectural - General | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | The Contractor has been using incorrect fixings for section of CMS support system (__ HKD) in corridor 5202 Level -2 west. The correct fixings, as per ITP C857-DML-A-ITP-CR143-50029 R2, should be __ HST3. The Contractor is in process or removing of incorrect fixings and replace with correct __ HST3
| 03SR - Stations (RfL) | Cxxx-NCR-000086 | NCR | __ Panels |  | Crossrail | XRL | CWS - Canary Wharf Station |  | 2019-07-05 | 2019-07-24 07:36 | 19 | 2019-05-02 11:34 | Fire - Detection | 500 |  | Material | Repair | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | Fire systems __ panels installation by not in accordance with MCR MCR-0006705 • __ Panel 7 - C854-SEP-E-RGN-CR143-50095 – Location of Panel Corridor 4110 – Room Volume 532m3 (room volume taken from Cxxx-XRL-O-TSC-CR143-50001 Rev 2.0) • __ Panel 8 - C854-SEP-E-RGN-CR143-50096 – Location of Panel Corridor 4204 – Room Volume 236m3 (room volume taken from Cxxx-XRL-O-TSC-CR143-50001 Rev 2.0) • __ Panel 9 - C854-SEP-E-RGN-CR143-50098 – Location of Panel Corridor 4470 – Room Volume 532m3 (room volume taken from Cxxx-XRL-O-TSC-CR143-50001 Rev 2.0) • __ Panel 10 - C854-SEP-E-RGN-CR143-50097 – Location of Panel Corridor 4510 – Room Volume 297m3 (room volume taken from Cxxx-XRL-O-TSC-CR143-50001 Rev 2.0)
| 03SR - Stations (RfL) | Cxxx-NCR-000087 | NCR | C857-SR3 Barset Installation-East Shaft Lev-1 |  | Crossrail | XRL | CWS - Canary Wharf Station |  | 2020-05-03 | 2019-10-11 11:25 | -205 | 2019-05-08 11:14 | Architectural - Security | 0 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Installation of grille panels do not appear to align with design detail. This has resulted in the incorrect installation of the fixings and are incorrect in terms of long term viability and durability of the design concept. The fixings locations are inconsistent and vary at each penetration suggesting that incorrect dimensions have been taken to consideration which is resulting the inconsistency. Almost 90% of the fixing penetrations at each location have punctured the edges of the existing installed main frame. This will compromise the structural integrity of the installation of grills and fixings, particularly the fixings that can be sheared off relatively easily. There is now a danger that the function of the security grilles will be compromised since the fixings are too weak and the grilles can be pulled off completely, thereby increasing the security risk.
| 03SR - Stations (RfL) | Cxxx-NCR-000088 | NCR | C857 - Incorrect installation of security barsets in TVS shafts east and west level -2 |  | Contr | DML | CWS - Canary Wharf Station |  | 2019-12-31 | 2019-08-02 09:53 | -151 | 2019-05-07 15:25 | Architectural - Security | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | 1. Following site inspection the Contractor would like to notify that security barsets (manufactured to survey taken by ) are to narrow by approx. 25 mm creating an installation problem AD2. 2. Few of the new holes (M10) have been drilled to close to edge of existing steel member flanges, bridging the industry standard of 1.25 x diameter of hole from edge of flange (12.5 mm from edge of the flange for M10 hole)
| 03SR - Stations (RfL) | Cxxx-NCR-000090 | NCR | C857 Benches |  | Crossrail | XRL | CWS - Canary Wharf Station |  | 2019-05-27 | 2019-09-16 15:11 | 112 | 2019-05-17 11:12 | Architectural - General | 0 |  | Incomplete Works | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The benches should have been completed by August / September 2018. We are still waiting for a close out date on the rectification due to their incredibly poor workmanship. Inspection had taken place January 2019 with all key personnel and comments were generated with actions planned with expected dates with response. Snag list has been produced and to date still remain outstanding. This delay will have major impact on our proposed critical path for delivery.
| 03SR - Stations (RfL) | Cxxx-NCR-000091 | NCR | C851 Cable Management Systems (CMS) Fire Stopped without Lids |  | Contr | FSL | CWS - Canary Wharf Station |  | 2019-06-12 | 2019-07-18 09:09 | 36 | 2019-05-29 13:17 | Fire - Compartmentation | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Cable Management Systems (CMS) with no lids in place through penetrations have been fire stopped with __ compound direct on to the cables. This is British Standards compliant but not Tube Lines specification. Proposed Answer: Obtain a concession for the 54no examples of CMS penetrations in question (fire stopped but not to Tube Line specification), on the basis of the following justifications: Fire Compartmentalisation: This is already achieved according to the fire stopping compound (an LU Approved product) manufacturerâ€™s instructions, thereby complying with/invoking the relevant British Standards governing fire compartmentalisation when the products are correctly installed. (Albeit, for the 54no penetrations in question, not in accordance with the best practice prescribed by the Tube Line specification). __ __ Compound meets British Standards for fire compartmentalisation: BS476 Part 20 (__, 2019). The fire stopping has been carried out by competent FIRAS assessed and registered operatives (FIRAS, 2019) who also hold NVQ2 or NVQ3 Passive Fire Protection Diploma â€˜Skilled Workerâ€™ CSCS credentials. Do Nothing assessment: The component of the â€˜tube line specificationâ€™ that has not been achieved might be summarised as â€˜ease of maintenanceâ€™ (installing additional cables for example). The cables within these 54no penetrations may not reach the end of their natural lifespan for 20 to 50 years (Eland, 2019). It is therefore proposed that the cost to bring the 54no penetrations up Proposed Answer to Tube Line specification is deferred until it is â€˜must-doâ€™, during essential maintenance; or to facilitate future requirements/alterations. It is, arguably, only â€˜nice to doâ€™ at this stage as compartmentation has already been achieved. Do Something Assessment: Of the 54no penetrations in question, 15no total are high voltage (HV) cables. The remaining 39no are standard voltage. There are risks attached to breaking out the fire-stopping compound that is in contact with live cables. There is a risk of damage to the cables. There is also a risk of impacting the progress of other Contractorsâ€™ works while extensive electrical isolations are organised and implemented (cause and effect). Extensions for key dates and overall completion dates for multiple contractors is likely, with an accompanying overall increase to the total of the prices for the Client. Conclusion: In terms of effort and cost versus reward; it is preferable to seek to obtain a concession for the 54no affected CMS penetrations on this occasion, and accept that there may be a long term future-cost residual risk to bring some penetrations up to Tube Line spec. This approach should assist the Client and Employer meet their overall programme aspirations in the short term. References: Eland: Eland Cables, (2019). FAQ: What Is The Lifespan of Electrical Cables? [Online]. Available at: https://www.elandcables.com/the-cable-lab/faqs/faq-what-is-the-life-expectancy-ofelectrical- cables (Accessed 28th February 2019) FIRAS: Firesafe Installations, (2019). Why Chose a FIRAS certified Installation Contractor? [Online]. Available at: http://www.firesafe-installations.co.uk/Accreditations.aspx (Accessed: 28th February 2019) __: __ Passive Fire Protection Specialists, (2019). __ Compound. [Online]. Available at: https://www.promat.co.uk/en/products/promaseal-fire-compound (Accessed: 28th February 2019)
| 03SR - Stations (RfL) | Cxxx-NCR-000092 | NCR | C857 - Incorrect manufactured security barsets for TVS shafts east and west level -2 |  | Contr | DML | CWS - Canary Wharf Station |  | 2019-12-31 | 2019-08-02 09:56 | -151 | 2019-06-19 11:56 | Architectural - General | 500 |  | Manufacturing Defect | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | Following on site review of materials the Contractor has checked the manufactured elements for North and South bays (GL RA towards GL RB, and GL RE towards GL RD) in both shafts East and West. Manufactured elements do not fit the existing Structural Steel openings. The Contractor will confirm the solution with their design team as well with the __ to check security rating. This will be issued for Employer acceptance via FCD.
| 03SR - Stations (RfL) | Cxxx-NCR-000093 | NCR | LV Switchpanels Esat PLC Comms Failure to RTU |  | Crossrail | XRL | CWS - Canary Wharf Station |  | 2019-07-19 | 2019-10-07 09:41 | 80 | 2019-07-05 14:37 | Systems - Other | 500 |  | System Defect | Use As-Is | 4 (0.5-3k) | Complete | Previous Construction - Problems based on previous construction errors | Completed |  | When commencing LV battery charger SCADA testing 30.6.19 with & __ in LV switchrooms east the __ engineers noted communications between __ PLC's & __ RTU had failed. This was a __ systems failure and upon investigation into PLC event log had been down since 27.6.19 __/CRL contacted __ PLC engineer who authorised __ CRL to isolate & re-start PLC which re-instated communications
| 03SR - Stations (RfL) | Cxxx-NCR-000094 | NCR | Faulty cell in LV B west battery charger |  | Crossrail | XRL | CWS - Canary Wharf Station |  | 2019-08-06 | 2019-08-21 08:38 | 15 | 2019-07-05 14:42 | Electrical - Power Distribution | 500 |  | Equipment Breakdown | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Not Defined | Completed |  | During SCADA battery charger testing 30.6.19 with __, & Dale Power Solutions a faulty cell was identified in the battery charger unit in LV B west switch room.
| 03SR - Stations (RfL) | Cxxx-NCR-000095 | NCR | LVAC Bus-Coupler Closing onto a LV Board in Fault |  | Crossrail | XRL | CWS - Canary Wharf Station |  | 2019-08-16 | 2019-10-04 11:56 | 49 | 2019-08-02 11:12 | Electrical - Switchgear | 5000 |  | Design | Reject | 3 (3-6k) | Complete | Design Problem - Other | Completed |  | Reference Cxxx-OVE-E-RSW-CR143-50001 r3 – Design Package - W32a Electrical Switchboard Modifications Scope of Works dated 17-03-17, clause 3.5.1.1. The Rappell Boards supplied on site do not comply with this clause as highlighted in CAPIITALS below: 3.5.1.1 Switchboard LV-A Switchboard LV-A is a Form 4B Type 6 LV Switchboard manufactured to withstand a fault rated at 80kA for 1second. The Switchboard is Floor mounted with rear access. Cable Entry and Exit is via the top of the switchboard. Main Switchboard Busbars are rated to 4000A (2 x 150 x 10mm) with Riser Busbars rated to 2500A (2 x 80 x 10mm). The Switchboard has a paint finish to BS381C Grey631 and an IP Rating of IP31. The Electrical Contractor shall make full allowance for the following alteration works to be carried out on Switchboard LV-A. (a) Supply, Install, Test and Commission a key operated 3 position selector switch (Local/Remote/Auto) to control the incoming ACB and bus-coupler. Selector Switch to be mounted above the ACB and cabled to local terminals within each functional unit compartment. The board shall generally operate with both incoming ACB’s closed and bussection switch open. IF IEITHER OF THE INCOMING SUPPLIES FAILS ON UNDER VOLTAGE, THAT INCOMING ACB SHALL OPEN AND THE BUS-SECTION SWITCH SHALL CLOSE. THE BUS-SECTION SWITCH SHALL NOT CLOSE IF AN ACB HAS TRIPPED ON FAULT. The “normal” position for the selector switch is when the switch is in automatic mode (Auto). The auto mode is only to be active when both incomers (A & B) are closed and the bus-section switch is open. During general operation both ACB incomers shall be closed and the bus-section switch shall be open. Should either of the incoming supplies fail on under voltage the associated incoming ACB shall open and the bus-section switch shall automatically close; this is flagged up at the RCC, via Modbus and relays; under voltage trip is via relays. SHOULD EITHER OF THE INCOMING SUPPLIES TRIP DUE TO A FAULT CONDITION ON THE LV SWITCHBOARD THE ASSOCIATED INCOMING ACB SHALL OPEN BUT THE BUS-SECTION WILL NOT CLOSE. Tripped circuit breakers require on-site attendance to investigate and where possible rectify the fault.
| 03SR - Stations (RfL) | Cxxx-NCR-000097 | NCR | C849 - Door & Fire Alarm Signage Falling Off |  | Contr | OVE | CWS - Canary Wharf Station |  | 2019-10-24 | 2019-12-16 13:17 | 53 | 2019-08-05 08:19 | Architectural - Signage | 1000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | A significant number of door and fire alarm signs that have been installaed at Ticket Hall Level -4 and Platform Level -5 have been falling off. These are generally the larger VE signs to walls and floors such as the fire alarm and emergency exit signs. When the signs are falling off they are getting damaged beyond repair and require replacement.
| 03SR - Stations (RfL) | Cxxx-NCR-000098 | NCR | C857 - Existing balustrade handrail around lifts and escalators at Level -4 |  | Contr | DML | CWS - Canary Wharf Station |  | 2020-04-01 | 2020-03-26 13:54 | -6 | 2019-10-04 13:30 | Architectural - Balustrade | 30000 |  | Material | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | would like to formally advise CRL that the existing handrail to the balustrade is of poor construction and incomplete and therefore cannot be installed properly. The handrail tube thickness varies and therefore when the previous contractor installed the handrails on the bosses, they taped around the bosses to give the handrail more rigidity. Delatim have not used this methodology as it is incorrect and will wear away / fray quickly and therefore the handrail is ill fitting. Delatim propose replacement of handrail. This has been communicated in various weekly meetings with CRL.
| 03SR - Stations (RfL) | Cxxx-NCR-000101 | NCR | WYG - Asset Tags allocated to Incorrect PFU/FUs |  | Crossrail | XRL | CWS - Canary Wharf Station |  | 2021-04-30 | 2021-05-07 14:04 | 7 | 2019-11-13 11:51 | Information Management - Asset Information | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - No evidence of program review from Contractor's Quality Manager or Management | Completed |  | There are approx. 800 assets tags identified which have been allocated to incorrect PFU/FU. This was initially highlighted to WYG by CRL Asset Information Team back in July 2019 and raised by Cxxx O&M team. It is now fundamentally affecting completion and consequently handover to Information Manager. List of some of the questioned assets are attached.
| 03SR - Stations (RfL) | Cxxx-NCR-000102 | NCR | Defects on Glass Bulstrade, Top hats, corner trims, plates, screws and skirting sections. |  | Crossrail | XRL | CWS - Canary Wharf Station |  | 2020-04-01 | 2020-04-14 15:44 | 13 | 2020-01-06 16:47 | Architectural - Balustrade | 0 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | This NCR covers the defects as identified during site inspections on the balustrades and associated handrails. The handrail item has been excluded and thus allows NCR 00100 to be addressed and closed out as a separate matter excluded from the defects being identified as follows : Top hat trims on glass balustrading : The top hats on the glass balustrades are not to an acceptable standard. The corner trims connection is poor leaving gaps between the two joints. Adhesive is also visible on the underside of the top hat trims at various locations. The break joints on the continuous run, the quality of the joints appears to be poor with some sharp edges being identified. The trims do not align, the quality of the cuts to the ends are not straight with edges being sharp. Design Defects : There are inconsistent gaps with the glass panels, gaps are larger than opposed to the top section being smaller and appear to be inconsistent. The design shows "no" gaps. The glass panel that adjoin the escalator side sections also have significant gaps in the region of 35mmm plus and needs to be rectified. Base Skirting : The skirting at low level around the perimeter of the balustrade are of low quality installation since the screw fixings used do not appear to align and the edges as inspected are sharp. Some of the screw fixings appear to be lose and not quite level. There is also some signs of poor installation of the silicone used and some missing at various locations. These have been captured in the attached snag list / excel work sheet.
| 03SR - Stations (RfL) | Cxxx-NCR-000103 | NCR | C857 - The 2 no VE panel telephone doors on the West end of Level -5 |  | Contr | DML | CWS - Canary Wharf Station |  | 2020-06-05 | 2020-04-20 15:40 | -46 | 2020-01-17 13:04 | Architectural - General | 500 |  | Incomplete Works | Rework | 4 (0.5-3k) | Complete | Design Problem - Not Defined | Completed |  | The 2 telephone doors on the West end of Level -5 have the backing panel missing
| 03SR - Stations (RfL) | Cxxx-NCR-000105 | NCR | C857 - Balustrade mastic debonding and oversized joints |  | Contr | OVE | CWS - Canary Wharf Station |  | 2020-03-15 | 2020-04-16 15:45 | 32 | 2020-01-27 16:40 | Architectural - Balustrade | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Mastic between the balustrade glass panels and the bulkhead aluminium cladding is debonding. Some of the mastic joints are also oversized and appear to be larger than the mastic product is designed for (50mm+) and not as the Cxxx design, specifically in locations behind the poster frames to the top of the escalators.
| 03SR - Stations (RfL) | Cxxx-NCR-000106 | NCR | C857 - Balustrade corner and end trims not installed as Cxxx design |  | Contr | OVE | CWS - Canary Wharf Station |  | 2020-02-24 | 2020-04-16 14:40 | 52 | 2020-01-27 17:17 | Architectural - Balustrade | 0 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The stainless trims to the balustrade corners and end panels adjacent to the escalator cladding and the lift cladding have either not been installed at all or not been installed as the Cxxx design creating large gaps between the trims and glass panels. The gaps to the corners create a finger trap and a safety risk to passengers. The lack of trims to the end panels exposes the glazing interlayer, which has been highlighted by CEG as a security risk and against LU fire guidance.
| 03SR - Stations (RfL) | Cxxx-NCR-000107 | NCR | C854 - Non-Compliant DNE Sign ~ Do not Enter Message is not being announced ~ South West ~ L-1 ~ N4 / L1 / 56 & 61 |  | Crossrail | XRL | CWS - Canary Wharf Station |  | 2020-02-21 | 2020-02-25 07:56 | 4 | 2020-01-31 16:26 | Fire - Fire Systems & General | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Personnel Error - Violation of requirement or procedure | Completed |  | During 3.0 Fire System Testing at CWS on the 31.01.2020, contractor Global/ informed Cxxx that EDNE sign on L-1 South West elevation has not been announcing the correct message as per CRL Specification outlined on the approved FCD (Cxxx-FCD-000225).
| 03SR - Stations (RfL) | Cxxx-NCR-000108 | NCR | Incorrect tagging and allocation of Fire Supression Asets in Canary Wharf Crossrail Station |  | Crossrail | XRL | CWS - Canary Wharf Station |  | 2020-09-30 | 2020-09-23 10:05 | -7 | 2020-02-11 16:51 | Information Management - Asset Information | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Management Problem - No evidence of program review from Contractor's Quality Manager or Management | Completed |  | During the revision of Fire Suppression System O & M documentation, whilst using the AIMS asset information contained under PFU-2-01095, it was found that many FU subsystems and assets allocated to them have been inconsistently and illogically tagged. Observations have been made including, but not limited to the below: FU-2-007662-Fire Suppression Water Supply 001 & FU-2-007663-Fire Suppression Water Supply 002; The logic behind separating these two systems doesn't make sense. Whilst the systems could be split geographically East and West, the assets allocated to each system don`t support this division. There is only one connection to town mains that serves the Charged Dry Falling Mains System tanks and Water Mist tanks at each end of the station. For this reasons CWS suggests that 1 no system be assigned to these assets. These tanks have not been tagged in the AIMS data we have been provided with, all tanks are tagged as being included in the water-mist systems and are shown as being located in the same room which is incorrect. CWS believe, this system type should also register the system between each Tunnel Hydrant Breeching Inlet and the connection to the tunnel hydrant system at the tunnel portals. Seperating the Tunnel Hydrant system into two systems makes sense, as they are clearly hydraulically seperate from eachother within the station, being served by their own breeching inlets at the East and West ends of the station. However the data CWS has been provided with does not demonstarte this logic. Currently there are only 3 of the 4 breeching inlets registered in the data system. The tagging and labelling of all 4 breeching inlets needs to be investigated and corrected. This would lead to a total of 3 no Fire Suppression Water Supply Systems registered in the AIMS database. FU-2-007264-Fire Mains 001, FU-2-007265-Fire Mains 002, FU-2-007266-Fire Mains 003 Again, the logic behind the separation of these systems is unclear. As CWS has two non-automatic systems, The Charged Dry Falling Mains system and Tunnel Hydrant Falling Mains system. It is unclear why 3 systems have been allocated. Geographic separation of the Charged Dry Falling Mains into East/West is acceptable, but as it is hydraulically one system, sub-dividing it may prove confusing in operation and maintenance, especially if the dividing points of the system are not clear from the schedule. CWS recommendation is that ONE system should be registered to pick up all station hydrants regardless of geographic location based on the fact that during normal operation there is no hydraulic separation. The system should be named to include a clear description of "Charged Dry Falling Main" as per Cross rail nomenclature. FU-2-007268-Water Mist System at Canary Wharf Station (West) & FU-2-007269-Water Mist System at Canary Wharf Station (East) Number of systems is correct, but the allocation of rooms served by each seems to be the wrong way around. System 007268 (West) actually serves rooms on the East of the station and vice versa. Full review of these systems within AIMS has not been undertaken, but CWS suggest that an in-depth QA is done.
| 03SR - Stations (RfL) | Cxxx-NCR-000109 | NCR | Access door leaking on SVP L-5 East end |  | Crossrail | XRL | CWS - Canary Wharf Station |  | 2020-03-27 | 2020-03-26 14:17 | -1 | 2020-02-13 11:27 | Mechanical - Public Health Engineering | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | removed the access door to the SVP pipework on L-5 East end adjacent to the Surface water storage tanks, the access door was removed to enable temporary sump pump discharge from the surface water drainage tanks whilst the pump panel serving these tanks was being replaced.
| 03SR - Stations (RfL) | Cxxx-NCR-000110 | NCR | C857-Lack of CCTV Evidences Post Cleaning of the Gravty Drainage pipes in East and West TVS and DR Shafts |  | Crossrail | XRL | CWS - Canary Wharf Station |  | 2021-03-04 | 2020-06-24 16:13 | -253 | 2020-02-19 17:26 | Civil - Civil Engineering General | 500 |  | Incomplete Works | Reject | 4 (0.5-3k) | Complete | Discipline/Workmanship - Not Defined | Completed |  | Contractor instructed to undertake a Water Ingress and Drainage Survey of the TVS and DR Shaft areas in the station and execute the recommendations contained on Cxxx Document (Cxxx-OVE-P-RGN-CR143-50003) issued as part of instruction Cxxx-NCE-00283.
| 03SR - Stations (RfL) | Cxxx-NCR-000112 | NCR | C843 UPS Asset Information |  | Crossrail | XRL | CWS - Canary Wharf Station |  | 2020-10-15 | 2020-09-23 10:08 | -22 | 2020-02-27 16:47 | Information Management - Asset Information | 500 |  | Incomplete Works | Repair | 4 (0.5-3k) | Complete | Verification Problems - Inspection points not adequate | Completed |  | The UPS asset information held within AIMS export dated 19/02/2020, generated from information gathered and compiled by WYG contains incorrect information. Batteries: Batteries are currently registered under FU-2-007270 - Emergency Lighting 001 at Canary Wharf Station and FU-2-007271 - Emergency Lighting 002 at Canary Wharf Station. They should be registered under the relevant UPS PFU System. Battery assets have been tagged as including 60 cells each, AIMS team confirmed that every individual battery cell should be tagged/labelled as per CRL1-XRL-Z3-ADDSD-CR001-50413 - Asset Naming and Labelling Convention (9.0). There are a number of control switches located in the two battery rooms, which act as DC battery isolators and as such, should be associated with the UPS systems. Currently they are referenced under LV systems. Protective Devices: There is one protective device labelled as a Castell Interlock included within UPS system PFU-2-01453 - Uninterruptible Power Supply (UPS) at Canary Wharf Station. This would be better registered as a control switch. However, it also appears that this device is an integral part of the UPS board, and in discussion with WYG is not part of their scope (as it lies within the board). We suggest this is either removed for clarity, or the remaining interlocks associated with each UPS board are registered for consistency.
| 03SR - Stations (RfL) | Cxxx-NCR-000113 | NCR | C843 Asset information for hatch and door asset |  | Crossrail | XRL | CWS - Canary Wharf Station |  | 2020-09-30 | 2020-09-23 10:13 | -7 | 2020-02-27 17:13 | Information Management - Asset Information | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | Premises asset information held within AIMS export dated 19/02/2020, generated from information gathered and compiled by WYG contains incorrect or incomplete entries. Hatches L412: There are Hatch assets (L412) registered in the following PFU systems: PFU-2-00013 - Door System (Arch) at Canary Wharf Station PFU-2-00111 - Wall Cladding System at Canary Wharf Station PFU-2-02539 - Floor System 001 at Canary Wharf Station PFU-2-02543 - Non-Structural Walls 001 at Canary Wharf Station Following confirmation from AIMS central team – hatches should be registered as part of the system in which they are installed. For example a hatch in wall cladding should be part of the wall cladding system. Within the AIMS export for Canary Wharf Station dated 19/02/2020 there are 98 hatch assets registered within the Door system (PFU-2-00013 - Door System (Arch) at Canary Wharf Station) There are no hatches installed within doors in the station, this referencing needs to be corrected. There are 49 hatch assets that do not have a room reference, this needs to be corrected. PFU-2-00013 - Door System (Arch) at Canary Wharf Station Many Back of House doors have a manufacturer reference as Ingersoll Rand, this is incorrect, only Front of House doors are manufactured by Ingersoll Rand. There are 6 entries under L41104 - Door Sliding/Folding. This asset class should only be applied to the Bostwick gates at -1 level, of which there are only 4no. installed within the station. The manufacturer is also incorrectly stated as Allegion UK Ltd. The correct manufacturer is Bradbury. As previously stated, there should be no hatches referenced under the Door System PFU.
| 03SR - Stations (RfL) | Cxxx-NCR-000114 | NCR | C843 Contractor Own Verification of Asset Information is deficient |  | Crossrail | XRL | CWS - Canary Wharf Station |  | 2020-06-15 | 2020-05-27 11:30 | -19 | 2020-03-11 17:03 | Information Management - Asset Information | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Supervision - Insufficient supervision | Completed |  | Asset information provided by contactor does not meet the contract requirements of self-certification (Work information Volume 2B Part 13) and undertaking "its own verification processes to ensure all the above deliverables are completed on time and without error (C843-XRL-Z3-GPS-CR143-50001)". As examples, Cxxx-NCR-00101 asset tags allocation, Cxxx-NCR-00108 Fire Suppression, Cxxx-NCR-00113 UPS and Cxxx-NCR-00113 hatch and doors show deficiencies including, but not limited to 1) Asset information not organised in accordance with the system schematics, potentially causing confusion and difficulty for asset owner and O&M team; 2) Equipment allocation schedule does not fully match MCRs and site install.
| 03SR - Stations (RfL) | Cxxx-NCR-000115 | NCR | The rivet connections within the Bostwick Gates have failed |  | Crossrail | XRL | CWS - Canary Wharf Station |  | 2021-03-25 | 2020-06-08 21:54 | -290 | 2020-03-11 17:00 | Architectural - General | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The rivet connections within the Bostwick gate has failed and the section has come apart. The section is completely exposed and will hamper operation to an SC3 rated Bostwick gate and possibly start to distort the sections forming part of the gate structure.
| 03SR - Stations (RfL) | Cxxx-NCR-000116 | NCR | Non-Conformance to Cxxx-FCD-00013 following removal of ATS 20 and ATS 22 |  | Crossrail | XRL | CWS - Canary Wharf Station |  | 2020-12-31 | 2021-01-29 13:21 | 29 | 2020-03-20 14:43 | Electrical - LV Equipment | 50000 |  | Incorrect Installation | Repair | 2 (6-60k) | Complete | Management Problem - Misunderstand the definition of the requirement | Completed |  | During LV Verification Phase 1 Surveys it has been identified that following removals of ATS 20 and ATS 22, loads originally supplied by these ATS have been re-terminated into single MCCBs at ERN 40E and ERN 40W. Refer to Updated As Built LV Schematics: C853-DRN-E-XSK-CR143-50001 & C853-DRN-E-XSK-CR143-50002 for details of the installed arrangement. This is against information included in Cxxx-FCD-00013 which specified that spare ways should be used for the second supply in each case (refer to items 12 and 24 on page 3).
| 03SR - Stations (RfL) | Cxxx-NCR-000117 | NCR | C843 BMS asset database correction |  | Crossrail | XRL | CWS - Canary Wharf Station |  | 2020-09-30 | 2020-09-14 13:44 | -16 | 2020-04-01 12:24 | Information Management - Asset Information | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Information not detailed | Completed |  | Fundamental to AIMS, each outstation shall has its own unique FU and is cross referenced to each unique CE controls enclosure, as detailed within the BMS O&M. It is key for maintence that it’s delivered to them this way. 248 FU – 2- 007199 BMS Outstation 001 Marshalling Cabinets do not contain outstations of any type 249 FU – 2- 007199 BMS Outstation 001 It belongs here and only here labelled to CE W11 in the BMS O&M 250 - Control Panel 001 This is a cooper fire panel and does not belong in the BMS 248 Marshalling cabinet 001 This is labelled as CR143 – BMS-001 and is correct East Network Cabinet 254 outstation N05 This is labelled on the West Network Cabinet, there is no outstation here. Maybe it should have gone as asset tag CR143 – BMS-002 Row 250 as being the second marshalling cabinet West Network Cabinet Marshalling cabinets and Network cabinets are the same thing, just lost in a bit of translation, there’s two of them 1 x East and 1x West, if that makes it clearer. 254 outstation N05 (to help make sense of this refer to BMS O&M page 28 & 29) the outstation number run 1- 25 against 1-25 CE unique control enclosures…Only one outstation number is missing against CE control enclosure CE W08, which is outstation N05 FU Outstations 26, 27, 28 & 29 need re jigging to get on the right rows. See attached "AIMS control conflicts"
| 03SR - Stations (RfL) | Cxxx-NCR-000118 | NCR | C843 PFUs for shaft (stair) pressurisation |  | Crossrail | XRL | CWS - Canary Wharf Station |  | 2020-10-31 | 2020-10-19 15:43 | -12 | 2020-04-01 12:43 | Information Management - Asset Information | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Misunderstand the definition of the requirement | Completed |  | Asset database in its current form has no asset assigned to Shaft Pressurisation PFU’s (PFU Code – PFU064). As a result, the related assets are not visible on the AIMS export, but are spread through HVAC PFU’s. such as PFU-2-01404 Shaft pressurisation system at Canary Wharf Station (west); PFU-2-02808 Shaft pressurisation system 002 at Canary Wharf Station (East), PFU-2-02809 Shaft pressurisation system 003 at Canary Wharf Station. The asset database requires "East separate shaft that has its own standalone Shaft Pressurisation will be counted as an individual PFU."
| 03SR - Stations (RfL) | Cxxx-NCR-000119 | NCR | C843 Asset database doors |  | Crossrail | XRL | CWS - Canary Wharf Station |  | 2021-03-19 | 2021-02-23 17:18 | -24 | 2020-04-01 12:59 | Information Management - Asset Information | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | There are 98 number of hatches that need to move from doors to related PFU as confirmed by the CRL asset team. L41101 needs to be reviewed and the data needs to be corrected. Although 6 number of doors in this L class, there are only 4 of them installed (Botswick gates) and the manufacturer is incorrect. Following 8 tags missing in the AIMS list: DOOR 038, DOOR 046, DOOR 065, DOOR 140, DOOR 146, DOOR 272, DOOR 289, DOOR 306 Four extra tags do not correspond to CWS door schedule: CR143-BAF-00447 DOOR 264 CR143-BAF-01795 DOOR 396 CR143-BAF-01807 DOOR 408 CR143-BAF-04391 DOOR 516 Incorrect Door manufacturer Incorrect door number Incorrect door type
| 03SR - Stations (RfL) | Cxxx-NCR-000120 | NCR | C843 Asset database for Furniture system PFU-2-00050 |  | Crossrail | XRL | CWS - Canary Wharf Station |  | 2020-10-30 | 2020-10-02 13:31 | -28 | 2020-04-01 13:13 | Information Management - Asset Information | 500 |  | Documentation and Records | Repair | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | L82255 – Benches Needs more information specifying two seat and four seat benches. Material information inconsistent (brushed steel, metal, steel..) L4422 - Barriers Handrail Some assets need description and some needs more information (if it is an anti climb barrier or handrail etc.) Roundel barriers needs to be included to the list Regarding to the AD4 balustrades should be listed in L661313 – Architectural glass and handrails attached to the balustrades should be listed in in L4422 - Barriers Handrail. References from AD4: Architectural Glass: ….. Glass is also used for internal partitions and as an architectural feature. When used in buildings, glass is often of a safety type, which include reinforced, toughened and laminated glasses. Barriers Handrail: A handrail is a rail that is designed to be grasped by the hand so as to provide stability or support. Handrails are commonly used on staircases, around glass balustrades and around other perimeter boundaries. L869 - Totems Totems should be added to this PFU L21253 Guardrails This L class needs to be moved to a different PFU L43211 - Access Ladders This L class needs to be moved to a different PFU
| 03SR - Stations (RfL) | Cxxx-NCR-000121 | NCR | C843 asset database for suspended ceiling system PFU-2-02545 |  | Crossrail | XRL | CWS - Canary Wharf Station |  | 2020-10-31 | 2020-10-02 13:34 | -29 | 2020-04-01 13:20 | Information Management - Asset Information | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Regarding L387 Suspended ceilings, some assets need more information (location, fire rating and finish). See CR143-BAF-04371 through CR143-BAF-04383. Soffit panels not captured in the AIMS database.
| 03SR - Stations (RfL) | Cxxx-NCR-000122 | NCR | C843 Asset database for Floor System PFU-2-02539 |  | Crossrail | XRL | CWS - Canary Wharf Station |  | 2020-12-31 | 2020-12-07 10:42 | -24 | 2020-04-01 13:32 | Information Management - Asset Information | 500 |  | Documentation and Records | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Information not detailed | Completed |  | L534 - Pavings: Some assets need location and type description, see CR143-BAF-04513 to CR143-BAF-04521; the existing ones need to be checked and corrected. L535 - Floor Screed: number of the assets decreased from ~200 to 13, needs to be checked. insufficient description, locations should be provided. See CR143-BAF-01957 to 01970. L536 - Floor Covering Sheets Flexible Sheets: Some assets have no location and type description. See CR143-BAF-04522 to CR143-BAF-04525. L661411 - Sheet Floor Grating: All assets need location and type description. See CR143-BSR-01392 to 01417. L412 – Hatches: There is only one item listed in this class, missing ones need to be included. L661414 - Sheet Steel: Missing L class in the AIMS. Where are stair floor finishes covered? L386 – Access Floors: Missing L class in the AIMS SOR Room (4460) floor is listed in the L536 - Floor Covering Sheets Flexible Sheets and in the L535 - Floor Screed. Why list them in two different L classes in one PFU? Also needs to be listed in L386 - Access Floors instead of L536 - Floor Covering Sheets Flexible Sheets. See below description from the ‘Asset Data Dictionary Definition Document’. Access floor otherwise known as raised floor are a type of floor that provide an elevated structural floor above a solid substrate (often a concrete slab) to create a hidden void or act as a finish. This class covers both the floor tiles and the supporting structure. It is not expected that each element of the access floor will be recorded separately but that the floor system will be recorded. Access floors are constructed of a number of individual tiles and supports. Each individual tile/support does not constitute an individual asset. The Asset will constitute a continuous floor of individual tiles and supports.
| 03SR - Stations (RfL) | Cxxx-NCR-000123 | NCR | C853-contractor removed a light from level -5 and not reinstated back |  | Crossrail | XRL | CWS - Canary Wharf Station |  | 2020-12-31 | 2021-01-11 21:30 | 11 | 2020-04-07 07:45 | Electrical - Lighting | 500 |  | Incomplete Works | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Improper storage of material | Completed |  | It came to Crossrail attention that the contractor removed a light from level -5 platform and the light was stored in the storage area (photos attached) and from there the light fitting was thrown away.
| 03SR - Stations (RfL) | Cxxx-NCR-000124 | NCR | C857 - Discoloration of Duplex Steel Handrail Brackets (Cxxx-NCR-000104) |  | Contr | DML | CWS - Canary Wharf Station |  | 2020-09-16 | 2020-05-11 21:53 | -128 | 2020-04-29 09:52 | Architectural - Balustrade | 6000 |  | Workmanship | Use As-Is | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Discoloration has appeared to the Duplex steel handrail brackets to the balustrade in the form of a white powder surrounding the bracket weld. An original Cxxx-NCR-000104 has been cancelled instead of closing. Following PMI C857-PMI-00078 this NCR has been de-scoped.
| 03SR - Stations (RfL) | Cxxx-NCR-000125 | NCR | NCR for Labels on LV B West |  | Contr | RAP | CWS - Canary Wharf Station |  | 2020-09-30 | 2020-09-18 08:19 | -12 | 2020-06-10 11:19 | Electrical - LV Equipment | 500 |  | Incomplete Works | Repair | 4 (0.5-3k) | Complete | Verification Problems - Inspection points not adequate | Completed |  | On LV B West it has been reported that 3 x External Labels for different outgoing MCCBs all have the same cable reference.
| 03SR - Stations (RfL) | Cxxx-NCR-000126 | NCR | C853 at Canary Wharf had not submitted a Quality Plan prior to starting the works on site (requirement: Works Information Vol 2B – 20.4) |  | Crossrail | XRL | CWS - Canary Wharf Station |  | 2020-08-31 | 2020-08-07 15:43 | -24 | 2020-07-14 10:24 | Electrical - General | 500 |  | Documentation and Records | Repair | 4 (0.5-3k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | C853 at Canary Wharf had not submitted a Quality Plan prior to starting the works on site (requirement: Works Information Vol 2B – 20.4). The issue was identified during the Surveillance Cxxx-XRL-O4-RGN-CR001-50014 on 19/06/2020. had later submitted the Quality Plan on eB which is under review (14/07/2020).
| 03SR - Stations (RfL) | Cxxx-NCR-000127 | NCR | C853 redline drawings do not refer to any PTRs: FCDs, NCRs, RFIs |  | Crossrail | XRL | CWS - Canary Wharf Station |  | 2020-10-31 | 2020-10-14 20:27 | -17 | 2020-07-14 15:19 | Electrical - General | 500 |  | Documentation and Records | Repair | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | As discovered in the surveillance Cxxx-XRL-O4-RGN-CR001-50014 regarding the FCDs Management of , the Redline Drawings that have been issued up to now by C853 do not refer to any PTRs. The Package that were checked during the surveillance were refering to the related PTRs but none of the redline drawings had any information or markups of the applicable NCRs, RFIs or FCDs eventhough the actual changes had been done. Details of the package listings that had been sample checked are in the Surveillance Report.
| 03SR - Stations (RfL) | Cxxx-NCR-000128 | NCR | C854 - Defects Identified During LV Verification Surveys |  | Crossrail | XRL | CWS - Canary Wharf Station |  | 2021-04-30 | 2021-04-28 14:46 | -2 | 2020-07-28 10:33 | Electrical - General | 2000 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Management Problem - Misunderstand the definition of the requirement | Completed |  | In order to facilitate accurate updates to Station As-Built records, LV verification surveys have been undertaken to confirm circuit designations for all LV equipment supplied via Canary Wharf's LV and UPS systems. During the course of these surveys, a number of defects have been recorded which are associated with work packages completed by C854 (). Sample issues include: - Incorrect circuit references displayed on assurance documentation (e.g. red lines, test packs) - Incorrect circuit reference labels installed on equipment at site (e.g. at Damper Control Panel isolators, light fitting) - Incorrect circuit reference labels applied to supply cabling Please refer to NCR attachments for a schedule of items identified to date and accompanying photo/report evidence.
| 03SR - Stations (RfL) | Cxxx-NCR-000129 | NCR | C852-__ not following the Redline Procedure |  | Crossrail | XRL | CWS - Canary Wharf Station |  | 2020-12-31 | 2021-02-01 10:20 | 32 | 2020-08-11 11:26 | Electrical - General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Misunderstand the definition of the requirement | Completed |  | As discovered in the surveillance Cxxx-XRL-O4-RGN-CR001-50016 regarding the redline drawings process and procedure as per Crossrail document CRL1-XRL-Z-GPD-CR001-50010, the Redline Drawings that have been issued up to now by __ C852 do not refer to any PTRs. The __ sampled redline drawings (C852-HWB-E-DWG-CR143-50035, C852-HWB-E-DWG-CR143-50046 and C852-HWB-E-DWG-CR143-50056) that were checked during the surveillance don’t have any PTRs number. The details of the sample drawings are in the surveillance report (Cxxx-XRL-O4-RGN-CR001-50016).
| 03SR - Stations (RfL) | Cxxx-NCR-000130 | NCR | PES and PSD Interface, Sectional VE Panel is too short at the interface end of platform. |  | Crossrail | XRL | CWS - Canary Wharf Station |  | 2020-12-31 | 2020-11-11 12:36 | -50 | 2020-08-28 12:06 | Architectural - Finishes | 1000 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Conflicting information on drawings | Completed |  | It is understood that the PES / PSD re-design is Non-Coordinated since large gaps have picked up during a site inspection in January 2020 where the Grills at high level and VE panels do not quite meet. RfL had asked to provide Architectural design drawings (not electrical) that show how the end wall is co-ordinated with the PSDs as part of the process to verify the coordination. In addition 2 Nos. SCC have been put forward as part of the completion of the respective works as two separate packages. Architectural certification provided below, confirming works completed. PES Grilles SCC - C859-KCR-A-CER-CR143-50004 PED SCC - C857-DML-A-CER-CR143-50007 There is also an observation raised on this - CRL-OBS-25341 which also captures the fact that panels are not aligned, are lose and are hanging with large gaps and further lack of consistencies and anomalies.
| 03SR - Stations (RfL) | Cxxx-NCR-000131 | NCR | LVA West Bus coupler functionality |  | Crossrail | XRL | CWS - Canary Wharf Station |  | 2021-05-15 | 2021-06-01 14:41 | 17 | 2021-02-16 19:21 | Electrical - LV Equipment | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Lack of procedure | Completed |  | After the functionality testing on the 27th of November was identified by AP's that LVA West when racking out the Bus Coupler ACB the LVA incoming ACB from TX A2 opens of its own accord. Also, whilst the LVA Bus coupler ACB is racked out the ACB will not close again until the bus coupler was reinstated. The on and off buttons do not function. Going forward this would mean that isolations of LVB from the Bus Coupler in LVA would result in half the station being off. Also the LVA Bus coupler ACB can not be serviced/maintained without LVA being off. This does not happen in the East of the station. Videos sequence as follows: With West LV-A Switchboard in Local mode, AP racks out N/O Buscoupler ACB à Incomer ACB Opens, Switchboard de-energised AP attempts to Close Incomer ACB using pushbutton à Push button does not operate, ACB remains Open AP racks in N/O Buscoupler ACB à Relay audibly engages within control compartment AP attempts to Close Incomer ACB using pushbutton à Push button operates, ACB Closes and Switchboard is re-energised AP powers down PLC-A and PLC-B and repeats above sequence à No difference observed In Video 10 it can be seen that relays labelled R14 and R15 are switched when the Buscoupler ACB is racked in/out
| 02SL - Stations (LUL) | Cxxx-NCR-000009-F | NCR | Low Strength Concrete Cubes |  | Contr |  | FAR - Farringdon Station (West) |  | 2012-05-14 | 2012-10-01 17:43 | 140 | 2012-03-30 | Utilities Engineering - Water | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | Cube results for all thrust blocks (1, 2, 3 and 4) show a 28 day compressive test result of less than the required design strength of 20N/mm-2. The Contractor has failed to raise this NCR with CRL. This was discovered by CRL when reviewing the certification packages.
| 02SL - Stations (LUL) | Cxxx-NCR-000014-B | NCR | Document Approvals |  | Contr |  | BOS - Bond Street Station (West) |  | 2010-10-14 | 2011-05-19 09:22 | 217 | 2010-10-07 | Civil - Civil Engineering General | 500 |  |  | Rework |  | Complete |  | Completed |  | C240 - Documents including quality plan and ITP without contractor signautes and/or PDP decal code 1 or 2 acceptance.
| 02SL - Stations (LUL) | Cxxx-NCR-000043 | NCR | __ Hollowcore planks |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2010-12-03 | 2011-02-08 15:21 | 67 | 2010-11-26 | Structural Engineering - Pre-cast | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | The first batch of Hollowcore slabs were delivered to site with loose, dried concrete slurry in the base of the voids
| 02SL - Stations (LUL) | Cxxx-NCR-000044 | NCR | Loading CW126 without approval |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2010-12-03 | 2011-01-20 17:53 | 48 | 2010-11-26 | Construction Health & Safety - Construction Health & Safety General | 500 |  | Planning | Use As-Is |  | Complete |  | Completed |  | commenced mobilisation works in Essex Wharf which included placing Type 1 sub-base on top of Covered Way 126. This was considered a non-conformance on 2 counts:- 1) Method statement for site set up was not fully approved 2) CW126 is an LO asset which required a licence issuing to Crossrail (and onto Kier) to permit the placing of sub-base on top of the structure. This was not received prior to the works commencing.
| 02SL - Stations (LUL) | Cxxx-NCR-000045 | NCR | Error on baseplate 8B |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2011-04-04 | 2011-05-19 09:46 | 45 | 2011-03-23 | Structural Engineering - Steel Member | 500 |  |  | Repair |  | Complete |  | Completed |  | The holes in baseplate 8B (ie SOP's 70 & 71) of spreader beam 1094X (as shown on Hares Drg A1017-2), which is part of tower A1017 on Platform 5 did not match up to the holes drilled into the platform as per design. Also the protruding area of the baseplate from column/baseplate A1017 will clash with the base plate of the column 1046 at SOP 73
| 02SL - Stations (LUL) | Cxxx-NCR-000046 | NCR | Longitudinal cracks in __ planks |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2010-12-03 | 2011-02-08 15:49 | 67 | 2010-11-29 | Structural Engineering - Pre-cast | 500 |  |  | Use As-Is |  | Complete |  | Completed |  | completed void filling works to the __ planks to the agreed design and method statement but found there were longitudinal cracks forming on the 2.6m and 1.2m units. All the cracks are located at the bottom of the plank in the flange.
| 02SL - Stations (LUL) | Cxxx-NCR-000047 | NCR | Pull out test failure SOP 45 |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2010-12-03 | 2011-02-08 15:51 | 67 | 2010-11-27 | Structural Engineering - Testing | 500 |  |  | Rework |  | Complete |  | Completed |  | The SE corner bolt of SOP 45 failed a pull out test at 20kN
| 02SL - Stations (LUL) | Cxxx-NCR-000048 | NCR | Pull test failure SOP 48 |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2010-12-03 | 2011-02-08 15:53 | 67 | 2010-11-27 | Structural Engineering - Testing | 500 |  |  | Rework |  | Complete |  | Completed |  | The NE corner bolt to SOP 48 failed a pull out test at 40kN
| 02SL - Stations (LUL) | Cxxx-NCR-000049 | NCR | Pull test failure - SOP 62 |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2010-12-03 | 2011-02-08 15:54 | 67 | 2010-11-27 | Structural Engineering - Testing | 500 |  |  | Repair |  | Complete |  | Completed |  | The NW bolt to SOP 62 failed a pull test at 15kN
| 02SL - Stations (LUL) | Cxxx-NCR-000050 | NCR | Pull test failure SOP 11 |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2010-12-03 | 2011-02-08 15:57 | 67 | 2010-11-27 | Structural Engineering - Testing | 500 |  |  | Rework |  | Complete |  | Completed |  | The NE bolt to SOP 11 started to creep at 31kN and moved 3mm on 35kN during a pull test. It was decided this constituted a pull test failure
| 02SL - Stations (LUL) | Cxxx-NCR-000051 | NCR | Pull test failure SOP 22 |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2010-12-03 | 2011-02-08 16:18 | 67 | 2010-11-27 | Structural Engineering - Bolted Connections | 500 |  | Material | Repair |  | Complete |  | Completed |  | The SE corner bolt of SOP 22 moved by 4mm on 34kN during a pull test. Although it took 80kN to actually pull it out it was judged as a failure
| 02SL - Stations (LUL) | Cxxx-NCR-000052 | NCR | Pull test failure SOP 6 |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2010-12-03 | 2011-02-08 16:21 | 67 | 2010-11-27 | Structural Engineering - Testing | 500 |  |  | Rework |  | Complete |  | Completed |  | The SE corner bolt to SOP 6 failed a pull out test at 25kN
| 02SL - Stations (LUL) | Cxxx-NCR-000053 | NCR | Pull test failure SOP 7 |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2010-12-03 | 2011-02-08 16:27 | 67 | 2010-11-27 | Structural Engineering - Testing | 500 |  |  | Repair |  | Complete |  | Completed |  | The corner bolt to SOP 7 failed a pull out test at 16kN
| 02SL - Stations (LUL) | Cxxx-NCR-000054 | NCR | Pull test failure SOP 15 |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2010-12-03 | 2011-02-08 16:28 | 67 | 2010-11-27 | Structural Engineering - Testing | 500 |  |  | Repair |  | Complete |  | Completed |  | The corner bolt to SOP 15 failed a pull test at 34kN
| 02SL - Stations (LUL) | Cxxx-NCR-000055 | NCR | Pull test failure SOP 51 |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2010-12-03 | 2011-02-08 16:30 | 67 | 2010-11-27 | Structural Engineering - Testing | 500 |  |  | Rework |  | Complete |  | Completed |  | The corner bolt to SOP 51 failed a pull out test at 20kN
| 02SL - Stations (LUL) | Cxxx-NCR-000056 | NCR | Pull test failure SOP 41 |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2010-12-03 | 2011-02-08 16:32 | 67 | 2010-11-27 | Structural Engineering - Testing | 500 |  | Material | Rework |  | Complete |  | Completed |  | The corner bolt to SOP 41 failed a pull out test at 20kN
| 02SL - Stations (LUL) | Cxxx-NCR-000057 | NCR | Vehicle deck towers SOP's 42 & 46 |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2010-12-03 | 2011-02-08 16:33 | 67 | 2010-11-29 | Structural Engineering - Steel Member | 500 |  |  | Use As-Is |  | Complete |  | Completed |  | The towers at SOP's 42 & 46 have been installed with an orientation 180' to the design. This means the bracings in the north-south direction are set with an opposite hand to the other bracings on the vehicle deck
| 02SL - Stations (LUL) | Cxxx-NCR-000058 | NCR | Mismatch of baseplate holes with drilled bolt holes - vehicle deck |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2010-12-03 | 2011-04-07 13:49 | 125 | 2010-11-29 | Structural Engineering - Structural Engineering - General | 500 |  |  | Rework |  | Complete |  | Completed |  | 31no holes in various locations of the vehicle deck baseplates do not line up cleanly with the bolt holes drilled into the platform. See attached drawing
| 02SL - Stations (LUL) | Cxxx-NCR-000071 | NCR | Damage to LU property |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2011-01-31 | 2011-07-21 11:40 | 171 | 2011-01-24 | Construction Health & Safety - Construction Health & Safety General | 500 |  | Damaged | Use As-Is |  | Complete |  | Completed |  | During steelwork lifting operations in possession on 18th January 2011 the load came into contact with the Secondary Means of Escape stairs (SME). This caused minor damage to a 1.5m section of the northern flashing on the crossbridge between Platforms 5 & 6.
| 02SL - Stations (LUL) | Cxxx-NCR-000072 | NCR | Steel member clash with parapet wall |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2011-01-31 | 2011-07-21 11:45 | 171 | 2011-01-28 | Structural Engineering - Steel Member | 500 |  | Design | Rework |  | Complete |  | Completed |  | The horizontal member shown on the attached Word document at level +108.462 clashed with the brick parapet wall. Referring to Drg Cxxx-HYD-S-DDB-D061_WS105_Z-70003 P06 the member is shown as partially running through the brick wall so it would appear that this is what was required
| 02SL - Stations (LUL) | Cxxx-NCR-000073 | NCR | Steel member clash with SME exit |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2011-02-07 | 2011-07-21 11:50 | 164 | 2011-01-28 | Structural Engineering - Steel Member | 500 |  | Design | Rework |  | Complete |  | Completed |  | During a survey of the steelwork around the SME exit it was discovered that part of the 686x254 UB on Platform 6 side between GL's 12 & 13 clashed with the roof of the SME exit onto Durward St
| 02SL - Stations (LUL) | Cxxx-NCR-000087 | NCR | Making of concrete cubes - 6th April 2011 |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2011-05-04 | 2011-07-25 09:20 | 82 | 2011-04-17 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | Samples taken for the eastern run on slab ramp were compacted using a metal bar that did not have a rounded end.
| 02SL - Stations (LUL) | Cxxx-NCR-000091 | NCR | 8no trimmer beams on Pedestrian deck not fire-proofed |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2011-06-03 | 2011-07-25 09:07 | 52 | 2011-05-26 | Fire - Fire Systems & General | 500 |  | System Defect | Use As-Is |  | Complete |  | Completed |  | Trimmer beams have been installed in the Pedestrian Deck, connected to the welded frames, with the surface painted.
| 02SL - Stations (LUL) | Cxxx-NCR-000095 | NCR | The Concrete Cube Results for the RC Walls on the East Run on Slab |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2011-07-08 | 2011-08-11 13:37 | 34 | 2011-06-29 | Civil - Civil Engineering General | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | The Concrete Cube Results for the RC Walls on the East Run on Slab have not gained the Specified Strength.
| 02SL - Stations (LUL) | Cxxx-NCR-000096 | NCR | Missing Nuts to the Vehicle Deck |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2011-08-19 | 2011-08-17 08:14 | -2 | 2011-08-16 | Civil - Structural Engineering | 500 |  | Supervision/Management | Repair |  | Complete |  | Completed |  | Four missing nuts has been identified ( two each side) from north and south end of the trimmer beam located at grid line A between 2 and 1A.
| 02SL - Stations (LUL) | Cxxx-NCR-000004 | NCR | Pile 2A out of position |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2010-11-12 | 2011-02-16 19:05 | 96 | 2010-10-29 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Repair |  | Complete |  | Completed |  | Pile 2A out of positiion as indicated on the attached sketch 110563 /SK/ 0123
| 02SL - Stations (LUL) | Cxxx-NCR-000006 | NCR | M Statement Schedule |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2010-11-19 | 2010-11-19 14:54 | 0 | 2010-11-18 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Repair |  | Complete |  | Completed |  | JMS Schedule LCxxx40/REG/0001 updated 25 Oct 10 had no entry for the submission of Mst for the Utility Building M & E installation during a surveilance audit on 28th Oct 10
| 02SL - Stations (LUL) | Cxxx-NCR-000009 | NCR | Temporary Meter Room - lifting Eyes |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2011-03-17 | 2011-12-01 16:15 | 259 | 2011-03-03 | Civil - Construction Health & Safety | 500 |  | Supervision/Management | Repair |  | Complete |  | Completed |  | Bent T12 reinforcement stirrups cast into the precast slab to enable the lifting of each end off the shutter is non compliant with response to TQ XX and potential for use as primary non certificated lifting points. Remedy 1. Approved Lifting Plan for the slab 2. Remedial measures to cut out remove temp lifting stirrups; provide compliant cover and make good with a proprietary material.
| 03SR - Stations (RfL) | Cxxx-NCR-000163 | NCR | No slump or cubes taken - Piling Platform |  | Contr |  | PML - Pudding Mill Lane Portal (Central) |  | 2010-10-22 | 2011-02-15 13:27 | 116 | 2010-10-20 | Civil - Civil Engineering General | 500 |  | System Defect | Use As-Is |  | Complete |  | Completed |  | No slump test to concrete and no cube samples taken during concrete pour for Piling Platform A Section 3.
| 03SR - Stations (RfL) | Cxxx-NCR-000164 | NCR | No compaction to fill material |  | Contr |  | PML - Pudding Mill Lane Portal (Central) |  | 2010-10-25 | 2010-11-03 13:42 | 9 | 2010-10-20 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | Cohesive backfill material not compacted in north D wall trench as per HA specification SHW 800 series.
| 03SR - Stations (RfL) | Cxxx-NCR-000165 | NCR | Insufficient management of concrete pour |  | Contr |  | PML - Pudding Mill Lane Portal (Central) |  | 2010-10-24 | 2010-11-10 13:59 | 17 | 2010-10-20 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | Time between concrete discharges exceeded HA specification SHW 1700 series clause 1710 (please refer to the attached marked sketch-pour location)
| 03SR - Stations (RfL) | Cxxx-NCR-000169 | NCR | Concrete Pour 13/10/2010 |  | Contr |  | PML - Pudding Mill Lane Portal (Central) |  | 2010-11-03 | 2010-11-29 18:56 | 26 | 2010-10-27 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | 1. Cover to reinforcement not as per design 2. Supports under screed rails out of HA specification 3. FOD's in the pour area 4. Tying wire out of HA specification.
| 03SR - Stations (RfL) | Cxxx-NCR-000170 | NCR | IRF Not submitted 13/10/2010 |  | Contr |  | PML - Pudding Mill Lane Portal (Central) |  | 2010-11-03 | 2010-11-10 13:17 | 7 | 2010-10-27 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | Inspection requests (IRF) were not raised for the piling platform works.
| 03SR - Stations (RfL) | Cxxx-NCR-000171 | NCR | ITP not accepted by CRL |  | Contr |  | PML - Pudding Mill Lane Portal (Central) |  | 2010-11-03 | 2010-11-10 13:25 | 7 | 2010-10-27 | Civil - Civil Engineering General | 500 |  | System Defect | Use As-Is |  | Complete |  | Completed |  | Piling platform works started without an ITP accepted by the CRL project Manager.
| 03SR - Stations (RfL) | Cxxx-NCR-000181 | NCR | Time between concrete discharge exceeded HA Spec |  | Contr |  | PML - Pudding Mill Lane Portal (Central) |  | 2010-11-10 | 2010-12-06 15:29 | 26 | 2010-11-03 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | Time between concrete discharges exceeded HA specification SHW 1700 series clause 1710, exceed specification by 6 minutes. (location: Piling platform A section 7)
| 03SR - Stations (RfL) | Cxxx-NCR-000190 | NCR | Insufficient management of concrete pour |  | Contr |  | PML - Pudding Mill Lane Portal (Central) |  | 2010-11-15 | 2010-11-16 18:00 | 1 | 2010-11-09 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | Time between concrete discharges exceeded HA specification SHW 1700 series clause 1710 (Location: Guide walls S3 S4 S5)
| 03SR - Stations (RfL) | Cxxx-NCR-000203 | NCR | NCR - Piling Platform E |  | Contr |  | PML - Pudding Mill Lane Portal (Central) |  | 2011-05-31 | 2011-05-27 17:02 | -4 | 2010-11-29 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | Time between concrete discharges exceeded HA specification SHW 1700 series clause 1710 (Piling Platform E)
| 03SR - Stations (RfL) | Cxxx-NCR-000209 | NCR | Documents not in Documentum/eB |  | Contr |  | PML - Pudding Mill Lane Portal (Central) |  | 2010-12-24 | 2011-05-16 09:36 | 143 | 2010-12-02 | Civil - Civil Engineering General | 500 |  | System Defect | Rework |  | Complete |  | Completed |  | Approximately 80 documents out of the approximately 290 documents listed in the C248 DRIR (approx 25%) have notes that they are to be loaded into Documentum. A check of a sample of 5 of the documents (eg P30202-C1M62-C00-D-73450 Rev A1) noted as not loaded into Documentum confirmed this.
| 03SR - Stations (RfL) | Cxxx-NCR-000210 | NCR | Identification of Superseded Drawings |  | Contr |  | PML - Pudding Mill Lane Portal (Central) |  | 2010-12-24 | 2011-06-17 13:44 | 175 | 2010-12-02 | Civil - Civil Engineering General | 500 |  | System Defect | Rework |  | Complete |  | Completed |  | The site file of hard copies of drawings contains copies of both the FDC reinforcement design and the contractor’s reinforcement design of diaphragm wall panels N7 to N10 and S7 to S10 with no indication that the FDC design of these panels has been superseded. Documentum contains copies of the FDC design drawings with no indication on those that have been superseded by the contractor’s reinforcement design of diaphragm wall panels N7 to N10 and S7 to S10.
| 03SR - Stations (RfL) | Cxxx-NCR-000216 | NCR | Construction Drawings Produced by CSJV |  | Contr |  | PML - Pudding Mill Lane Portal (Central) |  | 2010-12-08 | 2010-12-08 15:04 | 0 | 2010-12-07 | Civil - Civil Engineering General | 500 |  | Design | Use As-Is |  | Complete |  | Completed |  | We are aware of the production of fabrication drawings by , however formal issue of these documents is outstanding. Once received these may require transmission to certain FDC's for acceptance, this matter requires urgent resolution.
| 03SR - Stations (RfL) | Cxxx-NCR-000243 | NCR | Test records - signatures not identifiable |  | Contr |  | PML - Pudding Mill Lane Portal (Central) |  | 2010-12-23 | 2011-01-04 12:25 | 12 | 2010-12-20 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | Geothechnical Services test records - signatures not identifiable
| 03SR - Stations (RfL) | Cxxx-NCR-000244 | NCR | CBR Test |  | Contr |  | PML - Pudding Mill Lane Portal (Central) |  | 2010-12-23 | 2011-01-04 12:37 | 12 | 2010-12-20 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | Geothechnical Services using jack on CBR test past calibration test. The error was leaving an old calibration label on the jack.
| 03SR - Stations (RfL) | Cxxx-NCR-000245 | NCR | Insufficient management of concrete pour |  | Contr |  | PML - Pudding Mill Lane Portal (Central) |  | 2010-12-23 | 2011-01-04 12:54 | 12 | 2010-12-20 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | Time between concrete discharges exceeded HA specification SHW 1700 series clause 1710, exceed specification. (location: Piling platform E section 2)
| 03SR - Stations (RfL) | Cxxx-NCR-000246 | NCR | No UKAS test house on site |  | Contr |  | PML - Pudding Mill Lane Portal (Central) |  | 2010-12-23 | 2011-01-04 12:43 | 12 | 2010-12-20 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | No UKAS accredited test house on site during concrete pour of Guide Wall pannel S12. no slump test, cubes or temperature was taken. Location: Guide Walls Panel S12
| 03SR - Stations (RfL) | Cxxx-NCR-000247 | NCR | Incorrect number of cubes |  | Contr |  | PML - Pudding Mill Lane Portal (Central) |  | 2010-12-23 | 2011-01-04 12:49 | 12 | 2010-12-20 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | Following the concreting of panels S08, S07 & S06 it has been noted that not enough cubes have been taken. Panel S08 should have had 10nr sets of 7 taken (6nr sets of 4 actually taken). Panel S07 should have had 9nr sets of 7 taken (6nr sets of 4 actually taken). Panel S06 should have had 12nr sets of 7 taken (6nr sets of 4 actually taken).
| 03SR - Stations (RfL) | Cxxx-NCR-000248 | NCR | Cold weather concreting |  | Contr |  | PML - Pudding Mill Lane Portal (Central) |  | 2010-12-23 | 2011-01-04 12:59 | 12 | 2010-12-20 | Civil - Civil Engineering General | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | Concrete temperature was not monitored through out the pour. Location: Platform E section 3
| 03SR - Stations (RfL) | Cxxx-NCR-000249 | NCR | Steel reinforcement temperature not monitored prior to welding. |  | Contr |  | PML - Pudding Mill Lane Portal (Central) |  | 2010-12-23 | 2011-01-04 12:15 | 12 | 2010-12-20 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | Steel reinforcement temperature not monitored prior to welding. Location PML (SITE 1) D Wall Panel S5
| 03SR - Stations (RfL) | Cxxx-NCR-000268 | NCR | Concrete loads rejected |  | Contr |  | PML - Pudding Mill Lane Portal (Central) |  | 2011-01-25 | 2011-01-28 16:27 | 3 | 2011-01-18 | Civil - Civil Engineering General | 500 |  | Material | Rework |  | Complete |  | Completed |  | 5 loads of concrete from same concrete pour have been rejected on site due to flow test being out of specification. (D Wall panel S5)
| 03SR - Stations (RfL) | Cxxx-NCR-000269 | NCR | Material not inspected in the batching plan |  | Contr |  | PML - Pudding Mill Lane Portal (Central) |  | 2011-01-31 | 2011-01-28 14:32 | -3 | 2011-01-18 | Civil - Civil Engineering General | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | Following audit of __ batching plant (Bow) on 12/01/2011, nonconformity was identified as below: - There is no evidance of Incoming materials (sand, aggregate) inspection in the batching plant (Audit report ref:-C248-RPT-006)
| 03SR - Stations (RfL) | Cxxx-NCR-000270 | NCR | Some shells in the sand |  | Contr |  | PML - Pudding Mill Lane Portal (Central) |  | 2011-01-31 | 2011-03-17 17:38 | 45 | 2011-01-18 | Civil - Civil Engineering General | 500 |  | Material | Repair |  | Complete |  | Completed |  | Following audit (Audit report ref:-C248-RPT-006) of __ batching plant (Bow) on 12/01/2011, nonconformity was identified as below: - There is some contamination in the sand stock bay used for the PML project (Some shells, evidence of 2 type of sand (mortar type).
| 03SR - Stations (RfL) | Cxxx-NCR-000271 | NCR | IFC drawing (N10 RC detailing) with TBC note |  | Contr |  | PML - Pudding Mill Lane Portal (Central) |  | 2011-01-19 | 2011-01-21 17:20 | 2 | 2011-01-18 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | Drawing No. 271035-DRG-N10-001 Rev C02, NF elevation on panel No.N10, panel No.S10 sim but handed detail shows detail 1 (section x-x) roof slab level detail as being TBC (To be Confirmed). As this is a for contruction drawing, TBC should not be on there.
| 03SR - Stations (RfL) | Cxxx-NCR-000272 | NCR | Welders varying detail without approval from Engineer in charge |  | Contr |  | PML - Pudding Mill Lane Portal (Central) |  | 2011-01-19 | 2011-01-21 17:27 | 2 | 2011-01-18 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Repair |  | Complete |  | Completed |  | Lifting band detail welded not as per approved construction drawing The 300mm tail on the lifting band part 1 (lifting band detail, Drawing No. 271035-DRG-N10-001 Rev C02) has been supplied as 400mm. As a result the 450mm long splice, part 2 (lifting band detail, Drawing No. 271035-DRG-N10-001 Rev C02) was omitted from the lifting band detail. The two 400mm tails on the lifting band part 1 have been welded together instead.
| 03SR - Stations (RfL) | Cxxx-NCR-000280 | NCR | Missing shear links cage N9 |  | Contr |  | PML - Pudding Mill Lane Portal (Central) |  | 2011-01-25 | 2011-01-28 16:05 | 3 | 2011-01-24 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Rework |  | Complete |  | Completed |  | 1 set of 7no. Links (BM43 & BM44) missing above top box-out and 3 sets of 7no. links (BM43 & BM44) missing above lower box-out of cage for Diaphragm wall panel N9. This was noticed by the __ engineer during a routine inspection. and CRL were immediately informed of the problem prior to the formal inspection.
| 03SR - Stations (RfL) | Cxxx-NCR-000290 | NCR | The reinforcement cage for Pile E35 on the East Retaining Wall lifted during concrete pour |  | Contr |  | PML - Pudding Mill Lane Portal (Central) |  | 2011-02-11 | 2011-06-02 10:23 | 111 | 2011-01-28 | Civil - Civil Engineering General | 500 |  | Workmanship | Rework |  | Complete |  | Completed |  | The reinforcement cage for Pile E35 on the East Retaining Wall lifted during concrete pour. This has resulted in an as-built top of steel of 108.133m TD. As-built cage toe level = 93.783m TD. This is a function of the light cages and workability of the concrete, being placed through small diameter tremmies.
| 03SR - Stations (RfL) | Cxxx-NCR-000291 | NCR | Extracting the temporary casing on Pile E35 |  | Contr |  | PML - Pudding Mill Lane Portal (Central) |  | 2011-02-11 | 2011-06-14 14:03 | 123 | 2011-01-28 | Civil - Civil Engineering General | 500 |  | Design | Repair |  | Complete |  | Completed |  | When extracting the temporary casing on Pile E35, the concrete slumped into a cavity under the piling platform. The as-built concrete casting level is 106.912m TD. Some piling platform material fell into the top of the pile (see attached photographs). In order to maintain the integrity of the piling platform, the pile was topped up to ground level with concrete. During casing installation, whole bricks and large lumps of concrete were encountered which can displace additional material into the bore.
| 03SR - Stations (RfL) | Cxxx-NCR-000295 | NCR | The coupled slab starters (BM21) are out of tolerance |  | Contr |  | PML - Pudding Mill Lane Portal (Central) |  | 2011-02-15 | 2011-06-21 15:21 | 126 | 2011-02-01 | Civil - Civil Engineering General | 500 |  | Design | Use As-Is |  | Complete |  | Completed |  | The coupled slab starters (BM21) are +40mm out of tolerance. (PML Site 1 D Wall panel S11)
| 03SR - Stations (RfL) | Cxxx-NCR-000329 | NCR | 1 No. __ Lock coupler for top of wall (panel N6) cracked |  | Contr |  | PML - Pudding Mill Lane Portal (Central) |  | 2011-03-03 | 2011-03-09 17:15 | 6 | 2011-02-17 | Civil - Civil Engineering General | 500 |  | Material | Rework |  | Complete |  | Completed |  | During installation of __ Lock couplers (LL25B1) to D wall panel N6 the coupler split along the line of bolts. The bolts were being tightened using an air powered impact wrench. Likely material defect
| 03SR - Stations (RfL) | Cxxx-NCR-000349 | NCR | 2 number 28 day cube results from D wall Panel S5 Cast failed to meet the requirements of the project specification |  | Contr |  | PML - Pudding Mill Lane Portal (Central) |  | 2011-03-18 | 2011-04-07 17:20 | 20 | 2011-03-04 | Civil - Civil Engineering General | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | 2 number 28 day cube results from Panel S5 Cast on 17/12/10 failed to meet the requirements of the project specification. Average 28 day cube result was 31n/mm2 i.e. < fck-4.
| 03SR - Stations (RfL) | Cxxx-NCR-000351 | NCR | The reinforcement cage for Pile E19 on the East Retaining Wall lifted during concrete pour |  | Contr |  | PML - Pudding Mill Lane Portal (Central) |  | 2011-03-25 | 2011-06-02 10:26 | 69 | 2011-03-04 | Civil - Civil Engineering General | 500 |  | Workmanship | Rework |  | Complete |  | Completed |  | On Pile E19 the cage was placed and the TOS level was taken at 108.021 TD(approximately 124mm above design level to allow for potential slumping). However, after extracting the temporary casing on Pile E19, the As Built Level of top of steel was taken at 108.074m TD (177mm above design level) Which is 27mm out of tolerance.
| 03SR - Stations (RfL) | Cxxx-NCR-000352 | NCR | Sheet pile installed at the City Mill River hit an obstruction |  | Contr |  | PML - Pudding Mill Lane Portal (Central) |  | 2011-03-18 | 2011-05-26 11:42 | 69 | 2011-03-04 | Civil - Civil Engineering General | 500 |  | Design | Use As-Is |  | Complete |  | Completed |  | The first pile installed at the City Mill River hit an obstruction and was cut in order for the rest of the sheet piles to be installed. The sheet pile has a total length of 7.5 mtrs and only reached a toe depth of 97.489 (refused penetration by 4.639m). Please see attached sketch for the position of the sheet pile.
| 03SR - Stations (RfL) | Cxxx-NCR-000353 | NCR | The Configuration of the CMR Sheet piles at SOP 6 has been installed incorrectly |  | Contr |  | PML - Pudding Mill Lane Portal (Central) |  | 2011-03-21 | 2011-05-26 11:32 | 66 | 2011-03-04 | Civil - Civil Engineering General | 500 |  | Workmanship | Rework |  | Complete |  | Completed |  | The Configuration of the Sheet piles at SOP 6 on drawing P30202-C1M62-R00-D-73231 has been installed incorrectly. The sheet piles along the line between SOP5 and SOP6 have been intersected by the sheet pile line along the line of SOP6 and SOP7
| 03SR - Stations (RfL) | Cxxx-NCR-000370 | NCR | Guide Walls S24 - S26 Time between concrete discharge exceed HA specification |  | Contr |  | PML - Pudding Mill Lane Portal (Central) |  | 2011-03-22 | 2011-06-01 15:46 | 71 | 2011-03-15 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | Guidewall (temporary works) for panels 24 to 26 were cast on 17/02/11. Total concrete volume was 20m3, formed of 2no. 8m3 loads, and a single 4m3 part load to complete the pour. Highways agency specification 1700 for time between pouring of concrete loads specifies no longer than 30mins. The 4m3 part load exceeded this maximum allowable time. (1h 30min)
| 03SR - Stations (RfL) | Cxxx-NCR-000371 | NCR | Guide Walls S24 - S26 no slump test to concrete taken during concrete pour for last wagon delivery |  | Contr |  | PML - Pudding Mill Lane Portal (Central) |  | 2011-03-22 | 2011-06-01 15:31 | 71 | 2011-03-15 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | Guidewall (Temporary works) for panels 24 to 26 were cast on 17/02/11. Total concrete volume was 20m3, formed of 2no. 8m3 loads, and a single 4m3 part load to complete the pour. ITP specifies the consistence of concrete is to be slump tested on every load. The third part load of 4m3 was not slump tested. The consistence of the concrete was observed by the guidewall subcontractor to be no dissimilar from the previously tested 8m3 loads, which were within tolerance.
| 03SR - Stations (RfL) | Cxxx-NCR-000372 | NCR | Diaphragm Wall Panel S6 was damaged during preparatory works for the temporary sheet piles tie back ground beam |  | Contr |  | PML - Pudding Mill Lane Portal (Central) |  | 2011-03-30 | 2011-06-01 16:03 | 63 | 2011-03-16 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Repair |  | Complete |  | Completed |  | The 75mm concrete cover (to reinforcement) of the corner of the D-Wall S6 Panel (West side of the North-West corner) was damaged and was removed during demolition of the Guide wall works (Diaphragm Wall Panel S6 was damaged during preparatory works for the temporary sheet piles tie back ground beam). The local damage comprises only about 400mm of the permanent works (from the top of the diaphragm wall) in the TBM chamber area.
| 03SR - Stations (RfL) | Cxxx-NCR-000387 | NCR | 2 number 28 day cube results from DLR Retaining Wall Pile E25 failed to meet the requirements of the project specification. |  | Contr |  | PML - Pudding Mill Lane Portal (Central) |  | 2011-04-22 | 2011-06-17 14:05 | 56 | 2011-03-30 | Civil - Civil Engineering General | 500 |  | Material | Rework |  | Complete |  | Completed |  | 2 number 28 day cube results (31.8N/mm2 and 33.6 N/mm2) from Pile E25 Cast on 17/02/11 failed to meet the requirements of the project specification 40N/mm2. Average 28 day cube result was 32.7N/mm2
| 03SR - Stations (RfL) | Cxxx-NCR-000414 | NCR | D wall panel S6 the 1200 leaf that is in the 11KVA design was detailed and cast with the wrong couplers |  | Contr |  | PML - Pudding Mill Lane Portal (Central) |  | 2011-04-29 | 2011-06-21 15:13 | 53 | 2011-04-15 | Civil - Civil Engineering General | 500 |  | Design | Rework |  | Complete |  | Completed |  | D wall panel S6 (constructed on 10/12/10) the 1200 north leaf was detailed and cast with the wrong couplers. Site fabrication drawings 271035-DRG-S06-001 C01 and 271035-DRG-S06-002 C01 were issued for construction on 30/11/10. These drawings were based on Mott Mcdonald drawings P30303-C1M62-C00-D-71220 C01 and P30303-C1M62-C00-D-71230 C01. Post panel installation, __ were informed that drawings 271035-DRG-S06-001 C01 and 271035-DRG-S06-002 C01 should have been based on Mott Mcdonald drawings P30303-C1M62-C00-D-71150 C01 and P30303-C1M62-C00-D-71160 C01. These drawings indicated a panel width of 1000mm. The site fabrication drawings were issued for acceptance. No comment was made on the drawings prior to constructing the panel. Comment was made on the __ drawings on 28/01/11, and Panel N6 was changed in time for construction. (Please refer to PTR number: RFI 221 & 222)
| 03SR - Stations (RfL) | Cxxx-NCR-000415 | NCR | D Wall panel N7 (1 No.) top row of couplers are out of tolerance due to cumulative errors i.e. Guide wall tolerance, coupler set out. |  | Contr |  | PML - Pudding Mill Lane Portal (Central) |  | 2011-04-29 | 2011-06-21 15:07 | 53 | 2011-04-15 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | D Wall panel N7 (constructed on 01/02/11) 1 No. top row of couplers are out of tolerance due to cumulative errors i.e. Guide wall tolerance, coupler set out. As built guidewall levels were recorded by to be within tolerance. Upon placing the cage, the cage was found to be 67mm lower than the design level. Guidewall: Design top of guidewal = +104.900 ATD Level of top of guidewall immediately after GW construction = 104.895ATD Post panel construction, top of guide wall level = +104.889m ATD Panel reinforcement: Design top of steel (from top of lifting band) = +105.100m ATD Pre Pour Top of Steel (from top of lifting band) = +105.096m ATD Post Pour Top of Steel (from top of lifting band) = + 105.033m ATD (demonstrating guidewall and cage drop of approximately 63mm during construction of panel).
| 03SR - Stations (RfL) | Cxxx-NCR-000428 | NCR | Bent starter bars on the East retaining wall |  | Contr |  | PML - Pudding Mill Lane Portal (Central) |  | 2011-04-28 | 2011-06-20 13:24 | 53 | 2011-04-26 | Civil - Civil Engineering General | 500 |  | Damaged | Repair |  | Complete |  | Completed |  | Due to bars not being debonded correctly it was difficult to drill and hydraulic burst or use a pile muncher to break down the piles to the correct cut off level. therefore decided to use a Brokk (robotic rock drill) to break the piles. This process has resulted in some of the bars bending on the piles where this technique was used. Please see attached picture.
| 03SR - Stations (RfL) | Cxxx-NCR-000429 | NCR | City Mill River pile starter bars broken |  | Contr |  | PML - Pudding Mill Lane Portal (Central) |  | 2011-04-28 | 2011-06-30 19:15 | 63 | 2011-04-26 | Civil - Civil Engineering General | 500 |  | Damaged | Repair |  | Complete |  | Completed |  | During the pile breakdown process 1no starter bar has broken from the following piles; E7, E33, E52, E55, E59. Please see the attached pictures. This has occured where the top band has encroached past the pile cut odff level. The starter bars were welded to the top band at this point.
| 03SR - Stations (RfL) | Cxxx-NCR-000431 | NCR | Non compliance of specification-pile concrete |  | Contr |  | PML - Pudding Mill Lane Portal (Central) |  | 2011-05-13 | 2011-07-06 18:26 | 54 | 2011-05-06 | Civil - Structural Engineering | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | A blockage occured in the tremmie pipe when concreting Pile E14 on DLR Bridge at CMR which took time to resolve and resulted in the concrete wagon standing.
| 03SR - Stations (RfL) | Cxxx-NCR-000432 | NCR | Adding water to premix concrete on site |  | Contr |  | PML - Pudding Mill Lane Portal (Central) |  | 2011-06-10 | 2011-07-06 18:38 | 26 | 2011-05-06 | Civil - Structural Engineering | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | A blockage in the tremmie pipe when concreting Pile E14 on DLR Bridge at CMR which took time to resolve led to the concrete wagon standing. The concreted started to go stiff during this time and to avoid a further blockage as no further concrete could be batched, water was added to the concrete mix against the requirements within the specification. Concrete Batching plant closed without confirmation that no further loads were required
| 03SR - Stations (RfL) | Cxxx-NCR-000433 | NCR | Withdrawal and insertion of tremie pipe during pile concreting |  | Contr |  | PML - Pudding Mill Lane Portal (Central) |  | 2011-05-09 | 2011-07-06 18:44 | 58 | 2011-05-06 | Civil - Structural Engineering | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | A blockage in the tremmie pipe while concreting pile E14 on DLR Bridge at CMR could not be rectifed by surging of the tremmies (normal procedure) which had to be removed from the pile which conflicts with the approved ITP / WPP which requires the tremmies to be 3m in the concrete at all times.
| 03SR - Stations (RfL) | Cxxx-NCR-000459 | NCR | DLR East Retainig Wall pile B3 - cage installed/placed 10mm high |  | Contr |  | PML - Pudding Mill Lane Portal (Central) |  | 2011-06-07 | 2011-06-02 15:24 | -5 | 2011-05-31 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | The reinforcement cage (pile B03) was spliced into 5 no. sections, when the cage was installed/placed. it was recorded as being 10mm high and could not be lowered any further.
| 03SR - Stations (RfL) | Cxxx-NCR-000465 | NCR | Specs Applicable to CMR Bridge Retaining Wall |  | Contr |  | PML - Pudding Mill Lane Portal (Central) |  | 2011-06-30 | 2011-06-23 11:35 | -7 | 2011-06-03 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Rework |  | Complete |  | Completed |  | Specifications for the retaining wall including piles, pilecaps and wall are not clearly defined in the contract. Only the ICE Piling Specification is listed with respect to concrete and reinforcement work for the retaining wall and appears inappropriate for the pilecaps and wall. The C248 Project Engineer was unable to confirm that this issue has been resolved.
| 03SR - Stations (RfL) | Cxxx-NCR-000467 | NCR | Specification of CMR Retaining Wall Concrete |  | Contr |  | PML - Pudding Mill Lane Portal (Central) |  | 2011-07-01 | 2011-06-16 11:09 | -15 | 2011-06-03 | Civil - Civil Engineering General | 500 |  | Design | Rework |  | Complete |  | Completed |  | There is a conflict in the specification for the concrete for the CMR retaining wall pilecaps where the civil/structural specification specifies C35/45 concrete and a drawing specifies C30/40 concrete.
| 03SR - Stations (RfL) | Cxxx-NCR-000468 | NCR | Storage of Formwork Sample for Record Purposes |  | Contr |  | PML - Pudding Mill Lane Portal (Central) |  | 2011-07-15 | 2011-10-24 15:54 | 101 | 2011-06-03 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | Neither nor Crossrail Field Engineers are aware of the process/procedure for supplying a sample of formwork board and the Crossrail Field Engineer is not aware of the process/procedure for keeping the sample “for record purposes”.
| 03SR - Stations (RfL) | Cxxx-NCR-000469 | NCR | Records of Pile Cap Dimensions and Levels |  | Contr |  | PML - Pudding Mill Lane Portal (Central) |  | 2011-06-24 | 2011-06-14 16:54 | -10 | 2011-06-03 | Civil - Civil Engineering General | 500 |  | System Defect | Rework |  | Complete |  | Completed |  | Checklist ITP018-1B contains no record of post concrete pour dimensions and levels. An example is checklist ITP018-1B completed for pile caps for panel E5.
| 03SR - Stations (RfL) | Cxxx-NCR-000478 | NCR | Coring took place on the previously cast pile |  | Contr |  | PML - Pudding Mill Lane Portal (Central) |  | 2011-06-16 | 2011-11-29 19:59 | 166 | 2011-06-09 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | DLR Bridge west abutment Pile W16 was cast on the 07/06/11 and cored on 08/06/11. Engineer set out pile W16 of the DLR Bridge west abutment instead of pile W15. Pile casing length of 2.5m was installed and coring of 2m of pile head concrete took place. The coring did not reach the top of the pile reinforcement. Please see attached sketch -C248-SKC-038 Rev 1.0
| 03SR - Stations (RfL) | Cxxx-NCR-000492 | NCR | Plunge column head level out of tolerance |  | Contr |  | PML - Pudding Mill Lane Portal (Central) |  | 2011-06-22 | 2011-06-27 17:14 | 5 | 2011-06-17 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | Plunge column 1 & 2 head level out of tolerance Column 1: 2mm out of tolerance (low) Column 2: 7mm out of tolerance (low)
| 03SR - Stations (RfL) | Cxxx-NCR-000498 | NCR | DLR Bridge West abutment Pile W04 - Cage lifted by 1.6 mtrs above design toe level |  | Contr |  | PML - Pudding Mill Lane Portal (Central) |  | 2011-06-24 | 2011-06-27 17:15 | 3 | 2011-06-20 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | Whilst constructing pile W4, the tremmie pipe got caught on the pile cage. The result of this was that the cage was lifted up approximately 1.6m above design toe level. This gives the top of steel at 102.275m AOD. The dig level was at 81.800 m AOD
| 03SR - Stations (RfL) | Cxxx-NCR-000506 | NCR | Installation of Propping System started without an ITP accepted by the CRL project Manager. |  | Contr |  | PML - Pudding Mill Lane Portal (Central) |  | 2011-06-30 | 2011-07-20 13:37 | 20 | 2011-06-24 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | ITP-015 (C248-SKC-04-STP-CR094_WS111-50028) Installation of Propping System issued via eB to CRL on 14/04/11 and installation of proping system (Temporary works) started on site 18/04/11 without an ITP accepted by the CRL project Manager.
| 03SR - Stations (RfL) | Cxxx-NCR-000513 | NCR | Plunge Column head connection works started without an ITP accepted by the CRL project Manager. |  | Contr |  | PML - Pudding Mill Lane Portal (Central) |  | 2011-07-01 | 2011-07-04 17:37 | 3 | 2011-06-27 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | Plunge Column head connection works started without an ITP accepted by the CRL project Manager. Weld procedure has been accepted (please refer to document No. C248-SKC-C-GPD-CR094_WS111-50009)
| 03SR - Stations (RfL) | Cxxx-NCR-000515 | NCR | Plunge Column No. 2 head plate positioned 90º out of line. |  | Contr |  | PML - Pudding Mill Lane Portal (Central) |  | 2011-07-01 | 2011-07-28 11:05 | 27 | 2011-06-27 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Rework |  | Complete |  | Completed |  | Plunge Column head plate positioned 90º out of line.
| 03SR - Stations (RfL) | Cxxx-NCR-000533 | NCR | Permeation grouting works-The calibration certificates for flow pressure guages does not indicate when the next calibration is due |  | Contr |  | PML - Pudding Mill Lane Portal (Central) |  | 2011-07-11 | 2011-07-14 09:05 | 3 | 2011-07-08 | Civil - Civil Engineering General | 500 |  | System Defect | Rework |  | Complete |  | Completed |  | Permeation grouting works-The calibration certificates for flow pressure guages does not indicate when the next calibration is due and the guages do not have a tag indicating calibrated date/next calibration due date.
| 03SR - Stations (RfL) | Cxxx-NCR-000534 | NCR | Cast in couplers have been displaced during the construction process of D wall panel S9 |  | Contr |  | PML - Pudding Mill Lane Portal (Central) |  | 2011-07-11 | 2011-07-28 13:17 | 17 | 2011-07-08 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | Cast in couplers have been displaced during the construction process of D wall panel S9 to 99.800 m AOD. Please refer to PTR RFI-00523
| 03SR - Stations (RfL) | Cxxx-NCR-000535 | NCR | Damaged thread to cast in couplers to north and south D Wall in the 11 KV box during the construction joint preparation. |  | Contr |  | PML - Pudding Mill Lane Portal (Central) |  | 2011-07-11 | 2011-07-28 13:31 | 17 | 2011-07-08 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Repair |  | Complete |  | Completed |  | Damaged thread to cast in couplers (Approx 30 No.) to north and south D Wall in the 11 KV box during the construction joint preparation for the 11KV roof slab.
| 03SR - Stations (RfL) | Cxxx-NCR-000536 | NCR | D Wall 11kv Box - north Panel N8 |  | Contr |  | PML - Pudding Mill Lane Portal (Central) |  | 2011-07-14 | 2011-09-28 19:03 | 76 | 2011-07-08 | Civil - Civil Engineering General | 500 |  | Damaged | Repair |  | Complete |  | Completed |  | On excavation of the D Wall north Panel 8 in the 11 KV Box, an out of tolerance projection from the D wall was observed this has been caused due to ground obstruction removal. The protrusion was removed in an inappropriate manner. Reinforcement was exposed on removal of part of the protrusion. Please see attached photo.
| 03SR - Stations (RfL) | Cxxx-NCR-000539 | NCR | 11KV box - Plunge columns cross hole sonic logging ducts not grouted up as per specification. |  | Contr |  | PML - Pudding Mill Lane Portal (Central) |  | 2011-07-14 | 2011-07-13 19:28 | -1 | 2011-07-12 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | Plunge columns cross hole sonic logging ducts not grouted up as per specification.
| 03SR - Stations (RfL) | Cxxx-NCR-000541 | NCR | Stiffener plates on Plunge Column 2E was welded without chamfer |  | Contr |  | PML - Pudding Mill Lane Portal (Central) |  | 2011-07-15 | 2011-07-21 11:09 | 6 | 2011-07-13 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | Stiffener plates on Plunge column 2E (see drawing Cxxx-MMD-C-EDR-CRG06-00017 Rev 4.0 for location) was welded without chamfer (25 x 25 snipe).
| 03SR - Stations (RfL) | Cxxx-NCR-000542 | NCR | As-built coordinates of the plunge piles and plunge columns |  | Contr |  | PML - Pudding Mill Lane Portal (Central) |  | 2011-07-15 | 2011-12-14 19:24 | 152 | 2011-07-13 | Civil - Civil Engineering General | 500 |  | Design | Use As-Is |  | Complete |  | Completed |  | As a result of a possible ambiguity in the drawings, the information given may be unclear. The plunge piles have been installed as per the coordinates given on drawing Cxxx-MMD-C-EDR-CRG06-00014 Rev C03. The plunge columns however, have been installed to the offsets shown on drawing no. Cxxx-MMD-C-EDR-CRG06-00017 Rev C02 instead of the coordinates shown on drawing Cxxx-MMD-C-EDR-CRG06-00014 Rev C03.
| 03SR - Stations (RfL) | Cxxx-NCR-000544 | NCR | Diaphragm Wall - water leak to north panel N 7 /8 |  | Contr |  | PML - Pudding Mill Lane Portal (Central) |  | 2011-07-15 | 2011-07-28 07:46 | 13 | 2011-07-13 | Civil - Civil Engineering General | 500 |  | Design | Repair |  | Complete |  | Completed |  | D Wall-water leak to north panel N 7 /8 at approx 99.000 m AOD level.
| 03SR - Stations (RfL) | Cxxx-NCR-000546 | NCR | B32 coupler to 11KV roof slab cast in to Diaphragm wall misaligned during installation of panel S9 |  | Contr |  | PML - Pudding Mill Lane Portal (Central) |  | 2011-07-15 | 2011-07-28 13:20 | 13 | 2011-07-14 | Civil - Civil Engineering General | 500 |  | Damaged | Rework |  | Complete |  | Completed |  | B32 coupler to 11KV roof slab cast in to Diaphragm wall misaligned during installation of panel S9 (1m from panel S8 joint)
| 03SR - Stations (RfL) | Cxxx-NCR-000551 | NCR | 11kV Box Section and Roof Slab Installation Constructed Not in Accordance with Drawing and Specification |  | Contr |  | PML - Pudding Mill Lane Portal (Central) |  | 2011-07-21 | 2011-07-28 10:57 | 7 | 2011-07-20 | Civil - Structural Engineering | 500 |  | Supervision/Management | Rework |  | Complete |  | Completed |  | 11kV Box section and roof slab has been installed incorrectly.
| 03SR - Stations (RfL) | Cxxx-NCR-000552 | NCR | 11kV Box Section and Roof Slab Installation Constructed Not in Accordance with Drawing and Specification |  | Contr |  | PML - Pudding Mill Lane Portal (Central) |  | 2011-07-21 | 2011-07-28 13:27 | 7 | 2011-07-20 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Rework |  | Complete |  | Completed |  | failed to comply with ITP (Ref: C248-SKC-04-STP-CR094_WS111-50027 Rev 2.0) Inspection and Test Plan Reinforced Concrete for Portal Works Point 11 of Section 2 - Inspection and Test Plan referencing the preparation of "Expansion and/or Construction Joint" as a Subcontractor and Contractor hold Point. There is no indication at any point that observed this hold point nor has there been any request made to the Project Manager to undertake review point of inspection.
| 03SR - Stations (RfL) | Cxxx-NCR-000554 | NCR | 11kV Cut & Cover Box Roof Slab Construction Joint - Failure to Install |  | Contr |  | PML - Pudding Mill Lane Portal (Central) |  | 2011-07-21 | 2011-07-28 07:50 | 7 | 2011-07-20 | Civil - Civil Engineering General | 500 |  | Workmanship | Rework |  | Complete |  | Completed |  | installed hydrophilic strips between the D-wall and roof slab in the 11kV box section incorrectly.
| 03SR - Stations (RfL) | Cxxx-NCR-000560 | NCR | 11kV Box Roof Slab - Potential Error to RC Details in Downstand Beam |  | Contr |  | PML - Pudding Mill Lane Portal (Central) |  | 2011-07-28 | 2011-08-17 18:47 | 20 | 2011-07-28 | Civil - Structural Engineering | 500 |  | Design | Rework |  | Complete |  | Completed |  | Jurgen Keiser (Motts MacDonald) said that a few closing off bars may be required for the 11 kV slab at the ends of the beams. B16 would be preferable perhaps B20 nothing bigger.
| 03SR - Stations (RfL) | Cxxx-NCR-000564 | NCR | CMR DLR Bridge West Abutment Piles - Starter bars were bent during pile breakdown and excavation process. |  | Contr |  | PML - Pudding Mill Lane Portal (Central) |  | 2011-08-05 | 2011-09-01 12:34 | 27 | 2011-08-03 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | During the pile breakdown and excavation process starter bars were bent on the following piles; W01, W03, W05, W17 & W18.
| 03SR - Stations (RfL) | Cxxx-NCR-000565 | NCR | Barbers Road - Damage to new potable water main 225mm Ø |  | Contr |  | PML - Pudding Mill Lane Portal (Central) |  | 2011-08-05 | 2011-09-28 19:06 | 54 | 2011-08-04 | Civil - Civil Engineering General | 500 |  | Damaged | Repair |  | Complete |  | Completed |  | During the works on the new manhole MH5 the close by new water main 225mm Ø (MDPE pipe) was damaged with the excavator bucket. Please see attached photos.
| 03SR - Stations (RfL) | Cxxx-NCR-000577 | NCR | Manufacturing of Bridge Bearings started without an ITP accepted by CRL project Manager. |  | Contr |  | PML - Pudding Mill Lane Portal (Central) |  | 2011-08-24 | 2011-11-22 17:34 | 90 | 2011-08-17 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | The 1no fixed and 1no guided bearings for the DLR City Mill River Bridge were manufactured without an ITP accepted by CRL project Manager. ITP (C248-SKC-O4-STP-CR094_WS111-50041) was submitted on 26/7/11 to CRL for acceptance.
| 03SR - Stations (RfL) | Cxxx-NCR-000579 | NCR | South-West Upstand Wall Tie In Detail Into D-Wall (Panel S6) |  | Contr |  | PML - Pudding Mill Lane Portal (Central) |  | 2011-08-19 | 2011-10-07 09:17 | 49 | 2011-08-18 | Civil - Civil Engineering General | 500 |  | Damaged | Repair |  | Complete |  | Completed |  | The South-West Upstand wall tie in detail into panel S6 has a damaged corner due to the guide wall over break operation. (see attached photo).
| 03SR - Stations (RfL) | Cxxx-NCR-000592 | NCR | 4No. pre-stressed beams for the City Mill River failed to meet the requirements of the project specification 60N/mm2. |  | Contr |  | PML - Pudding Mill Lane Portal (Central) |  | 2011-09-26 | 2011-10-24 16:54 | 28 | 2011-09-12 | Civil - Civil Engineering General | 500 |  | Material | Reject |  | Complete |  | Completed |  | have been informed that the 28 day compressive strength for the 4No. pre-stressed beams failed to meet the requirements of the project specification 60N/mm2. Please note the beams have not been incorporated into the permanent works.
| 03SR - Stations (RfL) | Cxxx-NCR-000594 | NCR | 1 number 28 day cube result from DLR Dridge - West Abutment Pile caps cast on 11/08/11 failed to meet the requirements of the project specification 40N/mm2 |  | Contr |  | PML - Pudding Mill Lane Portal (Central) |  | 2011-10-10 | 2012-01-11 17:48 | 93 | 2011-09-14 | Civil - Civil Engineering General | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | One of four concrete cubes taken for the DLR Bridge West abutment pile cap failed to meet the City Mill River Bridges - Civil / Structural Specification (Cxxx-MMD-C-TSC-CRG06-OOOO1 Rev 4.0) 28 day minimum compressive strength of 40N/mm2. A compressive strength of 35.8N/mm2 was achieved. (Please see attached cube results) - Criterion 1 (BS EN206-1:200 Table B.1) Average 28 day cube result was 39.5 N//mm2 i.e. < fck + 1 - Criterion 2 (BS EN206-1:200 Table B.1) test result of 35.8N/mm2 < fck - 4
| 03SR - Stations (RfL) | Cxxx-NCR-000600 | NCR | 11kV Box Section and 25kV Drawpits Installation - RC Detailing & Schedule |  | Contr |  | PML - Pudding Mill Lane Portal (Central) |  | 2011-09-27 | 2011-12-01 19:08 | 65 | 2011-09-23 | Civil - Civil Engineering General | 500 |  | Design | Rework |  | Complete |  | Completed |  | Cxxx revised the 11kV Roof Slab design, raising the finished level of the slab by 100mm.The drawing for the roof slab was reissued along with a reissued drawing of the upstand walls to amend detail. The drawings for the the 25kV Drawpits to sit on top of the slab were not reissued to reflect this change meaning that the bending schedules and reinforcement detailing were incorrect.
| 03SR - Stations (RfL) | Cxxx-NCR-000631 | NCR | Concrete placed in the 11kV Box Draw pit 2 covers slumped 20 mm out of tolerance |  | Contr |  | PML - Pudding Mill Lane Portal (Central) |  | 2012-02-10 | 2012-02-10 19:29 | 0 | 2012-02-02 | Civil - Civil Engineering General | 500 |  |  | Use As-Is |  | Complete |  | Completed |  | Concrete placed in the 11kV Box Draw pit 2 covers slumped 20 mm out of tolerance (slump at 260 mm), used to get concrete to flow under side of Gatic frame otherwise voids would have been formed. see attached site records
| 03SR - Stations (RfL) | Cxxx-NCR-000632 | NCR | Material used to backfill 11kV Box-Chemical Analysis gave values outside the limits in clause 601.14 of SHW. |  | Contr |  | PML - Pudding Mill Lane Portal (Central) |  | 2012-03-02 | 2012-02-27 11:45 | -4 | 2012-02-27 | Civil - Civil Engineering General | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | Material used to backfill 11kV Box structures complied with the Specification for Highway Works Tables 6/1 and 6/2 but the Chemical Analysis gave values outside the limits in clause 601.14. Please find attached chemical test results i.e. tests for WS, OS, and pH value.
| 03SR - Stations (RfL) | Cxxx-NCR-000002 | NCR | Incorrect markings at temporary bus stand |  | Contr |  | PAD - Paddington Station (West) |  | 2010-10-04 | 2010-10-06 15:28 | 2 | 2010-10-06 | Consents - Traffic & Highways | 500 |  | Workmanship | Rework |  | Complete |  | Completed |  | Solid line on all four sides
| 03SR - Stations (RfL) | Cxxx-NCR-000004 | NCR | WCC sign not fitted |  | Contr |  | PAD - Paddington Station (West) |  | 2010-10-20 | 2010-11-03 09:19 | 14 | 2010-10-13 | Consents - Traffic & Highways | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | No sign fitted as yet.
| 03SR - Stations (RfL) | Cxxx-NCR-000014 | NCR | Setting out of __ deep chamber by no40 EBT |  | Contr |  | PAD - Paddington Station (West) |  | 2011-02-18 | 2011-04-13 09:20 | 54 | 2011-02-11 | Utilities Engineering - Telecomms | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | Setting out dimensions perpendicular to station box is acceptable. Setting out parallel to station box is considerably out of position and will potentially have an impact on other chambers and services.
| 03SR - Stations (RfL) | Cxxx-NCR-000237 | NCR | Platform 13/14 infill works |  | Contr |  | PAD - Paddington Station (West) |  | 2010-12-03 | 2010-12-21 11:21 | 18 | 2010-11-26 | Structural Engineering - Steel Member | 500 |  | Design | Use As-Is |  | Complete |  | Completed |  | See attached file NCR 010.
| 03SR - Stations (RfL) | Cxxx-NCR-000238 | NCR | Platform 13/14 canopy infill |  | Contr |  | PAD - Paddington Station (West) |  | 2010-12-03 | 2010-12-14 20:51 | 11 | 2010-11-26 | Structural Engineering - Steel Member | 500 |  | Supervision/Management | Rework |  | Complete |  | Completed |  | See attached NCR 011.
| 03SR - Stations (RfL) | Cxxx-NCR-000239 | NCR | Plat 13/14 canopy infill |  | Contr |  | PAD - Paddington Station (West) |  | 2010-12-03 | 2010-12-21 11:24 | 18 | 2010-11-26 | Structural Engineering - Steel Member | 500 |  | Design | Use As-Is |  | Complete |  | Completed |  | See attached NCR 012.
| 03SR - Stations (RfL) | Cxxx-NCR-000274 | NCR | Listing of contractor documents and storage in eB |  | Contr |  | PAD - Paddington Station (West) |  | 2011-02-03 | 2011-07-14 11:44 | 161 | 2011-01-13 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Rework |  | Complete |  | Completed |  | 1) The document currently used as the equivalent to the CDML does not list any contractor's drawings. Examples are large Diameter Pile reinforcement drawings 02000432Rev A, 0106481 Rev A and 0106412 Rev C. 2)The Management and Acceptance of Field Documentation Procedure requires the contractor to prepare a CDML using the template specified. The template requires links to eB/Documentum. The document currently used as the equivalent to the CDML does not include links to eB/Doumentum or list eB/Doumentum numbers. Examples include ITPs and method statements.
| 03SR - Stations (RfL) | Cxxx-NCR-000275 | NCR | Availability of IFC drawings in eB |  | Contr |  | PAD - Paddington Station (West) |  | 2011-02-03 | 2011-07-14 11:45 | 161 | 2011-01-13 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | Not all of the current IFC status FDC drawings listed in drawing register C131-MMD-Z-LRG-B071-00001 Rev 19.0 are stored in eB. Examples are drawings C131-MMD-S-DDJ-B071_Z-15101 Rev C03, C131-MMD-S-DDA-B071_1-12304 Rev C01 and C131-MMD-A-DDA-B071-2-52010 Rev C01.
| 03SR - Stations (RfL) | Cxxx-NCR-000276 | NCR | __ Fabrication Drawing Submission |  | Contr |  | PAD - Paddington Station (West) |  | 2011-01-14 | 2011-02-17 15:46 | 34 | 2011-01-13 | Civil - Civil Engineering General | 500 |  | Design | Rework |  | Complete |  | Completed |  | The Drawings issued under PAD-CRL-RFI-C271-00267 & 270 were not correctly referenced for Revision and were lacking "checked by" and "approved by" initial/signature.
| 03SR - Stations (RfL) | Cxxx-NCR-000280 | NCR | Lightweight concrete batcher breakdown |  | Contr |  | PAD - Paddington Station (West) |  | 2011-01-28 | 2011-07-14 11:47 | 167 | 2011-01-24 | Civil - Fill | 500 |  | Equipment Breakdown | Repair |  | Complete |  | Completed |  | Lightweight wedge will now be 3 pours instead of the planned 2, so will have construction joints as indicated on the sketch.
| 03SR - Stations (RfL) | Cxxx-NCR-000281 | NCR | P152 position |  | Contr |  | PAD - Paddington Station (West) |  | 2011-01-31 | 2011-07-14 11:49 | 164 | 2011-01-24 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | P152 is out of position by 30mm (North, parallel with GL 59) and 100mm (East, along GL N). Tolerance is 75mm plan position.
| 03SR - Stations (RfL) | Cxxx-NCR-000290 | NCR | Pile 307 - Out of position |  | Contr |  | PAD - Paddington Station (West) |  | 2011-01-28 | 2011-02-09 11:22 | 12 | 2011-01-27 | Civil - Civil Engineering General | 500 |  |  | Rework |  | Complete |  | Completed |  | Coordinates E N 76796.381 36380.164
| 03SR - Stations (RfL) | Cxxx-NCR-000298 | NCR | Shunt Tunnel Rebar Cover |  | Contr |  | PAD - Paddington Station (West) |  | 2011-02-05 | 2011-03-04 14:31 | 27 | 2011-02-03 | Civil - Civil Engineering General | 500 |  |  | Rework |  | Complete |  | Completed |  | The shunt tunnel southern wall (front face) has neglible cover to the starter bar reinforcing. The northern wall (back face) has 100mm cover.
| 03SR - Stations (RfL) | Cxxx-NCR-000305 | NCR | Wind Post Holding Down Bolts |  | Contr |  | PAD - Paddington Station (West) |  | 2011-02-21 | 2011-07-14 11:51 | 143 | 2011-02-14 | Civil - Civil Engineering General | 500 |  | Damaged | Repair |  | Complete |  | Completed |  | The 4No. M12 bolts cast into the concrete foundation have been damaged by the demolition works.
| 03SR - Stations (RfL) | Cxxx-NCR-000309 | NCR | Casing to Pile P114 |  | Contr |  | PAD - Paddington Station (West) |  | 2011-03-09 | 2011-07-14 12:03 | 127 | 2011-02-23 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | Crossrail Input: Casing to be altered to allow follow on works - suggest cut down to below 122.00 (C271 finished level) - note pile platform level is currently around 122.7. Please confirm initial answer from FDC (mail) that permanent casing can be incroporated for permanent design. For information - set-out positions of pile 114/115 are as follows (moved away from sheet wall as per RFI answer). 114: E 76853.631, N 36381.915 115: E 76857.300, N 36380.199
| 03SR - Stations (RfL) | Cxxx-NCR-000314 | NCR | DP10 SteelWork Certification and Records |  | Contr |  | PAD - Paddington Station (West) |  | 2013-03-01 | 2013-01-22 16:56 | -38 | 2011-03-02 | Structural Engineering - Structural Engineering - General | 500 |  | System Defect | Rework |  | Complete |  | Completed |  | Records and certification provided for C271 DP10 steelwork are not compliant with the specification. The following items have not been provided as evidence of certification: 1. Independent Third Party Inspector CV and inspection reports (Sec. 130) 2. Steel Fabrication Records including (Sec. 131): Weld Procedures and approvals, flame cutting procedures, shear cutting procedures, stud welding procedures, N__ procedures, ISO 9001 certification, welder qualification records, N__ qualification records, bolt and fastener certification and welding consumable certification. 3. Steel Protective Treatment Records (Sec. 133) including: protective treatment certification, paint data sheets, surface preparation inspection reports, paint shop environmental reports, concrete encasement pre and post pour records and concrete mix design.
| 03SR - Stations (RfL) | Cxxx-NCR-000321 | NCR | Pilecap G Starter Bars |  | Contr |  | PAD - Paddington Station (West) |  | 2011-03-28 | 2011-07-14 12:06 | 108 | 2011-03-14 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | The un-threaded L-bar (Shape Code 21 - Bar Mark 11 on BS 4030-13-D017), which had an overall length of 1625mm, an A dimension of 1280mm and a B dimension of 475mm, was cast with its top protruding 440mm above the top of concrete, giving an effective anchorage length of 1265mm (or 25d). In addition, the bars do not have a threaded end to accept a threaded __ coupler.
| 03SR - Stations (RfL) | Cxxx-NCR-000330 | NCR | DP10 - Column 1.C5* top plate alignment |  | Contr |  | PAD - Paddington Station (West) |  | 2011-03-31 | 2011-04-28 15:16 | 28 | 2011-03-31 | Civil - Civil Engineering General | 500 |  | Design | Repair |  | Complete |  | Completed |  | As above
| 03SR - Stations (RfL) | Cxxx-NCR-000331 | NCR | Damage to Paint finish on DP10 Steelwork |  | Contr |  | PAD - Paddington Station (West) |  | 2011-04-11 | 2012-08-12 14:45 | 489 | 2011-03-31 | Architectural - Roofing & Exterior Treatment | 500 |  | Supervision/Management | Repair |  | Complete |  | Completed |  | As above
| 03SR - Stations (RfL) | Cxxx-NCR-000332 | NCR | DP10-Encasement to 2.B36 |  | Contr |  | PAD - Paddington Station (West) |  | 2011-04-14 | 2011-09-28 17:26 | 167 | 2011-03-31 | Civil - Civil Engineering General | 500 |  | Design | Rework |  | Complete |  | Completed |  | The last 5m of the beam which should be fully encased (NR side) has been delivered to site without any concrete encasement.
| 03SR - Stations (RfL) | Cxxx-NCR-000333 | NCR | Steework fireproofing - Truss 2T2 (DP10 steelwork) |  | Contr |  | PAD - Paddington Station (West) |  | 2011-04-08 | 2011-10-25 18:12 | 200 | 2011-04-01 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Rework |  | Complete |  | Completed |  | The Truss has been delivered to site without the sprayed vermiculite cement spray. (The truss sections requiring the steel are within an area of 12m by 1.9m (both sides)). There has been no previous proposal to site apply this product in-situ (MS does not state, no temporary works proposals, no possessions booked) - the design intent was to propose a product that can be applied off-site to mitigate the risk/programme quality, cost, and assurance issues with trying to apply insitu above NR and LUL tracks.
| 03SR - Stations (RfL) | Cxxx-NCR-000334 | NCR | DP10 - Concrete encasement |  | Contr |  | PAD - Paddington Station (West) |  | 2011-04-15 | 2013-01-09 15:54 | 635 | 2011-04-01 | Civil - Civil Engineering General | 500 |  | Workmanship | Rework |  | Complete |  | Completed |  | Beams 2.B30, 2.B34, 2.B35, 2.B36, 2.T2 do not meet clause 750 - section 4.3.4 of the specification. (No chamfer to soffit of beams) Beams 2.B30, 2.B34, 2.B35, 2.B36 do not meet clause 660 - section 4.3.4 of the specification. (Dis-colouration - see attached photographs) Beam 2.B36 does not meet clause 105F - section 4.2.1 of the spec. (Void beneath the shelf angle on visible on the northern end of the beam - see attached photograph)
| 03SR - Stations (RfL) | Cxxx-NCR-000335 | NCR | DP10 - Beam 2.T2 Encasement |  | Contr |  | PAD - Paddington Station (West) |  | 2011-04-15 | 2011-07-14 12:11 | 90 | 2011-04-01 | Civil - Civil Engineering General | 500 |  | Workmanship | Rework |  | Complete |  | Completed |  | Please see attached photographs of truss 2.T2. There are several non-conformances against the specification. 1) Surface dis-colouration not acceptable. 2) Surfaces blemishes not acceptable. 3) Formwork jointing not acceptable. 4) Evidence of honeycombing around pockets formed for ties 2.2B4 and 2.2B5. 5) Concrete spacer blocks used on soffit of truss. These have not been submitted for approval. They appear to be garden paving slabs. Their appearance is dissimilar to the concrete used for the encasement which makes them visually unacceptable. 6) Large void and honeycombing noted around several of the spacer blocks used on the soffit (see attached photos). 7) Part of the soffit concrete at the east end of the truss has broken off (see attached photos). 8) Concrete residue from the encasement process left on the basecoat of the steel and not cleaned off.
| 03SR - Stations (RfL) | Cxxx-NCR-000336 | NCR | Steelwork Struts Link Over Platform 14 & 15 |  | Contr |  | PAD - Paddington Station (West) |  | 2013-03-01 | 2013-01-29 09:49 | -31 | 2011-04-04 | Structural Engineering - Structural Engineering - General | 500 |  | Damaged | Repair |  | Complete |  | Completed |  | Struts and splice connection plates installed to bottom flanges of the jack arch on eastern end on platform 14 & 15 have protective coating damage as per attached photo. Materials have been stored track side since August 2010.
| 03SR - Stations (RfL) | Cxxx-NCR-000340 | NCR | DP10 - Beam 2.B34 orientation |  | Contr |  | PAD - Paddington Station (West) |  | 2011-04-28 | 2011-07-21 15:20 | 84 | 2011-04-27 | Civil - Structural Engineering | 500 |  | Supervision/Management | Rework |  | Complete |  | Completed |  | The end plates (1F21 & 1F37) to beam 1108 have been welded on the wrong ends of the beam
| 03SR - Stations (RfL) | Cxxx-NCR-000347 | NCR | Misalignment of bracings 1124 & 1125 |  | Contr |  | PAD - Paddington Station (West) |  | 2011-10-21 | 2012-06-28 08:55 | 251 | 2011-10-18 | Structural Engineering - Bracing | 500 |  | Planning | Use As-Is |  | Complete |  | Completed |  | Bracings are not in line with adjacent members
| 03SR - Stations (RfL) | Cxxx-NCR-000348 | NCR | Damage to geothermal loops in 3No piles |  | Contr |  | PAD - Paddington Station (West) |  | 2011-10-21 | 2012-08-10 17:34 | 294 | 2011-10-18 | Geotechnical Engineering - Concrete - Bored Pile | 500 |  | Damaged | Use As-Is |  | Complete |  | Completed |  | See attached schematic of pipes in piles concerned
| 03SR - Stations (RfL) | Cxxx-NCR-000224 | NCR | Orientation of baseplate |  | Contr |  | PAD - Paddington Station (West) |  | 2011-03-11 | 2011-09-16 12:39 | 189 | 2011-02-17 | Structural Engineering - Steel Member | 500 |  | Design | Rework |  | Complete |  | Completed |  | Bolt hole alignments in fabricated columns were 30 degrees out of alignment. 4No columns affected C301 /C302 / C303 / Cxxx
| 03SR - Stations (RfL) | Cxxx-NCR-000453 | NCR | No approval of design calculations |  | Contr |  | PAD - Paddington Station (West) |  | 2011-05-13 | 2011-07-25 16:57 | 73 | 2011-04-21 | Structural Engineering - Steel Member | 500 |  | Design | Repair |  | Complete |  | Completed |  | design calculations for the steel truss (TW-L109-1), Platform Lift Shaft (LS-03-01D) and Bracing End Connection (LS-03-046) have been submitted to with no evidence of approval
| 03SR - Stations (RfL) | Cxxx-NCR-000520 | NCR | Beam Pre-Casting B1133 |  | Contr |  | PAD - Paddington Station (West) |  | 2011-05-18 | 2011-06-07 13:28 | 20 | 2011-05-16 | Civil - Civil Engineering General | 500 |  | Material | Repair |  | Complete |  | Completed |  | 2No small voids have been noted beneath the shelf angle on Beam B1133 (2B22). This was due to the Top flow 400 concrete stiffening/hydrating during the pour.
| 03SR - Stations (RfL) | Cxxx-NCR-000540 | NCR | Paint Application to Connections |  | Contr |  | PAD - Paddington Station (West) |  | 2011-05-31 | 2011-07-25 17:00 | 55 | 2011-05-19 | Civil - Structural Engineering | 500 |  | Design | Use As-Is |  | Complete |  | Completed |  | Certain TCB's on 's Structural Steel Loads 101 & 102 have paint applied in error due to a missing note on the design drawing.
| 03SR - Stations (RfL) | Cxxx-NCR-000571 | NCR | Water Addition to Concrete |  | Contr |  | PAD - Paddington Station (West) |  | 2011-06-17 | 2011-12-09 14:31 | 175 | 2011-05-24 | Civil - Structural Engineering | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | Initially the concrete delivery failed the workability testing requirements, supplier was advised and the batcher instructed the truck driver to add water (approx 120 litres) to the load. This apparently is allowed in current British / European Standards.
| 03SR - Stations (RfL) | Cxxx-NCR-000572 | NCR | Metal Fibres in Concrete Delivery |  | Contr |  | PAD - Paddington Station (West) |  | 2011-06-17 | 2011-08-15 14:11 | 59 | 2011-05-24 | Civil - Structural Engineering | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | One load on concrete delivered with evidence of metal fibre reinforcement in the mix.
| 03SR - Stations (RfL) | Cxxx-NCR-000606 | NCR | PLatform 15 & 16 Paving |  | Contr |  | PAD - Paddington Station (West) |  | 2011-07-05 | 2011-08-16 17:46 | 42 | 2011-06-07 | Civil - Concrete Pavement | 500 |  | Workmanship | Reject |  | Complete |  | Completed |  | Top level of paving is higher than adjacent platform copings, Joints between top chamfers of slabs is approx 20mm, Excessive steps between joints, Poor quality finish of tiles around column.
| 03SR - Stations (RfL) | Cxxx-NCR-000612 | NCR | Cementitious Splashes on Structural Columns |  | Contr |  | PAD - Paddington Station (West) |  | 2011-08-31 | 2011-09-16 12:54 | 16 | 2011-06-07 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | Platform 15/16 column at GL 60 and liftshaft steel at GL63 have been splashed with concrete when carrying out platform concrete works.
| 03SR - Stations (RfL) | Cxxx-NCR-000613 | NCR | Damaged Paintwork to Structural Steel Columns |  | Contr |  | PAD - Paddington Station (West) |  | 2011-07-26 | 2011-09-19 10:09 | 55 | 2011-06-07 | Civil - Civil Engineering General | 500 |  | Damaged | Repair |  | Complete |  | Completed |  | Paintwork to Gridline 'M' Columns (1st lift - support concourse slab) have been damaged during erection / dismantling of scaffolding. (Brogan)
| 03SR - Stations (RfL) | Cxxx-NCR-000615 | NCR | Triangle Site / LU Platform Steelwork |  | Contr |  | PAD - Paddington Station (West) |  | 2011-07-05 | 2011-09-12 18:36 | 69 | 2011-06-07 | Civil - Civil Engineering General | 500 |  | Material | Rework |  | Complete |  | Completed |  | Member B1212 Fabricated 10mm too long or creep during erection prevented member being bolted in position. Member B1227 within manufacturing tolerances but 6mm short preventing it being bolted into position.
| 03SR - Stations (RfL) | Cxxx-NCR-000618 | NCR | Minipile MP17 600mm out of position (northing) |  | Contr |  | PAD - Paddington Station (West) |  | 2011-07-08 | 2011-09-28 18:04 | 82 | 2011-06-08 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Rework |  | Complete |  | Completed |  | Setting out Northing for minipile MP17 601mm from that specified, casing deviation recorded as 606mm.
| 03SR - Stations (RfL) | Cxxx-NCR-000629 | NCR | Structural Steelwork - Missing Angles on Stubs |  | Contr |  | PAD - Paddington Station (West) |  | 2011-07-11 | 2011-09-19 10:24 | 70 | 2011-06-13 | Civil - Structural Engineering | 500 |  | Design | Repair |  | Complete |  | Completed |  | omitted support angles in the north - south direction from their fabrication drawings thus these angles where not attached during fabrication. __ requested extra supports in an East West Direction following the approval of 's fabrication drawings in order to make the __ design work.
| 03SR - Stations (RfL) | Cxxx-NCR-000630 | NCR | Notching of Structural Steel Column |  | Contr |  | PAD - Paddington Station (West) |  | 2011-06-27 | 2011-09-28 18:02 | 93 | 2011-06-13 | Civil - Structural Engineering | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | Column C204 notched on site due to a fabrication error to allow the connection of beam to the column.
| 03SR - Stations (RfL) | Cxxx-NCR-000631 | NCR | Concrete Encasement - Box Outs too small |  | Contr |  | PAD - Paddington Station (West) |  | 2011-08-05 | 2011-09-12 18:01 | 38 | 2011-06-13 | Civil - Civil Engineering General | 500 |  | Planning | Repair |  | Complete |  | Completed |  | Boxouts in concrete encasement to beams along GL L and J were cast too small to allow connection of BR504 bracings.
| 03SR - Stations (RfL) | Cxxx-NCR-000640 | NCR | Gridline 63/64 Induced Joint |  | Contr |  | PAD - Paddington Station (West) |  | 2011-06-28 | 2011-08-18 11:57 | 51 | 2011-06-14 | Civil - Concrete Pavement | 500 |  | Design | Use As-Is |  | Complete |  | Completed |  | A dowelled construction joint was formed in the platform slab between GL 663 and 64. This should have been an induced joint.
| 03SR - Stations (RfL) | Cxxx-NCR-000657 | NCR | Bedding Mortar to platform 15/16 finishes |  | Contr |  | PAD - Paddington Station (West) |  | 2011-06-30 | 2012-02-10 19:21 | 225 | 2011-06-17 | Civil - Civil Engineering General | 500 |  | Workmanship | Reject |  | Complete |  | Completed |  | Platform slab poured low therefore pavers used excessive bedding depth to lay platform finishes.
| 03SR - Stations (RfL) | Cxxx-NCR-000658 | NCR | Platform Paving |  | Contr |  | PAD - Paddington Station (West) |  | 2011-07-31 | 2011-08-16 18:20 | 16 | 2011-06-17 | Civil - Civil Engineering General | 500 |  | Workmanship | Reject |  | Complete |  | Completed |  | Central section of the platform laid to incorrect height therefore specified gradients from nosing stones have not been acheived. Effected area between GL 60-63.
| 03SR - Stations (RfL) | Cxxx-NCR-000675 | NCR | Platform 15/16 RVAR Nosing Stones |  | Contr |  | PAD - Paddington Station (West) |  | 2011-07-01 | 2012-08-08 14:22 | 404 | 2011-06-24 | Architectural - Flooring | 500 |  | Damaged | Rework |  | Complete |  | Completed |  | Cracks in the mortar between the newly installed RVAR nosing stones and the platform surfacing have been observed at Platform 15/16 between GL 60-62. This is in the area where have recently broken out to form the Stair 02 foundation and the platform slab. It has been reported in the T002 inspection that approx 10No nosing stones have moved by approximately 5-13mm. See attached T002 inspection.
| 03SR - Stations (RfL) | Cxxx-NCR-000690 | NCR | Installation With a Code 3 ITP |  | Contr |  | PAD - Paddington Station (West) |  | 2011-07-15 | 2011-08-22 17:07 | 38 | 2011-07-01 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Repair |  | Complete |  | Completed |  | Pre-cast concrete planks has been installed whilst ITP C272-CAR-O4-STP-B071-50024 Rev 2.0 has staus Code 3 - Not accepted. Work may not proceed.
| 03SR - Stations (RfL) | Cxxx-NCR-000691 | NCR | Pre-cast planks |  | Contr |  | PAD - Paddington Station (West) |  | 2011-07-22 | 2011-08-31 17:44 | 40 | 2011-07-01 | Civil - Civil Engineering General | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | Clause 80.041 The contractor cannot demonstrate that requirements for straightness, squareness, twist and flatness of precast planks have been met.
| 03SR - Stations (RfL) | Cxxx-NCR-000692 | NCR | Lack of Certification and Records from Precast concrete plank Supplier |  | Contr |  | PAD - Paddington Station (West) |  | 2011-07-22 | 2012-07-31 10:16 | 375 | 2011-07-01 | Civil - Civil Engineering General | 500 |  | System Defect | Use As-Is |  | Complete |  | Completed |  | cannot demonstrate the planks received from __ are compliant with the requirements of the Works Information.
| 03SR - Stations (RfL) | Cxxx-NCR-000693 | NCR | Camber of Pre-cast Planks has not been checked. |  | Contr |  | PAD - Paddington Station (West) |  | 2011-07-22 | 2011-08-18 12:09 | 27 | 2011-07-01 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | 1) ITP for installation of pre cast flooring units Rev 3.0, Line 7 - Delivery Inspection and Unit Strength requires a sample check of unit camber (min 10% of delivery) where the acceptance criteria is that camber is no greater than 30% of design figure (not spec requirement of 30% more than predicted value). 2) Checks of camber have not taken place and some planks have been installed. 3) The contractor could not provide the predicted value of the camber.
| 03SR - Stations (RfL) | Cxxx-NCR-000694 | NCR | Records of Differential Camber of Pre-cast Planks |  | Contr |  | PAD - Paddington Station (West) |  | 2011-07-22 | 2012-03-16 10:35 | 238 | 2011-07-01 | Civil - Civil Engineering General | 500 |  | System Defect | Use As-Is |  | Complete |  | Completed |  | When planks are laid side by side to form a suspended floor, the variation in camber shall not exceed 6mm. This requirement of C131-MMD-C-RSP-B071-00012 Rev 4.0, 80.041 will be checked as part of item 11 of the ITP for installation of pre cast flooring units Rev 3.0, the results being recorded on Form CI/CE/HSSQ/PROJFORM/CR/016. Form CI/CE/HSSQ/PROJFORM/CR/016 has no provision for recording differential camber.
| 03SR - Stations (RfL) | Cxxx-NCR-000707 | NCR | Change in conncections at named location |  | Contr |  | PAD - Paddington Station (West) |  | 2011-07-11 | 2011-08-16 09:57 | 36 | 2011-07-07 | Structural Engineering - Bolted Connections | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | The situation sketched on the first page has been installed at B7001-B7006 and B7208-B7210. The situation on the second page is just at one location (B7709). The first sketch showing the 5 lower plug welds (as stated on the drawing) is the case for stiffeners to the following beams: B7001-B7006 and B7208-B7210. The second sketch is specific to just one stiffener for B7006. Both sketches are therefore relevant to B7006. Therefore, use as is is relevant to all the stiffeners, but there is an additional repair to B7006!
| 03SR - Stations (RfL) | Cxxx-NCR-000708 | NCR | RSD Waterproofing |  | Contr |  | PAD - Paddington Station (West) |  | 2011-07-11 | 2012-05-22 12:57 | 316 | 2011-07-08 | Civil - Civil Engineering General | 500 |  | System Defect | Rework |  | Complete |  | Completed |  | Waterproofing works at RSD have commenced without an accepted Inspection and Test Plan. Granite kerb stones have been placed between GL 20 - 19 without waterproofing being tested. How will C272 certify that waterproofing is compliant with specification? CRL have had no visibility of waterproofing inspection and testing process and records.
| 03SR - Stations (RfL) | Cxxx-NCR-000712 | NCR | Mini pile grout strength |  | Contr |  | PAD - Paddington Station (West) |  | 2011-09-02 | 2011-10-27 17:00 | 55 | 2011-07-09 | Civil - Structural Engineering | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | 8No piles are below the required strength at 28 days. See attached spreadsheet for results. 7No of these are expected to achieve the required 40 N/mm2 at 56 days (see predictions in italics) propose to use the 56 day result to demonstrate the required 40N/mm2. For the remaining pile, MP19, the lab has crushed all available cubes. propose to take a core sample from the pile during breaking/trimming to confirm adequate strength. After reviewing the C271 cube results from last year the average increase from 28 days to 56 days is approximately 10N/mm2. This is also demonstrated in the attached strength curve graph supplied by __ for the N-Sure S60 mix. are currently liaising with __ to perform cement content tests on the batches supplied to site and with __ on testing procedures to try and gain a better understanding of why the results were so low. Please see attached cube summary. (Note: Predicted results are shown in italics.)
| 03SR - Stations (RfL) | Cxxx-NCR-000759 | NCR | Precast Hollow Core Flooring Planks East End Concourse (__s 2069 - 2073, 2057 - 2060) |  | Contr |  | PAD - Paddington Station (West) |  | 2011-08-19 | 2011-08-16 18:15 | -3 | 2011-07-21 | Civil - Structural Engineering | 500 |  | System Defect | Repair |  | Complete |  | Completed |  | Planks arrived too short.
| 03SR - Stations (RfL) | Cxxx-NCR-000763 | NCR | Dry riser washout on western section of platform 15/16 |  | Contr |  | PAD - Paddington Station (West) |  | 2011-07-26 | 2011-12-12 18:38 | 139 | 2011-07-22 | Mechanical - Piping | 500 |  | Design | Use As-Is |  | Complete |  | Completed |  | Drawing C131-MMD-M-DDA-B071_2-63110 shows the washout as 25mm. JW (CRL) Comment: The washout pipework has been installed as 25mm diameter instead of the 100mm diameter as shown on the IFC drawing. The pipework has been installed to the correct position as shown in the IFC drawing. Please note drawing 63110 was not issued for construction.
| 03SR - Stations (RfL) | Cxxx-NCR-000766 | NCR | Cracked Hollow Core Flooring Planks (__ 1025, 1033 & 2001) |  | Contr |  | PAD - Paddington Station (West) |  | 2011-08-19 | 2011-08-16 18:02 | -3 | 2011-07-22 | Civil - Structural Engineering | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | __ Units 1025, 1033 & 2001 - units found to be cracked during installation process.
| 03SR - Stations (RfL) | Cxxx-NCR-000767 | NCR | Precast Hollowcore Flooring Planks (__ 2011) - Cracked slabs |  | Contr |  | PAD - Paddington Station (West) |  | 2011-08-19 | 2011-08-18 12:12 | -1 | 2011-07-22 | Civil - Structural Engineering | 500 |  | Damaged | Reject |  | Complete |  | Completed |  | After installation a crack was noticed on __ 2011. On further investigation during daylight it was discovered that the crack went full depth of the units.
| 03SR - Stations (RfL) | Cxxx-NCR-000768 | NCR | Hollowcore Precast Flooring Units (__ 2013) clashes with Column M56 |  | Contr |  | PAD - Paddington Station (West) |  | 2011-08-19 | 2011-08-08 10:29 | -11 | 2011-07-22 | Civil - Structural Engineering | 500 |  | Design | Repair |  | Complete |  | Completed |  | __ plank 2013 clashes with the column at location M56 by 100mm.
| 03SR - Stations (RfL) | Cxxx-NCR-000795 | NCR | Lack of Fencing ITP - Platform 1A Works |  | Contr |  | PAD - Paddington Station (West) |  | 2011-07-29 | 2011-07-26 12:37 | -3 | 2011-07-26 | Civil - Civil Engineering General | 500 |  | System Defect | Use As-Is |  | Complete |  | Completed |  | Inspection and Test Plan was not prepared for the Palisade Fencing erected by H A Marks.
| 03SR - Stations (RfL) | Cxxx-NCR-000796 | NCR | Deck span for new steelwork on RSD |  | Contr |  | PAD - Paddington Station (West) |  | 2011-08-04 | 2011-08-15 14:00 | 11 | 2011-07-26 | Structural Engineering - Structural Engineering - General | 500 |  | Design | Use As-Is |  | Complete |  | Completed |  | Further to PTR 698, the span East of GL 9 of 2175mm is greater than the suggested 1750mm maximum.
| 03SR - Stations (RfL) | Cxxx-NCR-000838 | NCR | Envirodeck Kerbing (KD1) |  | Contr |  | PAD - Paddington Station (West) |  | 2011-08-10 | 2011-08-25 10:36 | 15 | 2011-08-03 | Civil - Kerbs | 500 |  | Supervision/Management | Rework |  | Complete |  | Completed |  | Concrte has been poured to the wrong level at this location.
| 03SR - Stations (RfL) | Cxxx-NCR-000841 | NCR | B1414 orientation |  | Contr |  | PAD - Paddington Station (West) |  | 2011-08-11 | 2011-10-11 15:18 | 61 | 2011-08-04 | Civil - Structural Engineering | 500 |  | Supervision/Management | Repair |  | Complete |  | Completed |  | Beam 2.B13 (REL B1414) has been installed with its web on the north side instead of the southern side adjacent to the __ planks.
| 03SR - Stations (RfL) | Cxxx-NCR-000853 | NCR | column 1.c9 |  | Contr |  | PAD - Paddington Station (West) |  | 2011-08-25 | 2012-05-04 16:55 | 253 | 2011-08-09 | Structural Engineering - Bolted Connections | 500 |  | Damaged | Repair |  | Complete |  | Completed |  | Column base plates have been fabricated prior to handover of as-built information of the holding down bolts locations. As a result there are several cases along GL N where the holding down bolts are not fully aligned with the holes in the column baseplates. These bolts are through the holes of the column baseplates but protrude at an angle. 1No bolt is cranked at GL 59/N. 3No bolts are cranked at GL 60/N. 1No holding down bolt on GL 57/N was damaged with an excavator. This requires removal.
| 03SR - Stations (RfL) | Cxxx-NCR-000854 | NCR | Infill between __ Planks and concourse steelwork |  | Contr |  | PAD - Paddington Station (West) |  | 2011-08-12 | 2011-08-18 11:59 | 6 | 2011-08-09 | Civil - Civil Engineering General | 500 |  | Workmanship | Rework |  | Complete |  | Completed |  | The infills between the __ planks and the structural concourse beams was poured during a weekend track closure of the H&C line. Once the formwork was struck it was clear that the concrete used was sub-standard. The concrete was poured very dry and several holes were noted. This occured at the following locations: East and west of GL 59/M-L. East of GL 60/M-L and West of GL 54/M-L.
| 03SR - Stations (RfL) | Cxxx-NCR-000855 | NCR | Infills between Concourse level __ Planks |  | Contr |  | PAD - Paddington Station (West) |  | 2011-08-12 | 2011-08-18 12:19 | 6 | 2011-08-09 | Civil - Civil Engineering General | 500 |  | Workmanship | Rework |  | Complete |  | Completed |  | A non compliant S12 material (black foam) was used to seal the gaps between the __ planks on the LUL concourse between GL 60-53/M-J. The material was used to prevent grout leakage prior to the gap being filled with concrete.
| 03SR - Stations (RfL) | Cxxx-NCR-000856 | NCR | GL M columns |  | Contr |  | PAD - Paddington Station (West) |  | 2011-08-23 | 2011-09-12 18:47 | 20 | 2011-08-09 | Civil - Structural Engineering | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | The shear studs and steel surfaces in contact with concrete should not be painted. The GL M columns (2.C2) have been delivered to site and installed with the stubs at taxi ramp level and the shear studs fully painted.
| 03SR - Stations (RfL) | Cxxx-NCR-000868 | NCR | Insitu encasement to B1432 |  | Contr |  | PAD - Paddington Station (West) |  | 2011-08-19 | 2012-08-08 15:10 | 355 | 2011-08-11 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | The concrete encasement to beam (REL No B1432) 2B40 was cast insitu with the use of a hanging formwork system. Several of the __ Planks had been landed on this beam prior to the encasement thus complicating the placement of the self consolidating concrete. After removal of the formwork it could be seen that the concrete encasement had not reached the top of the shelf angle as desired therefore leaving a 10-20mm gap between the encasement and the shelf angle.
| 03SR - Stations (RfL) | Cxxx-NCR-000879 | NCR | Solid infilled cores in the precast unit |  | Contr |  | PAD - Paddington Station (West) |  | 2011-08-15 | 2011-08-22 17:09 | 7 | 2011-08-12 | Structural Engineering - Pre-cast | 500 |  | Supervision/Management | Repair |  | Complete |  | Completed |  | The precast units with the infilled cores have been placed in the incorrect orentation on the steel frame unit number 2014,2015,2017 & 2018
| 03SR - Stations (RfL) | Cxxx-NCR-000907 | NCR | Rowecord Steel Castings for Tree Columns |  | Contr |  | PAD - Paddington Station (West) |  | 2011-09-08 | 2012-02-10 19:29 | 155 | 2011-08-19 | Structural Engineering - Steel Member | 500 |  | Damaged | Reject |  | Complete |  | Completed |  | 1. Steel casting units observed on 17-08-11 as per attached pictures have numerous surface irregularities and defects including dents, notched edges, and a degree of variation (indents/fa__ing) exhibited in the overall shape of the central casting. to provide inspection and test records and evidance that castings have been fabricated in accordance with BS EN 10340 : 2007 and SCI Publication 172. to provide a signed inspection report from the contract inspector as per section 130.009A of contract specification. 2. C272 has not submitted an ITP to CRL for acceptance.
| 03SR - Stations (RfL) | Cxxx-NCR-000921 | NCR | Bearing Plinth Cast Low |  | Contr |  | PAD - Paddington Station (West) |  | 2011-09-30 | 2011-09-15 16:40 | -15 | 2011-08-28 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Rework |  | Complete |  | Completed |  | The plinth is lower than required
| 03SR - Stations (RfL) | Cxxx-NCR-000923 | NCR | Cast in rainwater design change |  | Contr |  | PAD - Paddington Station (West) |  | 2011-09-30 | 2011-09-12 17:54 | -18 | 2011-08-30 | Civil - Drainage | 500 |  | Design | Use As-Is |  | Complete |  | Completed |  | RFI number C272-00688 resulted in changes to the cast in rainwater layout and details as shown on drawing C131-MMD-P_DDA-B071_2-43117 rev C01. No Change was made to an FCD and no formal design document revision was issued. The changes were instructed by sketches referenced on the RFI.
| 03SR - Stations (RfL) | Cxxx-NCR-000925 | NCR | ITP verification records for cast in rainwater drains |  | Contr |  | PAD - Paddington Station (West) |  | 2011-09-30 | 2011-12-12 18:42 | 73 | 2011-08-30 | Civil - Drainage | 500 |  | Supervision/Management | Repair |  | Complete |  | Completed |  | The drainage installation was not fully recorded on the above referenced form. Approximately half of the drainage installation is recoded on another form which is not identified on the ITP and omits the surround and back fill operations.
| 03SR - Stations (RfL) | Cxxx-NCR-000926 | NCR | Unsuitable compaction method |  | Contr |  | PAD - Paddington Station (West) |  | 2011-09-30 | 2012-05-11 17:57 | 224 | 2011-08-30 | Civil - Fill | 500 |  | Supervision/Management | Repair |  | Complete |  | Completed |  | The supplied material test results ( C272-CAR-C-CER-B071-50024) showed it to be unsuitable for compaction in accordance with Table 6/1.
| 03SR - Stations (RfL) | Cxxx-NCR-000934 | NCR | As erected Steel levels |  | Contr |  | PAD - Paddington Station (West) |  | 2011-09-09 | 2012-02-10 19:24 | 154 | 2011-09-02 | Architectural - Balustrade | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | Following an on site discussion with Kevin this morning i believe that the 24mm high spot is at the holding down bolts section and that the levels to existing girder are approx 15 mm high,
| 03SR - Stations (RfL) | Cxxx-NCR-000969 | NCR | Bolting- non preload type bolts |  | Contr |  | PAD - Paddington Station (West) |  | 2011-10-14 | 2011-10-03 13:03 | -11 | 2011-09-14 | Civil - Structural Engineering | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | Records were not available during surveillance of 5th September to demonstrate implementation
| 03SR - Stations (RfL) | Cxxx-NCR-000970 | NCR | Timely submission for acceptance |  | Contr |  | PAD - Paddington Station (West) |  | 2011-10-14 | 2012-07-31 09:48 | 291 | 2011-09-14 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | Not all submissions are submitted 28 days before acceptance is required. The surveillance sample showed that the Contractors submission for acceptance dated 31st August, commenced installation on 2nd September
| 03SR - Stations (RfL) | Cxxx-NCR-000971 | NCR | Specified procurement requirement for steel plate |  | Contr |  | PAD - Paddington Station (West) |  | 2011-10-14 | 2012-09-09 15:32 | 331 | 2011-09-14 | Structural Engineering - Steel Member | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | No clear evidence of implementation
| 03SR - Stations (RfL) | Cxxx-NCR-000972 | NCR | movement joint on corner near GL 12C is not present and corner has been grouted up |  | Contr |  | PAD - Paddington Station (West) |  | 2011-09-30 | 2012-01-27 10:43 | 119 | 2011-09-14 | Architectural - Brickworks/Blockworks | 500 |  |  | Use As-Is |  | Complete |  | Completed |  | Movement joint on corner near GL 12C is not present and corner has been grouted up
| 03SR - Stations (RfL) | Cxxx-NCR-000973 | NCR | Platform 12/BOH Blockwork mortar |  | Contr |  | PAD - Paddington Station (West) |  | 2011-10-14 | 2011-12-12 18:32 | 59 | 2011-09-14 | Architectural - Brickworks/Blockworks | 500 |  |  | Use As-Is |  | Complete |  | Completed |  | M4 (i) has been used for all blockwork in the platform 11 area. This is the correct mortar to use above teh DPC.
| 03SR - Stations (RfL) | Cxxx-NCR-000976 | NCR | no record of compliant waterproofing repair |  | Contr |  | PAD - Paddington Station (West) |  | 2011-10-15 | 2012-01-11 10:58 | 88 | 2011-09-15 | Civil - Kerbs | 500 |  | Supervision/Management | Rework |  | Complete |  | Completed |  | no record of compliant material
| 03SR - Stations (RfL) | Cxxx-NCR-000980 | NCR | Enlarging Connection Pockets on Pre-Encased Beams |  | Contr |  | PAD - Paddington Station (West) |  | 2011-09-30 | 2011-09-28 17:46 | -2 | 2011-09-17 | Civil - Civil Engineering General | 500 |  | Planning | Repair |  | Complete |  | Completed |  | Remove 1.2 long sections of pre-encased sections to allow for installation. There is no specification on how much gap is required for these pockets
| 03SR - Stations (RfL) | Cxxx-NCR-000981 | NCR | Truss 2T4 and 2T3 |  | Contr |  | PAD - Paddington Station (West) |  | 2011-10-31 | 2012-07-17 13:53 | 260 | 2011-11-03 | Structural Engineering - Steel Member | 500 |  | Design | Repair |  | Complete |  | Completed |  | Rework on these sections required on site on or prior to installation
| 03SR - Stations (RfL) | Cxxx-NCR-000986 | NCR | Slab level on VCC Stair 20 slab |  | Contr |  | PAD - Paddington Station (West) |  | 2011-10-03 | 2011-10-17 13:34 | 14 | 2011-09-21 | Structural Engineering - Structural Engineering - General | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | as above
| 03SR - Stations (RfL) | Cxxx-NCR-000995 | NCR | Bollard Installation - Red Star Deck - High Concrete Fill |  | Contr |  | PAD - Paddington Station (West) |  | 2011-10-21 | 2012-05-18 12:45 | 210 | 2011-09-22 | Civil - Landscaping | 500 |  | Workmanship | Rework |  | Complete |  | Completed |  | concrete was laid high in some areas resulting in too little space to lay granite setts to finished footpath level.
| 03SR - Stations (RfL) | Cxxx-NCR-000997 | NCR | Concrete being poured with no QA |  | Contr |  | PAD - Paddington Station (West) |  | 2011-10-23 | 2011-11-29 14:07 | 37 | 2011-09-23 | Structural Engineering - Concrete Member | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | Concrete did not meet the specification with regard to cover to bottom matt (there was 0mm cover on some bars). The concrete got ordered/confirmed by a foreman in advance of a pre-pour check and signed sheet. decided to allow concrete pour to commence despite Crossrail field engineer advising there were issues that required resolution. Due to intervention from crossrail, agreement was gained in remediating where possible and stop ending an area that could where the rebar cover issue could not be resolved within the conrete pour window.
| 03SR - Stations (RfL) | Cxxx-NCR-001007 | NCR | __ 1012 |  | Contr |  | PAD - Paddington Station (West) |  | 2011-10-04 | 2011-11-10 13:39 | 37 | 2011-09-27 | Structural Engineering - Pre-cast | 500 |  | Damaged | Repair |  | Complete |  | Completed |  | There is a crack 3500mm from the end of the __ plank unit number 1012, this is a Transverse Crack on the top of the unit and extentends 230mm down both sides
| 03SR - Stations (RfL) | Cxxx-NCR-001011 | NCR | Works commenced without signed ITP. |  | Contr |  | PAD - Paddington Station (West) |  | 2011-10-28 | 2012-08-20 15:52 | 297 | 2011-09-28 | Architectural - Roofing & Exterior Treatment | 500 |  | Supervision/Management | Repair |  | Complete |  | Completed |  | draft __ roof sheet ITP (that had not been signed and approved by ) was given on the day that work was planned to start. let work commence without signed ITP. Comments were sent back on ITP and as yet these have not been addressed
| 03SR - Stations (RfL) | Cxxx-NCR-001022 | NCR | Waterproofing around tree bases to incorrect detail |  | Contr |  | PAD - Paddington Station (West) |  | 2011-10-30 | 2012-01-04 17:57 | 66 | 2011-09-30 | Structural Engineering - Bolted Connections | 500 |  |  | Rework |  | Complete |  | Completed |  | Waterproofing is at the top of concrete level and does not protect the bolt heads or the base plate for the trees.
| 03SR - Stations (RfL) | Cxxx-NCR-001041 | NCR | Works Information Document Not Submitted |  | Contr |  | PAD - Paddington Station (West) |  | 2011-10-20 | 2012-02-10 19:11 | 113 | 2011-10-06 | Human Factors - Human Factors General | 500 |  | Planning | Rework |  | Complete |  | Completed |  | The plan was due 4 weeks from project start date (20-10-10), and is yet to be submitted for approval.
| 03SR - Stations (RfL) | Cxxx-NCR-001056 | NCR | Waterproofing layer on Bishops Bridge Footpath |  | Contr |  | PAD - Paddington Station (West) |  | 2013-02-28 | 2013-02-28 12:01 | 0 | 2011-10-11 | Civil - Civil Engineering General | 500 |  | Damaged | Repair |  | Complete |  | Completed |  | Existing water proofing membrane on Bishops Bridge walkway has been damaged whilst operative have been breaking out concrete for duct installation and cable route.
| 03SR - Stations (RfL) | Cxxx-NCR-001082 | NCR | Canopy Secondary Steelwork - Production Procedures |  | Contr |  | PAD - Paddington Station (West) |  | 2011-11-21 | 2011-12-12 18:45 | 21 | 2011-10-20 | Civil - Structural Engineering | 500 |  | Planning | Use As-Is |  | Complete |  | Completed |  | First panel of the canopy has arrived on site prior to above documents receiving Crossrail Code 1 or 2 decal.
| 03SR - Stations (RfL) | Cxxx-NCR-001083 | NCR | Supply and Manufacture control documentation (Sommer) |  | Contr |  | PAD - Paddington Station (West) |  | 2011-11-21 | 2012-09-11 17:14 | 295 | 2011-10-20 | Civil - Structural Engineering | 500 |  | Planning | Use As-Is |  | Complete |  | Completed |  | Quality Planning Documentation for the manufacture of Taxi Canopy not submitted prior to the work commencing.
| 03SR - Stations (RfL) | Cxxx-NCR-001118 | NCR | NCR (repair) – VCC steel angles concrete repair |  | Contr |  | PAD - Paddington Station (West) |  | 2011-11-11 | 2011-12-08 16:14 | 27 | 2011-10-31 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | The 10 no steel angles were added as additional items at a late stage (refer to RFI 1001). Due to the lead time of these steel angles it was decided so as to not delay erection of VCC steelwork (critical) the concrete would be poured with box outs left for the angles to be cast at a later date. The amount of concrete required to cast these angles in was less than half a cube and the decision was made to use our own labour force. The job was done to an unsatisfactory standard.
| 03SR - Stations (RfL) | Cxxx-NCR-001154 | NCR | Lap Lengths on U bars on Taxi Ramp Parapets |  | Contr |  | PAD - Paddington Station (West) |  | 2011-11-09 | 2012-02-10 15:48 | 93 | 2011-11-08 | Structural Engineering - Reinforcement | 500 |  | Design | Use As-Is |  | Complete |  | Completed |  | Bar Mark 03 (16mm U-bars) detailed on DRW-Cxxx0-TPS-038 (attached) were detailed too short. The lap acheived on site is 400mm which is 160mm short.
| 03SR - Stations (RfL) | Cxxx-NCR-001162 | NCR | RSD holding down bolts -too short |  | Contr |  | PAD - Paddington Station (West) |  | 2011-12-10 | 2011-12-14 14:13 | 4 | 2011-11-10 | Structural Engineering - Steel Member | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | The top of the threads are approximately 5mm above the TOS of the baseplate.
| 03SR - Stations (RfL) | Cxxx-NCR-001164 | NCR | Functional Test Report not stored in eB and transmitted to CRL |  | Contr |  | PAD - Paddington Station (West) |  | 2011-12-08 | 2012-03-21 14:30 | 104 | 2011-11-10 | Fire - Fire Systems & General | 500 |  | Supervision/Management | Rework |  | Complete |  | Completed |  | The test report has been registered in eB but no copy is stored in eB and there is no record of transmittal of the report to CRL in eB. In addition, as-built drawings have not been issued as stand-alone documents but are included in the functional test report; therefore no as-built drawings have been issued to CRL to date. The report is dated 27 August 2011. The temporay fire alarm system that is the subject of the report has been accepted by LUL (Note: retains maintenance responsibility)
| 03SR - Stations (RfL) | Cxxx-NCR-001166 | NCR | BOH structural steel in drained cavity not painted as specified on drawing. |  | Contr |  | PAD - Paddington Station (West) |  | 2011-12-11 | 2011-12-14 14:03 | 3 | 2011-11-11 | Structural Engineering - Surface Treatment | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | Exposed steel in drain cavity is not painted but painted. The blockwork is now installed as are the mezzanine level roof sheets.
| 03SR - Stations (RfL) | Cxxx-NCR-001168 | NCR | No ITP before works comenced paving/ screed |  | Contr |  | PAD - Paddington Station (West) |  | 2011-12-11 | 2012-11-23 16:06 | 348 | 2011-11-11 | Architectural - Flooring | 500 |  | Planning | Rework |  | Complete |  | Completed |  | No ITP was presented to CRL for sign off before works comenced for paving and the laying of screed in the gateline/ platform/ BOH location. This was initially just a trial pane. Works then continued with no ITP after the agreed trial panel had been completed.
| 03SR - Stations (RfL) | Cxxx-NCR-001175 | NCR | Shelf angle levels / __ Planks |  | Contr |  | PAD - Paddington Station (West) |  | 2011-11-16 | 2011-12-13 17:53 | 27 | 2011-11-14 | Structural Engineering - Steel Member | 500 |  | Design | Use As-Is |  | Complete |  | Completed |  | The shelf angles supporting the bison planks in the north entrance have been fabricated to the wrong levels, ie 50mm to high. The bison planks have since been installed, achieving the bearing to make them stable, but 50mm to high, basically standing proud of the support steel members and encroaching into the proposed finishes make up. Planks affected are 6055 - 6071.
| 03SR - Stations (RfL) | Cxxx-NCR-001180 | NCR | HD Bolts For Taxi Ramp Parapets |  | Contr |  | PAD - Paddington Station (West) |  | 2011-12-15 | 2012-02-29 11:08 | 76 | 2011-11-15 | Structural Engineering - Structural Engineering - General | 500 |  | Supervision/Management | Repair |  | Complete |  | Completed |  | The bolts are in the wrong position
| 03SR - Stations (RfL) | Cxxx-NCR-001181 | NCR | Connection Plates for Stairs to 2B19 |  | Contr |  | PAD - Paddington Station (West) |  | 2011-11-21 | 2012-02-10 15:53 | 81 | 2011-11-15 | Structural Engineering - Structural Engineering - General | 500 |  | Design | Repair |  | Complete |  | Completed |  | The connection plates near GL L have been removed and rewelded to the offsets shown on ' drawing GA A1- GA001, (GA0012 and GA003).
| 03SR - Stations (RfL) | Cxxx-NCR-001204 | NCR | RSD - Canopy Column Tree Protective Treatment Defects |  | Contr |  | PAD - Paddington Station (West) |  | 2013-03-15 | 2013-03-13 13:04 | -2 | 2011-11-17 | Structural Engineering - Surface Treatment | 500 |  |  | Rework |  | Complete |  | Completed |  | Canopy column trees and branches types 11C5, 11C6, 11C7 delivered to site have protective treatment surface defects including chips, scratches and discolouration due to material delivery and handling methods. Please see attached pictures.
| 03SR - Stations (RfL) | Cxxx-NCR-001230 | NCR | Escalator Pit Concrete Finishing |  | Contr |  | PAD - Paddington Station (West) |  | 2011-11-29 | 2012-07-03 18:35 | 217 | 2011-11-22 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | During concrete pour BOH on Saturday 19/11/11, the shuttering to the escalator pit wall along G/L 4 moved due to insufficient support. As a result there is a step in the line of the perimeter of the pit as per attached sketch. There is also 20mm concrete additional past the cast in bearing plate on the inside face of the escalator pit. The bearing plate should be flush with the edge of escalator.
| 03SR - Stations (RfL) | Cxxx-NCR-001233 | NCR | BOH Maintenance deck screws do not tap into supporting steelwork. |  | Contr |  | PAD - Paddington Station (West) |  | 2011-12-26 | 2012-05-18 12:50 | 144 | 2011-11-24 | Architectural - Roofing & Exterior Treatment | 500 |  |  | Rework |  | Complete |  | Completed |  | Screws protrude through kingspan but not structural steelwork below in around 10% of cases. Some screws have not yet been installed.
| 03SR - Stations (RfL) | Cxxx-NCR-001260 | NCR | Triangle - Concrete Encasement Defect Beam 4.B12 |  | Contr |  | PAD - Paddington Station (West) |  | 2012-03-22 | 2012-07-30 09:12 | 130 | 2011-11-30 | Civil - Civil Engineering General | 500 |  | Workmanship | Rework |  | Complete |  | Completed |  | The concrete encasement to Beam BM 4.B12 has de-laminated. This is GL N eastern end under the cellular ramp.
| 03SR - Stations (RfL) | Cxxx-NCR-001271 | NCR | Incorrect grade bolts temporarily installed. |  | Contr |  | PAD - Paddington Station (West) |  | 2012-01-09 | 2012-03-25 20:36 | 76 | 2011-12-09 | Structural Engineering - Steel Member | 500 |  |  | Rework |  | Complete |  | Completed |  | Bolts installed are grade 8.8. The Contractor and sub-contactor were aware of this and these are being replaced. These bolts have been installed from apprximately GL 5- 13. The explanation given for the initial installation of the grade 8.8 bolts was the length of the lead time of the 10.9 bolts and the programme constraints.
| 03SR - Stations (RfL) | Cxxx-NCR-001272 | NCR | GRANITE SETTS GROUTING |  | Contr |  | PAD - Paddington Station (West) |  | 2011-12-08 | 2012-02-10 20:07 | 64 | 2011-12-01 | Structural Engineering - Grouting | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | At times Szerelemey were adding an extra 1 to 1.5 litres to achieve a more workable mixture.
| 03SR - Stations (RfL) | Cxxx-NCR-001282 | NCR | Alignment of north entrance Stairs |  | Contr |  | PAD - Paddington Station (West) |  | 2011-12-19 | 2012-07-18 14:33 | 212 | 2011-12-05 | Structural Engineering - Pre-cast | 500 |  | Design | Repair |  | Complete |  | Completed |  | The steps of the three precast concrete stairs units at the north entrance (stair 10) do not align, there is a difference in level and alignment. Survey sketch attached.
| 03SR - Stations (RfL) | Cxxx-NCR-001317 | NCR | VCC Lift Motor Room Electrical Installation Issues |  | Contr |  | PAD - Paddington Station (West) |  | 2011-12-16 | 2012-04-05 17:18 | 111 | 2011-12-09 | Electrical - Electrical Engineering General | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | On the 30.11.2011 I visited the LMR in the VCC platform level ( P-409 )I noted that Stannah electrical operatives were progressing with the electical installation. a number of issues were noted and I believed that the installation was not as detailed in the electrical spec for the project.The issues noted were as follows. Section 4.3.5 of the spec states that no materials will be in direct contact with the building surfaces ( standard install is to space trunking/tray of the walls/floor by installing a section of 41mmx41mm unistrut first. Section 4.8 of the spec states that no knockout sections in back boxes to be utilised ( the contractor has used back boxes with knockouts ) Spec C131-MMD-E-RSP-B071-00008 ( data sheets ) clearly states that all conduit , trunking & distribution boards in lift motor rooms to be IP55 rated. ( installed does not match the required IP rating ) The spec states that flange couplers shall be used as a connection interface between backboxes and conduit. ( these have not been used ) The project stanadard fixing method is via chemfix fixings to walls/soffit, these can be tested as required. ( standard rawplugs have been used with screws ) We believe that no ITP/ITR was signed off by prior to wiring commecing, this is a project requirement.
| 03SR - Stations (RfL) | Cxxx-NCR-001323 | NCR | Bishop Road Bridge Cantilever Beams - Rowecord fabrication process |  | Contr |  | PAD - Paddington Station (West) |  | 2011-12-30 | 2012-02-29 08:10 | 61 | 2011-12-12 | Structural Engineering - Surface Treatment | 500 |  | Material | Rework |  | Complete |  | Completed |  | The Cantilever beams have been fabricated and delivered to site painted white. The NCR is raised on the fabrication / treatment process.
| 03SR - Stations (RfL) | Cxxx-NCR-001327 | NCR | Floor Screed |  | Contr |  | PAD - Paddington Station (West) |  | 2011-12-19 | 2012-02-10 19:40 | 53 | 2011-12-12 | Civil - Civil Engineering General | 500 |  | Damaged | Repair |  | Complete |  | Completed |  | It was determined that the finish of screed to be unacceptable in room 455, this was the direct result of the screed going off whilst being laid. There was also some minor damage to gateline switch room 407, this was due to rebar screed level guide being removed whilst screed was curing. (refer to photos attached)
| 03SR - Stations (RfL) | Cxxx-NCR-001335 | NCR | Shelf Angle Support for BISON not Painted |  | Contr |  | PAD - Paddington Station (West) |  | 2011-12-27 | 2012-03-10 14:34 | 74 | 2011-12-13 | Structural Engineering - Finishes | 500 |  | Workmanship | Rework |  | Complete |  | Completed |  | Additional Information to be Supplied by : Ledge bearing angle along GL M has been welded on site. The Bearing angle has no protective coating currently.
| 03SR - Stations (RfL) | Cxxx-NCR-001360 | NCR | Damage to Span 4 |  | Contr |  | PAD - Paddington Station (West) |  | 2012-03-30 | 2012-05-18 12:59 | 49 | 2011-12-21 | Architectural - General | 500 |  | Damaged | Repair |  | Complete |  | Completed |  | Damage has been sustained to the coving on the span 4 structure.
| 03SR - Stations (RfL) | Cxxx-NCR-001361 | NCR | Nuts for 10.9 grade galvanized biolts |  | Contr |  | PAD - Paddington Station (West) |  | 2011-12-23 | 2012-07-03 18:00 | 193 | 2011-12-21 | Structural Engineering - Bolted Connections | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | No evidence available to demonstrate that the nuts in use were grade 12
| 03SR - Stations (RfL) | Cxxx-NCR-001382 | NCR | Taxi ramp as-built levels |  | Contr |  | PAD - Paddington Station (West) |  | 2012-01-11 | 2012-02-08 17:03 | 28 | 2012-01-04 | Civil - Concrete Pavement | 500 |  | Supervision/Management | Repair |  | Complete |  | Completed |  | The as-built taxi ramp levels are shown on the attached survey. The as-built levels are higher than design therefore reducing the thickness of the surfacing to unacceptable levels.
| 03SR - Stations (RfL) | Cxxx-NCR-001387 | NCR | BRB tie slab - cut reinforcement |  | Contr |  | PAD - Paddington Station (West) |  | 2012-01-13 | 2012-02-08 17:06 | 26 | 2012-01-06 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Repair |  | Complete |  | Completed |  | Several longitudinal bars cut flush with the face of the concrete at the southern and northern cut line. 2No transerve bars cut over new beam 13CE1.
| 03SR - Stations (RfL) | Cxxx-NCR-001404 | NCR | Tree column 21C |  | Contr |  | PAD - Paddington Station (West) |  | 2012-01-31 | 2012-02-11 14:32 | 11 | 2012-01-10 | Structural Engineering - Structural Engineering - General | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | The tree column on gridline 21C has been surveyed post erection and is showing error of up to 460mm out of alignment. The holding down bolts have been surveyed and are within tolerance. Looking at the issue on site it would appear that problem is in the fabrication of the top section of the steel trunk before this was delivered to site. This appears to have been welded out of alignment with the baseplate resulting in the arms being out alignment. This will require re-working to get the arms back within tolerance.
| 03SR - Stations (RfL) | Cxxx-NCR-001414 | NCR | BISON Soffit Remedials (Installation Damage) |  | Contr |  | PAD - Paddington Station (West) |  | 2012-01-26 | 2012-07-30 09:20 | 186 | 2012-01-12 | Architectural - General | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | Several __ units across the LU concourse have damaged edges. This was caused during the installation and delivery process. Visually these damaged __s are unacceptable.
| 03SR - Stations (RfL) | Cxxx-NCR-001415 | NCR | LUL Lift Shaft Damage to Galvanised Beams |  | Contr |  | PAD - Paddington Station (West) |  | 2012-11-25 | 2012-11-07 10:20 | -18 | 2012-01-12 | Architectural - Finishes | 500 |  | Damaged | Rework |  | Complete |  | Completed |  | Galvanised Beams and Columns have damage.
| 03SR - Stations (RfL) | Cxxx-NCR-001419 | NCR | Works commenced without signed ITP. |  | Contr |  | PAD - Paddington Station (West) |  | 2012-02-13 | 2012-07-25 10:52 | 163 | 2012-01-13 | Fire - Compartmentation | 500 |  | Supervision/Management | Repair |  | Complete |  | Completed |  | Works on the BOH compartment ceilings commenced on 28 November 2011, Advance ITP recieved on the 09/12/11( this would have been a code 3 if formally submitted). No other documents have been recieved since and the works are still ongoing. It appears Ardent have comprehensive check sheets for their works, but the ITP/sheets have not yet been submitted as required.
| 03SR - Stations (RfL) | Cxxx-NCR-001424 | NCR | fireboarding not |  | Contr |  | PAD - Paddington Station (West) |  | 2012-02-13 | 2012-02-11 14:16 | -2 | 2012-01-13 | Fire - Compartmentation | 500 |  | Workmanship | Rework |  | Complete |  | Completed |  | In room 409, 405, 406 the fire ceiling was installed incorrectly by killnbridge. see attatchments for technical data on what was installed, what is beleived should have beein installed and photos. Issues regarding -Joints not being staggered in boarding (4 sheets meeting at a corner point)- Incorrect framework used. See atatchement (p1 and p3) . Product used ( GL 1) is for walls not ceilings. Product required is beleived to be MF7. -Hangers for framework not vertical in several instances see photo 4. - Connection to kingspan is not kingspan product. We beleive this is required for it to be certified by kingspan.
| 03SR - Stations (RfL) | Cxxx-NCR-001425 | NCR | Omnia Plank Reinforcement Size |  | Contr |  | PAD - Paddington Station (West) |  | 2012-01-20 | 2012-02-11 14:14 | 22 | 2012-02-06 | Structural Engineering - Concrete Member | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | The Omnia Planks were formed using 3 no. 12mm diameter reinforcing bars instead of 16mm diameter as was expected.
| 03SR - Stations (RfL) | Cxxx-NCR-001476 | NCR | Lift Shaft 4 Holding Down Bolts |  | Contr |  | PAD - Paddington Station (West) |  | 2012-02-09 | 2012-03-10 14:36 | 30 | 2012-01-26 | Structural Engineering - Bolted Connections | 500 |  |  | Use As-Is |  | Complete |  | Completed |  | 3/4 bolts are installed to each column. 4th bolts unable to be installed due to minimal concrete cover to escalator pit. Bolt attempted to be installed to one column but conrete crack and broke off.
| 03SR - Stations (RfL) | Cxxx-NCR-001477 | NCR | Taxi Deck Column Base Grouting |  | Contr |  | PAD - Paddington Station (West) |  | 2012-02-09 | 2012-10-04 18:54 | 238 | 2012-01-26 | Structural Engineering - Grouting | 500 |  | Workmanship | Reject |  | Complete |  | Completed |  | Requires further work to meet specification/design.
| 03SR - Stations (RfL) | Cxxx-NCR-001487 | NCR | Bolted connection 2.B10+2.C13 |  | Contr |  | PAD - Paddington Station (West) |  | 2012-02-07 | 2012-02-02 12:42 | -5 | 2012-01-31 | Structural Engineering - Bolted Connections | 500 |  | System Defect | Repair |  | Complete |  | Completed |  | Bolted connection is not flush. On the east side of the joint a 10mm gap exists which narrows to a flush fit at the west end of the joint.
| 03SR - Stations (RfL) | Cxxx-NCR-001497 | NCR | Paving to Platform 15/16, Bays 5&18 |  | Contr |  | PAD - Paddington Station (West) |  | 2012-02-15 | 2012-10-04 16:04 | 232 | 2012-02-01 | Architectural - Flooring | 500 |  | Workmanship | Reject |  | Complete |  | Completed |  | Bay 18: Several joints reached 11mm width. General joint spacing poor. Several chipped pavers. Concrete joint between the tactile and the nosing stone poor in terms of finish. Level of tactile stone at west end plat 16 (bay 18) causing a tripping hazard. Infill paver on plat 16 (bay 18) rocking. Alignnment of the cut stones does not appear to have been carried out with much accuracy. Concrete used for the transistion from the pavers to the sacrificial concrete was still damp and is being rutted rapidly. Bay 5: Same issues as above. Levels at the east end of the CER room are wrong. Plat 15 the tactile height is much higher than the adjacent paver therefore several tripping hazards.
| 03SR - Stations (RfL) | Cxxx-NCR-001510 | NCR | BRB pre-cast parapets |  | Contr |  | PAD - Paddington Station (West) |  | 2012-02-09 | 2012-08-08 15:23 | 181 | 2012-02-02 | Architectural - General | 500 |  | System Defect | Repair |  | Complete |  | Completed |  | As struck condition of the parapets has revealed several defects; -Dark staining to the finish in several areas. -Dark staining along the form joints. -Grout loss at base of pour. -Use of perspex form has created a high gloss finish similar to polished marble. See photographs attached.
| 03SR - Stations (RfL) | Cxxx-NCR-001513 | NCR | Damage to waterprooing when breacking out tarmac for quing system. |  | Contr |  | PAD - Paddington Station (West) |  | 2013-04-26 | 2013-04-05 18:19 | -21 | 2012-02-03 | Civil - Civil Engineering General | 500 |  | Damaged | Rework |  | Complete |  | Completed |  | Waterproofing has been damaged through saw cutting the tarmac in order to place the queuing system posts on RSD between approximately at GL 6. This was raised as a Quality DWB on 18/01/12. informed Crossrail this didn’t appear to be part of their method and that this would require repair Subsequently these voids have been filled with sand and then the whole area covered with bedding mortar and sets (the sets in the area of posts were to be removed following for post base install).. The sets required then have then been broken out in the post areas. The waterproofing had then had some patch repairs applied but only centrally in the original area of each break out. verbally informed me that and _ Laser (the waterproofing sub-contractor) believed that the waterproofing works had been finished. On inspection the cuts in the water proofing from the original saw-cuts were still present on the perimeter of some of the break outs without repair. It was necessary to trowel out some of the sand in order to inspect this. CRL noted that a specific method statement for these works does not appear to be present (they site team referred to a kerb installation method statement)
| 03SR - Stations (RfL) | Cxxx-NCR-001515 | NCR | Incorrect size holding down bolts taxi ramp parapet |  | Contr |  | PAD - Paddington Station (West) |  | 2012-02-21 | 2012-08-03 10:20 | 164 | 2012-02-07 | Structural Engineering - Bolted Connections | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | Theses should have been M24 bolts we have installed M20
| 03SR - Stations (RfL) | Cxxx-NCR-001543 | NCR | Staircase 1 treads gaps and chipped surfaces. |  | Contr |  | PAD - Paddington Station (West) |  | 2013-03-01 | 2013-03-06 17:55 | 5 | 2012-02-16 | Architectural - Flooring | 500 |  | Material | Repair |  | Complete |  | Completed |  | 1 -14mm gap between treads. 10mm gap between treads and kicker plate 2 -Treads are chipped in corners. Some patch repairs have been carried out and are of poor standard (see photo1544) 3 -No ITP and works have been opened to the public. 4
| 03SR - Stations (RfL) | Cxxx-NCR-001544 | NCR | balistrade to staircase 1 - workmanship and materials |  | Contr |  | PAD - Paddington Station (West) |  | 2012-12-07 | 2012-12-21 15:48 | 14 | 2012-02-16 | Architectural - Balustrade | 500 |  | Material | Reject |  | Complete |  | Completed |  | Handrail has: - supports have been cut on lower handrail inorder to make handrail fit leaving handrail with void on underside and sharp edge on support on lower hand rail top flight - handrail does not align at splice locations. - missing end handrail. - Colour has not been agreed with c131 architects. - fitting is not countersunk -screws missing and non-counter sunk screws used. - gap between hand rail support and tred.
| 03SR - Stations (RfL) | Cxxx-NCR-001545 | NCR | Stair 01 (RSD to BOH between escalators)- kicker plate installed incorrectly |  | Contr |  | PAD - Paddington Station (West) |  | 2012-03-21 | 2012-07-18 15:46 | 119 | 2012-02-21 | Architectural - Flooring | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | 10-15mm gap between kicker plate sections. Gap is not straight. and 10mm gap between kicker plate and stair treds (also raised in NCR about treads).
| 03SR - Stations (RfL) | Cxxx-NCR-001546 | NCR | incorrect detail surrounding escalator |  | Contr |  | PAD - Paddington Station (West) |  | 2012-03-16 | 2012-07-18 15:29 | 124 | 2012-02-21 | Architectural - Flooring | 500 |  | Workmanship | Reject |  | Complete |  | Completed |  | Pavers are canti-levering approximately 50mm to escaltors. 10mm gap left in most places to escaltor. See Photo.
| 03SR - Stations (RfL) | Cxxx-NCR-001558 | NCR | ACO drain wiers |  | Contr |  | PAD - Paddington Station (West) |  | 2012-03-24 | 2012-05-22 15:44 | 59 | 2012-02-24 | Civil - Drainage | 500 |  | Material | Rework |  | Complete |  | Completed |  | Wier is in incorrect direction. Weir is only across 75% of the channel. See attatched photo showing a blockage and plate in wrong direction. Instalaltion guidlines from Aco should also be submitted to CRL..
| 03SR - Stations (RfL) | Cxxx-NCR-001563 | NCR | bent handrail on disney queue (BAL-10) balistrade |  | Contr |  | PAD - Paddington Station (West) |  | 2012-03-27 | 2012-04-05 19:32 | 9 | 2012-02-27 | Architectural - Balustrade | 500 |  | Damaged | Rework |  | Complete |  | Completed |  | Handrail has been bent. It is understood that this is due to an access tower falling onto it (this incident was reported on RIVO). SAM_0981 bent handrail/ balustrade, SAN_0515 incident that caused the haindrail to be damaged.
| 03SR - Stations (RfL) | Cxxx-NCR-001579 | NCR | Onmia Planks - Setting Out Check |  | Contr |  | PAD - Paddington Station (West) |  | 2012-03-30 | 2012-03-13 16:52 | -17 | 2012-03-02 | Structural Engineering - Pre-cast | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | Box to record setting out check (ITP item 9) was omitted from project form ref CI/CE/HSSQ/PROJFORM/CR/024 and therefore check was not recorded.
| 03SR - Stations (RfL) | Cxxx-NCR-001594 | NCR | VCC concrete formed faces including parapet walls, beams, columns and soffits |  | Contr |  | PAD - Paddington Station (West) |  | 2012-10-29 | 2012-12-20 13:49 | 52 | 2012-03-14 | Structural Engineering - Concrete Member | 500 |  | Workmanship | Rework |  | Complete |  | Completed |  | Parapets and chamfered beam: P1: Tie bars are present on the parapet wall parallel to London Street GL 6. These have been filled with a repair concrete that has no colour match to the surrounding concrete. P2: Nail marks can be found all around the exposed concrete faces. P3: Blemishes are present on the chamfered beam on GL 6. P4: Spherical voids are not smooth and are poorly textured. P5: There was a yellow line that appeared to be from a spray can to mark a level. This was pointed out to the contractor and the repair concrete was just smeared above this. P6: The construction joint is very visible along GL D. GL 6-7. P7: Temporary jack arch tie pieces have been cast in. P8: General water staining. Column C1:permanent marker showing a level line C2:missing mastic C3:formwork joints are not smooth C4: chipped concrete corner (note photo taken at BIU therefore not due to use) C5: Joint between column and beam GL 6 to be reworked and made good.
| 03SR - Stations (RfL) | Cxxx-NCR-001596 | NCR | Water Ingress into VCC Escalators |  | Contr |  | PAD - Paddington Station (West) |  | 2013-04-10 | 2013-04-29 16:52 | 19 | 2012-03-14 | Mechanical - Escalators | 500 |  | Damaged | Repair |  | Complete |  | Completed |  | A large quantity of water has ingressed into the 2 no operational escalators at the platform 12 vertical circulation core with the Paddington __ Station on 04-03-12 and 05-03-12. The water has leaked through the standing seam roof from above that was not completed or protected by the Contractor. As a result the 2 no escalators have been brought out of use by Stannah and the NR station team due to un safe condition and potential of equipment damaged.
| 03SR - Stations (RfL) | Cxxx-NCR-001602 | NCR | Drilling into precast concrete slabs |  | Contr |  | PAD - Paddington Station (West) |  | 2012-03-23 | 2012-04-28 16:55 | 36 | 2012-03-16 | Structural Engineering - Pre-cast | 500 |  | Supervision/Management | Repair |  | Complete |  | Completed |  | Following further investigations with the operative, he confirmed that in some locations the drill bit hit something solid, which we know to be the reinforcement in the units, where upon he stopped drilling and moved to the next hole guided by the unistrut holes, from the survey of the locations & depths drilled attached, we can see he stopped at 40mm, the concrete cover to the rebar The operative was not briefed by his superiors that the precast units could only be drilled through the centre of the hollow cores We have carried out a detailed survey of the exact locations & drill depths, due to the use of a normal masonary drill bit, we belive the reinforcement has not been damaged, any threaded bar not fixed in the correct location will be cut, any hole not required filled with a apprved repair compound
| 03SR - Stations (RfL) | Cxxx-NCR-001609 | NCR | ITP for VCC Standing Seam Roof Code 3 After Work Had Started |  | Contr |  | PAD - Paddington Station (West) |  | 2012-04-30 | 2012-04-05 17:51 | -25 | 2012-03-21 | Architectural - Roofing & Exterior Treatment | 500 |  | Supervision/Management | Rework |  | Complete |  | Completed |  | Work has started on a section of VCC standing seam roof and the ITP (C272-CAR-X-STP-B071-50049 Rev 1.0) status is code 3
| 03SR - Stations (RfL) | Cxxx-NCR-001610 | NCR | Samples and mock-up not submitted during design |  | Contr |  | PAD - Paddington Station (West) |  | 2012-04-13 | 2012-06-20 16:20 | 68 | 2012-03-21 | Architectural - Roofing & Exterior Treatment | 500 |  | Planning | Rework |  | Complete |  | Completed |  | No mock-ups or samples, have been submitted before or during detailed design as required by the clauses of the architectural specification referenced.
| 03SR - Stations (RfL) | Cxxx-NCR-001619 | NCR | Spark test not performed on gutter membrane |  | Contr |  | PAD - Paddington Station (West) |  | 2012-04-11 | 2012-05-11 18:14 | 30 | 2012-03-21 | Architectural - Roofing & Exterior Treatment | 500 |  | Supervision/Management | Rework |  | Complete |  | Completed |  | No electronic integrity test of the gutter of the VCC standing seam roof has taken place and it was stated that none was planned.
| 03SR - Stations (RfL) | Cxxx-NCR-001620 | NCR | No weathertightness testing of the VCC standing seam roof |  | Contr |  | PAD - Paddington Station (West) |  | 2012-04-18 | 2012-05-24 18:21 | 36 | 2012-03-21 | Architectural - Roofing & Exterior Treatment | 500 |  | Supervision/Management | Rework |  | Complete |  | Completed |  | A test of weathertightness of the works was is not included in the ITP and it was stated during surveillance that no weathertightness test was planned
| 03SR - Stations (RfL) | Cxxx-NCR-001621 | NCR | No Flood Test Planned |  | Contr |  | PAD - Paddington Station (West) |  | 2012-04-11 | 2012-05-04 16:24 | 23 | 2012-03-21 | Architectural - Roofing & Exterior Treatment | 500 |  | Planning | Rework |  | Complete |  | Completed |  | Flood Test in clause 825A has been omitted from the ITP. It is not clear if testing to meet Section J42 clause 825A will take place.
| 03SR - Stations (RfL) | Cxxx-NCR-001623 | NCR | VCC standing seam roof wind resistance testing |  | Contr |  | PAD - Paddington Station (West) |  | 2012-04-18 | 2012-05-22 09:26 | 34 | 2012-03-21 | Architectural - Roofing & Exterior Treatment | 500 |  | Planning | Rework |  | Complete |  | Completed |  | Wind resistance data does not confirm that testing was performed in accordance with BS12179 as modified by the CWCT Standard and Guide to Good Practice, that the peak test pressure was 1.5 times the design wind pressure and applied for a minimum of 10 seconds and that there was no permanent damage as required by Clause 201A of section H31 of the Architectural Specification. Note: this clause of the specification does not specify the design wind pressure
| 03SR - Stations (RfL) | Cxxx-NCR-001652 | NCR | Platform 12 cladding around lifts EWS-30 |  | Contr |  | PAD - Paddington Station (West) |  | 2012-12-07 | 2012-12-21 15:38 | 14 | 2012-04-04 | Architectural - General | 500 |  | Material | Reject |  | Complete |  | Completed |  | •Bowed Plates •Joints not abutted •Splice plate in front rather than behind cladding. As per drawing 141-002 •Marks/ blemishes on cladding panels •skiriting piece does not appear to be shot peaned as stated on __ drawing (this may be a drawing error please confirm) and there is a gap to ffl. •No mock up •No Inspection and Test Plan for the works •No NCR raised by contractor. Was installed incorrectly not correctable with in shift. New materials probably need to be ordered.
| 03SR - Stations (RfL) | Cxxx-NCR-001670 | NCR | Stair 1 anti-slip Nosing install |  | Contr |  | PAD - Paddington Station (West) |  | 2012-04-20 | 2012-05-28 18:01 | 38 | 2012-04-13 | Civil - Civil Engineering General | 500 |  | Damaged | Rework |  | Complete |  | Completed |  | 1-Setting out line and level of anti-slip nosing is incorrect. 2- Extremely poor workmanship 3- Poor end Product 4) added by Crossrail - treads were damaged by installation -
| 03SR - Stations (RfL) | Cxxx-NCR-001682 | NCR | __ Roofing Panels |  | Contr |  | PAD - Paddington Station (West) |  | 2012-05-09 | 2012-08-30 13:36 | 113 | 2012-04-18 | Architectural - Roofing & Exterior Treatment | 500 |  | Design | Repair |  | Complete |  | Completed |  | There are no design/workmanship details for installation of __ panels on the taxi rank roof. Without design/workmanship details it is not possible to confirm whether the following observations are acceptable: - 3 fixings were used at each end of __ panels with the exception of the eastern ends of the panels and the ends of the panels on the North spur where only 2 fixings were used - short sections of panel secured by just one fixing have been fitted at the West end of the taxi ramp roof - gaps of up to 30mm were observed between the ends of a number of panels (see attached photo) .
| 03SR - Stations (RfL) | Cxxx-NCR-001692 | NCR | Paving Sets |  | Contr |  | PAD - Paddington Station (West) |  | 2012-05-23 | 2012-05-18 10:39 | -5 | 2012-04-23 | Civil - Street Architecture | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | Inspection and Test Plan C272-CAR-O4-STP-B071-50038 did not reference the above requirement This may result in the installation of paving that also does not meet the above requirement
| 03SR - Stations (RfL) | Cxxx-NCR-001693 | NCR | Protecting newly laid paving form traffic |  | Contr |  | PAD - Paddington Station (West) |  | 2012-11-30 | 2012-11-10 10:48 | -20 | 2012-04-23 | Civil - Street Architecture | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | ITP C272-CAR-O4-STP-B071-50038 rev 1.0 omitted the above requirement, the Contractor confirmed that no other planned arrangements were in place and it could not be demonstrated that the above specified requirement had been implemented . Installed paving may therefore had not received the specified protection and may therefore no meet the specific requirements
| 03SR - Stations (RfL) | Cxxx-NCR-001694 | NCR | Mortar compaction and adhesion testing |  | Contr |  | PAD - Paddington Station (West) |  | 2013-01-28 | 2013-03-05 17:58 | 36 | 2012-04-23 | Civil - Street Architecture | 500 |  |  | Use As-Is |  | Complete |  | Completed |  | Above requirement not included in the Contractors ITP C272-CAR-O4-STP-B071-50038 rev 1.0. Contractor confirmed that the test area & tests were not implemted
| 03SR - Stations (RfL) | Cxxx-NCR-001740 | NCR | GL7 Clash and PCC 25 |  | Contr |  | PAD - Paddington Station (West) |  | 2012-05-11 | 2012-06-12 11:07 | 32 | 2012-05-10 | Structural Engineering - Structural Engineering - General | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | MM drawings gave freedom of beam placement West of GL7. surveyed the existing beams for new locations to avoid clashes, and part of their final design moved the beam on GL7. These new plans were submitted for approval, but work continued on site before approval was given. The Beam at GL 7 should not have been moved because of support requiremed to the VCC above. Two PTR items (1002 and 1027) were raised regarding the situation at GL7.
| 03SR - Stations (RfL) | Cxxx-NCR-001775 | NCR | Windposts to Mezzanine Level - Triangle Site |  | Contr |  | PAD - Paddington Station (West) |  | 2012-06-15 | 2012-06-22 17:33 | 7 | 2012-06-06 | Structural Engineering - Structural Engineering - General | 500 |  | Material | Rework |  | Complete |  | Completed |  | Mild steel plate has been used.
| 03SR - Stations (RfL) | Cxxx-NCR-001785 | NCR | Tread Levels of Stair 2 and 3 |  | Contr |  | PAD - Paddington Station (West) |  | 2013-03-14 | 2013-03-15 16:15 | 1 | 2012-06-11 | Architectural - Flooring | 500 |  | Workmanship | Rework |  | Complete |  | Completed |  | After the treads have been set to finished level and bolted to position, a survey has been conducted to determine stair 2 and stair 3, tread levels. Four points have been surveyed, the first tread height at both the top and the bottom and the first tread either side of the landing. The upper flight has 11 stair rises, the lower flight has 13 stair rises. Stair 2. FFL Upper Flight top tread = 127.850-0.1625 Survey Level = 127.531 Variance = +6mm FFL Top Landing Tread = 125.574+0.1625 Survey Level = 125.742 Variance = +5.5mm FFL Bottom Landing Tread = 125.574-0.1625 Survey Level = 125.427 Variance = +15.5mm FFL Lower Flight Bottom Tread = 123.299+0.1625 Survey Level = 123.475 Variance = +13.5mm Stair 3. Upper Flight Top Tread Variance = -21mm Top Landing Tread Variance = -4mm Bottom Landing Tread Variance = -3mm Lower Flight Bottom Tread Variance = -15mm Their is significant variation in design to survey levels, which needs to be addressed. The major concern is the upper top flight stair due to the concourse FFL already having been determined. It should be further noted assoicated rework was unplanned and could comprimise deadlines.
| 03SR - Stations (RfL) | Cxxx-NCR-001791 | NCR | Cable Strike - London Street |  | Contr |  | PAD - Paddington Station (West) |  | 2012-06-27 | 2012-08-14 11:12 | 48 | 2012-06-13 | Communications and Control Systems - Fibre Optic Network | 500 |  | Damaged | Repair |  | Complete |  | Completed |  | During planing works there was a strike to a cable duct that caused approx 60m-70m of 15 core multi mode fibre optic cable to be cut and pulled out from the duct. Damage to duct as shown on attached report
| 03SR - Stations (RfL) | Cxxx-NCR-001795 | NCR | Blockwork self certification records |  | Contr |  | PAD - Paddington Station (West) |  | 2012-07-11 | 2012-06-28 18:12 | -13 | 2012-06-18 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | during surveillance QS272-16 six forms presented by the Contractor to demonstrate implemetation of Blockwork inspection were reviewed and found to be incomplete, . The boxes allocated to record the inspection dates, locations and signatures were blank. 5 of the 6 forms were different to the form identifed in the ITP C272-CAR-X-STP-B071-50063 rev 1.0
| 03SR - Stations (RfL) | Cxxx-NCR-001796 | NCR | Block & Brick identification |  | Contr |  | PAD - Paddington Station (West) |  | 2012-07-11 | 2012-06-25 14:15 | -16 | 2012-06-18 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | Clause 7.4.3 of the current ISO 9001 specifies” The organization shall establish and implement the inspection or other activities necessary for ensuring that purchased product meets specified purchase requirement. During surveillance QS272 -16 no objective evidence was made avaialbe to demonstrate that the Blocks and Bricks are inspected to ensurw that they meet purchase requirement.
| 03SR - Stations (RfL) | Cxxx-NCR-001797 | NCR | Blockwork reinforcement installation inspection records |  | Contr |  | PAD - Paddington Station (West) |  | 2012-07-11 | 2012-07-03 18:20 | -8 | 2012-06-18 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | Verification records were not made avaialble during surveillance QS272-16
| 03SR - Stations (RfL) | Cxxx-NCR-001802 | NCR | London st drainage pipe from new manhole towards old manhole |  | Contr |  | PAD - Paddington Station (West) |  | 2012-07-20 | 2012-07-03 18:08 | -17 | 2012-06-20 | Civil - Drainage | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | 150 dia. perforated pipe encased in mass concrete
| 03SR - Stations (RfL) | Cxxx-NCR-001806 | NCR | Taxi Canopy Bullnose Cladding - Failure of Stud Weld Bolted Connection |  | Contr |  | PAD - Paddington Station (West) |  | 2012-11-05 | 2012-10-11 15:24 | -25 | 2012-06-22 | Structural Engineering - Bolted Connections | 500 |  | Workmanship | Rework |  | Complete |  | Completed |  | operatives were installing bullnose "soffit" cladding panels at height to Red Star Deck Taxi canopy during night shift Wednesday evening (Approx 03:10 - 21-06-12). Shortly after they installed a panel and moved to the next position, the panel fell to the ground. On initial investigation it appeared that the bolted connection and welded studs (M6x16 hexagon unit) on the panel failed. Shop Fabrication ITP for bullnose cladding has not been provided to CRL for review and acceptance. Works have commenced with Site Installation ITP for bullnose cladding at code 3 dated (01-03-12) - C272-CAR-X-STP-B071-50040
| 03SR - Stations (RfL) | Cxxx-NCR-001826 | NCR | Beam 1227 Installation |  | Contr |  | PAD - Paddington Station (West) |  | 2012-07-06 | 2012-10-04 19:10 | 90 | 2012-06-29 | Structural Engineering - Welding | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | Beam 1227 could not be installed due to the state in which the end plates were left in from the previous installation attempt by Rowecode(see attached photographs)
| 03SR - Stations (RfL) | Cxxx-NCR-001838 | NCR | Taxi Canopy Bullnose Soffit panell system - Finish Of Cover Plates incomparison to Panels. |  | Contr |  | PAD - Paddington Station (West) |  | 2012-11-05 | 2012-10-12 12:05 | -24 | 2012-07-06 | Architectural - Ceilings & Soffits | 500 |  | System Defect | Reject |  | Complete |  | Completed |  | The colours are inconsistant creating a pin stripe effect to the canopy.
| 03SR - Stations (RfL) | Cxxx-NCR-001847 | NCR | Concrete Base Slab level in EDF Substation |  | Contr |  | PAD - Paddington Station (West) |  | 2012-07-14 | 2012-07-25 11:18 | 11 | 2012-07-13 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | as above.
| 03SR - Stations (RfL) | Cxxx-NCR-001865 | NCR | Not logging minor defects |  | Contr |  | PAD - Paddington Station (West) |  | 2012-08-17 | 2012-08-28 10:43 | 11 | 2012-07-20 | Electrical - LV Equipment | 500 |  | System Defect | Rework |  | Complete |  | Completed |  | The system for identifying M&E minor defects and recording that they have been closed before completion is not being applied for all minor defects. eg Replacement of temporary labels on DB116 and the damaged roof + missing bolts and washers on UPS PR11473/W21878 have not been recorded for rectification.
| 03SR - Stations (RfL) | Cxxx-NCR-001870 | NCR | clouding and 'fern' pattern emerging on LUL facade glass panels |  | Contr |  | PAD - Paddington Station (West) |  | 2013-03-07 | 2013-03-05 17:37 | -2 | 2012-07-20 | Architectural - Glazing | 500 |  | System Defect | Rework |  | Complete |  | Completed |  | Clouding as described above - see attachments. They appear to signed of delamination.
| 03SR - Stations (RfL) | Cxxx-NCR-001875 | NCR | misalignment of cladding on stairs and escalators EWS-40 |  | Contr |  | PAD - Paddington Station (West) |  | 2012-10-01 | 2012-10-26 17:11 | 25 | 2012-07-31 | Architectural - General | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | The cladding West of GL 5 (existing column) has been set incorrectly ( is set south of north column face) and is thus different from cladding to the East which as been set as per drawing (150mm north of south ace of column).This has resulted in there being a step in the line of the cladding and there is also a temporary timber infill that may be as a result of this.
| 03SR - Stations (RfL) | Cxxx-NCR-001884 | NCR | Balustrade Sharp Edges |  | Contr |  | PAD - Paddington Station (West) |  | 2013-05-10 | 2013-05-11 16:24 | 1 | 2012-07-27 | Architectural - Handrail | 500 |  | System Defect | Rework |  | Complete |  | Completed |  | Stantions Bars and Beads of balustrades have squared edges, which are sharp
| 03SR - Stations (RfL) | Cxxx-NCR-001893 | NCR | Cracks in precast units |  | Contr |  | PAD - Paddington Station (West) |  | 2012-08-07 | 2012-08-01 14:11 | -6 | 2012-07-31 | Structural Engineering - Pre-cast | 500 |  | Damaged | Repair |  | Complete |  | Completed |  | __s 2046, 2050 & 2053 have cracks in the top and in the case of unit 2053 extend down the sides these are visible in the photographs attached
| 03SR - Stations (RfL) | Cxxx-NCR-001917 | NCR | RC Wall – concrete finish |  | Contr |  | PAD - Paddington Station (West) |  | 2012-10-22 | 2012-11-12 13:53 | 21 | 2012-08-13 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | Cracking in the wall Surface finish to top of wall and around bolt clusters Lips / steps in vertical concrete faces Honeycombing / Exposed aggregate at bottom of wall in places Nails for level control left in wall Uniform level not maintained along top of the wall Repair concrete does not match wall concrete colour
| 03SR - Stations (RfL) | Cxxx-NCR-001946 | NCR | __ Water Pipe Supports |  | Contr |  | PAD - Paddington Station (West) |  | 2013-02-13 | 2013-02-26 15:29 | 13 | 2012-08-20 | Civil - Civil Engineering General | 500 |  | Design | Use As-Is |  | Complete |  | Completed |  | Due to as found conditions on site we require an alternative installation for unistrut supprt system.
| 03SR - Stations (RfL) | Cxxx-NCR-001950 | NCR | Damage to Waterproofing on Steel Brackets Taxi Canopy Roof |  | Contr |  | PAD - Paddington Station (West) |  | 2012-12-31 | 2012-12-20 12:52 | -11 | 2012-08-20 | Architectural - Roofing & Exterior Treatment | 500 |  | Damaged | Rework |  | Complete |  | Completed |  | __ fil sheet has been penetrated by fixing brackets to the steel upstands that form part of the gantry rail system. See attached picture.
| 03SR - Stations (RfL) | Cxxx-NCR-001965 | NCR | __ Service Route Brackets |  | Contr |  | PAD - Paddington Station (West) |  | 2012-10-26 | 2012-11-06 18:50 | 11 | 2012-08-23 | Civil - Civil Engineering General | 500 |  | Workmanship | Rework |  | Complete |  | Completed |  | The Canal Wall Service Route brackets have been fabricated without sufficient depth between the bottom two angles supporting the proposed location of 2no. __ cable ducts. The clear space is 165mm and the outside diameter of the ducts is 167mm. Drawing C131-MMD-S-DDH-B071_Z-90347 required 175mm. Modification is required the full length of the route to resolve this issue.
| 03SR - Stations (RfL) | Cxxx-NCR-001975 | NCR | Water damage to ductworks & services generally |  | Contr |  | PAD - Paddington Station (West) |  | 2013-01-24 | 2013-01-17 09:26 | -7 | 2012-08-29 | Mechanical - Heating Ventilation & Air Conditioning | 500 |  | Damaged | Rework |  | Complete |  | Completed |  | Ductwork/supports/light fittings are getting water damaged as no protection is in place-see attached photo report .
| 03SR - Stations (RfL) | Cxxx-NCR-001977 | NCR | Bishops Bridge Stair Holding Down Bolts |  | Contr |  | PAD - Paddington Station (West) |  | 2012-10-20 | 2012-10-04 17:27 | -16 | 2012-08-29 | Structural Engineering - Structural Engineering - General | 500 |  | System Defect | Rework |  | Complete |  | Completed |  | Holding down bolts have been cast approximately 100mm out of place, see attached survey.
| 03SR - Stations (RfL) | Cxxx-NCR-001980 | NCR | Discolouration of Granite Sets on RSD and Northern Entrance and Link |  | Contr |  | PAD - Paddington Station (West) |  | 2013-02-15 | 2013-02-21 18:03 | 6 | 2012-08-30 | Architectural - Flooring | 500 |  | Material | Rework |  | Complete |  | Completed |  | Clear colour/shade variations of granite sets on the red star deck resulting in an unacceptable appearance.
| 03SR - Stations (RfL) | Cxxx-NCR-001982 | NCR | bullnose tips - pour workmanship, inspection s and records. |  | Contr |  | PAD - Paddington Station (West) |  | 2012-12-07 | 2013-01-10 12:10 | 34 | 2012-10-02 | Structural Engineering - Steel Member | 500 |  | Workmanship | Rework |  | Complete |  | Completed |  | a)Support angle did not work and therefore sub-contractor tried to fit an angle that would not fit. This was repetitively down 25+ down the span 4 side of the taxi deck. b)There is almost no edge distance in places. c)Damage to bull nose tip. d)checked/supervised by competent person and recorded on check sheet. e)No damage to surrounding works
| 03SR - Stations (RfL) | Cxxx-NCR-001994 | NCR | Sand not removed before grouting granite setts |  | Contr |  | PAD - Paddington Station (West) |  | 2013-02-28 | 2013-02-28 12:56 | 0 | 2012-09-10 | Architectural - Flooring | 500 |  | Workmanship | Rework |  | Complete |  | Completed |  | It has been found in several areas that the jointd are made up of a Thin layer of grout only with sand beneath at various sample locations across the deck. This can particularly be found beneath the disney queue. This appears to have occured due to temporary sand joints not being fully removed prior to final grouting.
| 03SR - Stations (RfL) | Cxxx-NCR-002017 | NCR | ITP Prodcution and Acceptance |  | Contr |  | PAD - Paddington Station (West) |  | 2012-10-26 | 2012-10-31 16:03 | 5 | 2012-09-14 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Rework |  | Complete |  | Completed |  | Works commenced without CRL acceptance of prerpared ITP's for HA MARKS (NR Toilets, __ Stairs Bishops Bridge and Mero at the Northern Entrance (due to commence Monday 17.09.12).
| 03SR - Stations (RfL) | Cxxx-NCR-002032 | NCR | Block work ties |  | Contr |  | PAD - Paddington Station (West) |  | 2012-09-27 | 2012-12-07 16:16 | 71 | 2012-09-20 | Architectural - Brickworks/Blockworks | 500 |  | Workmanship | Rework |  | Complete |  | Completed |  | near the top of the wall the ties are not positioned near the centre of the block work
| 03SR - Stations (RfL) | Cxxx-NCR-002083 | NCR | Local rutting of taxi deck surfacing |  | Contr |  | PAD - Paddington Station (West) |  | 2013-06-28 | 2013-06-24 19:44 | -4 | 2012-10-26 | Civil - Wearing Course | 500 |  | Material | Rework |  | Complete |  | Completed |  | An issue has become apparent on the surfacing of the Taxi deck. The 2No. Inbound __ 1-2 between GL 8-13 near the East end of the deck have developed rutting. Additionally upon inspection there are areas of rutting either side of the taxi drop off island.
| 03SR - Stations (RfL) | Cxxx-NCR-002086 | NCR | Taxi Deck - Pothole in wearing course at GL19 Lane 1 induction loop |  | Contr |  | PAD - Paddington Station (West) |  | 2013-03-28 | 2013-03-14 17:32 | -14 | 2012-10-26 | Civil - Wearing Course | 500 |  | Material | Reject |  | Complete |  | Completed |  | A 4" square peace of wearing course has broken away at the intersection of the induction loop saw cuts for the taxi call forward system. The taxi call forward system is still operational but the loop will need to be replaced. The ongoing issues of EWN 704 and RFI 2006 may have contributed to this failure of the material and this location.
| 03SR - Stations (RfL) | Cxxx-NCR-002108 | NCR | Sagging omia planks |  | Contr |  | PAD - Paddington Station (West) |  | 2013-07-15 | 2013-07-10 17:04 | -5 | 2012-11-07 | Structural Engineering - Formwork | 500 |  | Damaged | Repair |  | Complete |  | Completed |  | These were discovered after the concrete was poured, on top of the taxi deck at these location their appear to be no depression on the surface (photos attached)
| 03SR - Stations (RfL) | Cxxx-NCR-002171 | NCR | Halfan channels lift 3 |  | Contr |  | PAD - Paddington Station (West) |  | 2013-01-24 | 2013-01-29 10:56 | 5 | 2012-11-30 | Structural Engineering - Steel Member | 500 |  | Design | Rework |  | Complete |  | Completed |  | Drawing C131-MMD-S-DDH-B071_Z-90888 detail above level 128.660, show the depth of the halfan channel north face 325mm and south face 365mm, includinding the 10mm packer to allow for any deviations in rhe block work, the north face will intrude in the clear openning by 35mm and south face by 25mm
| 03SR - Stations (RfL) | Cxxx-NCR-002179 | NCR | Damage to KeyBemo sheets |  | Contr |  | PAD - Paddington Station (West) |  | 2013-01-25 | 2013-01-31 18:04 | 6 | 2012-12-07 | Architectural - Roofing & Exterior Treatment | 500 |  | Damaged | Rework |  | Complete |  | Completed |  | Damage caused during installation by &Rock 2No. end panels damaged during installation by Rock Panels damaged by follow on trades storing /stacking materials improperly Warrantee requirements of Welwood the new supplier to allow for inspection of sub layer
| 03SR - Stations (RfL) | Cxxx-NCR-002194 | NCR | Number of fixings in halfan channel |  | Contr |  | PAD - Paddington Station (West) |  | 2013-01-18 | 2013-01-10 10:02 | -8 | 2012-12-13 | Structural Engineering - Steel Member | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | We currently have two fixings top & bottom
| 03SR - Stations (RfL) | Cxxx-NCR-002198 | NCR | Metal trims failure |  | Contr |  | PAD - Paddington Station (West) |  | 2013-01-25 | 2013-01-31 18:23 | 6 | 2012-12-19 | Architectural - Finishes | 500 |  | Material | Rework |  | Complete |  | Completed |  | The detail was a change from the original design to correct a visual snagging but had not been approved by or Crossrail.
| 03SR - Stations (RfL) | Cxxx-NCR-002210 | NCR | Hair line cracks in the blockwork at the location the secondary steel has been installed |  | Contr |  | PAD - Paddington Station (West) |  | 2013-03-29 | 2013-04-02 12:24 | 4 | 2013-01-09 | Structural Engineering - Load Bearing Walls | 500 |  | Design | Repair |  | Complete |  | Completed |  | At the locations where the larger and heavier secondary steel has been fixed to the block work at levels 129.525 to the north and south walls and at level 131.110 north face wall, hair line cracks have appeared in the block work after the installation and appear to be between the top & bottom fixing points of the channels As we have fabricated and installed the secondary steel as per specified design to the block work, Crossrail are to liaise with C131 to provide a solution as the issue may be related to design
| 03SR - Stations (RfL) | Cxxx-NCR-002218 | NCR | Granite Setts: Brass Studs |  | Contr |  | PAD - Paddington Station (West) |  | 2013-01-03 | 2013-02-01 16:22 | 29 | 2013-01-13 | Civil - Civil Engineering General | 500 |  | Workmanship | Rework |  | Complete |  | Completed |  | The Stainless steel studs were all drilled and fixed in the granite setts in the Spring of 2012. Since then the studs have been dislodged and become separated from the granite sett. When these have been replaced they have been replaced with brass studs which are a different colour.
| 03SR - Stations (RfL) | Cxxx-NCR-002219 | NCR | Granite setts: Sand in joints |  | Contr |  | PAD - Paddington Station (West) |  | 2013-08-15 | 2013-08-15 17:05 | 0 | 2013-01-13 | Civil - Civil Engineering General | 500 |  | Workmanship | Rework |  | Complete |  | Completed |  | The granite setts identified on the attachments 'Sand check inspection locations.pdf' and 'Sand check results.pdf' have sand present in their joints.
| 03SR - Stations (RfL) | Cxxx-NCR-002220 | NCR | Granite Setts: Level defects |  | Contr |  | PAD - Paddington Station (West) |  | 2013-08-15 | 2013-08-21 16:09 | 6 | 2013-01-13 | Civil - Civil Engineering General | 500 |  | Workmanship | Rework |  | Complete |  | Completed |  | Granite setts identified on the attachment C272_SZR_GSLEVELS_001.doc are out of level tolerance.
| 03SR - Stations (RfL) | Cxxx-NCR-002221 | NCR | P12 BOH screeding: level errors |  | Contr |  | PAD - Paddington Station (West) |  | 2013-03-31 | 2013-03-14 15:12 | -17 | 2013-01-14 | Civil - Civil Engineering General | 500 |  | Workmanship | Reject |  | Complete |  | Completed |  | The as built levels were out of tolerance.
| 03SR - Stations (RfL) | Cxxx-NCR-002229 | NCR | Column C2 Grouting - Low Cube Results |  | Contr |  | PAD - Paddington Station (West) |  | 2013-02-28 | 2013-01-29 16:08 | -30 | 2013-01-16 | Structural Engineering - Grouting | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | C272 have used “LA REPAIR CONCRETE" technical data sheet attached. Please refer to RFI 1061 and 1117 for history of strengthening works to column C2. Attached cube test results from __ testing lab indicate low cube results at 28 days with 4 no results of 62.5, 61, 61.5 and 60.5 N/mm^2.
| 03SR - Stations (RfL) | Cxxx-NCR-002230 | NCR | NR Plant room 2 TEF 01 fan motor location ( Access Issues for Maintenance ) |  | Contr |  | PAD - Paddington Station (West) |  | 2013-04-26 | 2013-04-19 11:49 | -7 | 2013-01-17 | Mechanical - Heating Ventilation & Air Conditioning | 500 |  | Design | Rework |  | Complete |  | Completed |  | Difficult access due to design/installation.
| 03SR - Stations (RfL) | Cxxx-NCR-002231 | NCR | Water Damage to Electrical services |  | Contr |  | PAD - Paddington Station (West) |  | 2013-06-30 | 2013-07-01 15:39 | 1 | 2013-01-17 | Electrical - LV Equipment | 500 |  | Damaged | Rework |  | Complete |  | Completed |  | Electrical cms/lightfittings have not been protected as per drawing C272-CAR-H-DDA-B071-2-45202
| 03SR - Stations (RfL) | Cxxx-NCR-002233 | NCR | London Street Screen |  | Contr |  | PAD - Paddington Station (West) |  | 2013-05-10 | 2013-04-28 17:52 | -12 | 2013-01-18 | Structural Engineering - Structural Engineering - General | 500 |  | System Defect | Repair |  | Complete |  | Completed |  | 1. Mock-up of London Street Screen has not been provided to CRL for acceptable. 2. Activity 18 of ITP calls for CRL hold point for approval of test piece / weld sample that was not agreed by CRL. 3. C272 have not provided evidence to CRL for weld procedure approvals, welder qualifications, weld equipment certification. 4. Discrepancy between SIDR submission and Fabrication Drawing (indicative sample): • SIDR drawing D002 shows fillet weld of 10mm for up rights whilst fabrication drawing 343 UK-LSS-00 shows fillet weld of 3.5mm. Filet welds on site observed to be between 5-7mm. 5. General notes drawing C-001 states that fillet welds to be ground smooth in exposed areas. Welds have not been ground smooth on site installed posts. 6. Fabrication drawings have not been provided to CRL for review and comments. 7. Steel components do not have unique certification traceability marking related to batch number / mill testing certificates. 8. Bolting down bots, nuts and washers are showing signs of corrosion. General notes drawing C-001 states anchor bolts/washer nut to be provided in galvanized finish therefore corrosion should not be present. 9. __ independent inspection authority report to be provided to CRL for review.
| 03SR - Stations (RfL) | Cxxx-NCR-002249 | NCR | Discolouration of EWS-20 Rainscreen Cladding Panels |  | Contr |  | PAD - Paddington Station (West) |  | 2013-04-04 | 2013-04-02 10:25 | -2 | 2013-01-31 | Architectural - General | 500 |  | Material | Reject |  | Complete |  | Completed |  | 3 No panels fall outside the upper and lower limits of the Anolok 541 colour range. Pattern has faded
| 03SR - Stations (RfL) | Cxxx-NCR-002260 | NCR | Branch Drainage connections |  | Contr |  | PAD - Paddington Station (West) |  | 2013-04-08 | 2013-04-02 11:10 | -6 | 2013-02-06 | Mechanical - Piping | 500 |  | Material | Rework |  | Complete |  | Completed |  | Drainage connections installed with swept 90 degree tees instead of 45 degree tees
| 03SR - Stations (RfL) | Cxxx-NCR-002268 | NCR | GRC Panel Installation |  | Contr |  | PAD - Paddington Station (West) |  | 2013-04-26 | 2013-04-29 12:21 | 3 | 2013-02-11 | Architectural - Walls | 500 |  | Workmanship | Reject |  | Complete |  | Completed |  | Panels have a bow in excess of +/- 6mm
| 03SR - Stations (RfL) | Cxxx-NCR-002270 | NCR | __ – __ Covers |  | Contr |  | PAD - Paddington Station (West) |  | 2013-06-27 | 2013-06-07 13:00 | -20 | 2013-02-12 | Architectural - General | 500 |  | Material | Repair |  | Complete |  | Completed |  | Rusting has formed on parts of the angle frames adjacent to M10 fixings for the __ Access covers. See attached photo.
| 03SR - Stations (RfL) | Cxxx-NCR-002297 | NCR | West Plaza: Paving and South wall cladding mismatch |  | Contr |  | PAD - Paddington Station (West) |  | 2013-03-21 | 2013-03-18 10:26 | -3 | 2013-02-28 | Architectural - Landscape Architectural | 500 |  | Workmanship | Rework |  | Complete |  | Completed |  | The wall panels do not register/align with the alignment of the paving blocks that butt up to them. There is also a strip of made up screed between the paving slab and the face of the wall cladding that should not be visible.
| 03SR - Stations (RfL) | Cxxx-NCR-002307 | NCR | GRC PANELS LUL CONCOURSE |  | Contr |  | PAD - Paddington Station (West) |  | 2013-03-21 | 2013-04-03 18:20 | 13 | 2013-03-07 | Architectural - Walls | 500 |  | Workmanship | Rework |  | Complete |  | Completed |  | Panels as erected do not reflect the examples examined at the factory and delivered to site. Quality of finish is not in line with sample and records of previous mock ups. What is particularly apparent with the uneven finish and colour of each panel. There are differences in colour/shade between panels particular on the corners/edges. There is construction damage to panels. Reference is also made to sections 6, 7and 15 of the ITP. Note that quality concerns have been repeatedly raised by way of QDWB and in emails to C272 dated 25 February 2013 (3#) and 18 February These emails have also asked for official inspection of a mock up to be presented as these panels have been in place much longer than 24 hours. There has so far been no adequate response from C272, thus CRL are obliged to reiterate and re-confirm their concerns with the current finish/visual aspect of the panels as erected on the concourse. CRL note that the 6th panel from the West end is of quality/appearance closer to the sample. All others are reletively poor in relation to the sample and mock up provided.
| 03SR - Stations (RfL) | Cxxx-NCR-002311 | NCR | Stair 5 Landing levels |  | Contr |  | PAD - Paddington Station (West) |  | 2013-04-25 | 2013-05-17 10:50 | 22 | 2013-03-11 | Architectural - Finishes | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | These have been installed at 132.165 & 130.776 respectively. Therefore the top landing is 35mm below the specified FFL.
| 03SR - Stations (RfL) | Cxxx-NCR-002320 | NCR | LUL Station Concourse and Platform: GRC panels. Non Section 12 Compliant |  | Contr |  | PAD - Paddington Station (West) |  | 2013-05-10 | 2013-05-09 11:05 | -1 | 2013-03-15 | Architectural - Walls | 500 |  | Material | Reject |  | Complete |  | Completed |  | GRC panels contain void formers that are not Section 12 compliant.
| 03SR - Stations (RfL) | Cxxx-NCR-002324 | NCR | Out of tolerance screed in west plaza |  | Contr |  | PAD - Paddington Station (West) |  | 2013-05-23 | 2013-05-10 10:34 | -13 | 2013-03-19 | Civil - Landscaping | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | There is an 8mm deviation
| 03SR - Stations (RfL) | Cxxx-NCR-002326 | NCR | BAl 07: Incorrect Glass Fitted |  | Contr |  | PAD - Paddington Station (West) |  | 2013-04-21 | 2013-05-02 09:36 | 11 | 2013-03-21 | Architectural - Balustrade | 500 |  | Material | Rework |  | Complete |  | Completed |  | Glass is clear
| 03SR - Stations (RfL) | Cxxx-NCR-002327 | NCR | Incorrect Levels on Frit |  | Contr |  | PAD - Paddington Station (West) |  | 2013-03-28 | 2013-04-05 18:29 | 8 | 2013-03-21 | Architectural - General | 500 |  | Design | Use As-Is |  | Complete |  | Completed |  | Frit on Bal-07 is at 975mm above FFL and frit on column cladding is at 1050 above FFL
| 03SR - Stations (RfL) | Cxxx-NCR-002351 | NCR | Bishops Bridge Connections (PCC-22) |  | Contr |  | PAD - Paddington Station (West) |  | 2013-04-15 | 2013-04-29 17:57 | 14 | 2013-04-08 | Structural Engineering - Bolted Connections | 500 |  | Design | Use As-Is |  | Complete |  | Completed |  | drawing shows the shear studs to the splice plates have been omitted
| 03SR - Stations (RfL) | Cxxx-NCR-002360 | NCR | Canal Wall Cladding/Artwork |  | Contr |  | PAD - Paddington Station (West) |  | 2013-08-15 | 2013-08-19 14:54 | 4 | 2013-04-09 | Architectural - General | 500 |  | Material | Rework |  | Complete |  | Completed |  | The installed Canal Wall artwork panels fail to provide an adequate level of colour/tonal consistency. The C272 sub-contractor provided samples early in the design and procurement process which were agreed, on the basis of a number of criteria, including colour variation. In particular, a pair of ‘benchmark’ panels were installed in situ and were referred to at the time by the subcontractor as follows…. “…it has been confirmed it was made by exactly the same process as the pre-approved sample. We feel what needs to be examined in detail is the benchmark [panels] as this is the final product…” This benchmark was accepted as an agreed sample. The installed panels fail to meet the level of colour/tonal consistency provided by these agreed samples and as such are non-compliant with the contract specification requirements. More recently , the Contractors supplier, United Anodisers, has produced a pair of upper and lower colour limit samples, but these have only been presented to Crossrail since the panels have been installed, and after the visual inconsistency had been identified. They do not represent any form of agreed tolerance limits.
| 03SR - Stations (RfL) | Cxxx-NCR-002365 | NCR | Basement Service Road -Bindercourse Levels out of Spec |  | Contr |  | PAD - Paddington Station (West) |  | 2013-05-17 | 2013-04-19 12:13 | -28 | 2013-04-12 | Civil - Wearing Course | 500 |  | Workmanship | Rework |  | Complete |  | Completed |  | Existing bindercourse levels are higher than design levels see attached sheet
| 03SR - Stations (RfL) | Cxxx-NCR-002375 | NCR | NR Signage - Lettering |  | Contr |  | PAD - Paddington Station (West) |  | 2013-10-30 | 2013-11-06 11:59 | 7 | 2013-04-25 | Architectural - Signage | 500 |  |  | Rework |  | Complete |  | Completed |  | There appears to be several signs on plat 12 and RSD are non compliant to NR specifications and appear to be predominately vinyl opposed to being printed.
| 03SR - Stations (RfL) | Cxxx-NCR-002379 | NCR | P12 toilets cubicle door coat hooks |  | Contr |  | PAD - Paddington Station (West) |  | 2013-05-31 | 2013-05-15 08:19 | -16 | 2013-04-29 | Civil - Civil Engineering General | 500 |  | Design | Reject |  | Complete |  | Completed |  | The coat hooks specified have been installed and in the time since the toilets have opened have been shown to not be fit for purpose in the environment they are in. The hooks keep falling from the door when the general public hang coats/small bags from the hooks.
| 03SR - Stations (RfL) | Cxxx-NCR-002397 | NCR | Crane Rail Galvanising: Delamination. |  | Contr |  | PAD - Paddington Station (West) |  | 2013-07-10 | 2013-07-08 18:16 | -2 | 2013-05-10 | Civil - Structural Engineering | 500 |  | Workmanship | Rework |  | Complete |  | Completed |  | The coatings are peeling, showing an extremely rough texture as if there are slag inclusions, and showing signs of blistering and corrosion in adjacent areas.
| 03SR - Stations (RfL) | Cxxx-NCR-002400 | NCR | Platform ceiling levels |  | Contr |  | PAD - Paddington Station (West) |  | 2013-05-24 | 2013-06-06 09:29 | 13 | 2013-05-15 | Architectural - Ceilings & Soffits | 500 |  | Design | Use As-Is |  | Complete |  | Completed |  | The levels do not match the design across the extent of the platform. At GL50 the ceiling has been set lower to avoid a clash with M&E trunking and concrete beam downstand. At GL50 the ceiling is 47mm low (to avoid the trunking clash) and this runs out to around 20mm low at GL54.
| 03SR - Stations (RfL) | Cxxx-NCR-002409 | NCR | Concrete Stength at 28 days |  | Contr |  | PAD - Paddington Station (West) |  | 2013-06-21 | 2013-06-20 12:28 | -1 | 2013-05-24 | Civil - Civil Engineering General | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | Cubes highlighted in the attached cube summary do not meet required strength after 28 days. Areas are: Triangle Site Props __ Gap infills - Concourse Level Column M6 - Triangle Site West Side Concourse North Wall Upstand GL57 - 61 Concourse Level slap 53-55 Looking at full __ report this seems to have been caused by low/high temperatures at their lab during the curing period.
| 03SR - Stations (RfL) | Cxxx-NCR-002410 | NCR | Bishops Bridge to Public Plaza Area Staircase Nosings |  | Contr |  | PAD - Paddington Station (West) |  | 2013-07-01 | 2013-06-04 15:37 | -27 | 2013-05-30 | Architectural - Landscape Architectural | 500 |  | Workmanship | Rework |  | Complete |  | Completed |  | Current fixings do not have anti tamper heads
| 03SR - Stations (RfL) | Cxxx-NCR-002411 | NCR | Required Concrete Strength not met at 28 days |  | Contr |  | PAD - Paddington Station (West) |  | 2013-06-06 | 2013-06-10 13:50 | 4 | 2013-05-30 | Civil - Civil Engineering General | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | All cubes detailed on this NCR did not meet required strength at 28 days but met requirement at 56 days as detailed in Cube Results NCR document attached.
| 03SR - Stations (RfL) | Cxxx-NCR-002418 | NCR | Damage/Wear to Terrazzo Tiles |  | Contr |  | PAD - Paddington Station (West) |  | 2013-07-02 | 2013-06-28 14:59 | -4 | 2013-06-04 | Architectural - Flooring | 500 |  | System Defect | Rework |  | Complete |  | Completed |  | Tiles/grout are breaking up around their edges. This is adjacent to the eastern most wide gate, non paying side.
| 03SR - Stations (RfL) | Cxxx-NCR-002421 | NCR | __ sub frame to Cladding |  | Contr |  | PAD - Paddington Station (West) |  | 2013-06-21 | 2013-06-12 10:22 | -9 | 2013-06-07 | Architectural - Walls | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | Cladding subframe is being constructed with a __ type system. This is galvanised. The cut ends should have the bare steel coated to provide equivalent corrosion protection. The assembly as it stands has not had such treatment to any of the cut ends.
| 03SR - Stations (RfL) | Cxxx-NCR-002424 | NCR | Incorrect Strength of Concrete used to fill column M64 |  | Contr |  | PAD - Paddington Station (West) |  | 2013-06-17 | 2013-06-14 12:50 | -3 | 2013-06-10 | Structural Engineering - Structural Engineering - General | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | For column at GL 64M 40N concrete used in error. See attached delivery tickets and highlighted cube results(in yellow). All other column pours have also been included to show compliance with specification.
| 03SR - Stations (RfL) | Cxxx-NCR-002431 | NCR | Concourse terrazzo expansion joints |  | Contr |  | PAD - Paddington Station (West) |  | 2013-06-14 | 2013-06-20 12:25 | 6 | 2013-06-11 | Architectural - Flooring | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | The movement joints were installed throughout the concourse, but was missed under BAL07 & BAL05
| 03SR - Stations (RfL) | Cxxx-NCR-002432 | NCR | Entrance to Lift 5 east plaza |  | Contr |  | PAD - Paddington Station (West) |  | 2013-06-19 | 2013-06-21 13:00 | 2 | 2013-06-12 | Architectural - Flooring | 500 |  | Design | Use As-Is |  | Complete |  | Completed |  | subsequently their is a gap of 30mm between the claddding & entrance matt
| 03SR - Stations (RfL) | Cxxx-NCR-002433 | NCR | Non Conforming Architectural Fastenings |  | Contr |  | PAD - Paddington Station (West) |  | 2013-08-10 | 2013-07-15 16:21 | -26 | 2013-06-19 | Architectural - General | 500 |  | Material | Reject |  | Complete |  | Completed |  | Current installed fastenings are deemed non-conforming.
| 03SR - Stations (RfL) | Cxxx-NCR-002437 | NCR | Architrave detail |  | Contr |  | PAD - Paddington Station (West) |  | 2013-07-26 | 2013-07-10 16:57 | -16 | 2013-06-27 | Architectural - Doors | 500 |  | Design | Rework |  | Complete |  | Completed |  | Therefore the design detail at this location cannot be used
| 03SR - Stations (RfL) | Cxxx-NCR-002456 | NCR | Link Roof Welding |  | Contr |  | PAD - Paddington Station (West) |  | 2013-10-30 | 2013-10-03 16:35 | -27 | 2013-09-03 | Structural Engineering - Welding | 500 |  |  | Use As-Is |  | Complete |  | Completed |  | Welder did not have qualification for 6 mm full penetration fillet weld carried out off site
| 03SR - Stations (RfL) | Cxxx-NCR-002475 | NCR | Taxi Deck Signage Position |  | Contr |  | PAD - Paddington Station (West) |  | 2013-09-17 | 2013-10-30 | 43 | 2013-09-03 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | Taxi Deck signs S132,S133,S134,S135,S136, and S137 have all been installed 90 degrees different to the design orientation shown on the Taxi Deck Signage Setting out drawing C131-MMD-A-DDA-B071_1-10191, see photo attached.
| 03SR - Stations (RfL) | Cxxx-NCR-002481 | NCR | Northern Entrance ATG Bollards -Vehicle Impact Type - EXT 40 |  | Contr |  | PAD - Paddington Station (West) |  |  | 2013-10-28 |  | 2013-10-03 | Structural Engineering - Structural Engineering - General | 500 |  | Incorrect Installation | Use As-Is |  | Complete |  | Completed |  | "The bollards installed at the northern entrance do not comply with the manufactures specification and IFC drawing layout. Northern Entrance bollards as indicated on as-built site sketch ‘2407DEF022.pdf’ and photo attached show 2 no triple leg bollard facing the opposite direction. As the direction has been changed at these 2 locations the pinned connection between the bollards and orientation is not in accordance with the manufacturer's specification and requirements. In addition there is an array of 2 bollards on the east side that do not comply with manufacturer specification. See PAD-CRL RFI-C272-02436 for C272 as-built condition reponse and history. "
| 01CV - Civils | Cxxx-NCR-000045 | NCR | reinforcement to MDU base |  | Contr |  | OAC - Old Oak Common Depot (West) |  | 2011-07-01 | 2011-08-11 14:18 | 41 | 2011-07-11 | Civil - Structural Engineering | 500 |  | Material | Rework |  | Complete |  | Completed |  | bar mark 31 and 32 incorrectly bent by reinforcement manufacture
| 01CV - Civils | Cxxx-NCR-000046 | NCR | Missing reinforcement from __ chamber 1 |  | Contr |  | OAC - Old Oak Common Depot (West) |  | 2011-06-30 | 2011-08-17 09:15 | 48 | 2011-07-11 | Civil - Structural Engineering | 500 |  | Workmanship | Rework |  | Complete |  | Completed |  | On the offered final inspection visit it was noted by the Crossrail team that the __ box was missing reinforcement bars to the end walls by the duct entry positions.
| 01CV - Civils | Cxxx-NCR-000047 | NCR | Quality system |  | Contr |  | OAC - Old Oak Common Depot (West) |  | 2011-07-15 | 2011-08-17 09:15 | 33 | 2011-07-13 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Rework |  | Complete |  | Completed |  | Failure to follow the Quality system by the contractor not carrying out all the checks and hold points required by the ITP's. Resulting in rework, insufficient or no notification to the Crossrail team prior to comencing to the next stage of the works.
| 01CV - Civils | Cxxx-NCR-000048 | NCR | Missing reinforcement to __ chamber 2 |  | Contr |  | OAC - Old Oak Common Depot (West) |  | 2011-07-07 | 2011-08-17 09:13 | 41 | 2011-07-13 | Civil - Structural Engineering | 500 |  | Workmanship | Rework |  | Complete |  | Completed |  | missing reinforcement interanl face
| 01CV - Civils | Cxxx-NCR-000049 | NCR | Installation of wrong colour ducting for the lighting columns |  | Contr |  | OAC - Old Oak Common Depot (West) |  | 2011-07-04 | 2011-08-17 09:13 | 44 | 2011-07-13 | Electrical - Cable Management | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | Black cable ducting was installed across access road instead of orange ducting
| 01CV - Civils | Cxxx-NCR-000050 | NCR | Honeycomb |  | Contr |  | OAC - Old Oak Common Depot (West) |  | 2011-07-12 | 2011-08-17 09:12 | 36 | 2011-07-13 | Civil - Structural Engineering | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | honeycomb accured due to lack of compaction during pouring
| 01CV - Civils | Cxxx-NCR-000051 | NCR | HV cable ducting not sanded or warning taped |  | Contr |  | OAC - Old Oak Common Depot (West) |  | 2011-07-18 | 2011-08-17 09:09 | 30 | 2011-07-14 | Civil - Utilities Engineering | 500 |  | Workmanship | Rework |  | Complete |  | Completed |  | no sand or warning tape over ducting adjacent to the sub station
| 01CV - Civils | Cxxx-NCR-000052 | NCR | Compaction around sub-station |  | Contr |  | OAC - Old Oak Common Depot (West) |  | 2011-07-18 | 2011-08-17 09:07 | 30 | 2011-07-14 | Civil - Fill | 500 |  | Workmanship | Rework |  | Complete |  | Completed |  | Material not suitably compacted
| 01CV - Civils | Cxxx-NCR-000053 | NCR | Electrical chamber built late proir to road surfacing |  | Contr |  | OAC - Old Oak Common Depot (West) |  | 2011-07-15 | 2011-08-17 09:06 | 33 | 2011-07-14 | Civil - Structural Engineering | 500 |  | Planning | Use As-Is |  | Complete |  | Completed |  | Not constructed with sufficient time to cure
| 01CV - Civils | Cxxx-NCR-000054 | NCR | No flexcell installed on concrete surround to drainage pipe |  | Contr |  | OAC - Old Oak Common Depot (West) |  | 2011-07-12 | 2011-08-17 09:04 | 36 | 2011-07-14 | Civil - Drainage | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | flexcell admitted from concrerte surround
| 01CV - Civils | Cxxx-NCR-000055 | NCR | Insufficient space to construct backdrop in existing SW manhole |  | Contr |  | OAC - Old Oak Common Depot (West) |  | 2011-07-29 | 2011-08-17 08:51 | 19 | 2011-07-14 | Civil - Drainage | 500 |  | Design | Rework |  | Complete |  | Completed |  | no backdrop provided
| 01CV - Civils | Cxxx-NCR-000056 | NCR | Concrete design mix not submitted |  | Contr |  | OAC - Old Oak Common Depot (West) |  | 2011-07-14 | 2011-08-17 08:50 | 34 | 2011-07-14 | Civil - Civil Engineering General | 500 |  | Design | Use As-Is |  | Complete |  | Completed |  | design not provided
| 01CV - Civils | Cxxx-NCR-000057 | NCR | Tack coat |  | Contr |  | OAC - Old Oak Common Depot (West) |  | 2011-07-18 | 2011-08-17 08:49 | 30 | 2011-07-14 | Civil - Base Course | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | Tack coat was not applied to the existing planned carriageway for the length of the regulating course from the junction at the bottom of the hill to the top. This is shown in the attached photos.
| 01CV - Civils | Cxxx-NCR-000029 | NCR | Pier Road TM01 Manhole defects |  | Crossrail | XRL | ZAW - Asset Wide (All Locations) (Projectwide) |  | 2015-06-30 | 2014-12-18 14:33 | -194 | 2013-11-15 09:47 | Civil - Utilities Engineering | 5000 |  | Design | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | TM01 movement in frame and HRA reinstating has sunk.
| 01CV - Civils | Cxxx-NCR-000030 | NCR | Pier Road UTM01 Manhole Defects |  | Crossrail | XRL | ZAW - Asset Wide (All Locations) (Projectwide) |  | 2015-06-30 | 2014-12-18 14:34 | -194 | 2013-11-15 09:50 | Civil - Utilities Engineering | 5000 |  | Design | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | UTM01 movement in frame noisy as vehicles pass over, suggesting potential defects.
| 01CV - Civils | Cxxx-NCR-000031 | NCR | Whitehorse Road UTM05 Manhole Defects |  | Crossrail | XRL | ZAW - Asset Wide (All Locations) (Projectwide) |  | 2015-06-30 | 2014-12-18 14:35 | -194 | 2013-11-15 09:55 | Civil - Utilities Engineering | 5000 |  | Design | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Whitehorse Road UTM05. Movement in frame as traffic passes over, noisy ,also HRA Reinstament has sunk
| 01CV - Civils | Cxxx-NCR-000032 | NCR | Rhodeswell Road TM01 Manhole Defects |  | Crossrail | XRL | ZAW - Asset Wide (All Locations) (Projectwide) |  | 2015-06-30 | 2014-12-18 14:37 | -194 | 2013-11-15 09:57 | Civil - Utilities Engineering | 5000 |  | Design | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Rhodeswell Road TM01 Movement in frame, noisy.
| 01CV - Civils | Cxxx-NCR-000033 | NCR | Fairfield Road TM05 Manhole Defects |  | Crossrail | XRL | ZAW - Asset Wide (All Locations) (Projectwide) |  | 2015-06-30 | 2014-12-18 14:38 | -194 | 2013-11-15 10:00 | Civil - Utilities Engineering | 5000 |  | Design | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Fairfield Road TM05 movement in frame ,noisy . Has been replaced previously - 2nd time this has failed.
| 01CV - Civils | Cxxx-NCR-000034 | NCR | Bow Road UTM05 Manhole Defects |  | Crossrail | XRL | ZAW - Asset Wide (All Locations) (Projectwide) |  | 2015-06-30 | 2014-12-18 14:39 | -194 | 2013-11-15 10:03 | Civil - Utilities Engineering | 5000 |  | Design | Repair | 3 (3-6k) | Complete | Design Problem - Other | Completed |  | Bow Road UTM05 manhole - movement, noise and reinstatement sunk .
| 01CV - Civils | Cxxx-NCR-000035 | NCR | Non installation of boundary box to TM03 South Place |  | Contr | SKC | ZAW - Asset Wide (All Locations) (Projectwide) |  | 2013-12-02 | 2013-12-09 11:14 | 7 | 2013-11-18 11:58 | Civil - Utilities Engineering | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Boundary boxes are designed to be installed within the footway near to each Hydroguard installation. They have a radio frequency transparent lid and are designed to house the aerial from the hydroguard to increase the quality of the signal. At TM03 South Place the installation took place within the centre of a dual carriageway road and no access was possible to the footpath. The aerial is therefore located within the main chamber and seated below the metallic cover. If there are any signal issues due to the aerials location we should find out shortly following the initial signal monitoring period.
| 01CV - Civils | Cxxx-NCR-000037 | NCR | Bow Road TM03 Manhole Defects |  | Crossrail | XRL | ZAW - Asset Wide (All Locations) (Projectwide) |  | 2015-06-30 | 2014-12-18 14:41 | -194 | 2013-11-29 07:57 | Civil - Utilities Engineering | 5000 |  | Workmanship | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Bow Road TM03 manhole - movement, noise and reinstatement cracking.
| 01CV - Civils | Cxxx-NCR-000040 | NCR | Construction arrangement of resin manhole sections |  | Contr | SKC | ZAW - Asset Wide (All Locations) (Projectwide) |  | 2015-06-30 | 2014-12-18 14:32 | -194 | 2013-12-05 13:33 | Civil - Utilities Engineering | 5000 |  | Design | Use As-Is | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Whilst completing the erection of TWUL specified polymer man hole sections the two section immediately above the I frame have been installed in the standard arrangement, with the interlocking lip pointing up. This is a departure from the design in that it shows the section directly above the I frame inverted and screwed to the section immediately above it. On preliminary examination the chamber sections are of a similar size to the I frame meaning that they do not overlap it sufficiently to allow the interlocking lip to sit around the outside of the I frame. This is currently being investigated as these were produced with standard sizes from the specified framework supplier.
| 01CV - Civils | Cxxx-NCR-000041 | NCR | Manhole Steel I-Frame Bitumen Coating |  | Crossrail | XRL | ZAW - Asset Wide (All Locations) (Projectwide) |  | 2015-06-30 | 2014-12-18 14:43 | -194 | 2013-12-06 13:52 | Civil - Utilities Engineering | 0 |  | Supervision/Management | Repair | 4 (0.5-3k) | Complete | Personnel Error - Inattention to detail | Completed |  | __ drawing STDS-PL-02215-IN has a note stating "I SECTION FRAME TO BE BITUMEN COATED ON SITE FOR ADDITIONAL CORROSION RESISTANCE". None of the chambers installed on C295 have had a bitumen coating applied to the galvanised steel I-frames.
| 01CV - Civils | Cxxx-NCR-000042 | NCR | Manholes - polymer sections below I-frame - no reinforcement installed |  | Crossrail | XRL | ZAW - Asset Wide (All Locations) (Projectwide) |  | 2015-06-30 | 2014-12-18 14:45 | -194 | 2013-12-10 11:57 | Civil - Utilities Engineering | 50000 |  | Supervision/Management | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | __ drawing STDS-PL-02215-IM rev E states in Detail C "2NO. 15mm HOLES EQUALLY SPACED PER LOWER SECTION WITH 10mm MILD STEEL REINFORCING BAR". All chambers installed on C295 have no reinforcement bars installed on the lower polymer sections below the I-frames.
| 01CV - Civils | Cxxx-NCR-000045 | NCR | Back to back chamber design reinstatement failure |  | Contr | SKC | ZAW - Asset Wide (All Locations) (Projectwide) |  | 2014-03-03 | 2014-02-28 13:03 | -3 | 2014-02-17 12:17 | Civil - Utilities Engineering | 1000 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | The reinstatement on Bow Road around the smaller chamber from the back-to-back design has broken out between the two boxes and sunk around the smaller, non-reinforced chamber. With the two boxes being installed together and joined through the sections the area of surface to apply reinstatement is too small and doesn't meet Hauc reinstatement specifications. It appears that this has resulted in the reinstatement at this position breaking out, having not had enough area to bind on to. The area around the small chamber has also sunk.
| 01CV - Civils | Cxxx-NCR-000047 | NCR | Man hole frame cracked at Fairfield Road UTM05 chamber |  | Contr | SKC | ZAW - Asset Wide (All Locations) (Projectwide) |  | 2014-03-31 | 2014-03-17 09:18 | -14 | 2014-02-21 16:09 | Civil - Utilities Engineering | 1000 |  | Damaged | Reject | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | On inspection of the manhole chamber frame and lid following a nuisance noise complaint it was found that the D400 carriageway frame installed at Fairfield Road was cracked at the hinge section. An investigation is underway as soon as the frame can be replaced and the cracked one examined.
| 01CV - Civils | Cxxx-NCR-000048 | NCR | Damage found to D400 man hole cover on Bow Road UTM05 |  | Contr | SKC | ZAW - Asset Wide (All Locations) (Projectwide) |  | 2015-06-30 | 2014-12-18 14:33 | -194 | 2014-02-26 11:39 | Civil - Utilities Engineering | 3000 |  | Damaged | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | A colleague noticed on passing that a carriageway man hole cover was smashed at one corner and could present a hazard due to its location. A replacement was installed within an hour to rectify the fault. On inspection of the cover it was identified that it was not of __ framework approval. It is a D400 rated lid however and should not have failed.
| 01CV - Civils | Cxxx-NCR-000049 | NCR | Peto Street/Caxton Street working without 3F highway approval |  | Crossrail | XRL | ZAW - Asset Wide (All Locations) (Projectwide) |  | 2014-03-25 | 2014-03-17 09:34 | -8 | 2014-03-04 10:54 | Consents - Traffic & Highways | 0 |  | Planning | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | LB Newham has advised Crossrail that a contractor is working at Peto Street/Caxton Street without consent as the agreed 3F form expired on 26th February.
| 01CV - Civils | Cxxx-NCR-000050 | NCR | Victoria Dock Road TM01 Incorrect Manhole Lid |  | Crossrail | XRL | ZAW - Asset Wide (All Locations) (Projectwide) |  | 2014-07-31 | 2014-07-16 07:38 | -15 | 2014-07-08 15:46 | Civil - Utilities Engineering | 0 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Manhole lid installed at this location is not of type approved by __.
| 05SY - Systemwide | Cxxx-NCR-000001 | NCR | Testing NCR C298 CRL |  | Crossrail | XRL | PLU - Plumstead Portal (East) |  | 2013-12-16 | 2013-12-02 14:13 | -14 | 2013-12-02 14:10 | Archaeology - General | 500 |  | Damaged | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Change to drawings not provided on time | Completed |  | Testing NCR C298
| 05SY - Systemwide | Cxxx-NCR-000004 | NCR | Working without ITPs in place |  | Crossrail | XRL | PLU - Plumstead Portal (East) |  | 2014-05-02 | 2014-04-25 13:39 | -7 | 2014-04-07 15:03 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Repair | 4 (0.5-3k) | Complete | Procedure Problem - Not Defined | Completed |  | Whilst carrying out a CRL led surveillance of the enabling works records, it was found that the Contractor had commenced work on the following activities; wick drainage and formation earthworks with no approved ITP in place.
| 05SY - Systemwide | Cxxx-NCR-000005 | NCR | Temporary works |  | Crossrail | XRL | PLU - Plumstead Portal (East) |  | 2014-05-06 | 2014-05-06 12:55 | 0 | 2014-04-07 15:23 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Repair | 4 (0.5-3k) | Complete | Procedure Problem - Not Defined | Completed |  | Whilst carrying out a CRL led surveillance on enabling works records It was confirmed by the Contractor that the pile mats for the sheet piling and the deep soil mixing had been installed without the ITPs for both activities being approved and no consideration to the design and inspection regime, although the pile mats are temporary works there is a requirement for an ITP for this activity.
| 05SY - Systemwide | Cxxx-NCR-000006 | NCR | Compaction Testing |  | Crossrail | XRL | PLU - Plumstead Portal (East) |  | 2014-05-06 | 2014-05-06 12:52 | 0 | 2014-04-07 16:12 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | During a CRL led Surveillance at __'s site office the Contractor’s engineer stated he was not aware of the requirement in the specification Cxxx-OVE-A-RSP-CR148-50002 rev 6 clause 6/6.6 to carry out compaction test on the formation and confirmed that this had not been carried out
| 05SY - Systemwide | Cxxx-NCR-000007 | NCR | Dry Soil Mixing Columns Rows 26 -59 |  | Contr | __P | PLU - Plumstead Portal (East) |  | 2014-07-03 | 2014-07-09 12:29 | 6 | 2014-05-29 15:32 | Civil - Civil Engineering General | 5000 |  | Incorrect Installation | Repair | 3 (3-6k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | The dry soil mixing (DSM) columns were set out using a GPS system. The GPS system was not correctly configured during installation meaning that columns in rows 27 -59 and 64 and 67have been installed with a column interlock less than 0.6D specified (480mm). The minimum interlock measured has been 420mm. Please see attached sketch for details – please note due to delay on removal of site platform and recent standing water on the site this survey is only partially complete, but full as-builts will be completed as soon as possible and testing will be focussed on areas that were installed under incorrect GPS direction to ensure that they meet the testing requirements as specified.
| 05SY - Systemwide | Cxxx-NCR-000008 | NCR | Insufficient information on backfill check sheets |  | Crossrail | XRL | PLU - Plumstead Portal (East) |  | 2014-07-11 | 2014-07-09 11:56 | -2 | 2014-06-06 12:36 | Civil - Fill | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | During a planned surveillance at the __ site office, a sample review of backfill check sheets dated 13/03/14, 19/03/2014, found that the check sheets had been signed in the relevant places but there were no site locations referenced and the attached marked up drawings were also not referenced onthe check sheet. Both the check sheet and the ITP do not document the inspection frequency for any of the check items.
| 05SY - Systemwide | Cxxx-NCR-000009 | NCR | MCR not in place for DSM binder (Portland Cement) |  | Crossrail | XRL | PLU - Plumstead Portal (East) |  | 2014-06-30 | 2014-06-26 11:40 | -4 | 2014-06-16 14:01 | Civil - Geotechnical Engineering | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Use of unapproved materials | Completed |  | Materials Compliance Records (MCR) were reviewed during the CRL Deep Soil Mixing (DSM) surveillance dated 15th May 2014. It was indentified that an MCR was in place for Portland Limestone cement, however no MCR existed for Lafarge/ __ cement which is additionally being used as a binder in the DSM works. Works Information Vol 2B Part 13 Clause 13.3.8 states “The Contractor shall utilise the template attached in Appendix 13J (MCR) for the purpose of recording material and product acceptances for the works and submit such records to the Project Manager for acceptance”. To ensure compliance with the Works Information this NCR was raised.
| 05SY - Systemwide | Cxxx-NCR-000010 | NCR | InsituSi and GeoSonic being used for DSM sampling and testing activities without UKAS accreditation or PM's acceptance |  | Crossrail | XRL | PLU - Plumstead Portal (East) |  | 2014-06-30 | 2014-06-30 14:15 | 0 | 2014-06-16 14:09 | Civil - Geotechnical Engineering | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Verification Problems - Other | Completed |  | It was identified during the CRL DSM surveillance dated 15th May 2014 that the following testing laboratories were being used for carrying out DSM sampling and testing activities during the works. • InsituSi – Electrical cone and piezoncone penetration testing • GeoSonic – Core sampling • __ – Laboratory testing A post surveillance request was made to confirm whether InsituSi and GeoSonic held UKAS accreditation or PM’s acceptance to carry out the above testing and sampling activities. Works Information Vol 2B Part 20.8 states “All on-site and off-site testing shall be carried out by laboratories accredited by UKAS or similar ….. The requirements for UKAS accreditation may be waived for the testing of systems and their components, subject to an alternative testing proposal by the Contractor and the acceptance of the proposal by the Project Manager”. Both InsituSi and GeoSonic fall under the requirements of UKAS ISO 17025:2005 General requirements for the competence of testing and calibration laboratories. No UKAS accreditation or PM’s acceptance was produced for InsituSi and GeoSonic and as such this NCR was raised as part of the surveillance.
| 05SY - Systemwide | Cxxx-NCR-000011 | NCR | Test Equipment Schedule |  | Crossrail | XRL | PLU - Plumstead Portal (East) |  | 2014-07-29 | 2014-07-29 13:57 | 0 | 2014-07-07 09:28 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | During a CRL led surveillance The contractor confirmed they had no schedule of all inspection, measuring and test equipment, the contractor maintained a file with the with all the measuring and test equipment details including the calibration certificates.
| 05SY - Systemwide | Cxxx-NCR-000012 | NCR | Deep Soil Mixing testing requirements |  | Crossrail | PDP | PLU - Plumstead Portal (East) |  | 2014-10-13 | 2014-10-07 13:39 | -6 | 2014-07-21 16:34 | Civil - Geotechnical Engineering | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | It has not been adequately demonstrated that the requirements of clause 6/13.15 of Volume 2C Specification - Cxxx-OVE-A-RSP-CR148-50002 Rev 7.0 have been complied with. 6/13.15 The unconfined compression strength of the DSM columns at 28 days after mixing throughout the full depth and over the full cross section of the column shall be: Target unconfined compression strength 250KPa Minimum unconfined compression strength 225kPa No more than 10% of columns shall have unconfined compression strength below the target strength. The methods for determining the strength are given in Clauses 6/13.24 and 6/13.25. Further to this, clause 6/13.27 relating to dimensions of the testing equipment have not been complied with. 6/13.27 The testing has not been carried out as per the specification “The tests shall be carried out in accordance with Section 2, Appendix B of SGF Report 4:95E.” Additionally, compliance with clauses 6/13.23 and 6.13/24 has not been adequately demonstrated, particularly those parts as indicated below 6/13.23 The following information shall be recorded: • Column number • Date, time and duration of the installation • Commencing level • Length and diameter of column • Quantity of binder per metre of depth during penetration and retrieval • Applied energy and power during penetration and retrieval • Pushing and lifting force during penetration and retrieval • Rotation speed during penetration and retrieval • Feed and exhaust pressures • Penetration and retrieval rate versus depth • Evidence of penetration into the River Terrace Deposits 6/13.24 (Part) Testing in the demonstration area shall comprise: • Standard column penetration tests or cone penetration tests at the centre of the column and 0.3d from the centre of the column (where d is the column diameter) on not less than 8 columns carried out in accordance with clause 6/13.27. The results of these tests shall be correlated with the undrained shear strength measured on core or tube samples.
| 05SY - Systemwide | Cxxx-NCR-000013 | NCR | Deep Soil Mixing |  | Crossrail | PDP | PLU - Plumstead Portal (East) |  | 2014-10-17 | 2014-10-15 10:17 | -2 | 2014-09-05 17:10 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Misunderstand the definition of the requirement | Completed |  | A zone of 300mm to 450mm of untreated or poorly mixed soil exists at the base of all the columns contrary to cl 6/13.15 "The unconfined compression strength of the DSM columns at 28days should meet the minimum required strength after mixing throughout the full depth and over the full cross section of the column."
| 05SY - Systemwide | Cxxx-NCR-000014 | NCR | Omission of chamfer detail on support slab |  | Contr | __C | PLU - Plumstead Portal (East) |  | 2014-10-24 | 2014-10-21 13:52 | -3 | 2014-09-30 17:08 | Civil - Civil Engineering General | 1000 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Support slab bays 21 to 25 have been cast without sufficient chamfer detail.
| 05SY - Systemwide | Cxxx-NCR-000015 | NCR | Depth of support slab not as per design |  | Contr | __C | PLU - Plumstead Portal (East) |  | 2014-10-24 | 2014-10-21 13:56 | -3 | 2014-09-30 17:14 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Support slab between bays 21 and 25 is 220mm instead of the 250mm as per the drawing
| 05SY - Systemwide | Cxxx-NCR-000016 | NCR | 20mm dia links cut to aid installation of coping units |  | Contr | __C | PLU - Plumstead Portal (East) |  | 2014-10-14 | 2014-10-03 15:00 | -11 | 2014-09-30 17:18 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | The links (shape code 063) have been cut on site effectively becoming shape code 51. This was to assist in the installation of the coping units where the additional link was causing an obstruction.
| 05SY - Systemwide | Cxxx-NCR-000017 | NCR | Location of SW-MH-1T-CP |  | Contr | __C | PLU - Plumstead Portal (East) |  | 2014-10-29 | 2014-10-23 09:53 | -6 | 2014-10-15 09:17 | Civil - Drainage | 1000 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Misunderstand the definition of the requirement | Completed |  | The line of drainage run 2.000T has been installed in the wrong direction, resulting in SW-MH-1T-CP being installed approximately 6.5m to the south west of the design location.
| 05SY - Systemwide | Cxxx-NCR-000018 | NCR | Fencing surveillance - Contractor's Declaration |  | Contr | __C | PLU - Plumstead Portal (East) |  | 2014-11-04 | 2014-11-05 16:05 | 1 | 2014-10-21 16:51 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Surveillance on fencing has identified that the Contractor's Declaration was not approved prior to commencing works. Correspondance trail is in place for these works. Littlewoods (fencing contractor) to supply current fabrication drawings for submission via eB.
| 05SY - Systemwide | Cxxx-NCR-000019 | NCR | Compressible filler - bays 40-42 |  | Contr | __C | PLU - Plumstead Portal (East) |  | 2014-11-05 | 2014-10-27 16:18 | -9 | 2014-10-22 16:58 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Compressible filler was not installed between the blinding and precast panels on bays 40-42. Note - this still complies with the 'Typical Top of Wall Detail' shown on drawing Cxxx-OVE-S-DDA-CR148_Z-87191.
| 05SY - Systemwide | Cxxx-NCR-000020 | NCR | Reduced cover to bars - stitch slab bays 1 and 2 |  | Contr | __C | PLU - Plumstead Portal (East) |  | 2014-11-28 | 2014-11-27 12:43 | -1 | 2014-11-05 09:39 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Reduced cover between links and coping unit on stitch slabs bays 1 and 2 (approx 20mm). In other locations the bars were able to be bent back prior to pouring in order to achieve the required cover.
| 05SY - Systemwide | Cxxx-NCR-000021 | NCR | Concrete Cube Strengths |  | Contr | __C | PLU - Plumstead Portal (East) |  | 2014-12-05 | 2014-11-28 10:27 | -7 | 2014-11-21 09:19 | Civil - Civil Engineering General | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Worker not correctly instructed | Completed |  | Concrete cube strength results are lower than specifiied in certain locations. We have requested a report from our supplier regarding these results. Please see attached spreadsheet for cube test results.
| 01CV - Civils | Cxxx-NCR-000120 | NCR | ROP-Removal of inclinometer IE70111 |  | Contr |  | TUX - Tunnel Drive X (West) |  | 2011-12-15 | 2012-01-09 08:57 | 25 | 2011-09-27 | Civil - Geotechnical Engineering | 500 |  | Damaged | Use As-Is |  | Complete |  | Completed |  | The existing inclinometer has been damaged following trial hole excavation works to locate any unknown structures prior to piling causing the inclinometer to stop working.
| 01CV - Civils | Cxxx-NCR-000134 | NCR | ATS non conformance to Specification |  | Contr |  | TUX - Tunnel Drive X (West) |  | 2011-11-09 | 2011-12-20 16:19 | 41 | 2011-10-26 | Surveying - Instrumentation and Monitoring | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | The Automatic Total Stations that are being used on this contract conforms to the distance measuring accuracy of +/-1mm +1ppm, but measures angular accuracy of 1.0secons of arc rather than 0.5sec.
| 01CV - Civils | Cxxx-NCR-000151 | NCR | Steel fibre dosing unit on batching plant |  | Contr |  | TUX - Tunnel Drive X (West) |  | 2011-12-13 | 2012-01-09 15:35 | 27 | 2011-12-06 | Tunnelling - Linings - Precast | 500 |  | Equipment Breakdown | Repair |  | Complete |  | Completed |  | Steel fibre hopper dosing unit stopped giving information about quantities to the reporting system, concrete tickets have steel fiber quantities written down manually.
| 01CV - Civils | Cxxx-NCR-000152 | NCR | Segment turning device |  | Contr |  | TUX - Tunnel Drive X (West) |  | 2011-12-20 | 2012-01-06 12:48 | 17 | 2011-12-06 | Tunnelling - Linings - Precast | 500 |  | Design | Rework |  | Complete |  | Completed |  | Segment turning device is damaging segments in the area of the gasket groove during clamping/lifting.
| 01CV - Civils | Cxxx-NCR-000154 | NCR | Production of Segments Prior to Receiving CRL Acceptance of Control Documents |  | Contr |  | TUX - Tunnel Drive X (West) |  | 2011-12-23 | 2012-02-10 09:31 | 49 | 2011-12-07 | Tunnelling - Linings - Precast | 500 |  | Supervision/Management | Rework |  | Complete |  | Completed |  | Limited production of precast concrete segments commenced at OOC on 6th Dec based upon the following ITP's: Cxxx--C-ITP-CRT00_ST005-50026 1.0 OOC Incoming Materials Inspection Cxxx--C-ITP-CRT00_ST005-50027 1.0 OOC Concrete testing Cxxx--C-ITP-CRT00_ST005-50028 1.0 OOC Segment Manufacture Cxxx--C-ITP-CRT00_ST005-50029 1.0 OOC Segment Trial Ring Erection Cxxx--C-ITP-CRT00_ST005-50030 1.0 OOC Segment & Mould dimensional inspection All the above ITP's were submitted for acceptance on 4th Nov 11
| 01CV - Civils | Cxxx-NCR-000157 | NCR | Discrepancies between pile records and concrete tickets |  | Contr |  | TUX - Tunnel Drive X (West) |  | 2011-12-13 | 2012-01-06 13:25 | 24 | 2011-12-13 | Civil - Geotechnical Engineering | 500 |  | System Defect | Use As-Is |  | Complete |  | Completed |  | Following an audit of the __ piling records it was found that there were a large number (circa 30No) of the records did not have the correct delivery ticket reference.
| 01CV - Civils | Cxxx-NCR-000158 | NCR | Pile 1034 depth not installed to designed depth |  | Contr |  | TUX - Tunnel Drive X (West) |  | 2011-12-13 | 2012-05-15 12:21 | 154 | 2011-12-13 | Civil - Geotechnical Engineering | 500 |  | Design | Rework |  | Complete |  | Completed |  | The drilling of pile 1034 involved cutting through pile A133. The cutting of this pile proved very slow, therefore pile 1034 was abandoned at a depth of 5.0m.
| 01CV - Civils | Cxxx-NCR-000159 | NCR | Low strength concrete in MFC piles |  | Contr |  | TUX - Tunnel Drive X (West) |  | 2011-12-13 | 2012-05-15 12:25 | 154 | 2011-12-13 | Civil - Geotechnical Engineering | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | Following a check of the concrete cube results (Bert Mix) it was found that a number of 28 day cubes had not attained the targeted 3N/mm2.
| 01CV - Civils | Cxxx-NCR-000169 | NCR | WALL BOLTED FIXINGS |  | Contr |  | TUX - Tunnel Drive X (West) |  | 2012-10-01 | 2012-02-10 13:17 | -234 | 2012-01-10 | Structural Engineering - Bolted Connections | 500 |  |  | Repair |  | Complete |  | Completed |  | Structural fixings made in a wall that is not our property.
| 01CV - Civils | Cxxx-NCR-000170 | NCR | Low Cube and Cylinder Test Results |  | Contr |  | TUX - Tunnel Drive X (West) |  | 2012-03-30 | 2012-04-04 09:12 | 5 | 2012-03-06 | Tunnelling - Linings - Precast | 500 |  |  | Reject |  | Complete |  | Completed |  | Both compressive and tensile results to date for the cast segments are significantly below their 28 day target strengths.
| 01CV - Civils | Cxxx-NCR-000172 | NCR | Pile left open due to batching plant breakdown |  | Contr |  | TUX - Tunnel Drive X (West) |  | 2012-01-13 | 2012-02-10 10:06 | 28 | 2012-01-10 | Geotechnical Engineering - Concrete - Bored Pile | 500 |  | Equipment Breakdown | Use As-Is |  | Complete |  | Completed |  | Following the augering of raking pile G55 the piling subcontractor was informed that batching plant supplying the concrete broke down causing the pile bore to remain open overnight until 08.00 the following morning. The pile was left overnight with the augers kept in the bore to provide the required stability.
| 01CV - Civils | Cxxx-NCR-000182 | NCR | High strength concrete in MFC piles |  | Contr |  | TUX - Tunnel Drive X (West) |  | 2012-02-03 | 2012-02-10 11:43 | 7 | 2012-01-28 | Geotechnical Engineering - Concrete - Bored Pile | 500 |  | Material | Rework |  | Complete |  | Completed |  | Following a review of the concrete cube results for the 80% PFA mix it was found that a number of 56 day cubes will potentially attain strength that would exceed the targeted maximum strength of 15N/mm2 at time of tunnelling. Following an analysis of the concrete cube results the worst case scenario has been assumed, being that all piles concreted on 11/10/11, 11/10/11 and 13/10/11 were of 'high strength concrete'. A total of 10No 1200m diameter piles are to be removed and replaced.
| 01CV - Civils | Cxxx-NCR-000231 | NCR | Piles V22, V31, V32 and V34 are out of the horizontal position tolerance |  | Contr |  | TUX - Tunnel Drive X (West) |  | 2012-03-23 | 2012-07-20 08:07 | 119 | 2012-03-19 | Civil - Geotechnical Engineering | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | Following a check of the as-built position piles V22, V31, C32 and V34 are out of tolerance. Please refer to attached sketch, "As-built position of South Wall Piles"
| 01CV - Civils | Cxxx-NCR-000232 | NCR | Damaged pile reinforcing bar |  | Contr |  | TUX - Tunnel Drive X (West) |  | 2012-03-23 | 2012-05-15 12:39 | 53 | 2012-03-19 | Civil - Civil Engineering General | 500 |  | Damaged | Repair |  | Complete |  | Completed |  | Reinforcing bars damaged and sheared off due to pile breakdown operations. There were 17no damaged bars in total.
| 01CV - Civils | Cxxx-NCR-000247 | NCR | Pile V41 steel cage out of tolerance |  | Contr |  | TUX - Tunnel Drive X (West) |  | 2012-04-10 | 2012-07-20 08:10 | 101 | 2012-03-28 | Geotechnical Engineering - Concrete - Bored Pile | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | Following a check of the as-built reinforcement level, the required level for the steel is 121.540mOD. The as-built steel level was 123.740mOD
| 01CV - Civils | Cxxx-NCR-000248 | NCR | Change in concrete mix for piles in Contig Piles (750mm) - Phase 2 |  | Contr |  | TUX - Tunnel Drive X (West) |  | 2012-04-10 | 2012-07-20 08:12 | 101 | 2012-03-28 | Geotechnical Engineering - Concrete - Bored Pile | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | Due to difficulty in installing the reinforcement cages for the North and South Contig walls between ROP and LHB a change in mix design was required. To facilitate the installation of the cages the concrete was changed from C35/45 to a C32/40 following agreement with the design team
| 01CV - Civils | Cxxx-NCR-000254 | NCR | 1200mm Dia MFC Pile B56 out of position |  | Contr |  | TUX - Tunnel Drive X (West) |  | 2012-04-20 | 2012-05-15 12:55 | 25 | 2012-04-12 | Geotechnical Engineering - Concrete - Bored Pile | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | Following a check of the as-built pile location, the centre-point of Pile B56 was found to be 265mm away from the pile design position as detailed on attached sketch "As Built Position of pile B56"
| 01CV - Civils | Cxxx-NCR-000258 | NCR | Slab works in ROP |  | Contr |  | TUX - Tunnel Drive X (West) |  | 2012-05-13 | 2012-05-15 13:14 | 2 | 2012-04-13 | Civil - Concrete Pavement | 500 |  | Supervision/Management | Repair |  | Complete |  | Completed |  | ITP for Slab works wasn’t accepted before start of the work.
| 01CV - Civils | Cxxx-NCR-000266 | NCR | High Water Permeability and Chloride Ion Penetration Results |  | Contr |  | TUX - Tunnel Drive X (West) |  | 2012-05-23 | 2012-05-15 13:16 | -8 | 2012-04-23 | Tunnelling - Linings - Precast | 500 |  |  | Use As-Is |  | Complete |  | Completed |  | Both results to date for the cast segments are not meeting the specification requirements for their 28 day results.
| 01CV - Civils | Cxxx-NCR-000292 | NCR | Damage of segments during ring-build |  | Contr |  | TUX - Tunnel Drive X (West) |  | 2012-05-25 | 2012-07-20 08:15 | 56 | 2012-05-22 | Tunnelling - Linings - Precast | 500 |  | Damaged | Reject |  | Complete |  | Completed |  | During the day shift of the 20th May 2012, there was a loss of 235 mins. for replacing a segment on the segment feeder due to clash of segments on feeder which were connected with dowels. Pulling the dowels apart resulted in spalling of the segment. The damaged segment had to be replaced.
| 01CV - Civils | Cxxx-NCR-000293 | NCR | Cracking of segments |  | Contr |  | TUX - Tunnel Drive X (West) |  | 2012-06-01 | 2012-07-30 11:57 | 59 | 2012-05-22 | Tunnelling - Linings - Precast | 500 |  | Damaged | Repair |  | Complete |  | Completed |  | Cracks were noted in the following segments during ring-build: Ring 8 - crack appeared in built-in invert segment Ring 5 - crack appeared in built-in invert segment Ring 1 - crack appeared in built-in invert segment
| 01CV - Civils | Cxxx-NCR-000294 | NCR | Damage of segments at WBP segment yard |  | Contr |  | TUX - Tunnel Drive X (West) |  | 2012-05-22 | 2012-07-20 08:18 | 59 | 2012-05-22 | Tunnelling - Linings - Precast | 500 |  | Damaged | Reject |  | Complete |  | Completed |  | The edges of the following segments were damaged when being handled with the crane grabs. TRR 56 27/1/12 (cast date) & TRR 52 15/02/12 (cast date)
| 01CV - Civils | Cxxx-NCR-000299 | NCR | Reinforcement segments |  | Contr |  | TUX - Tunnel Drive X (West) |  | 2012-06-10 | 2012-07-20 08:38 | 40 | 2012-05-28 | Tunnelling - Linings - Precast | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | Some of the reinforcement segments 7 day strenght test results used in the tunnel are belove required 28 day 60N.
| 01CV - Civils | Cxxx-NCR-000312 | NCR | Reduced instrumentation in Eastbourne Terrace. |  | Contr |  | TUX - Tunnel Drive X (West) |  | 2012-06-18 | 2012-08-10 17:02 | 53 | 2012-06-11 | Geotechnical Engineering - Geotechnical Monitoring | 500 |  | Design | Use As-Is |  | Complete |  | Completed |  | Following the excavation of 5No trial pits within the area of 2No Shallow Datums a large number of obstructions were found. These 2No instruments could not be installed and were therefore deleted from the scope. Also, due to obstructions found at the proposed position of a number of inclinometers and extensometers the location of these instruments was changed.
| 01CV - Civils | Cxxx-NCR-000325 | NCR | KTT grout shaft prop strain monitoring |  | Contr |  | TUX - Tunnel Drive X (West) |  | 2012-06-15 | 2012-07-30 12:29 | 45 | 2012-06-15 | Surveying - Instrumentation and Monitoring | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | The data has not been uploaded as per ITP Cxxx--C-ITP-CRT00_ST005-50078, it can therefore not be discussed in an SRG meeting with the site team. The site teamcannot assess the stability of the temporary works.
| 01CV - Civils | Cxxx-NCR-000326 | NCR | Method Statment requires submission to CRL through eB |  | Contr |  | TUX - Tunnel Drive X (West) |  | 2012-07-02 | 2012-11-19 08:24 | 140 | 2012-06-18 | Construction Health & Safety - Construction Health & Safety General | 500 |  | Planning | Repair |  | Complete |  | Completed |  | Method Statement is not submitted to CRL through eB.
| 01CV - Civils | Cxxx-NCR-000327 | NCR | Incorrect information on inspection/delivery records |  | Contr |  | TUX - Tunnel Drive X (West) |  | 2012-07-02 | 2012-09-12 13:45 | 72 | 2012-06-18 | Tunnelling - Tunnelling General | 500 |  | Supervision/Management | Repair |  | Complete |  | Completed |  | Ring 27 inspection/delivery record doesn't relate to actual segment ID (should be ring 25).
| 01CV - Civils | Cxxx-NCR-000328 | NCR | Ring build and damage records not available |  | Contr |  | TUX - Tunnel Drive X (West) |  | 2012-07-02 | 2012-07-30 12:43 | 28 | 2012-06-18 | Tunnelling - Tunnelling General | 500 |  | Supervision/Management | Repair |  | Complete |  | Completed |  | Ring build and damage records not available at the time of inspection.
| 01CV - Civils | Cxxx-NCR-000330 | NCR | Ring segment Damage |  | Contr |  | TUX - Tunnel Drive X (West) |  | 2012-07-31 | 2012-11-15 11:37 | 107 | 2012-06-20 | Tunnelling - Linings - Precast | 500 |  | Damaged | Repair |  | Complete |  | Completed |  | (14th June 2012) Two reinforced segments were found in the yard which despite having passed through the contractor’s quality check and positioned in the ‘green’ zone to be delivered, were found to be damaged. This damage was sufficient for the segment to be rejected and not used in the tunnel. The ID’s of the segments are; 1) TRR 59 / 11-05-12 – damaged on both leading and trailing side at extrados 2) BR19 / 11-05-12 – damaged around the trailing edge of gasket
| 01CV - Civils | Cxxx-NCR-000335 | NCR | Tunnel Grout Early Strength |  | Contr |  | TUX - Tunnel Drive X (West) |  | 2012-08-31 | 2012-11-15 11:46 | 76 | 2012-06-29 | Tunnelling - Grouting | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | No records to date. Frequent promises to test the samples but currently two test, the first Failed, the second no results seen
| 01CV - Civils | Cxxx-NCR-000336 | NCR | Damage to Permanent Lining |  | Contr |  | TUX - Tunnel Drive X (West) |  | 2012-10-07 | 2012-11-05 08:50 | 29 | 2012-06-29 | Tunnelling - Linings - Precast | 500 |  | Damaged | Repair |  | Complete |  | Completed |  | On 28th May 2012 between 1500 Hrs – 1600 Hrs, conducted a grout test on a newly installed permanent ring number 43 (reinforced) approximately close to the invert. Since it was a reinforced ring there is a strong likelihood of damage caused to the segment reinforcement which requires repair as per the acceptable method. The drilling was through a permanent ring and will need to be reinstated
| 01CV - Civils | Cxxx-NCR-000339 | NCR | Grout Strength Tests |  | Contr |  | TUX - Tunnel Drive X (West) |  | 2012-09-30 | 2012-10-19 12:56 | 19 | 2012-07-02 | Tunnelling - Linings - Precast | 500 |  | Damaged | Repair |  | Complete |  | Completed |  | On monday the 18th of June, took core samples of the grout behind the permanent lining of the following rings 1,3,5,7,8,9,11,13,15. The 150 dia. cores centred on the grout socket of the segment closest to the invert in line with RFI Cxxx 00318.
| 01CV - Civils | Cxxx-NCR-000365 | NCR | Release of PC Segments from Casting Facility |  | Contr |  | TUX - Tunnel Drive X (West) |  | 2012-12-24 | 2012-12-20 15:15 | -4 | 2012-07-31 | Tunnelling - Linings - Precast | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | The status of serveral batches of concrete and thier related segment production is currently unclear due to non-compliant beam test results. Some of the segments concerned have already been released from OOC and are in the WBP suface handling facility and installed within the westbound tunnel.
| 01CV - Civils | Cxxx-NCR-000376 | NCR | Cruciform Joint - Rings 302 to 303 Westbound Tunnel |  | Contr |  | TUX - Tunnel Drive X (West) |  | 2012-09-16 | 2012-09-20 14:03 | 4 | 2012-07-31 | Tunnelling - Linings - Precast | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | A cruciform joint is apparent along the radial joint in the 4 o'clock position
| 01CV - Civils | Cxxx-NCR-000405 | NCR | SGI Segment manufacturing without accepted ITP |  | Contr |  | TUX - Tunnel Drive X (West) |  | 2012-09-30 | 2012-09-13 08:50 | -17 | 2012-08-14 | Tunnelling - Linings - SGI Rings | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | Manufacturing started without accepted ITP.
| 01CV - Civils | Cxxx-NCR-000418 | NCR | ITP not accepted by the Supervisor |  | Contr |  | TUX - Tunnel Drive X (West) |  | 2012-09-06 | 2012-10-03 10:26 | 27 | 2012-08-23 | Tunnelling - Linings - SGI Rings | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | There is no Supervisor accepted ITP for SGI manufacture
| 01CV - Civils | Cxxx-NCR-000419 | NCR | Verification of purchased product |  | Contr |  | TUX - Tunnel Drive X (West) |  | 2012-09-06 | 2012-09-12 14:03 | 6 | 2012-08-23 | Tunnelling - Linings - SGI Rings | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | Compliance with ISO 9001 could not be demonstrated with respect to verification of purchased product - SGI
| 01CV - Civils | Cxxx-NCR-000420 | NCR | Verification record |  | Contr |  | TUX - Tunnel Drive X (West) |  | 2012-11-30 | 2012-11-23 13:39 | -7 | 2012-08-23 | Tunnelling - Linings - SGI Rings | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | Contractor failed to demonstrate compliance with the Technical Requirement during surveillance QS300/410 -03 with respect to the hydrophilic strip installation.
| 01CV - Civils | Cxxx-NCR-000421 | NCR | Task-specific method statements |  | Contr |  | TUX - Tunnel Drive X (West) |  | 2012-09-06 | 2012-10-03 11:13 | 27 | 2012-08-23 | Tunnelling - Tunnelling General | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | The Contractor confirmed that the hydrophilic strip was protected from wet weather by the placement of covers, The Method Statement for Installation of SGI segments Cxxx--C-GMS-CRT00_ST005-50339 rev 2.0 does not include this work item.
| 01CV - Civils | Cxxx-NCR-000432 | NCR | Using quarantined segments in tunnel |  | Contr |  | TUX - Tunnel Drive X (West) |  | 2012-09-07 | 2012-10-03 11:43 | 26 | 2012-08-24 | Tunnelling - Linings - Precast | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | 30/07/12 delivery number 460 arraived containing TLR64 (02/04/12). This delivery was checked at OOC by S.Nandra and at WBP by M.Valle. 16 hours later delivery 460 was sent to the tunnel and istalled as ring 360.
| 01CV - Civils | Cxxx-NCR-000435 | NCR | Casting date on segments has been corrected |  | Contr |  | TUX - Tunnel Drive X (West) |  | 2012-09-09 | 2012-09-17 08:28 | 8 | 2012-08-28 | Tunnelling - Linings - Precast | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | The date of casting has been stamped on segment 04 03 12. And changed later by hand to 04 04 12.
| 01CV - Civils | Cxxx-NCR-000444 | NCR | Quality control tests have not been undertaken |  | Contr |  | TUX - Tunnel Drive X (West) |  | 2012-09-17 | 2012-09-20 15:20 | 3 | 2012-09-03 | Shafts - Grouting | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | does not have documentation to prove that quality control tests have been carried out.
| 01CV - Civils | Cxxx-NCR-000462 | NCR | Spalling of the segment TRR in Ring 38 |  | Contr |  | TUX - Tunnel Drive X (West) |  | 2012-09-27 | 2012-11-15 11:51 | 49 | 2012-09-13 | Tunnelling - Tunnelling General | 500 |  | Damaged | Repair |  | Complete |  | Completed |  | Ring 39 was initially erected beginning with Plate A in the wrong position. The action of removing the installed plate caused spalling to the edge of the adjacent plate (TRR) in Ring 38. Repair work was done without accepted Method Statment and Materials.
| 01CV - Civils | Cxxx-NCR-000467 | NCR | Unavailability of Some PLP Transects in Royal Oak Portal Area |  | Contr |  | TUX - Tunnel Drive X (West) |  | 2012-09-26 | 2012-11-05 07:47 | 40 | 2012-09-19 | Surveying - Instrumentation and Monitoring | 500 |  | Damaged | Reject |  | Complete |  | Completed |  | Four No PLP Transects in the Royal Oak Portal Area have been damaged beyond use due to the stockpiling of spoil over them. These transects would have been used to calculate volume loss and are not assigned to a specific assets. Locations for these PLP transects are described below (based on Cxxx I&M drawing) and are highlighted on the attached sketch: 1) at CH 69900 2) immediatley west of Ranelagh Bridge (not referring to the transect installed over the sewer) 3) at CH 70010 4) over Thames-Lea Tunnel (these PLP's do not form requirement of monitoring on this asset) As the spoil heap will be present for some time, any potential reperation of the PLP's would be too late to obtain useful data to use for volume loss calculations. There is no possibilty of moving the spoil from on top of the PLP's either.
| 01CV - Civils | Cxxx-NCR-000468 | NCR | TAMs installed out of tolerance in FIS GS1 |  | Contr |  | TUX - Tunnel Drive X (West) |  | 2012-10-03 | 2012-11-05 11:51 | 33 | 2012-09-19 | Geotechnical Engineering - Compensation Grouting | 500 |  | Design | Repair |  | Complete |  | Completed |  | The following TaMs have been drilled out of design tolerance and have been corrected : F23: 675mm out of tolerance F60: 373mm out of tolerance
| 01CV - Civils | Cxxx-NCR-000483 | NCR | Damaged Instruments Royal Oak Portal |  | Contr |  | TUX - Tunnel Drive X (West) |  | 2012-10-19 | 2012-11-05 08:01 | 17 | 2012-10-01 | Surveying - Instrumentation and Monitoring | 500 |  | Damaged | Repair |  | Complete |  | Completed |  | Rod Extensometer, Cxxx RX200003, and Piezometer, Cxxx VP20003, ahve been damaged by ground works being undertaken at Royal Oak Portal.
| 01CV - Civils | Cxxx-NCR-000488 | NCR | Pile M22 - Steel cage level out of tolerance |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2013-07-26 | 2013-07-17 11:55 | -9 | 2012-10-02 | Geotechnical Engineering - Concrete - Bored Pile | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The top level of the steel cage is 125.30, 760mm over the theoretical level. Due to the reduced clearance between the reinforcement cage spacers and the steel casing, when the piling subcontractor was extracting the casing the steel cage came up 760mm. It was not possible to push it back down. This issue will be mitigated removing a 2 m section of casing prior the installation of the steel reinforcement. This will not comprise the stability of the open bore as a self-supported dry clay strata is present at that level. Then the concrete on that section will anchor the steel cage avoiding any further movements.
| 01CV - Civils | Cxxx-NCR-000492 | NCR | TBM Muck Stockpiles Not in Accordance with TW Design |  | Contr |  | TUX - Tunnel Drive X (West) |  | 2012-10-31 | 2012-11-23 13:20 | 23 | 2012-10-04 | Tunnelling - Excavation - TBM | 500 |  |  | Rework |  | Complete |  | Completed |  | The stockpiles at ROP are currently not in accordance with the above drawings
| 01CV - Civils | Cxxx-NCR-000496 | NCR | Strain Gauges on Gas Main at Hydepark - Poor Readings |  | Contr |  | TUX - Tunnel Drive X (West) |  | 2012-11-15 | 2012-11-21 07:56 | 6 | 2012-10-09 | Surveying - Instrumentation and Monitoring | 500 |  | Damaged | Repair |  | Complete |  | Completed |  | Discrepancy in the readings that the Strain Gauges are providing has been detected by analysing the recently obtained readings via the data logger installed. This points out a possibility of the strain gauges having detached from the gas main’s surface.
| 01CV - Civils | Cxxx-NCR-000500 | NCR | Concrete plugs in segment sockets |  | Contr |  | TUX - Tunnel Drive X (West) |  | 2012-10-26 | 2012-11-26 14:08 | 31 | 2012-10-10 | Tunnelling - Linings - Precast | 500 |  | Supervision/Management | Rework |  | Complete |  | Completed |  | On 02/10/12 a segment with a socket containing a plug was found on the TBM. The segment had been unloaded from the train and was ready to go onto the feeder. To reach that point the segment had passed through multiple checks at Old Oak Common and Westbourne Park, none of which had done anything about the socket with the plug or the socket containg the uncleaned out debris of a broken plug.
| 01CV - Civils | Cxxx-NCR-000501 | NCR | Conveyor Structure Bolting Assemblies |  | Contr |  | TUX - Tunnel Drive X (West) |  | 2012-10-19 | 2012-11-06 11:44 | 18 | 2012-10-10 | Structural Engineering - Bolted Connections | 500 |  | Material | Repair |  | Complete |  | Completed |  | The nuts and bolts recovered from the collapse conveyor structure did not conform to the requirements of the standard. The recovered bolts were property class 10.9 which had been assembled with property class 10 nuts.
| 01CV - Civils | Cxxx-NCR-000510 | NCR | Monitoring instrumentation within the secant piles installed not following DRX-RFI-CRL-Cxxx-00433 |  | Contr |  | TUX - Tunnel Drive X (West) |  | 2012-10-31 | 2012-11-13 16:24 | 13 | 2012-10-17 | Geotechnical Engineering - Geotechnical Monitoring | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | Due to logistic matters has installed a void former for an electronic inclinomiter as per Cxxx original lay out instead of as per the RFI
| 01CV - Civils | Cxxx-NCR-000521 | NCR | HV Cable Support in Tunnel |  | Contr |  | TUX - Tunnel Drive X (West) |  | 2012-11-09 | 2012-11-15 13:07 | 6 | 2012-10-22 | Electrical - Cable Management | 500 |  | System Defect | Rework |  | Complete |  | Completed |  | The HV supply cable is supported on the tunnel wall above the walkway by steel cantilever arm brackets. The design of these backets is unsuitable for use as a cable support as it has sharp and serrated edges that can damage the cable outer sheath, which could result in cable failure. Also the HV cable is just laid onto the brackets, with no securing cleats or fixings (except for a few cable ties). In the event of a cable fault, see above, the HV cable will thrash about the tunnel, possibly causing injury to operatives and / or damage to equipment. The issue was observed in the westbound tunnel during a HV inspection on the 29th September and reported to the contractor. Since when not only has it not been rectified but the same support system is being adopted for the eastbound tunnel.
| 01CV - Civils | Cxxx-NCR-000529 | NCR | Quarantined segments |  | Contr |  | TUX - Tunnel Drive X (West) |  | 2012-11-12 | 2012-11-15 11:57 | 3 | 2012-10-29 | Tunnelling - Linings - Precast | 500 |  | Design | Use As-Is |  | Complete |  | Completed |  | Lower characteristic tensile strength, LOP and FR1 results than specified in KH11.
| 01CV - Civils | Cxxx-NCR-000530 | NCR | Nortfleet Coveyor |  | Contr |  | TUX - Tunnel Drive X (West) |  | 2012-11-18 | 2012-11-21 07:53 | 3 | 2012-10-29 | Structural Engineering - Structural Engineering - General | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | There isn’t CRL accepted ITP in place for Conveyor installation.
| 01CV - Civils | Cxxx-NCR-000531 | NCR | PLPs Above Ranelagh Sewer (ROP) |  | Contr |  | TUX - Tunnel Drive X (West) |  | 2012-11-02 | 2012-11-23 13:10 | 21 | 2012-10-30 | Surveying - Instrumentation and Monitoring | 500 |  | Damaged | Repair |  | Complete |  | Completed |  | Damaged or/and not reading leading to a lack of sufficient baseline data prior to TBM2 reaching the Zone of Influence of the sewer.
| 01CV - Civils | Cxxx-NCR-000532 | NCR | Concrete cube curing at Fisher St. |  | Contr |  | TUX - Tunnel Drive X (West) |  | 2012-11-06 | 2012-11-06 10:59 | 0 | 2012-10-31 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | During surveillance of 30/10/12 curing of cubes was found nonconforming. The cubes were dry and stored at a temperature below 15 ºC ( __C published temperature for the above date was 9 to 11ºC) no monitoring thermometer available in the cube making/storage area.
| 01CV - Civils | Cxxx-NCR-000536 | NCR | Damaged Extensometer Royal Oak Portal |  | Contr |  | TUX - Tunnel Drive X (West) |  | 2012-11-06 | 2012-11-23 13:32 | 17 | 2012-11-01 | Surveying - Instrumentation and Monitoring | 500 |  | Damaged | Rework |  | Complete |  | Completed |  | Extensometer damaged and unable to be read.
| 01CV - Civils | Cxxx-NCR-000541 | NCR | Imported material chemical properties |  | Contr |  | TUX - Tunnel Drive X (West) |  | 2013-01-02 | 2013-01-11 15:54 | 9 | 2012-11-07 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | Records were not made available for surveillance QS300-03 to demonstrate implementation of __ 340 clause 3.3 with respect to imported material being free of contamination.
| 01CV - Civils | Cxxx-NCR-000566 | NCR | M32 and M15 - steel cages out of tolerance |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2013-07-26 | 2013-07-25 08:09 | -1 | 2012-11-28 | Geotechnical Engineering - Concrete - Bored Pile | 500 |  |  | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The steel reinforcement level of the piles M32 and M15 are out of tolerance. In the case of pile M32, the steel cage is 114mm below the target level. In the case of pile M15, the steel cage is 263mm above the target level.
| 01CV - Civils | Cxxx-NCR-000585 | NCR | Repair to Ring 38 (eastbound tunnel) |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2014-10-14 | 2014-11-24 13:50 | 41 | 2012-12-05 | Tunnelling - Linings - Precast | 2000 |  | Supervision/Management | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Ring 39 was initially erected with plate A in the wrong position. The action of removing the installed plate caused spalling to the edge of the adjacent plate (TRR) in ring 38. First repairs were done according to Method Statement Cxxx--C4-GMS-CRT00_ST005-50055. On the 13th Sept 2012, OOC Lab received 3 No 100mm Cubes made by site/tunnel staff. asked __ to test cubes at 3, 6 and 12 Hours. 1 No - After 3 Hours Cube Stripped, cube placed in to testing Machine, No result from cube 2 No - After 6 Hours Cube Stripped, cube placed in to testing Machine, No result from cube 3 No - After 6 Hours Cube Stripped place in curing tank, During the time the cube was in the tank approx 6 Hours, the cube just fall apart in the curing tank
| 01CV - Civils | Cxxx-NCR-000600 | NCR | Quarantined segments installed in permanent works |  | Contr |  | TUX - Tunnel Drive X (West) |  | 2013-01-17 | 2013-01-14 12:16 | -3 | 2012-12-20 | Tunnelling - Linings - Precast | 500 |  | Planning | Reject |  | Complete |  | Completed |  | Following quarantined segments installed in permanent works: Ring WB-25 segment AL 87(09/03/12) - first notice to quarantine this date was on 07/09/12, 4months and 16days after segment was installed on the 23/05/12. Ring WB-694 segment CL104 (08/08/12) - notice to quarantine this date was on 10/09/12, segment arrived on site on 27/09/12 and was installed on 24/10/12. Human error for loading it in OOC and sending it to the tunnel. Ring WB-760 segment KR71 (01/08/12) - notice to quarantine this date was on 24/09/12, segment arrived on site on 30/10/12 and was installed on 30/10/12. Human error for loading it in OOC and sending it to the tunnel. Ring EB-50 segment DR33 (09/03/12) - notice to quarantine this date was on 07/09/12, segment arrived on site on 13/09/12 and was installed on 14/09/12. This ring was in the middle of Paddington ring delivery and sent from OOC for Paddington. Ring WB-11, 14 and 17 segments CL 106 (02/04/12), TRR 55 (02/04/12) and CL107 (02/04/12) - first notice to quarantine this date was on after segments were installed. Ring WB-784 segment KL 157 (20/03/12) - notice to quarantine this date was on 07/09/12, segment arrived on site on 01/08/12 and was installed on 03/11/12. Human error for loading it in OOC and sending it to the tunnel.
| 01CV - Civils | Cxxx-NCR-000623 | NCR | Installation of California Crossing without accepted ITP |  | Contr |  | TUX - Tunnel Drive X (West) |  | 2013-02-08 | 2013-02-08 13:36 | 0 | 2013-01-21 | Tunnelling - Tunnelling General | 500 |  | Supervision/Management | Repair |  | Complete |  | Completed |  | California Crossing was installed without accepted ITP.
| 01CV - Civils | Cxxx-NCR-000630 | NCR | Rejected Segments |  | Contr |  | TUX - Tunnel Drive X (West) |  | 2013-02-08 | 2013-02-12 08:07 | 4 | 2013-01-25 | Tunnelling - Linings - Precast | 500 |  | Damaged | Reject |  | Complete |  | Completed |  | Segments damaged during production
| 01CV - Civils | Cxxx-NCR-000631 | NCR | Rejected Segments (51-100) |  | Contr |  | TUX - Tunnel Drive X (West) |  | 2013-01-31 | 2013-02-12 07:48 | 12 | 2013-01-25 | Tunnelling - Linings - Precast | 500 |  | Damaged | Reject |  | Complete |  | Completed |  | Segment Damaged/Rejected
| 01CV - Civils | Cxxx-NCR-000637 | NCR | Northfleet Conveyor Capacity |  | Contr |  | TUX - Tunnel Drive X (West) |  | 2013-05-01 | 2013-05-14 08:00 | 13 | 2013-01-31 | Civil - Civil Engineering General | 500 |  | Design | Rework |  | Complete |  | Completed |  | Recent loading of ships at Northfleet have identified that the conveyor cannot currently meet the performance specification required.
| 01CV - Civils | Cxxx-NCR-000638 | NCR | Precast Segment Defects |  | Contr |  | TUX - Tunnel Drive X (West) |  | 2013-03-01 | 2013-03-05 13:13 | 4 | 2013-01-31 | Tunnelling - Linings - Precast | 500 |  | Damaged | Repair |  | Complete |  | Completed |  | Segments with honeycombing in the gasket grove are stored in the yard, marked with a green spot indicating they have passed checking and are fit for use. There is also no approved procedure for repair of damaged segments prior to them being installed in the tunnel.
| 01CV - Civils | Cxxx-NCR-000640 | NCR | Missing Segment Inspection Reports |  | Contr |  | TUX - Tunnel Drive X (West) |  | 2013-03-04 | 2013-03-07 13:03 | 3 | 2013-02-04 | Tunnelling - Linings - Precast | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | Inspection records were found to be missing for rings 20, 22 and 23 Westbound tunnel.
| 01CV - Civils | Cxxx-NCR-000657 | NCR | Missing Grout injection records |  | Contr |  | TUX - Tunnel Drive X (West) |  | 2013-03-12 | 2013-03-28 08:26 | 16 | 2013-02-12 | Tunnelling - Grouting | 500 |  | System Defect | Use As-Is |  | Complete |  | Completed |  | The grout injection records were found missing for WB rings 1, 3,4, 7 and 8 (TBM1)
| 01CV - Civils | Cxxx-NCR-000672 | NCR | North Audley Street - Reinstatement |  | Contr |  | TUX - Tunnel Drive X (West) |  | 2013-03-21 | 2013-04-03 11:46 | 13 | 2013-02-21 | Civil - Streets & Highways | 500 |  | Workmanship | Rework |  | Complete |  | Completed |  | Chippings adjacent to kerb line to be removed in line with original surfacing. Seamless joint between patching and original surface.
| 01CV - Civils | Cxxx-NCR-000678 | NCR | Non-Compliant Segments at WBP |  | Contr |  | TUX - Tunnel Drive X (West) |  | 2013-04-12 | 2013-04-23 13:49 | 11 | 2013-03-08 | Tunnelling - Linings - Precast | 500 |  | Supervision/Management | Reject |  | Complete |  | Completed |  | Segments which appear to be non-compliant with the defects/damage requirements of the above documents have been noted in the in the storage yard at WBP
| 01CV - Civils | Cxxx-NCR-000683 | NCR | Segments released from the casting yard before compliance confirmed |  | Contr |  | TUX - Tunnel Drive X (West) |  | 2013-04-30 | 2013-04-26 09:08 | -4 | 2013-03-12 | Tunnelling - Linings - Precast | 500 |  | Planning | Reject |  | Complete |  | Completed |  | On the 7th March 13 PC segments were noted to be at the WBP storage area with a cast date of 8th Feb 13.
| 01CV - Civils | Cxxx-NCR-000700 | NCR | FIS KTT Grout Shaft - TaM Drilling out of tolerance |  | Contr |  | TUX - Tunnel Drive X (West) |  | 2013-04-08 | 2013-04-17 18:12 | 9 | 2013-03-25 | Geotechnical Engineering - Compensation Grouting | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | The following TaMs are out of horizontal drilling tolerance: 1,3-6,8-10,16,17,19,20,22,23,24,25,29,30,36,40,50,57,59,60. The following TaM spacing are greater than 4m: 1 to 2, 20 to 21, 30 to 31. The following TaMs are outside vertical tolerance: 2,3,5,7,8,12,15-17,19,22,23A,24,26,27,2931,33-36,42,46-50,57,60A,61-63. The following TaMs are outside the design band: 3 and 57. See attached drill deviation assessment for full detail.
| 01CV - Civils | Cxxx-NCR-000702 | NCR | Competence records |  | Contr |  | TUX - Tunnel Drive X (West) |  | 2013-04-10 | 2013-04-19 17:50 | 9 | 2013-03-27 | Tunnelling - Linings - Precast | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | Records for Westbourne Park Provided during surveillance QS300/4100-04 were not complete, the record consisted of one Method Statement briefing record with no reference as to what was the briefing subject was and OOC provided no competency records.
| 01CV - Civils | Cxxx-NCR-000703 | NCR | Suppliers organisation charts |  | Contr |  | TUX - Tunnel Drive X (West) |  | 2013-04-10 | 2013-04-17 15:04 | 7 | 2013-03-27 | Tunnelling - Linings - Precast | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | Review of the Contractors most current organisation charts (Cxxx--N1-HRR-CRT00-ST005-50005,50004 and Cxxx -A-HRR-CRG03-Z-50001)failed to identify the inspection personnel
| 01CV - Civils | Cxxx-NCR-000704 | NCR | Measuring equipment for precast inspectors |  | Contr |  | TUX - Tunnel Drive X (West) |  | 2013-04-10 | 2013-04-26 08:49 | 16 | 2013-03-27 | Tunnelling - Linings - Precast | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | No schedule or evidence was made available to demonstrate that the inspectors at the OOC or WB had been issued with suitable measurement equipment.
| 01CV - Civils | Cxxx-NCR-000707 | NCR | Damaged segment placed in the tunnel |  | Contr |  | TUX - Tunnel Drive X (West) |  | 2013-04-25 | 2013-04-19 17:42 | -6 | 2013-03-28 | Tunnelling - Linings - Precast | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | Segment BR14 (20/02/13) was spotted in WBP segment yard with crack in the corner (as attached picture). The segment was placed in to the eastboundtunnel (ring nr 1514) on 21/03/13.
| 01CV - Civils | Cxxx-NCR-000708 | NCR | Segment with not acceptable blowholes built in tunnel |  | Contr |  | TUX - Tunnel Drive X (West) |  | 2013-04-25 | 2013-04-19 17:34 | -6 | 2013-03-28 | Tunnelling - Linings - Precast | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | Segment with blowholes bigger than accepted (as seen on attached picture) sent in to the tunnel and built in eastbound tunnel on 21/03/13 into ring number 1511.
| 01CV - Civils | Cxxx-NCR-000712 | NCR | Pre-Condition Survey - Prisms & __s |  | Contr |  | TUX - Tunnel Drive X (West) |  | 2013-05-28 | 2013-05-13 16:38 | -15 | 2013-04-03 | Surveying - Defects and Condition | 500 |  | Planning | Use As-Is |  | Complete |  | Completed |  | Pre-installation condition surveys for the installation of prisms and __ Studs have not been undertaken in accordance with the specification.
| 01CV - Civils | Cxxx-NCR-000714 | NCR | FIS KTT Grout Shaft - Sleeve Grout Records |  | Contr |  | TUX - Tunnel Drive X (West) |  | 2013-04-18 | 2013-04-26 09:24 | 8 | 2013-04-04 | Geotechnical Engineering - Compensation Grouting | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | There are only 4 on-site grout test forms available that recorded the batching and testing of the sleeve grout during the drilling operations at FIS grout shaft. This is an insufficient number as one should be produced per shift when grouting occurs. Additionally the temperature is not recorded on any sheet. There are also an insufficient number of cube results available.
| 01CV - Civils | Cxxx-NCR-000724 | NCR | Damaged Extensometer Head |  | Contr |  | TUX - Tunnel Drive X (West) |  | 2013-04-26 | 2013-04-23 12:08 | -3 | 2013-04-12 | Surveying - Instrumentation and Monitoring | 500 |  | Equipment Breakdown | Reject |  | Complete |  | Completed |  | Instrument Cxxx-XR600001 located on North Audley St is in a state where readings on 4 of the 6 GRP rods cannot be taken and on the remaining 2 the required accuracy cannot be matched. This instrument cannot be repaired due to the nature of a subsurface installation.
| 01CV - Civils | Cxxx-NCR-000737 | NCR | SGI installation of CP1 Westbound |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2014-03-14 | 2014-03-06 16:08 | -8 | 2013-04-22 | Tunnelling - Linings - SGI Rings | 2000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | SGI opening set for CP1 Westbound - Ring buid report shows that a few non-conformities are present and included: a missing bolt on the circumferential joint, some missing washers, etc....refer to attached inspection report.
| 01CV - Civils | Cxxx-NCR-000741 | NCR | Incorrect Geo-referencing of __ co-ordinates Observed in GTC |  | Contr |  | TUX - Tunnel Drive X (West) |  | 2013-05-13 | 2013-05-02 15:55 | -11 | 2013-04-23 | Surveying - Instrumentation and Monitoring | 500 |  |  | Rework |  | Complete |  | Completed |  | Incorrect __ and PLP co-ordinates in GTC have led to gradient calculations showing false trigger breaches in the BOS area. These are automatically calculated and presented in GroutControl by calculating the distance between the geo-referencing coordinates of the __s
| 01CV - Civils | Cxxx-NCR-000742 | NCR | Lack of Prism Readings in Osborne Tunnel Plant Room |  | Contr |  | TUX - Tunnel Drive X (West) |  | 2013-05-09 | 2013-05-16 12:35 | 7 | 2013-04-25 | Surveying - Instrumentation and Monitoring | 500 |  | Planning | Reject |  | Complete |  | Completed |  | have carried out only four sets of survey of the prisms in Osborne Tunnel Plant Room and none of these were carried out during TBM passage. Therefore were unable to monitor against horizontal triggers during TBM passage. However we were able to confirm that no triggers had been breached when the post-TBM readings were obtained.
| 01CV - Civils | Cxxx-NCR-000753 | NCR | Wrong Type of Ring Installed in Westbound tunnel |  | Contr |  | TUX - Tunnel Drive X (West) |  | 2013-07-01 | 2013-06-28 08:28 | -3 | 2013-05-13 | Tunnelling - Linings - Precast | 500 |  | Material | Reject |  | Complete |  | Completed |  | A standard right hand ring has been erected in the westbound tunnel instead of the designed FTS (floating track slab) ring. The ring was erected on the 13/05/13 during the am hours of the previous nights shift. The ring in question is ring number 2539.
| 01CV - Civils | Cxxx-NCR-000758 | NCR | Annulus grout acceptance record |  | Crossrail | PDP | TUX - Tunnel Drive X (West) |  | 2013-08-31 | 2013-07-24 15:14 | -38 | 2013-05-22 | Tunnelling - Linings - Precast | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Verification Problems - Other | Completed |  | Annulus grout compliance record(Cxxx--C-LRC-CRT00_ST005-50112 rev 1 )was not accepted on 14/06/2012 ( DECAL code2) and the record was not revised and resubmitted it is therefore not contemporaneous
| 01CV - Civils | Cxxx-NCR-000759 | NCR | Proof drilling |  | Contr |  | TUX - Tunnel Drive X (West) |  | 2013-07-19 | 2013-06-26 09:48 | -23 | 2013-05-22 | Tunnelling - Linings - Precast | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | Not included in a method statement, the Contractor confirmed that proof drilling not done ,any secondary grouting that may have been required as a result of the proof drilling findings also not done
| 01CV - Civils | Cxxx-NCR-000760 | NCR | Calibration records -Site laboratory |  | Contr |  | TUX - Tunnel Drive X (West) |  | 2013-06-21 | 2013-06-26 10:05 | 5 | 2013-05-22 | Tunnelling - Linings - Precast | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | No calibration records were available for the Marsh cone, 1000ml cylinder and 1000ml measuring cup.
| 01CV - Civils | Cxxx-NCR-000761 | NCR | TBM Design Parameters |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2014-07-01 | 2014-07-03 08:45 | 2 | 2013-05-22 | Tunnelling - Excavation - TBM | 0 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | The TBM does not meet the design parameters as outlined in section 3.8 of the Earth Pressure Balance TBM minimum requirements – CRL1-PDP-C4-RSP-CRG01-00001 issued in the contract documents volume 2C or subsequent document, Specification for procurement of tunnel boring machines (TBM) – Cxxx--C4-RSP-CRG01-50001 as issued to CRL by .
| 01CV - Civils | Cxxx-NCR-000763 | NCR | Position of CP4 Opening Set in East Bound Tunnel |  | Contr |  | TUX - Tunnel Drive X (West) |  | 2013-07-29 | 2013-06-07 08:22 | -52 | 2013-05-24 | Tunnelling - Linings - SGI Rings | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | The as-built chainage of of the EB CP4 opening set is 3045.67m Drawing Cxxx-OVE-C4-DDD-CR001_Z-23096 rev C04 states a chainage of 3047.199m which equates to a displacement of 1.529m. This has arisen due to the position being calculated from the previous revision C03 with Ch 3046.199m Rev C04 was issued 2nd April 13 (6 days prior to installation)
| 01CV - Civils | Cxxx-NCR-000796 | NCR | Trial Ring Build at 50% of Production |  | Contr |  | TUX - Tunnel Drive X (West) |  | 2013-07-19 | 2013-06-26 10:07 | -23 | 2013-06-06 | Tunnelling - Linings - Precast | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | Production has now passed the 50% and a trial ring bulid has not been carried out in accordance with KH11.3108 b.
| 01CV - Civils | Cxxx-NCR-000798 | NCR | Fault Inclonometer |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2013-07-26 | 2013-07-25 08:12 | -1 | 2013-06-07 | Shafts - Shafts General | 500 |  | Equipment Breakdown | Repair | 4 (0.5-3k) | Complete |  | Completed |  | Inclonometer IM900011 is displaying fluctuating readings 0-1m and 6-9m this dosnt relate to site opperations. The results are not through to be a reflection of the site excation.
| 01CV - Civils | Cxxx-NCR-000799 | NCR | Mix design BFK18 |  | Contr |  | TUX - Tunnel Drive X (West) |  | 2013-06-11 | 2013-06-13 17:31 | 2 | 2013-06-07 | Shafts -Sprayed Concrete | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | submitted 18 SCL mix design on the 22nd May to be used as the regulating smoothing layer. started using 18 mix onsite on the 4th, the mix design is still to be approved by crossrail.
| 01CV - Civils | Cxxx-NCR-000800 | NCR | pile void |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2013-10-31 | 2013-10-30 13:50 | -1 | 2013-06-07 | Shafts - Grouting | 2500 |  | System Defect | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Durring excation at 119.6mAOD __ came across a void and water ingress at 0.125 l/s coming into the shaft at the connection within the female and male pile 49. The extent of the void behind the piles is unknown. It is now thought that there leak is caused by Thames water as the level of the leak matches the ingress of water in the Southampton row basement and Kingsway tram tunnel. The water clarity matches piped and not ground water.
| 01CV - Civils | Cxxx-NCR-000805 | NCR | Futher to NCR 798 |  | Contr |  | TUX - Tunnel Drive X (West) |  | 2013-07-14 | 2013-07-03 15:18 | -11 | 2013-06-14 | Surveying - Instrumentation and Monitoring | 500 |  | Equipment Breakdown | Rework |  | Complete |  | Completed |  | IPI 11 and 12 recorded some interferences in the readings, this is showed in the two timeplots. After the intervention on the datalogger to check the cabling, the interferences stopped. Unfortunately two sensors in IPI 11 are now giving shifted readings (shown in a step on the timeplots and in the spikes in the profile).
| 01CV - Civils | Cxxx-NCR-000817 | NCR | Water Concrete to Sprayed Lining |  | Contr |  | TUX - Tunnel Drive X (West) |  | 2013-07-05 | 2013-07-09 13:29 | 4 | 2013-06-21 | Shafts -Sprayed Concrete | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | 50 L of water added to wagon load of 017 where 35L was specified as allowable on ticket.
| 01CV - Civils | Cxxx-NCR-000818 | NCR | Pile Toe Levels out of Tolerance |  | Contr |  | TUX - Tunnel Drive X (West) |  | 2013-07-05 | 2013-07-09 13:42 | 4 | 2013-06-21 | Shafts - Shafts General | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | Pile toes installed out of tolerance as per attached profile.
| 01CV - Civils | Cxxx-NCR-000820 | NCR | Standard instead of FTS ring 2634 Installed in Westbound tunnel |  | Contr | KIR | TUX - Tunnel Drive X (West) |  | 2013-09-30 | 2013-07-17 11:50 | -75 | 2013-06-24 | Tunnelling - Linings - Precast | 500 |  | Supervision/Management | Reject | 4 (0.5-3k) | Complete |  | Completed |  | A standard unreinforced ring has been installed
| 01CV - Civils | Cxxx-NCR-000823 | NCR | Grout batching plant calibration records |  | Contr | KIR | TUX - Tunnel Drive X (West) |  | 2013-09-25 | 2013-09-04 10:56 | -21 | 2013-06-25 | Tunnelling - Grouting | 2000 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | External Phenomenon - Other | Completed |  | The grout batching plant calibration is not in accordance with the technicalrequirements. Refer to Surveillance Report number QS300/410-06 for details
| 01CV - Civils | Cxxx-NCR-000824 | NCR | Availability of calibration records for grout injection measurement equipment |  | Contr | KIR | TUX - Tunnel Drive X (West) |  | 2013-07-31 | 2013-07-25 12:39 | -6 | 2013-06-25 | Tunnelling - Grouting | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | No calibration records of the annulus grouting measurement equipment were made avaialbe to demonstrate compliance with Works Information cause 20.8
| 01CV - Civils | Cxxx-NCR-000843 | NCR | Approved MCR not in place for couplers and mix when pouring the first section of Ring Beam |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2013-08-06 | 2013-07-17 12:53 | -20 | 2013-07-05 | Shafts - Shafts General | 500 |  |  | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Lack or improper material identification and traceability | Completed |  | During a planned surveillance on the 26/6 it was observed that: The concrete used for the pour was C32/40 from tarmac with retarder this was not the concrete mentioned on the ITP a place holder was is in eB for this mix Cxxx--C-LRC-CRT00_ST005-50237 at the time. The concrete mentioned in the ITP Cxxx--C-LRC-CRT00_ST005-50229 was code 3. MCR for __ couplers was a place holder on eB Cxxx--C-LRC-CRT00_ST005-50235 and it could be not determined if there was an approved MCR.
| 01CV - Civils | Cxxx-NCR-000846 | NCR | Facelogging Missed |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2013-08-09 | 2013-07-17 12:10 | -23 | 2013-07-08 | Geotechnical Engineering - Geotechnical Monitoring | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Defective or inadequate procedure | Completed |  | The facelogging was missed on the lower 500mm of the 1st Quadrant of the ring beam excavation.
| 01CV - Civils | Cxxx-NCR-000847 | NCR | Non-Compliance With RESS |  | Contr |  | TUX - Tunnel Drive X (West) |  | 2013-08-09 | 2013-07-09 14:40 | -31 | 2013-07-08 | Shafts - Excavation | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | Excavation of ground in first Quadrant of ring beam not in accordance with RESS sheet. undertook sprayed an initial lining of 75mm to the initial 1m excavation and then progressed onto the next 800mm advance. The RESS clearly states that a lining of 200mm is required prior to proceeding to the next advance.
| 01CV - Civils | Cxxx-NCR-000852 | NCR | 60mm overspray on CH3 Enlargement crown between chainages 144.50 - 145.50 |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2013-07-31 | 2013-07-24 13:42 | -7 | 2013-07-10 17:54 | Tunnelling - Linings - Sprayed Concrete | 3000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Worker not correctly instructed | Completed |  | 60mm of concrete has been oversprayed on the crown of Advs 1/2 (Chn. 144.50 - 145.50) in the CH3 Enlarged tunnel
| 01CV - Civils | Cxxx-NCR-000854 | NCR | Quadrants excavated out of sequence |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2013-08-06 | 2013-07-25 10:44 | -12 | 2013-07-23 16:13 | Shafts - Excavation | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | During the excavation of the second first advance the 3 quarter to be excavated was excavated adjacent the second rather than the opposite quadrant.
| 01CV - Civils | Cxxx-NCR-000855 | NCR | Failure to apply initial lining |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2013-08-06 | 2013-07-25 15:57 | -12 | 2013-07-23 16:37 | Shafts - Linings | 500 |  | Planning | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | During the spraying of Advance 2, Quadrant 4 failed to apply the initial 75mm lining to the full extent of the quadrant following excavation as the site had used the available concrete spraying the primary lining. The face was left exposed for a short period waiting for additional concrete to arrive.
| 01CV - Civils | Cxxx-NCR-000856 | NCR | Eastbound Tunnel - Ring Roll allowance |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2014-03-07 | 2014-03-05 13:57 | -2 | 2013-07-24 09:01 | Civil - Tunnelling | 1000 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | Ring roll values outside allowance for rings . See attached spreadsheet for detail.
| 01CV - Civils | Cxxx-NCR-000857 | NCR | Westbound Tunnel - Ring Roll allowance |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2014-04-30 | 2014-04-24 13:45 | -6 | 2013-07-24 09:26 | Civil - Tunnelling | 1000 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | Ring roll values outside allowance between rings. See attached spreadsheet for detail.
| 01CV - Civils | Cxxx-NCR-000860 | NCR | Fisher st SCL primary lining 35 degree joint |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2013-08-10 | 2013-07-31 08:50 | -10 | 2013-07-27 03:14 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Worker not correctly instructed | Completed |  | Fisher st shaft advace 4, Quarter 1, SCL joint was not constructed as per the design. The 35degree SCL angle was not sprayed in, building up to 400mm in layers. Further spraying to rectify the situation when realised would be upon a cold joint.
| 01CV - Civils | Cxxx-NCR-000861 | NCR | Attendances at Site Testing |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2013-08-19 | 2013-08-13 08:40 | -6 | 2013-07-29 09:48 | Shafts -Sprayed Concrete | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete |  | Completed |  | According to the Concrete Testing ITP & __ should be attendance for all concrete testing. At several instances only __ attended Flow Test and Early Age Strength testing.
| 01CV - Civils | Cxxx-NCR-000862 | NCR | 50m3 Concrete Testing |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2013-09-20 | 2013-09-06 06:51 | -14 | 2013-07-29 09:55 | Shafts - Shafts General | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Subcontractor Problems - Insufficient surveillance of subcontractors | Completed |  | did not undertake the required Early age concrete testing at the 50m3 intervals as per KT20. The third Early age concrete testing was undertaken 63.9m3 following the second. The limit between tests was then exceeded by 13.9 m3.
| 01CV - Civils | Cxxx-NCR-000863 | NCR | Monitoring Failure over weekend |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2013-08-20 | 2013-08-02 10:47 | -18 | 2013-07-30 08:20 | Surveying - Tunnels/Portal/Shafts surveys | 500 |  | Equipment Breakdown | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Defective or inadequate procedure | Completed |  | On the 28/07/13 no convergence monitoring was undertaken as per I&M plan. This arose as the ATS installed at the base of the shaft moved out of the range of the compensators on the ATS on the Saturday night.
| 01CV - Civils | Cxxx-NCR-000864 | NCR | Non-Conformance with RESS 025 |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2013-08-20 | 2013-08-02 11:00 | -18 | 2013-07-30 08:29 | Shafts - Excavation | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Misunderstand the definition of the requirement | Completed |  | RESS 025 states that no excavation is to be undertaken until reinstatement of convergence prisms at -12m. Excavation was undertaking without baselining these prisms.
| 01CV - Civils | Cxxx-NCR-000867 | NCR | Lips and steps outside the allowable limit (Ring 3786) and ring damage for ring 3787 within the westbound tunnel. |  | Crossrail | XRL | TUX - Tunnel Drive X (West) |  | 2014-02-28 | 2014-02-27 13:41 | -1 | 2013-08-06 16:53 | Civil - Tunnelling | 2000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The lips and steps exceed the allowable limits stated in KT10 for ring 3786 within the Westbound tunnel. Ring 3786 was damaged during installation with reports of leaking grout through a crack. The ring also had open joints and approx 30mm step at the key.
| 01CV - Civils | Cxxx-NCR-000868 | NCR | Lips and steps outside the allowable limit for ring 3741 within the westbound tunnel. |  | Crossrail | XRL | TUX - Tunnel Drive X (West) |  | 2014-09-24 | 2014-09-17 16:01 | -7 | 2013-08-06 16:21 | Civil - Tunnelling | 1000 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Lips and steps outside the allowable limit for ring 3741 within the westbound tunnel.
| 01CV - Civils | Cxxx-NCR-000869 | NCR | Ring crack at Westbound tunnel Ring 1089 |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2015-04-24 | 2015-05-15 08:42 | 21 | 2013-08-09 10:28 | Tunnelling - Linings - Precast | 1500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Crack across Ring 1089 within Westbound tunnel. Left segment of a left hand ring. Maximum crack witdh 5mm. See atatched photos.
| 01CV - Civils | Cxxx-NCR-000870 | NCR | WB Ring 3182 - Damage to Segement near Gasket Area |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2013-09-11 | 2013-09-04 10:58 | -7 | 2013-08-14 09:54 | Civil - Tunnelling | 2000 |  | Damaged | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Segment with spalling (within 20mm of gasket groove) installed in WB Tunnel Ring 3182. (Refer to the attached Segment Inspection Report)
| 01CV - Civils | Cxxx-NCR-000871 | NCR | Excavation out of Sequence |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2013-09-12 | 2013-09-02 12:55 | -10 | 2013-08-15 06:20 | Shafts - Excavation | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Supervision - Not Defined | Completed |  | On the 9/08/13, the excavation of the shaft quadrants was taken in the incorrect sequence and not in accordance with RESS. Though still excavated and sprayed in quadrants the second and third quadrants were not undertaken at opposite sides but rather adjacent to each other.
| 01CV - Civils | Cxxx-NCR-000872 | NCR | Bedford Row East - Volume Loss and Actions Taken with TBM Parameters |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2013-09-16 | 2013-09-23 10:00 | 7 | 2013-08-19 18:32 | Surveying - Instrumentation and Monitoring | 2000 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | Volume loss has been calculated for the surface levelling transect at the east side of Bedford Row, located at WB chainage 6243 or built ring number = 3822. The volume loss has been calculated as 0.99% ( Cxxx--C4-RGN-CRT00_ST005-50838), against the permitted 0.58% volume loss, therefore this constitutes a breach. Cxxx-OVE-C2-RSP-CR001-00001 v14 specifies the volume loss as 0.5% between WB chainages 6230 to 6313, however the specified volume loss is an at source mitigation and the reflection of this in terms of surface settlements will have a transition zone near this change in volume loss. Therefore the stated specified volume loss of 0.58% is a back-calculation of the specified volume loss at the surface.
| 01CV - Civils | Cxxx-NCR-000873 | NCR | Fisher st a1 adit reinforcement |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2014-05-06 | 2013-09-26 13:16 | -222 | 2013-08-20 10:30 | Shafts - Alignment | 40000 |  | Planning | Repair | 2 (6-60k) | Complete | Subcontractor Problems - Insufficient surveillance of subcontractors | Completed |  | Seven of the above adit reinforcement bars in adit A1, Fisher st shaft have been placed in the wrong position and sprayed. Please refer to attached sketch for reference of the positioning of the steel.
| 01CV - Civils | Cxxx-NCR-000874 | NCR | SMM_FIS IPI incremental readings |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2013-09-04 | 2013-09-04 16:40 | 0 | 2013-08-21 15:16 | Surveying - Instrumentation and Monitoring | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The readings taken with the IPIs in FIS shaft are incremental instead of cumulative. This means that all the profiles presented cannot be directly compared with the triggers and some triggers have already been breached without any notification as discussed in the 14/8/13 CTC.
| 01CV - Civils | Cxxx-NCR-000875 | NCR | FIS pile out of tolerance |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2013-10-10 | 2013-10-15 09:47 | 5 | 2013-08-22 16:04 | Shafts - Alignment | 2000 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The pile reports confirm that all of the secant piles verticality was within tolerance. During excavation several piles were surveyed as out of tolerance at -9m, namely M71, M7, M10,M13, M19 and M22 where the verticality exceeded 1:150 enhanced by the positional tolerance at the top of the shaft at the 25mm extremity. Piles M37 and M33 verticality exceeded 1:150mm, protruding into the shaft.
| 01CV - Civils | Cxxx-NCR-000876 | NCR | Excavation of Quadrant prior to completion of previous Quadrant |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2013-09-25 | 2013-09-04 16:42 | -21 | 2013-08-28 09:40 | Shafts - Excavation | 500 |  | Planning | Use As-Is | 4 (0.5-3k) | Complete | Personnel Error - Inattention to detail | Completed |  | RFI 00788 requires the full 400mm of primary lining to be sprayed to a quadrant prior to excavation of the subsequent quadrant. On Advance 13, Quadrant 1 a 2m section of the quadrant had been sprayed with 100mm rather than 400mm prior to commencing to the excavation of Quadrant 2. The remaining 300mm was sprayed during spraying of the 2nd quadrant.
| 01CV - Civils | Cxxx-NCR-000877 | NCR | Young concrete compressive strength testing, distance between the studs |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2013-09-12 | 2013-09-04 16:44 | -8 | 2013-08-28 11:45 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Training Deficiency - No training provided | Completed |  | Three rows of studs were driven into the test panel to a depth that appeared satisfactory, however the distance between the studs in the middle row were less that the minimum specified. The BS EN 14488-2:2006 requires sufficient distance (> 80 mm) between the studs or when in grid form ≥80 ±10mm, the distance between two sets of studs in the middle row were measured as 50mm.
| 01CV - Civils | Cxxx-NCR-000879 | NCR | Tunnel Segment Damage to Ring 143 WB |  | Contr | KIR | TUX - Tunnel Drive X (West) |  | 2013-09-20 | 2013-09-23 13:53 | 3 | 2013-09-06 12:22 | Civil - Tunnelling | 4000 |  | Supervision/Management | Repair | 3 (3-6k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | While reviewing Tunnel Segment Inspection records for WB ring 101 – 495 found a damage segment TRL 137 – 15/03/12 which is built into the WB tunnel as ring number 143. (see attached record and photo) The damage is within the gasket groove which as per the damage criteria acceptance should have been rejected (>10 mm x 10mm on surface x 10mm deep) or at least repaired (<10mm x 10mm on surface x 10mm deep).
| 01CV - Civils | Cxxx-NCR-000880 | NCR | Initial Lining To Plug |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2013-10-01 | 2013-09-12 07:55 | -19 | 2013-09-10 04:56 | Shafts - Linings | 1000 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | It was agreed between , Crossrail, Cxxx and Donaldsons in the 10am SRG on the 06/09/13 that we would pour the Fisher st shaft SFR mass concrete infill to the base without spraying the 75mm sprayed layer as per the drawings. and there subcontractor were delayed on the 05/09/13 by a batching plant breakdown. It was deemed better therefore to pour the mass infill plug before the weekend than leave it with a 75mm layer and forgo the pour until the next week. therefore directly in filled the base post excavation, no exposed face was left. Note the mass pour uses the primary lining 17.1 mix design, only the application of the concrete varies.
| 01CV - Civils | Cxxx-NCR-000881 | NCR | BFK Mix 17.1 for insitu Slab |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2013-10-01 | 2013-09-17 10:20 | -14 | 2013-09-10 05:05 | Shafts - Linings | 1000 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | Refer to Cxxx-FCD-000865 Cxxx have accepted the use of 17.1 mix design for use of the SFR mass concrete infill but require this NCR to record that is doesn’t comply with the Cxxx FIS insitu spec KF10 used at Fisher st. The mix is recorded as having a DC-2 exposure class, yet still meets the XC3 exposure class required by the spec. The dry shrinkage for mix 17.1 was also tested at 40N and accepted, no further dry shrinkage would be expected .
| 01CV - Civils | Cxxx-NCR-000882 | NCR | Waterproofing Concical form MCR |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2013-09-24 | 2013-09-12 17:46 | -12 | 2013-09-10 05:10 | Shafts - Linings | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Other | Completed |  | site team submitted the witches hat MCR to their inhouse document control in August, a clerical mistake was made and the MCR not uploaded to CRL. ensured it was submitted on the 05/09/2013 however this has left minimal time for crossrail to review prior to installation on the 12/09/13.
| 01CV - Civils | Cxxx-NCR-000884 | NCR | Depressurisation Wells |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2013-10-01 | 2013-09-18 13:59 | -13 | 2013-09-10 05:30 | Shafts - Shafts General | 2500 |  | Planning | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Note 12 On drawing Cxxx-MMD-C4-DDA-CR086_SH003-02031 added May 2013 states ‘prior to construction of the internal elements of the shaft as identified on Cxxx-JUL-S-DDB-CR086_SH003-02400, the contractor is to monitor and take sufficient measures in order to limit the pore water pressure acting on the underside of the cast in-situ base slab to 50 kN/m2’ agreed in the SRG on 06/09/2013 with Cxxx, Crossrail and Donaldsons that the risk of pore water pressure is negligible. undertook piling of the OSD piles September-October 2012 to 92AOD and encountered no water (note OSD pile 1 hit localised Thames water flooding at -6m only). The installation of the depressurisation to -87.67AOD also recorded no water during installation and the daily SRG meeting has recorded no water during the installation 19th August to the 6th September. The geologists have recorded no water ingress during the shaft sinking in the London clay and Lambeth group, also recorded in the daily SRG. Cxxx stated that they envisaged the depressurisation monitoring to be brought through the mass infill and capped before the waterproofing and reinforced concrete slab. However there is no time between the infill curing and the waterproofing installation, therefore there is no point in installing. propose to undertake weekly monitoring of boxed out PLPs on the shaft base, to be reviewed over time.
| 01CV - Civils | Cxxx-NCR-000886 | NCR | OOC segments low test results |  | Contr | KIR | TUX - Tunnel Drive X (West) |  | 2013-12-09 | 2013-10-01 11:54 | -69 | 2013-09-10 16:00 | Tunnelling - Linings - Precast | 260000 |  | Workmanship | Use As-Is | 1 (>60k) | Complete | Management Problem - Other | Completed |  | Several days production of pre-cast segments at Old Oak Common have failed the beam test. See attached documents detailing days quarantined and a summary of test results. Cube and cylinder results generally compliant.
| 01CV - Civils | Cxxx-NCR-000887 | NCR | Ring beam Profile |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2013-09-26 | 2013-10-03 10:27 | 7 | 2013-09-12 06:17 | Shafts - Linings | 1000 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Profiles for the ring beam construction show that the there is insufficient space remaining for the 400mm secondary lining. The reamining area varies along the profile to a maximum loss of 56mm in one location.
| 01CV - Civils | Cxxx-NCR-000888 | NCR | Drive X - Westbound Tunnel Segment Damage - Ring 722 |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2013-10-31 | 2013-10-04 15:15 | -27 | 2013-09-12 12:16 | Tunnelling - Linings - Precast | 2000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | Segement damage along the corner (>50mm). See attached picture
| 01CV - Civils | Cxxx-NCR-000889 | NCR | Concrete Testing |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2013-09-27 | 2013-09-26 13:29 | -1 | 2013-09-13 12:47 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Verification Problems - Other | Completed |  | Flexural Strength Test The 3 x beams that were cut at 150x150x600mm where not within the tolarences stated in KT20, which referes to BS EN 14651. The worst example was in sample 'beam 1' where the average width exceeded the BS EN requirements by 0.45mm. Additionally the width of the notches in all the Beams exceeded the BS EN requirements by up to 0.3mm. Finally, the Residual flexural tensile strength values should have covered an extension of up to 4mm, however these tests only continue to 3.5mm. Fibre Washout test This test should have been conducted 1/month. However it has only been conducted once in a period that covers 3 months.
| 01CV - Civils | Cxxx-NCR-000890 | NCR | Earth Rod Seal Installation |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2013-09-30 | 2013-09-26 13:42 | -4 | 2013-09-13 15:02 | Shafts - Shafts General | 2500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Design Problem - Error in equipment or material selection | Completed |  | Drawing Cxxx-MMD-C4-DDD-CR086_SH003-04071 Shaft Earthing Mat Details sheet 2 of 2 clearly says in note 7 'The design is based on using the Furse earth rod seal ES220-15'. When the work was done, a conical waterproof sealant was used because it was believed that it would be similar and acceptable. Due to the fact that 5.5bar resistance cannot be guaranteed by any test the solution wasn’t accepted.
| 01CV - Civils | Cxxx-NCR-000892 | NCR | Overlap on Geotextile Fleece |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2013-10-23 | 2013-10-21 11:15 | -2 | 2013-09-18 16:27 | Shafts - Linings | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | The geotextile fleece laid on the base of the shaft had an approximate overlap of 100-150mm instead of the 200mm as specified in KW21. The laps were bond together with a LTP. This was done to bond the sheets and to ensure that there were no overlapping edges that will obstruct the LTS weld on the PVC membrane over the geotextile. There was a incorrect assumption that this was acceptable.
| 01CV - Civils | Cxxx-NCR-000893 | NCR | Modulus of elasticity |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2013-10-24 | 2013-10-01 12:51 | -23 | 2013-09-23 11:48 | Tunnelling - Linings - Sprayed Concrete | 4000 |  | Supervision/Management | Use As-Is | 3 (3-6k) | Complete | Verification Problems - Other | Completed |  | Modulus of elasticity was tested at 3 days instead of 1 day as required by KT 20 and ITP. One 28 day result is 26 GPa what is less than 31.9 GPa as required by KT 20 (results attached). Average of three tests is 31 GPa.
| 01CV - Civils | Cxxx-NCR-000894 | NCR | Volume loss between west of Bedford Row & Gray's Inn Gardens |  | Crossrail | PDP | TUX - Tunnel Drive X (West) |  | 2014-01-30 | 2014-01-07 11:54 | -23 | 2013-09-25 15:50 | Surveying - Instrumentation and Monitoring | 5000 |  | Supervision/Management | Use As-Is | 3 (3-6k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | A review has been undertaken of all monitoring available in the vicinity of the Bedford Row West PLP transect (WB tunnel drive), which initially indicated a breach of the allowable volume loss of 0.5%. Previously NCR 872 had been raised by the contractor to indicate a breach of the allowable volume loss at WB chainage 6243 (built ring 3822). A subsequent review by Cxxx indicates that volume loss is breached over a greater length of tunnel between WB chainage 6233 to 6372, a distance of 139 m - Please see Cxxx review attached.
| 01CV - Civils | Cxxx-NCR-000895 | NCR | Tape left on hydrophilic gaskets |  | Crossrail | PDP | TUX - Tunnel Drive X (West) |  | 2014-02-10 | 2014-02-10 09:18 | 0 | 2013-09-30 12:55 | Civil - Tunnelling | 4200 |  | Supervision/Management | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Insufficient information made available to the worker. | Completed |  | On the 02/08/13 it was noted that a standard ring with hydrophilic gasket had been delivered to the TBM - delivery no 6785. The segment was being placed on the magazine to be transported to the build area with tape placed over the hydrophilic gasket. After a conversation between the CRL FE and Pit Boss / Operatives it became clear that segments had been erected with tape on the hydrophilic gaskets since the start of the shift, affecting Rings 3770 - 3776.
| 01CV - Civils | Cxxx-NCR-000896 | NCR | Fisher Street SGI Adit 2 Installation - Westbound SGI |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2013-12-29 | 2013-12-19 16:23 | -10 | 2013-09-30 10:39 | Tunnelling - Linings - SGI Rings | 4000 |  | Workmanship | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | SGI opening set for FIS Adit 2 Westbound - Ring buid report shows that a few non-conformities are present. This includes missing nuts, dowels and loose bolts as shown on the Ring-build inspection report.
| 01CV - Civils | Cxxx-NCR-000898 | NCR | SGI Installation Cross Passage CP1 - Eastbound Rings 318 and 319 |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2014-06-27 | 2013-12-19 16:08 | -190 | 2013-09-30 11:06 | Tunnelling - Linings - SGI Rings | 4000 |  | Workmanship | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | SGI opening set for CP1 Eastbound - Ring buid report shows that a few non-conformities are present including missing dowels, missing or damaged grommet as shown in the Ring-build report and Inspection sheet.
| 01CV - Civils | Cxxx-NCR-000899 | NCR | SGI Installation CP3 - Westbound |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2014-04-18 | 2013-12-19 16:21 | -120 | 2013-09-30 12:46 | Tunnelling - Linings - SGI Rings | 4000 |  | Workmanship | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | SGI opening set for FIS CP£ Westbound - Ring buid report shows that a few non-conformities are present. This includes a missing dowel and missing bolt as shown in the Inspection reports
| 01CV - Civils | Cxxx-NCR-000900 | NCR | SGI Installation CP4a - Westbound Rings 2463, 2464 |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2014-04-18 | 2013-12-19 16:06 | -120 | 2013-09-30 13:07 | Tunnelling - Linings - SGI Rings | 4000 |  | Workmanship | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | SGI opening set for CP4a Westbound - Ring buid report shows that a few non-conformities are present. This includes loose bolts and segment lip as shown on attached inspection reports.
| 01CV - Civils | Cxxx-NCR-000902 | NCR | Missing Segment Inspection Report |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2013-10-21 | 2013-10-11 08:30 | -10 | 2013-09-30 16:13 | Civil - Tunnelling | 500 |  | System Defect | Use As-Is | 4 (0.5-3k) | Complete | Verification Problems - Other | Completed |  | The segment Report Sheets for the following Westbound Tunnel rings are identified to be missing: Ring 907 Ring 1406 Ring 1438
| 01CV - Civils | Cxxx-NCR-000903 | NCR | Missing Segment Reports |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2013-12-13 | 2013-12-12 17:40 | -1 | 2013-09-30 16:25 | Civil - Tunnelling | 1000 |  | System Defect | Use As-Is | 4 (0.5-3k) | Complete | Verification Problems - Other | Completed |  | The Segment Reports for the following rings in the Eastnound tunnel are missing: Ring 01 Ring 101
| 01CV - Civils | Cxxx-NCR-000904 | NCR | CH3 Sprayed Concrete Checklist Form 50 sheets are missing initial docket details |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2013-10-15 | 2013-10-11 13:28 | -4 | 2013-10-01 16:52 | Tunnelling - Linings - Sprayed Concrete | 1000 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | Sprayed Concrete Lining Checksheet form 50 should have the initial shotcrete docket number entered into the form by the engineer. This is missing on checksheets of advances 1, 3, 6, 11, 16, 18, 20, 21, 22, 23, 24, 26, 31, 34, 36, 39, 43, 48A, 48B, 50, 58, 70, 74, 75, 78, 90, 91, 92, 97 and 98.
| 01CV - Civils | Cxxx-NCR-000905 | NCR | CH3 Sprayed Concrete Checklist Form 50 sheets are missing nozzleman signatures |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2013-10-15 | 2013-10-11 13:43 | -4 | 2013-10-01 17:36 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | Sprayed Concrete Lining Checksheet form 50 should have the nozzleman signature entered into the form after spraying to complete the checksheet for the engineer. This is missing on the checksheets of advances 1, 4, 10, 11, 13, 14, 16, 17, 18, 20, 21, 23, 24, 31, 32, 34, 35, 36, 37, 38, 39, 40, 42, 44A, 44B, 45, 47B, 48A, 52, 53, 54, 56, 57, 58, 59, 60, 61, 62, 63, 64, 65, 66, 67, 28, 69, 70, 71, 72, 73, 74, 75, 79, 80, 83, 84, 85, 88, 96, 97, 98, 99B
| 01CV - Civils | Cxxx-NCR-000906 | NCR | Manufacturers recommended calibration frequency of grout flow measurement equipment within the TBM |  | Crossrail | PDP | TUX - Tunnel Drive X (West) |  | 2013-10-30 | 2013-10-22 16:31 | -8 | 2013-10-02 12:29 | Tunnelling - Grouting | 1200 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | External Phenomenon - Other | Completed |  | Further to the observations highlighted during CRL surveillance QS300/410-06 and raised in NCR-Cxxx-00823, there is a requirement for the contractor to provide details of the manufacturers recommended calibration frequency of the grout flow measurement equipment within the TBM. Please provide details of the recommended calibration frequency of the grout flow measurement equipment on the TBM.
| 01CV - Civils | Cxxx-NCR-000908 | NCR | Proof Drilling |  | Crossrail | PDP | TUX - Tunnel Drive X (West) |  | 2014-01-20 | 2014-01-23 15:04 | 3 | 2013-10-02 14:29 | Tunnelling - Grouting | 1200 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Procedure Problem - Not Defined | Completed |  | Further to observations highlighted during CRL surveillance QS300/410-05 and raised in NCR-Cxxx-00759, the contractor is required to demonstrate that proof drilling is being undertaken as per KT10.4224. Please provide details of ’s proof drilling methodology and subsequent results.
| 01CV - Civils | Cxxx-NCR-000909 | NCR | Missing Segment Reports |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2014-03-14 | 2014-02-07 13:00 | -35 | 2013-10-04 09:03 | Civil - Tunnelling | 1200 |  | System Defect | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | The following segment reports from the Westbound tunnel are missing: 1019, 1127,1144,1327 and 1328.
| 01CV - Civils | Cxxx-NCR-000911 | NCR | Crack in Segment |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2014-04-09 | 2014-04-01 11:05 | -8 | 2013-10-08 12:50 | Civil - Tunnelling | 10000 |  | Damaged | Use As-Is | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Segment ER 48 had a crack through the middle dowel hole and was built into the ring number 778 in the EB tunnel.
| 01CV - Civils | Cxxx-NCR-000912 | NCR | Loose Gasket in Segment in Eastbound Tunnel Ring 747 |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2013-11-30 | 2013-11-13 08:43 | -17 | 2013-10-08 13:04 | Civil - Tunnelling | 1000 |  | Damaged | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Segment BR 13 built in ring 747 had a loose gasket when the ring was inspected at Westnourne Park yard.
| 01CV - Civils | Cxxx-NCR-000913 | NCR | Qualilty of materials and workmanship - ATS system in the Osbourne Tunnel |  | Crossrail | XRL | TUX - Tunnel Drive X (West) |  | 2013-10-29 | 2013-10-30 13:00 | 1 | 2013-10-08 16:20 | Surveying - Instrumentation and Monitoring | 2000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | On the 09/08/2013 a site visit held to the Osbourne Tunnel to document the condition of the ATS installation prior to the Handover to Cxxx from Cxxx. was invited to the inspection but did not attend. During the inspection the poor condition of the electrical workmanship was noted. The photo attached in “2013-08-09 11.57 - Osbourne Tunnel ATS inspection” give and indication of the general lack of quality materials and workmanship. KX10.3201 a) states that “All instrumentation shall be securely fixed”. From the photo taken during the inspection it is evident that no care has been taken to secure the items correctly as items fall out of the logger box when opened. In addition to this the wiring and general layout of components is to a substandard with no ventilation and loose steel studding located directly above exposed battery terminals.
| 01CV - Civils | Cxxx-NCR-000914 | NCR | OOC segment low test results |  | Contr | KIR | TUX - Tunnel Drive X (West) |  | 2014-03-18 | 2014-03-18 09:06 | 0 | 2013-10-10 10:52 | Tunnelling - Linings - Precast | 60000 |  | Workmanship | Use As-Is | 2 (6-60k) | Complete | Material/Preservation Problems - Other | Completed |  | With reference to NCR 886. Further beam test results from samples made on 2nd, 3rd and 9th September have below minimum specified values. See attached spread sheet for the full list of test results which are below the minimum for this period of 3rd July to 9th September. Cube and cylinder results are compliant. Please review again all the low test results to determine if these segments can be used.
| 01CV - Civils | Cxxx-NCR-000915 | NCR | Drive X - Westbound Tunnel Ring Damage and Repair - ROP to Paddington Station |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2013-11-19 | 2013-11-11 16:59 | -8 | 2013-10-18 16:34 | Civil - Tunnelling | 25000 |  | Damaged | Repair | 2 (6-60k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | Cracks in installed tunnel precast segments.
| 01CV - Civils | Cxxx-NCR-000916 | NCR | Drive X - Westbound Tunnel Ring Damage and Repair - Paddington Station (Ring 660) to Bond Street Station (Ring 1994) |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2014-07-07 | 2013-11-19 16:36 | -230 | 2013-10-21 11:47 | Civil - Tunnelling | 25000 |  | Damaged | Repair | 2 (6-60k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | Defect/Cracks in installed Tunnel Segments - Paddington Station (Ring 660) to Bond Street Station (Ring 1994)
| 01CV - Civils | Cxxx-NCR-000917 | NCR | Drive X - Westbound Tunnel Ring Damage and Repair - Bond Street Station (Ring 2320) to Tottenham Court Road Station (Ring 2770) |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2014-07-07 | 2013-11-19 16:40 | -230 | 2013-10-21 11:49 | Civil - Tunnelling | 25000 |  | Damaged | Repair | 2 (6-60k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | Defect/Cracks in installed Tunnel Segments - Bond Street Station (Ring 2320) to Tottenham Court Road Station (Ring 2770)
| 01CV - Civils | Cxxx-NCR-000918 | NCR | Drive X - Westbound Tunnel Ring Damage and Repair - Tottenham Court Station (Ring 3037) to Fisher Street Crossover (Ring 3634) |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2014-07-07 | 2013-11-19 16:45 | -230 | 2013-10-21 12:47 | Civil - Tunnelling | 25000 |  | Design | Repair | 2 (6-60k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | Defect/Cracks in installed Tunnel Segments - Tottenham Court Station (Ring 3037) to Fisher Street Crossover (Ring 3634)
| 01CV - Civils | Cxxx-NCR-000919 | NCR | Drive X - Westbound Tunnel Ring Damage and Repair - Fisher Street Shaft (Ring 3635) to Farringdon Station (Ring 4293) |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2014-01-28 | 2014-01-28 15:30 | 0 | 2013-12-09 14:53 | Civil - Tunnelling | 35000 |  | Damaged | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Precast segments developed various defects (i.e cracks) after installation. See attached crack mapping summary for further details. Defect remedial has been included on Punchworks under reference DRX-Cxxx-00034.
| 01CV - Civils | Cxxx-NCR-000920 | NCR | Drive X - Eastbound Tunnel Ring Damage and Repair - ROP (Ring 1) to Paddington Station (Ring 502) |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2014-07-07 | 2013-11-20 20:50 | -229 | 2013-10-21 12:50 | Civil - Tunnelling | 25000 |  | Damaged | Repair | 2 (6-60k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | Defect/Cracks in installed Tunnel Segments - ROP (Ring 1) to Paddington Station (Ring 502)
| 01CV - Civils | Cxxx-NCR-000921 | NCR | Drive X - Eastbound Tunnel Ring Damage and Repair - Paddington Station (Ring 667) to Bond Street Station (Ring 1998) |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2014-07-07 | 2013-11-28 13:53 | -221 | 2013-10-21 12:52 | Civil - Tunnelling | 65000 |  | Damaged | Repair | 1 (>60k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | Defect/Cracks in installed Tunnel Segments - Paddington Station (Ring 667) to Bond Street Station (Ring 1998)
| 01CV - Civils | Cxxx-NCR-000922 | NCR | Drive X - Eastbound Tunnel Ring Damage and Repair - Bond Street Station (Ring 2284) to Tottenham Court Road Station (Ring 2745) |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2014-07-07 | 2013-11-28 13:49 | -221 | 2013-10-21 13:12 | Civil - Tunnelling | 20000 |  | Damaged | Repair | 2 (6-60k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | Defect/Cracks in installed Tunnel Segments - Bond Street Station (Ring 2284) to Tottenham Court Road Station (Ring 2745)
| 01CV - Civils | Cxxx-NCR-000923 | NCR | Drive X - Eastbound Tunnel Ring Damage and Repair - Tottenham Court Road Station (Ring 2993) to Fisher Street Crossover (Ring 3609) |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2014-09-08 | 2014-09-11 13:50 | 3 | 2013-11-25 14:13 | Civil - Tunnelling | 72000 |  | Damaged | Repair | 1 (>60k) | Complete | Discipline/Workmanship - Other | Completed |  | Defect/Cracks in installed Tunnel Segments - Tottenham Court Road Station (Ring 2993) to Fisher Street Crossover (Ring 3609)
| 01CV - Civils | Cxxx-NCR-000924 | NCR | Drive X - Eastbound Tunnel Ring Damage and Repair - Fisher Street Crossover to Farringdon Station |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2015-11-21 | 2015-11-17 10:10 | -4 | 2015-10-22 09:13 | Civil - Tunnelling | 50000 |  | Damaged | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Other | Completed |  | Defect/Cracks in installed Tunnel Segments - Fisher Street Crossover to Farringdon Station. This NCR is reference in Tunnel Records and raised to record crack repair records. This defect is reference in the Punchworks item Cxxx-PWK-00058 and this NCR can be closed.
| 01CV - Civils | Cxxx-NCR-000925 | NCR | Rejected Segments at OOC Production Site (101-150) |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2013-11-21 | 2013-11-20 20:55 | -1 | 2013-10-17 14:05 | Civil - Tunnelling | 31250 |  | Damaged | Repair | 2 (6-60k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | Damaged/defective tunnel segment at OOC. Refer to the attached list 101-150
| 01CV - Civils | Cxxx-NCR-000926 | NCR | Rejected Segments at OOC Production Site (151-194) |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2013-11-28 | 2013-11-20 21:00 | -8 | 2013-10-17 14:09 | Civil - Tunnelling | 15000 |  | Damaged | Reject | 2 (6-60k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | Damaged/defective tunnel segment at OOC. Refer to the attached list 151-194
| 01CV - Civils | Cxxx-NCR-000927 | NCR | SGI Installation - Eastbound CP2 - Missing bolts,dowel,grommet and 25mm lip |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2014-06-14 | 2013-12-19 16:12 | -177 | 2013-10-17 15:35 | Civil - Tunnelling | 2000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | SGI opening set for CP2 Eastbound - Ring buid report (Inspection 2 dated 23/08/13) shows that a few non-conformities are present and included: a missing bolt, dowel, grommet and 25mm lip. Refer to attached inspection report.
| 01CV - Civils | Cxxx-NCR-000928 | NCR | SGI Installation CP3 - Eastbound Rings 1325 / 1326 |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2014-05-23 | 2013-12-19 16:20 | -155 | 2013-11-04 13:33 | Tunnelling - Linings - SGI Rings | 4000 |  | Workmanship | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | SGI opening set for CP3 Eastbound - Ring buid report shows that a number of non-conformities are present. This includes missing dowels SGI-PCC, missing grommets, misaligned holes, incorrectly fitted bolts.
| 01CV - Civils | Cxxx-NCR-000932 | NCR | Surface finishing in secondary lining - pour no.1 |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2014-01-31 | 2013-12-06 17:31 | -56 | 2013-10-19 15:49 | Shafts - Linings | 3500 |  | Workmanship | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Some areas of the secondary lining in the first pour do not present the required finish surface according to KF10. There are some evidences of air bubbles and a cold joint.
| 01CV - Civils | Cxxx-NCR-000934 | NCR | SGI Installation CP4 - Eastbound Rings 1586/1587 |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2014-06-02 | 2014-06-03 09:59 | 1 | 2013-11-14 16:10 | Tunnelling - Linings - SGI Rings | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | A second inspection of CP4 Eastbound seems to indicate a bolt and grommet are missing.
| 01CV - Civils | Cxxx-NCR-000935 | NCR | SGI Installation BOS Adit S2 - Eastbound |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2014-05-23 | 2013-12-19 16:17 | -155 | 2013-11-04 14:39 | Tunnelling - Linings - SGI Rings | 4000 |  | Workmanship | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | BOS EB Adit S2 indicates some non- conformities to the SGI sets installed as shown in the attached reports.
| 01CV - Civils | Cxxx-NCR-000936 | NCR | Segment Production - Unsigned Pre and Post Pour Checksheets |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2013-11-19 | 2013-11-07 15:01 | -12 | 2013-10-22 16:06 | Civil - Tunnelling | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Verification Problems - Unavailability or inadequate M&TE | Completed |  | Some of the Pre and Post Pour checksheet for Segment Production at OOC Precast Yard, have not been fully signed.
| 01CV - Civils | Cxxx-NCR-000937 | NCR | Surface finishing in secondary lining - pour no 2 |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2014-02-03 | 2013-12-06 17:34 | -59 | 2013-10-22 17:13 | Shafts - Linings | 2500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Areas of the secondary lining in pour 2 in the shaft do not present the required surface finish according to KF10. There are evidences of air bubbles (bugholes) from under vibrating.
| 01CV - Civils | Cxxx-NCR-000938 | NCR | Drive X Westbound Tunnel Rings - Lips and Steps tolerance |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2015-07-31 | 2015-07-09 23:10 | -22 | 2013-10-28 15:30 | Civil - Tunnelling | 5000 |  | Workmanship | Use As-Is | 3 (3-6k) | Complete | Material/Preservation Problems - Other | Completed |  | Drive X Westbound Tunnel Rings - Lips and Steps tolerance outside +/-5mm List of locations where lips and steps outside tolerance to be confirmed by survey.
| 01CV - Civils | Cxxx-NCR-000939 | NCR | Drive X Eastbound Tunnel Rings - Lips and Steps tolerance |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2013-11-25 | 2013-11-19 11:24 | -6 | 2013-10-28 15:36 | Civil - Tunnelling | 20000 |  | Workmanship | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Drive X Eastbound Tunnel Rings - Lips and Steps tolerance outside +/-5mm List of locations where lips and steps outside tolerance to be confirmed by survey.
| 01CV - Civils | Cxxx-NCR-000942 | NCR | Segment Damage - Eastbound Tunnel - RIng 441 |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2013-11-29 | 2013-11-19 12:21 | -10 | 2013-11-01 15:22 | Civil - Tunnelling | 1200 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | Segment Damage - RIng 441 Eastbound (See attached pictures)
| 01CV - Civils | Cxxx-NCR-000943 | NCR | Secondary Lining Profile |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2014-06-27 | 2014-06-26 23:08 | -1 | 2013-11-01 16:18 | Shafts - Linings | 5000 |  | Workmanship | Use As-Is | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The Secondary Lining to the Fisher Street Shaft has been cast out of tolerance on lifts 1, 2 and 3. The attached profiles indicate that the lining is up to 40mm too narrow on the second lift. The radius on the profiles is 7500 - the design radius.
| 01CV - Civils | Cxxx-NCR-000945 | NCR | Seam Probe Testing |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2013-11-22 | 2013-11-21 16:46 | -1 | 2013-11-08 14:22 | Shafts - Linings | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Where single seams have been undertaken on the sheet waterproofing, testing of the welds has been undertaken using the test probe method as per the manufacturer's guidelines (see pg. 54 of attachment). KW21.3302 refers to testing by hand-held vacuum chamber. This was not undertaken as this is applicable to flat surfaces rather than rounded uneven surfaces such as the shaft.
| 01CV - Civils | Cxxx-NCR-000946 | NCR | Secondary Lining Profile - Lift 4 and 5 |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2014-07-01 | 2014-06-28 17:17 | -3 | 2013-11-13 09:13 | Shafts - Linings | 2000 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Please see attached secondary lining profiles for the Fisher Street Shaft. The profile is up to 15mm out of tolerance in localised locations. For the avoidance of doubt, the radius of the attached profiles is 7500.
| 01CV - Civils | Cxxx-NCR-000947 | NCR | SGI Installation FIS CP1 - Westbound |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2014-06-13 | 2014-06-18 10:48 | 5 | 2013-11-14 17:28 | Tunnelling - Linings - SGI Rings | 2000 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | SGI opening set for FIS CP1 Westbound - Second inspection may indicate some non-conformities as shown in the attachment.
| 01CV - Civils | Cxxx-NCR-000948 | NCR | Performance of Northfleet conveyor |  | Crossrail | XRL | TUX - Tunnel Drive X (West) |  | 2014-02-10 | 2014-01-31 11:16 | -10 | 2013-11-18 15:43 | Civil - Civil Engineering General | 2000 |  | System Defect | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The works information volume 2A part 2 section 26.2.5 states: “The Contractor shall provide sufficient capacity to allow the transfer of volumes of material up to 4500m3/day (bulked volume, 7 days/ week).” Based upon a 24 hour working day the conveyor (when operating) should be processing an absolute minimum of 375 tonnes per hour which equates to 187.50m3/hr. The conveyor is currently processing an average (based upon recent loading figures) of approximately 240 tonnes per hour. This performance is well below that expected of the conveyor and is impacting upon other works (e.g. stockpile management and shipping schedule). It has also been noted that the conveyor is experiencing numerous breakdowns.
| 01CV - Civils | Cxxx-NCR-000950 | NCR | Pre-cast tunnel segment shrinkage cracks |  | Contr | KIR | TUX - Tunnel Drive X (West) |  | 2014-01-31 | 2014-01-30 11:34 | -1 | 2013-11-20 18:40 | Tunnelling - Linings - Precast | 5000 |  | Material | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Some of the pre-cast tunnel segments exhibit a crack from the central dowel running directly to the extrados or intrados of the segment. These cracks are generally not greater than 0.2mm. The specification Cxxx-OVE-Z4-RSP-CR001-50008 cl KH11.3200 does not permit cracks.
| 01CV - Civils | Cxxx-NCR-000952 | NCR | SGI Installation CP4a - Eastbound Rings 1586 and 1587 |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2014-11-18 | 2014-05-20 11:18 | -182 | 2013-11-27 11:59 | Tunnelling - Linings - SGI Rings | 4000 |  | Workmanship | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | SGI opening set for CP4a Eastbound - A second inspection indicates some non-conformities including missing/shear dowels SGI to PCC.
| 01CV - Civils | Cxxx-NCR-000953 | NCR | Westbound Tunnel Alignment - Wriggle Survey |  | Contr | KIR | TUX - Tunnel Drive X (West) |  | 2015-03-18 | 2015-03-18 14:54 | 0 | 2013-12-04 15:17 | Civil - Tunnelling | 15000 |  | Workmanship | Use As-Is | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Further to close out of the main survey control (ROP-FAR) and subsequent completion of the westbound tunnel wriggle survey, it is noted that some parts of the final tunnel alignment are outside of the specified alignment tolerances stated in KT10.4221-4222. Wriggle Survey Report for the westbound tunnel Cxxx--C4-RGN-CRT00_ST005-50905 rev2.0 details the as-built aligment
| 01CV - Civils | Cxxx-NCR-000954 | NCR | SGI Installation FIS A1 - Eastbound |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2014-07-01 | 2014-07-02 11:33 | 1 | 2013-12-05 11:44 | Tunnelling - Linings - SGI Rings | 4000 |  | Workmanship | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | A first and second inspection indicate some broken dowels, missing grommets and lips greather than specified. Refer to attached inspection reports.
| 01CV - Civils | Cxxx-NCR-000955 | NCR | SMM - Lack of Readings of __'s on St Alban's Church |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2013-12-26 | 2013-12-19 16:36 | -7 | 2013-12-06 15:13 | Surveying - Instrumentation and Monitoring | 1000 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | The 3 eastern-most __'s located on the north façade of St Alban's Church, Brooke Street, were not baselined or read prior to the passage of the EB TBM (note they are not within the zone of influence of the WB TBM). Therefore the effect of the EB TBM has not be recorded by these __'s This is due to difficult access as the surveyors have to access via a locked gate which is part of the Mackanochie House property in Baldwin Gardens, the key to which is not readily available.
| 01CV - Civils | Cxxx-NCR-000956 | NCR | Installation of SGI rings - Eastbound FIS CP2 Rings 3607/3608 |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2014-08-05 | 2014-07-15 08:18 | -21 | 2013-12-10 12:46 | Tunnelling - Linings - SGI Rings | 4000 |  | Workmanship | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Other | Completed |  | SGI opening set for CP3 Eastbound - Ring buid report shows that a number of non-conformities are present. This includes missing / sheared dowels SGI-PCC, segments lips. Refer to attachments.
| 01CV - Civils | Cxxx-NCR-000958 | NCR | SGI Installation CP5 - Eastbound Rings 3885-3886 |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2014-10-07 | 2014-05-13 08:41 | -147 | 2013-12-11 10:54 | Tunnelling - Linings - SGI Rings | 4000 |  | Workmanship | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Other | Completed |  | SGI opening set for CP5 Eastbound - Ring buid report shows that a number of non-conformities are present. This includes sheared dowels SGI-PCC, segments lips. Refer to attachment.
| 01CV - Civils | Cxxx-NCR-000959 | NCR | Upload of profiles for SRG |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2014-01-15 | 2014-01-15 20:47 | 0 | 2013-12-16 18:55 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Other | Completed |  | Due to confusion with as build profiles, there were no profiles presented for advance 3 and 4 in time of the SRG.
| 01CV - Civils | Cxxx-NCR-000960 | NCR | Primary lining profiles of Intervention Adit2 |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2015-06-30 | 2015-05-28 01:22 | -33 | 2013-12-16 19:08 | Tunnelling - Linings - Sprayed Concrete | 2000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Some areas of the primary lining profile in intervention adit 2 are not according to the design profile and not compliant with the tolerances
| 01CV - Civils | Cxxx-NCR-000961 | NCR | Concrete requirements |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2014-01-15 | 2014-01-15 21:00 | 0 | 2013-12-16 19:36 | Tunnelling - Linings - Sprayed Concrete | 3000 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | When starting excavation of invert advance 5 the concrete was in spec (560mm and 16.5C). During the excavation (just before spraying) the concrete flow droped to 430mm (below spec). Due to stable condicions of the face the concrete was dumped and new concrete was ordered. The face wasn't sealed imediately after excavation finished as per KT20
| 01CV - Civils | Cxxx-NCR-000962 | NCR | Segments with cracks from the centre dowel socket installed in the Eastbound Tunnel |  | Crossrail | XRL | TUX - Tunnel Drive X (West) |  | 2015-06-25 | 2015-06-29 14:10 | 4 | 2013-12-18 11:48 | Tunnelling - Linings - Precast | 5000 |  | Damaged | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Worker not correctly instructed | Completed |  | An inspection was carried out by CRL of the storage yard at WBP on the 9th Dec 2013 where 7 number segments were identified with shrinkage cracks between the centre dowel socket and the extrados of the segment. These segments do not conform with the acceptance criteria that there should be “no cracks between the centre dowel socket and the extrados of the segment." and therefore should not be installed within the permanent works. Following raising this observation it was confirmed by that 5 of these segments have been installed within the Eastbound tunnel, the details are as follows: Ring 4103 – TRL140 02-10-13 – Delivery 8904 Ring 4103 – AL85 24-06-13 – Delivery 8904 Ring 4104 – TLL145 30-09-13 – Delivery 8897 Ring 4102 – TRL139 30-09-13 – Delivery 8907 Ring 4094 – AL89 10-08-13 – Delivery 8993
| 01CV - Civils | Cxxx-NCR-000964 | NCR | SMM_FIS_No I&M report available at the SRG on 19.12.13 |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2014-01-03 | 2014-01-06 11:54 | 3 | 2013-12-19 14:34 | Surveying - Instrumentation and Monitoring | 0 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Other | Completed |  | No I&M report was available at the FIS SRG on 19.12.13. The report has not been sent on time by KGI to other attendees as KGI could not attend to the meeting. However, the report has been reviewed and distributed to all parties just after the SRG.
| 01CV - Civils | Cxxx-NCR-000966 | NCR | Excavation not according to RESS |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2014-01-22 | 2014-01-15 21:05 | -7 | 2013-12-19 18:37 | Tunnelling - Linings - Sprayed Concrete | 0 |  | System Defect | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Other | Completed |  | Due to short advance 6, when doing excavation of invert 8 the face of excavation was too close to the headwall position. The decision was made to excavate invert 6 and 11A in one go and close the full ring in a shorter period of time. The sequence was not the mentioned on the RESS.
| 01CV - Civils | Cxxx-NCR-000967 | NCR | Damage to Monitoring sections RMS in IA2 advance 4 |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2014-02-20 | 2014-02-03 06:47 | -17 | 2013-12-19 18:43 | Tunnelling - Linings - Sprayed Concrete | 2000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | During excavation of advance 5, all 5no. RMS, installed in previous advance were damaged. This occured due to reduced size of the intervention adit tunnel. The monitoring section was installed in advance 4 in order to achieve more monitoring readings, the design only requires the section to be in advance 6.
| 01CV - Civils | Cxxx-NCR-000968 | NCR | Missing Segment Report EB-2645 |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2014-03-05 | 2014-02-20 09:47 | -13 | 2014-01-14 10:38 | Civil - Tunnelling | 500 |  | System Defect | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | The Segment Control Record for the Ring 2645 in the Eastbound Tunnel is missing
| 01CV - Civils | Cxxx-NCR-000969 | NCR | Underspray of Chainage 12.0 - FIS IA2 |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2014-04-04 | 2014-03-31 17:37 | -4 | 2014-01-14 17:42 | Tunnelling - Linings - Sprayed Concrete | 10000 |  | Workmanship | Rework | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The profiles and proof drilling of chainage 12 of Intervention Adit 2, at Fisher Street site, have revealed an insufficient thickness for the primary lining. The profile is inside the theoretical profile of the primary lining as per the attached profiles.
| 01CV - Civils | Cxxx-NCR-000970 | NCR | Missing Segment Report EB-3324 |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2014-03-19 | 2014-03-06 15:55 | -13 | 2014-01-24 15:55 | Civil - Tunnelling | 500 |  | System Defect | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The Segment Control Record for the Ring 3324 in the Eastbound Tunnel is missing
| 01CV - Civils | Cxxx-NCR-000971 | NCR | December Beams in Fisher Street 28 days & 90 days |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2014-05-29 | 2014-05-30 14:54 | 1 | 2014-01-30 10:12 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Damaged | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Out of the 3 Beams tested in the month of December at 28 days. (Taken at the same time as Tunnle 1A2 Advance 8b Invert Ch 11.2 to 12.03 was sprayed) One passed on both the D1 and D3 value Two failed on both D1 and D3 Out of the 3 beams tested t 90 days One passed in both the D1 and D3 values Two failed on both the D1 and D3
| 01CV - Civils | Cxxx-NCR-000972 | NCR | Handling and storage of January monthly testing concrete panels for Intervention adit 2 |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2014-05-15 | 2014-05-15 17:15 | 0 | 2014-01-31 13:06 | Tunnelling - Linings - Sprayed Concrete | 3000 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | Panels sprayed for the January monthly testing were not stored and transported from the shaft with the appropriated method and migth compromise the test results. The panels weren't moved for 18hours but after that period and before being sent to the lab were stored in top of each other
| 01CV - Civils | Cxxx-NCR-000973 | NCR | WBX enlargement Advance 2 - Concrete not available for immediate use |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2014-04-17 | 2014-04-09 02:15 | -8 | 2014-02-13 10:08 | Tunnelling - Linings - Sprayed Concrete | 4000 |  | Supervision/Management | Use As-Is | 3 (3-6k) | Complete | Material/Preservation Problems - Other | Completed |  | When starting excavation of advance 2 in WB enlargement (top heading chainages 2.34 - 3.34) concrete was available to be sprayed. During the excavation the concrete lost flow and wasn't compliant with KT 20. New concrete was ordered but didn't arrive on site on time for the spraying of the initial. Waiting time of 3 hours for the new concrete to arrive.
| 01CV - Civils | Cxxx-NCR-000974 | NCR | Kwikastrip installation in advance 3 of WBX enlargement |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2014-03-06 | 2014-02-28 09:19 | -6 | 2014-02-13 10:37 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Training Deficiency - Insufficient practice or hands -on experience | Completed |  | The quality of Kwikastrip installed in longitudinal joint in advance 3 wasn't up to the standards. Too much initial layer was sprayed and had to be trimmed back in order to place the kwikastrip. Also, wasn’t fixed with sufficient restrictions to avoid movements during the spraying.
| 01CV - Civils | Cxxx-NCR-000975 | NCR | WBX advance 7 - Concrete early age compressive strength 2hour below J2 |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2014-03-19 | 2014-02-28 09:03 | -19 | 2014-02-18 09:02 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | Results from 2 hour concrete early age compressive strength test were below modified J2 curve as defined in KT20-01 figure.
| 01CV - Civils | Cxxx-NCR-000976 | NCR | Frame installation for VD1 a, b & c started without approved ITP |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2014-03-12 | 2014-02-25 09:39 | -15 | 2014-02-19 09:06 | Tunnelling - Tunnelling General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Other | Completed |  | During a surveillance carried out on the 11/2/14 it was found that cross passage temporary propping frame was being erected without approved ITP at VD 1 a, b & C
| 01CV - Civils | Cxxx-NCR-000978 | NCR | Major Spalling Damage to EL Segment in Ring No. 1663 of the Westbound Tunnel |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2014-03-12 | 2014-03-11 11:59 | -1 | 2014-02-19 15:11 | Civil - Tunnelling | 2000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During the crack repairs survey ring number 1663 was discovered to have some major spalling on the EL segment. The defective material was removed which was quite a sizeable amount of the structural concrete. It roughly measures 800mm x 500mm x 70mm deep.
| 01CV - Civils | Cxxx-NCR-000980 | NCR | Lord Hill's Bridge Indirects-Water Main |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2014-03-06 | 2014-02-25 12:06 | -9 | 2014-02-20 10:08 | Utilities Engineering - Water | 0 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Verification Problems - Other | Completed |  | were unable to construct the southern connection detail in accordance with the __ WSI-Lord Hill's Bridge Indirects and drawing A041-A1-20932 rev D due to the below ground obstructions encountered -9" gas main and basement. A site meeting was held between the TWUL designer, our contractor, CRL and and a reduced arrangement was agreed. TWUL issued a hand amended drawing A041-A1-20932 rev E on 25th February 2012 showing the reduced arrangement. The southern connection detail was constructed to this revised drawing. The red line drawing produced Cxxx--U-DWG-CRT00_ST005-50024 X01 failed to show the descoped fittings.
| 01CV - Civils | Cxxx-NCR-000981 | NCR | Damage of steel mesh in primary lining invert of advance 14 of WBX |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2014-03-12 | 2014-03-11 15:26 | -1 | 2014-02-20 12:40 | Tunnelling - Linings - Sprayed Concrete | 1000 |  | Damaged | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During excavation of invert advance 14 and 18, the A393 mesh installed in the previous invert (advance 10/16) was damaged/oversprayed and overlapping between advances wasn't possible. An extension equivalent to 2no. sqaures should have been left for overlaping with the following advance. Bars were drilled and reinforcement re-installed as per design, 18 x B10 Dowel bars fixed into previous advance to replace damaged mesh
| 01CV - Civils | Cxxx-NCR-000982 | NCR | Inadequate Spraying of Kwika Strip (Advances 17/18 WBX Enlargement Section AA Invert/Bench) |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2014-03-20 | 2014-03-15 17:55 | -5 | 2014-02-21 18:17 | Tunnelling - Linings - Sprayed Concrete | 2000 |  | Damaged | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | When excavating invert Advance 18 a 1 metre length of the kwika strip was caught by the excavator bucket and riiped from the SCL lining.
| 01CV - Civils | Cxxx-NCR-000983 | NCR | Excavation of advance 19 in WBX enlargement not sealed immediately after end of excavation |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2014-03-26 | 2014-03-23 19:42 | -3 | 2014-02-26 09:51 | Tunnelling - Linings - Sprayed Concrete | 1000 |  | Equipment Breakdown | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate resources | Completed |  | After completion of excavation for advance 19 in WBX enlargement, the open excavation wasn’t immediately sealed due to concrete out of spec and broken down of the 3 available spraying equipment’s on site. Excavation opened for approx. 5 hours.
| 01CV - Civils | Cxxx-NCR-000984 | NCR | Early age results at 2 hours below modified J2 curve in advances 9 & 18 |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2014-03-26 | 2014-03-15 20:39 | -11 | 2014-02-26 10:34 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Early age results at 2 hours below modified J2 curve in advances 9 & 18 and no 4 hour testing was done
| 01CV - Civils | Cxxx-NCR-000986 | NCR | Low fresh fibre washout results - FIS - Dec 2013 and Feb 2014 |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2014-04-17 | 2014-04-04 23:21 | -13 | 2014-03-03 17:24 | Tunnelling - Linings - Sprayed Concrete | 500 |  | System Defect | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Not Defined | Completed |  | Fibre washout tests undertaken for samples FIS - 3 (13/12/2014) and FIS - 14 (18/02/2014) do not meet KT20 as the average fibre content of three 10 litre samples is below 35kg/m3. 32Kg/M3 for FIS -3 and 32.3Kg/m3 for FIS -14
| 01CV - Civils | Cxxx-NCR-000987 | NCR | Low concrete early age strength at advance 26 WBX |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2014-04-17 | 2014-04-17 23:23 | 0 | 2014-03-05 18:12 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | Early age strength values of the concrete sprayed in advance 26 where very low and below modified J2. No full early age test was planned for that advance but results from the lining were low. No advance started until minimum required strength achieved
| 01CV - Civils | Cxxx-NCR-000988 | NCR | Insufficient Early Age Strength testing results for Advance 33 |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2014-04-30 | 2014-04-20 06:25 | -10 | 2014-03-10 14:06 | Civil - Tunnelling | 500 |  | Testing and Commissioning | Use As-Is | 4 (0.5-3k) | Complete | Verification Problems - Other | Completed |  | Panel was sprayed in advance 33 for a full early age testing set. Testing was done for 10mnts, 30mnts, 1 hour, 2 hour and half of the 4hour required testing (as per attached). Due to non-related incident no further results from that panel were obtained
| 01CV - Civils | Cxxx-NCR-000989 | NCR | FIS - Early Age Strength tests up to 4hrs missing for Advance 36 |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2014-04-09 | 2014-04-01 12:41 | -8 | 2014-03-10 14:57 | Civil - Tunnelling | 500 |  | Testing and Commissioning | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | A test panel was not sprayed for Early Age Strength testing on Advance 36. During shift handover it was decided to test the primary lining insitu for advance 36 to allow for 4hr, 6hr and 12hr results. Advance 35 was missed to allow for the ring to be closed out and safe stop to be put in place. Results prior to the 4hr test were not taken on Advance 36.
| 01CV - Civils | Cxxx-NCR-000990 | NCR | FIS - Insufficient profiles for advance 33 CH15.6 and CH16.6 |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2014-03-31 | 2014-03-31 13:39 | 0 | 2014-03-10 18:13 | Civil - Tunnelling | 1000 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | Missing excavation profile at chainage 15.6 of advance 33 invert. Missing profiles for advance 33 chainage 16.6
| 01CV - Civils | Cxxx-NCR-000991 | NCR | FIS - Insufficient coverage of excavation profiles in advance 36 CH 17.6 bench |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2014-04-23 | 2014-04-20 06:26 | -3 | 2014-03-10 18:34 | Civil - Tunnelling | 1000 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Insufficient cover f the excavation profile in the bench of advance 36 chainage 17.6.
| 01CV - Civils | Cxxx-NCR-000993 | NCR | Fallout of shotcrete in the crown during spraying of primary lining advance 34 TH WBX |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2014-04-16 | 2014-04-08 00:36 | -8 | 2014-03-17 09:39 | Tunnelling - Linings - Sprayed Concrete | 5000 |  | Damaged | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Fallout of shotcrete in the crown from 12:00 to 02:00 during spraying of the primary lining, leaving delaminated areas within the remaining lining which required remedial works prior to complete spraying of primary to final profile
| 01CV - Civils | Cxxx-NCR-000995 | NCR | Eastbound Tunnel Alignment - Wriggle Survey ROP – Ch 1324(Pad West) |  | Contr | KIR | TUX - Tunnel Drive X (West) |  | 2014-05-19 | 2014-05-14 13:36 | -5 | 2014-03-20 15:51 | Civil - Tunnelling | 5000 |  | Workmanship | Use As-Is | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Further to close out of the main survey control (ROP-FAR) and subsequent completion of the eastbound tunnel wriggle survey, it is noted that some parts of the final tunnel alignment are outside of the specified alignment tolerances stated in KT10.4221-4222. Wriggle Survey Report for the eastbound tunnel Cxxx--C4-RGN-CRT00_ST005-50905 details the as-built alignment.
| 01CV - Civils | Cxxx-NCR-000996 | NCR | Eastbound Tunnel Alignment - Wriggle Survey Ch 1564 (Pad East) – Ch 1900 |  | Contr | KIR | TUX - Tunnel Drive X (West) |  | 2014-10-29 | 2014-10-27 17:52 | -2 | 2014-03-20 15:57 | Civil - Tunnelling | 10000 |  | Workmanship | Use As-Is | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Further to close out of the main survey control (ROP-FAR) and subsequent completion of the eastbound tunnel wriggle survey, it is noted that some parts of the final tunnel alignment are outside of the specified alignment tolerances stated in KT10.4221-4222. Wriggle Survey Report for the eastbound tunnel Cxxx--C4-RGN-CRT00_ST005-50905 details the as-built alignment.
| 01CV - Civils | Cxxx-NCR-000997 | NCR | Eastbound Tunnel Alignment - Wriggle Survey Ch 1901 – CH 3400 |  | Contr | KIR | TUX - Tunnel Drive X (West) |  | 2014-05-19 | 2014-04-08 08:28 | -41 | 2014-03-20 16:00 | Civil - Tunnelling | 1000 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Further to close out of the main survey control (ROP-FAR) and subsequent completion of the eastbound tunnel wriggle survey, it is noted that some parts of the final tunnel alignment are outside of the specified alignment tolerances stated in KT10.4221-4222. Wriggle Survey Report for the eastbound tunnel Cxxx--C4-RGN-CRT00_ST005-50905 details the as-built alignment
| 01CV - Civils | Cxxx-NCR-000998 | NCR | Eastbound Tunnel Alignment - Wriggle Survey Ch 3401 – Ch 3708 (BOS West) |  | Contr | KIR | TUX - Tunnel Drive X (West) |  | 2014-05-19 | 2014-05-16 17:00 | -3 | 2014-03-20 16:03 | Civil - Tunnelling | 3000 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Further to close out of the main survey control (ROP-FAR) and subsequent completion of the eastbound tunnel wriggle survey, it is noted that some parts of the final tunnel alignment are outside of the specified alignment tolerances stated in KT10.4221-4222. Wriggle Survey Report for the eastbound tunnel Cxxx--C4-RGN-CRT00_ST005-50905 details the as-built alignment.
| 01CV - Civils | Cxxx-NCR-000999 | NCR | Eastbound Tunnel Alignment - Wriggle Survey Ch 3957 (BOS East) – Ch 4764 (TCR West) |  | Contr | KIR | TUX - Tunnel Drive X (West) |  | 2014-09-30 | 2014-10-09 16:52 | 9 | 2014-03-20 16:06 | Civil - Tunnelling | 1000 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Further to close out of the main survey control (ROP-FAR) and subsequent completion of the eastbound tunnel wriggle survey, it is noted that some parts of the final tunnel alignment are outside of the specified alignment tolerances stated in KT10.4221-4222. Wriggle Survey Report for the eastbound tunnel Cxxx--C4-RGN-CRT00_ST005-50905 details the as-built alignment.
| 01CV - Civils | Cxxx-NCR-001000 | NCR | Eastbound Tunnel Alignment - Wriggle Survey Ch 4999 (TCR East) – Ch 7007 (Farringdon West) |  | Contr | KIR | TUX - Tunnel Drive X (West) |  | 2014-06-06 | 2014-06-06 20:35 | 0 | 2014-03-20 16:10 | Civil - Tunnelling | 1000 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Further to close out of the main survey control (ROP-FAR) and subsequent completion of the eastbound tunnel wriggle survey, it is noted that some parts of the final tunnel alignment are outside of the specified alignment tolerances stated in KT10.4221-4222. Wriggle Survey Report for the eastbound tunnel Cxxx--C4-RGN-CRT00_ST005-50905 details the as-built alignment.
| 01CV - Civils | Cxxx-NCR-001001 | NCR | Filling of quality cores in the WBX primary lining with non-approved material |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2014-09-09 | 2014-09-03 17:48 | -6 | 2014-03-25 09:36 | Tunnelling - Tunnelling General | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | When filling the quality cores in the primary lining of WBX, at invert level, the used material (5 star grout) was not approved via MCR. The location and number of holes are not recorded.
| 01CV - Civils | Cxxx-NCR-001002 | NCR | Low fresh fibre washout results - FIS - Feb 2014 |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2014-06-26 | 2014-05-28 00:51 | -29 | 2014-03-25 10:21 | Tunnelling - Linings - Sprayed Concrete | 1000 |  | System Defect | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | Fibre washout test undertaken for samples FIS - 16 (19/02/2014) does not meet KT20 as the average fibre content of three 10 litre samples is below 31.5kg/m3 ( 29.1 kg/m3)
| 01CV - Civils | Cxxx-NCR-001003 | NCR | FIS IA1 - Over Excavation of Chainage 1.0 / Advance 2 |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2014-06-10 | 2014-06-11 00:04 | 1 | 2014-04-01 08:44 | Tunnelling - Linings - Sprayed Concrete | 1000 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The profile of chainage 1.0 of Intervention Adit 1, at Fisher Street site, have revealed an over excavation profile. The profile of over excavation as per attached.
| 01CV - Civils | Cxxx-NCR-001005 | NCR | FIS WBX February Monthly testing - 28 and 90 Days Residual Flexural Tensile Strength Failures (Sprayed 19/02/2014 )- Advance 14 |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2014-09-04 | 2014-09-03 17:35 | -1 | 2014-04-03 08:57 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Testing and Commissioning | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | 28 days Sample Number FIS0032-.37+.38 beams failed to reach both specified Residual Flexural Tensile Strength of >1.8 at D1S and >1.4 at D3S for 28 day result. Results of D1S and D3S for samples .37 and .38 were 0.00 (D1S), 0.00 (D3S) for both. Abrupt failures recorded on both, so load applied over shortened test period. Sample .39 gave results of 1.74 (D1S), 1.13 (D3S) (FAIL). 90days - 1 beam close to the requirements (1.83<2.0; 1.43>1.4), beam with zero results (0<1.4; 0<2.0); beam with 1 posite and 1 negative result (4.04>2; 0.08>1.4)
| 01CV - Civils | Cxxx-NCR-001006 | NCR | Concrete out of spec during excavation of advance 10 IA1 |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2014-05-08 | 2014-05-04 14:36 | -4 | 2014-04-02 19:29 | Tunnelling - Linings - Sprayed Concrete | 0 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | During excavation of advance 10 IA1 the concrete on site went out of spec. Fresh concrete was ordered and arrived before excavation was finished. Old concrete dumped and fresh concrete used. Back up plant and mix (Picccola and ready mix) on site and ready to use if concrete not available by the end of excavation.
| 01CV - Civils | Cxxx-NCR-001007 | NCR | Overalls cast into FSC slab |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2014-05-20 | 2014-05-20 18:07 | 0 | 2014-04-03 11:50 | Civil - Civil Engineering General | 1000 |  | Supervision/Management | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Contamination | Completed |  | An operative discarded a pair of overalls in the invert pour beside the construction joint. The overalls were not removed before the concrete set.
| 01CV - Civils | Cxxx-NCR-001008 | NCR | Materials cast in slab that were not approved via MCR |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2014-05-08 | 2014-04-30 08:49 | -8 | 2014-04-03 12:09 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | For the drainage support in the FSC unistrut was used over a distance of 25 rings to support the drainage pipework. This material has not been approved via the MCR system.
| 01CV - Civils | Cxxx-NCR-001009 | NCR | Early age strenght results below modified J2 curve in Advance 14 - IA1 |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2014-04-30 | 2014-04-29 18:32 | -1 | 2014-04-07 10:27 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Testing and Commissioning | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | For Advance 14, IA1 adit tunnel, an early age strength (Penetrometer) test failed to meet the specified strengths of 0.52 and 0.78 Mpa at 1 and 2 hrs old respectively
| 01CV - Civils | Cxxx-NCR-001010 | NCR | Lining thickness in chainage 2.5 IA1 |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2014-05-15 | 2014-05-07 09:04 | -8 | 2014-04-12 15:15 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | When drilling quality cores in the lining of IA1 chainage 2.5 it was realized that an area of the lining had thickness around 300 mm. Design thicknesses in that area is 400mm. Further proof drill records show that area is restricted to approx. size of 260x600mm Rest of the lining with thickness above 450mm
| 01CV - Civils | Cxxx-NCR-001011 | NCR | Ove__raying on primary lining of Intervention adit 1 - chainage 0 to 9.5 |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2015-08-31 | 2015-09-11 02:27 | 11 | 2014-04-16 08:34 | Tunnelling - Linings - Sprayed Concrete | 5000 |  | Workmanship | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During excavation and Primary lining of Intervention adit 1 some areas are over sprayed and/or below the tolerances. Chainages are identified in attached table and areas marked in the as built sections. Thickness calculation show that when removing the oversprayed areas the lining is still according to the design
| 01CV - Civils | Cxxx-NCR-001012 | NCR | Eastbound TBM (2) Encapsulation - Grout Records |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2014-05-28 | 2014-05-13 18:55 | -15 | 2014-04-16 16:52 | Civil - Tunnelling | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | During the encapsulation works for the burial of the Eastbound TBM (2) at Farringdon, no material testing (compressive strength) was undertaken on the grout mixtures injected to fill any remaining void space within the excavation chamber and fill the annular space surrounding the shield.
| 01CV - Civils | Cxxx-NCR-001013 | NCR | Scabbling area between the kerb and invert |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2015-01-31 | 2015-02-02 08:36 | 2 | 2014-04-21 16:07 | Civil - Civil Engineering General | 2000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The a section between the kerb and invert concrete has been over-scabbled by 90mm along a 20m length of tunnel just west of TCR in the WB tunnel.
| 01CV - Civils | Cxxx-NCR-001014 | NCR | Insufficient Early Age Strength testing results for Advance 39 |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2014-05-31 | 2014-05-07 12:59 | -24 | 2014-04-23 10:48 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | For Advance 39, an early age strength test failed to meet the specified strengths of modified J2 curve, 0.52 and 0.78 Mpa at 1 and 2 hrs old respectively
| 01CV - Civils | Cxxx-NCR-001015 | NCR | Failing to adhere to RESS WBX - 038 during Installation of Reinforcement in Advance 55 |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2014-05-09 | 2014-05-07 03:29 | -2 | 2014-04-25 17:27 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | RESS No WBX38 specifies reinforcement in the invert should be 16@150FF/16@150NF (As per Section C-C of reinforcement drawing reference Cxxx-MMD-C4-DDD-CR086_SH003_5-01001). Drawing reference Cxxx-MMD-C4-DDB-CR086_SH003_02013 shows the start of Section C-C at SOP .0209, this equates to chainage 30.10 of the Westbound cavern. As advance 55 terminates at chainage 30.34, and has a leading edge of 300mm the reinforcement for this advance falls in the Section B-B. The reinforcement installed in advance 55 corresponds with that shown on drawing Cxxx-MMD-C4-DDD-CR086_SH003_5-01001 for section B-B.
| 01CV - Civils | Cxxx-NCR-001016 | NCR | Missing early age strenght results for Advance 57 |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2014-05-19 | 2014-05-19 16:20 | 0 | 2014-04-28 18:05 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Testing and Commissioning | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | Missing data for early age strength results of 2 hrs. and 4 hrs. for advance 57 (Top Heading).
| 01CV - Civils | Cxxx-NCR-001018 | NCR | Overexcavation in chainage Advance 63 WBX (Invert) |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2014-07-31 | 2014-07-31 15:23 | 0 | 2014-04-29 17:47 | Tunnelling - Linings - Sprayed Concrete | 1000 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | During excavation of invert 63, in order to open the full leght of the kwikastrip box, the face was over excavated approx. 800mm on the left side. Face should have stayed back at the correct chainage as per RESS and kwikastrip box opened with the following invert
| 01CV - Civils | Cxxx-NCR-001019 | NCR | Missing geotechnical face log for Advance 61 |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2014-05-13 | 2014-05-14 00:01 | 1 | 2014-04-29 18:21 | Geotechnical Engineering - Geotechnical Engineering - General | 500 |  | Incomplete Works | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | Due to mandatory briefing " Stepping Up ", geotechnical engineer was not present at the face to complete face log for Advance 61, shift engineer didn't take the picture of the face
| 01CV - Civils | Cxxx-NCR-001021 | NCR | Ambient Temperature no longer a check on latest revision of BFK 050 |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2014-05-23 | 2014-05-22 16:32 | -1 | 2014-05-02 16:08 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Verification Problems - Inspection points not adequate | Completed |  | During recent updates to Form 050 the box that recorded ambient temperature has been deleted mistakenly. This was noticed during a quality surveillance of advance 51 of westbound tunnel in Fisher street the check sheet has been attached.
| 01CV - Civils | Cxxx-NCR-001022 | NCR | Missig Drillers Log for Shallow Datum Catton Street |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2014-06-06 | 2014-06-05 16:22 | -1 | 2014-05-16 16:12 | Surveying - Instrumentation and Monitoring | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The drillers log related to shallow datum LP9000027 is not available and is unlikely to be found within the records. This will also affect the Installation Report content for Catton Street SD number: Cxxx--C4-RGN-CRT00_ST005-50744.
| 01CV - Civils | Cxxx-NCR-001023 | NCR | Quality of spraying in primary lining of inverts advance 75 and 71 in WBX |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2014-08-31 | 2014-07-28 22:34 | -34 | 2014-05-10 12:02 | Tunnelling - Linings - Sprayed Concrete | 15000 |  | Workmanship | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Quality cores taken from invert 71 and 75 WBX show bad encapsulation, shadowing and land layers. Cores have been grade 4 and 5 levels. Other cores taken from invert 67, 78 and 80 show better quality.
| 01CV - Civils | Cxxx-NCR-001024 | NCR | Cross passage CP4A - Overspray on primary lining advance 6 |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2014-09-30 | 2014-09-30 07:52 | 0 | 2014-05-19 12:20 | Tunnelling - Linings - Sprayed Concrete | 3000 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Cross passage CP4A primary lining in advance 6 (ch. 8.35) has been over-sparayed by 20-50mm in location between 11 and 1o'clock, and by 20mm in position of 7o'clock. Since excavation profiles show that sufficient thickness will be still in place if we partially remove concrete in over-sprayed areas -we propose to use roadheader to trim concrete back to designed primary lining profile. re-surveying will be done after trimming works completed.
| 01CV - Civils | Cxxx-NCR-001025 | NCR | Cover of Rebar not to 75mm MINIMUM requirement |  | Crossrail | PDP | TUX - Tunnel Drive X (West) |  | 2014-07-24 | 2014-07-16 12:55 | -8 | 2014-05-20 09:32 | Civil - Civil Engineering General | 2500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | On 12/05/2014 works progressed installing reinforcement to the -6 level of the NE Corner to the BOS WTH, these works progressed without considering the asbuilt of the couplers in a diaphragm wall panel. After trying to fix reinforcement numerous times and not achieving the required minimum cover to the reinforcement it was eventually realised that the reinforcement had to be removed. Upon surveying the couplers Cxxx-FCD-00913 refers, most were in tolerance. Due to the as built angles of couplers it was realised that an additional 100mm was required to allow for the reinforcement projection direction.
| 01CV - Civils | Cxxx-NCR-001026 | NCR | Quality of profiles for Advance 62,63,65,66 & 67 |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2014-06-19 | 2014-06-13 23:05 | -6 | 2014-05-22 13:56 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Incomplete Works | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The excavation as builts submitted in the SRG have been missing some points logs in the profile.
| 01CV - Civils | Cxxx-NCR-001028 | NCR | CP4a - SCL Advance 4 Overspray |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2014-09-30 | 2014-09-26 16:46 | -4 | 2014-05-22 16:07 | Tunnelling - Linings - Sprayed Concrete | 2000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Overspray approximately between 7-8 o'clock around profile
| 01CV - Civils | Cxxx-NCR-001029 | NCR | FSC slab broken out between rings 2397-2400 in the WB tunnel. |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2014-06-05 | 2014-06-05 17:04 | 0 | 2014-05-22 14:46 | Civil - Civil Engineering General | 2000 |  | Incomplete Works | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During a FSC pour we encountered problems with the concrete pump, i.e. it broke down. Due to this we could not get enough concrete down the tunnel to form a correct vertical faced construction joint.
| 01CV - Civils | Cxxx-NCR-001031 | NCR | CP4a - SCL Advance 5 Overspray |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2014-09-30 | 2014-09-26 16:48 | -4 | 2014-05-22 16:07 | Tunnelling - Linings - Sprayed Concrete | 2000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Overspray at approximately 6 o'clock around the profile.
| 01CV - Civils | Cxxx-NCR-001032 | NCR | CP4a -SCL Advance 7 Overspray |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2014-09-30 | 2014-09-30 07:55 | 0 | 2014-05-22 16:08 | Tunnelling - Linings - Sprayed Concrete | 5000 |  | Workmanship | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Advance 7- Overspray between 5 to 8 o'clock around the profile.
| 01CV - Civils | Cxxx-NCR-001033 | NCR | CP4a - SCL Advance 8 Overspray |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2014-10-28 | 2014-10-24 12:36 | -4 | 2014-05-22 17:20 | Tunnelling - Linings - Sprayed Concrete | 5000 |  | Workmanship | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Overspray - Approximately 5 to 8 o'clock and 9 o'clock.
| 01CV - Civils | Cxxx-NCR-001034 | NCR | Fisher Street Shaft Base Slab -Earthing mat resistivity testing |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2014-06-12 | 2014-06-11 00:08 | -1 | 2014-05-22 17:27 | Shafts - Shafts General | 1000 |  | Testing and Commissioning | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Earthing specification (BS BS7430, BS EN 62305, JW51.1203 a) & Cxxx-MMD-C4-DDD-CR086_SH003) requires soil mass resistivity to be measured in the ground and reported prior commencing the earthing. However, the resistance of the rods was taken instead.
| 01CV - Civils | Cxxx-NCR-001035 | NCR | Damages to monitoring points in the invert - WBX Fisher Street |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2014-08-31 | 2014-07-10 15:23 | -52 | 2014-05-23 09:21 | Tunnelling - Linings - Sprayed Concrete | 5000 |  | Damaged | Use As-Is | 3 (3-6k) | Complete | Discipline/Workmanship - Other | Completed |  | Invert monitoring points installed in WBX invert have been constantly damaged and the frequency of the readings as per Cxxx monitoring plan is compromised due to zero readings
| 01CV - Civils | Cxxx-NCR-001036 | NCR | Installation of reinforcement in advance 82 and 83 WBX fisher Street |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2014-08-31 | 2014-08-08 08:16 | -23 | 2014-05-23 09:40 | Tunnelling - Linings - Sprayed Concrete | 2000 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Bar mark 20 for the reinforcement in advances 82 and 83 of WBX was installed with splicing instead of a single bar as per drawing. Bar mark 19 was installed instead of 20. Bar mark 19 was shorter and had to be extended to be the same length as 20
| 01CV - Civils | Cxxx-NCR-001038 | NCR | Location of S2 SGI Opening Set |  | Contr | KIR | TUX - Tunnel Drive X (West) |  | 2014-07-22 | 2014-07-02 14:00 | -20 | 2014-05-23 13:44 | Civil - Tunnelling | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | have checked the design position of the S2 opening (measured at adit CL) as shown on the Cxxx drawings and compared it against the as-built position: - Cxxx = Ch 5016.072 (SGI opening set positions +/-300mm) - As-built = 5016.393 The as-built is 20mm out of tolerance. Please confirm this is acceptable
| 01CV - Civils | Cxxx-NCR-001039 | NCR | Geotechnical Face Log not produced for Advance 99 of WBX (Part 2) |  | Crossrail | XRL | TUX - Tunnel Drive X (West) |  | 2014-07-30 | 2014-08-01 14:52 | 2 | 2014-05-25 03:46 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Incomplete Works | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | Due to shift geotechnical engineer covering concurrent Works at TCR, FIS and CP4a SCL sites, he was not present at the face to produce a face log for Advance 99 (Bench) of WBX (Part 2). The shift engineer did not take photographs of the face either.
| 01CV - Civils | Cxxx-NCR-001040 | NCR | Missing Early Age Shotcrete Strength Results for Advance 95 of WBX (Part 2) |  | Crossrail | XRL | TUX - Tunnel Drive X (West) |  | 2014-06-24 | 2014-06-25 09:28 | 1 | 2014-05-25 04:35 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Testing and Commissioning | Use As-Is | 4 (0.5-3k) | Complete | Personnel Error - Verbal communication problem | Completed |  | Early Age Shotcrete Strength Results at 2 hours and 4 hours not taken/recorded for test panel sprayed on completion of Advance 95 (Invert) of WBX (Part 2)
| 01CV - Civils | Cxxx-NCR-001041 | NCR | CP4a - Advance 10 - No concrete at face |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2014-06-08 | 2014-06-03 17:55 | -5 | 2014-05-25 11:01 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate resources | Completed |  | CP4a - Advance 10 - Shotcrete testing found to be out of flow test specification at face. Shotcrete was Rejected. Unable to replace Shotcrete immediately onsite thus leaving the face open - Works had to wait for more shotcrete which eventually arrived after 6 hours due to heavy traffic between batching plant and TCR. On new delivery of shotcrete it was also found to be out of spec- TCR SCL team eventually supplied CP4a with shotcrete.
| 01CV - Civils | Cxxx-NCR-001042 | NCR | Catch Pit Location in Westbound Tunnel in HAS section |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2015-04-15 | 2015-04-16 00:44 | 1 | 2014-05-26 14:29 | Civil - Tunnelling | 10000 |  | Incorrect Installation | Use As-Is | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | In the Westbound tunnel two catch pits have been missed. These are at Ch1705.39 (ring 748) and CH1665.43 (ring 723). Therefore there is currently 120m gap between Catch pits.
| 01CV - Civils | Cxxx-NCR-001043 | NCR | WBX Fisher Street - Encapsulation of reinforcement in advances 93 and 96 in the crown of sidewall drift |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2014-07-10 | 2014-07-13 01:11 | 3 | 2014-05-28 10:34 | Tunnelling - Linings - Sprayed Concrete | 150000 |  | Manufacturing Defect | Repair | 1 (>60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Cores taken in the crown of WBX sidewall drift advances 89 to 97 (chainages 5.06 to 9.91) show poor encapsulation. Encapsulation of reinforcement in the far face (FF) is not according to requirements – Bar mark 13 and 17. Remaining lining has good quality, it is identified a layer of approx. 50mm to 100mm with poor concrete quality. Area has been identified has being up to 700mm of the joint (area of congestion reinforcement).
| 01CV - Civils | Cxxx-NCR-001044 | NCR | Low early strength results for advances 100 and 105 of WBX Fisher Street |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2014-07-10 | 2014-07-03 12:41 | -7 | 2014-06-02 11:40 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | Early strength results obtained in advances 100 and 105 in WBX show values below modified J2. Advance 100 – 2 hour testing 0.69Mpa < 0.78MPa (+/- 10%) Advance 105 – 1hour testing 0.43Mpa < 0.5MPa (+/- 10%) Low results due to spraying with low accelerator dosage for better reinforcement encapsulation
| 01CV - Civils | Cxxx-NCR-001046 | NCR | Pre-Condition Survey Information - I&M General |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2014-06-17 | 2014-06-10 11:16 | -7 | 2014-06-03 08:57 | Surveying - Instrumentation and Monitoring | 500 |  | Planning | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | The works specification, KX10.2111 (a) (ii), requires a pre-installation condition survey to be included within installation reports. However, Pre-installation condition surveys for the installation of some I&M instruments, have not been undertaken in accordance with the specification.
| 01CV - Civils | Cxxx-NCR-001047 | NCR | FIS WBX Early age strength & Compressive strengths every 50m^3 |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2014-09-29 | 2014-09-28 10:15 | -1 | 2014-06-18 10:34 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | In WBX tunnel advance 6 the 1 hour and 2 hour results both fell below the J2 requirement In advance 78 the 2 hour result fell below the J2 requirement. In advance 95 of WBX Part 1 & 2 there was no 2 or 4 hour test done. In advance 98 the 1 hour test fell below the 1 hour requirement. Between advances 60 & 64, 78 & 82 and 91 & 95 the tests have occurred on the 4th advance and not the required 3rd advance. In WBX tunnel at FIS there was a gap greater than 50m3 between compressive strength cores between advances 30 to 39 (69m3) and between advance 75 to 85 (82m3). 28 day results have been taken at advance 79 but the gap in 1 day results is greater than 50m3 between 75 and 85.
| 01CV - Civils | Cxxx-NCR-001048 | NCR | Early age strength |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2014-06-24 | 2014-06-25 09:49 | 1 | 2014-06-03 16:37 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | All from Tunnel IA2; FIS0011 (Advance 8B - Invert) - missing 10+30 min, 1,2 and 4 hour test. FIS0010 (Advance 8A - Invert) - missing 10+30 min, 1,2 and 4 hour test. FIS0009 (Advance 8 - Invert) - missing 10+30 min test FIS0007 (Advance 2 - Heading) - 2 hr test under strength (0.71 MPa). No 4 hour test performed FIS0006 (Pre-spraying panel) - 2 hr test under strength (0.66 MPa). No 4 hour test performed
| 01CV - Civils | Cxxx-NCR-001049 | NCR | Rebound Test Not performed at correct frequency |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2014-06-27 | 2014-06-26 23:26 | -1 | 2014-06-06 14:54 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | SCL work has been ongoing since December. No works in January, long stoppage in March. Rebound test should have taken place in February and April, instead first test took place in May.
| 01CV - Civils | Cxxx-NCR-001050 | NCR | No 1/2/3 day cores for compressive strength sample taken on 18/12/13 |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2014-07-15 | 2014-07-08 16:35 | -7 | 2014-06-06 15:05 | Tunnelling - Linings - Sprayed Concrete | 1500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | No 1/2/3 day cores for compressive strength sample taken on 18/12/13
| 01CV - Civils | Cxxx-NCR-001051 | NCR | Fisher Street cavern - Position of reinforcement (Bar mark 13 and 14) in joint between advances 84 RHS WBX2 and 107 LHS WX3 |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2014-08-06 | 2014-07-30 00:39 | -7 | 2014-06-11 11:33 | Tunnelling - Linings - Sprayed Concrete | 1500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | It was noticed during preparation of the joint and reinforcement installation in advance 107 in the left side enlargement of side wall drift (WBX), that bar mark 13 and 14 with couplers from the right hand side of enlargement side wall drift (advance 84 RHS) were installed in a lower position, not allowing the installation of continuity bars as per design. Bars were approx. 200mm lower in terms of vertical position. Advance was excavated and sealed during the joint preparation and installation of primary lining was required as soon as possible in order to complete the advance. Bar mark with an embedement of 500mm and bar mark 14 embedement of approx. 850mm. Resin used was __ HY 150
| 01CV - Civils | Cxxx-NCR-001053 | NCR | Missing signatures on SCL Waterproof System -Repair Form 93 |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2014-11-20 | 2014-11-17 12:04 | -3 | 2014-06-12 10:08 | Shafts - Shafts General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | Some of the Waterproof System - Repair Form 93 checksheet for Fisher Street shaft waterproofing , have not been fully signed.
| 01CV - Civils | Cxxx-NCR-001054 | NCR | Early Age Strength |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2014-07-12 | 2014-07-03 12:39 | -9 | 2014-06-12 17:37 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | FIS0034 WBX-1 Tunnel, Adv 18. Failed 2 hour test, no 4 hour test performed. FIS0047 Intervention Adit 1, Adv 2. Failed 2 hour test, no 4 hour test performed. FIS0049 Intervention Adit 1, Adv 5. Failed 2 hour test, no 4 hour test performed. Intervention Adit 1, Adv 8, 31.03.2014. No Early Age Strength test performed.
| 01CV - Civils | Cxxx-NCR-001056 | NCR | Long-Term Compressive Strength |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2014-07-16 | 2014-07-11 15:28 | -5 | 2014-06-16 16:21 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | FIS0028: Only 3 Cores taken for 1/2/3 day compressive strength instead of six FIS0040: 1/2/3 day cores crushed late (7 Days) FIS0050: 28 day cores set of 3 instead of set of 6 FIS0112: 28 day cores crushed at 30 days
| 01CV - Civils | Cxxx-NCR-001058 | NCR | Catch Pits in the wrong position in the Westboudn Tunnel West of Paddington |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2014-07-15 | 2014-07-04 16:58 | -11 | 2014-06-17 10:19 | Civil - Tunnelling | 5000 |  | Incorrect Installation | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Other | Completed |  | Catch Pits, west of Paddington have been placed at the wrong chainage (currently at 1300,1257 and 1207) as opposed to 1312,1272,1232 and 1192.
| 01CV - Civils | Cxxx-NCR-001059 | NCR | Damage to HAS Kerb rebar in the Westboudn tunnel |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2014-07-15 | 2014-07-09 17:24 | -6 | 2014-06-17 10:36 | Civil - Tunnelling | 2000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Damage has occurred to the HAS Kerb rebar in the Westbound tunnel, east of Paddington.
| 01CV - Civils | Cxxx-NCR-001060 | NCR | Fisher Street - Damage to monitoring points in invert of WBX sidewall drift chainage 0.7 |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2014-07-24 | 2014-07-23 10:56 | -1 | 2014-06-20 08:55 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Improper preservation of material after installation | Completed |  | Monitoring results, of invert points, constantly being rezeroed due to being damaged during excavation of following invert.
| 01CV - Civils | Cxxx-NCR-001061 | NCR | Fisher Street - Fibre washout content sample FIS -56 average results below requirements |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2014-07-30 | 2014-07-30 02:42 | 0 | 2014-06-20 09:35 | Tunnelling - Linings - In-situ Concrete | 500 |  | Testing and Commissioning | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | Average of fibre washout test FIS-56 was 30.7Kg/m3, below min requirement of 31.5Kg/m3 The shotcrete wasn't incorporated in the works. The load was only used to spray the monthly test panels. The load details are Batchin plant: / Victoria Deep 1 Thicket number: 1973329657 Date: 04/06/2014 Mix design: 17.2
| 01CV - Civils | Cxxx-NCR-001062 | NCR | Damage to SH-W1 Slab |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2014-11-11 | 2014-10-16 17:34 | -26 | 2014-06-22 15:14 | Civil - Tunnelling | 2000 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Worker not correctly instructed | Completed |  | During excavation of the foam concrete within SH-W1 (commenced 04/03/2014) damage was sustained to the underside and opening of the slab (largely surface markings and chipping).
| 01CV - Civils | Cxxx-NCR-001063 | NCR | SH-W1 Damaged L-Bars |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2014-11-11 | 2014-10-16 17:34 | -26 | 2014-06-22 15:42 | Civil - Tunnelling | 5000 |  | Damaged | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Other | Completed |  | During excavation of the foam concrete within SH-W1 (commenced 04/03/2014) the steel reinforcement (L- bars) of the circular shaft were damaged/bent/pulled out/sheared. It is estimated that 17 No. bars have been affected.
| 01CV - Civils | Cxxx-NCR-001064 | NCR | Fisher Street WBX - Use of couplers not covered by MCR |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2014-09-23 | 2014-09-25 16:09 | 2 | 2014-06-26 09:28 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Use of unapproved materials | Completed |  | During construction of WBX sidewall drift, the use of couplers was approved via FCD #908 but the couplers were used without being approved in an MCR.
| 01CV - Civils | Cxxx-NCR-001065 | NCR | Band layers in Cross passage CP4A in-situ quality cores from SCL primary lining |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2014-09-04 | 2014-09-04 14:07 | 0 | 2014-06-27 16:55 | Tunnelling - Linings - Sprayed Concrete | 1500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Some of in-situ quality cores have got a lamination / band layers in them. Each set has a two cores taken ~150m apart. There is minimum of sandy areas present and width/depth of any voids does not exceed 1 cm. All cores show thickness of lining(380-580 mm) which considerably more than designed thickness of 250mm. As thickness of constructed lining is of excess of designed one - most of cores would have min. 250mm thick layer of "good quality" lining present. Compressive strength of 28 days old cores are between 42MPa and 45 MPa. Grading of cores show that only two set exceeds grade 2.5, for which this NCR has been raised: - Set 3 (Advance 11 - grade level 3) - possible cores were drilled at leading edge area, hence the angle lamination. - Set 8 (Advance 16 - grade level 3.5) - this area falls within Concrete collars area.
| 01CV - Civils | Cxxx-NCR-001066 | NCR | Early Age Strength |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2014-08-02 | 2014-07-30 00:41 | -3 | 2014-07-03 11:14 | Tunnelling - Linings - Sprayed Concrete | 1000 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | FIS0137, WBX part 2, Advance 100. 2 Hour test failed to reach specified strength FIS0141, WBX part 3, Advance 105. 1 Hour and 2 Hour tests failed to reach specified strength FIS0157, WBX RHS Binocular, Advance 14. 1 Hour test failed to reach specified strength FIS0145, WBX part 3, Advance 115. Frequency of testing incorrect - no panel sprayed for Advance 114 FIS0150, WBX part 3, Advance 124. Panel for Advance 123 was damaged so another was sprayed for Advance 124 instead
| 01CV - Civils | Cxxx-NCR-001067 | NCR | Long term compressive strength |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2014-08-20 | 2014-08-23 09:23 | 3 | 2014-07-07 12:16 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | FIS0116, 0121, 122, 142 and 143 - No hardened fibre content test performed on cores. FIS0127, 0140 and 0144 - 1/2/3 day test was performed late (4 days old)
| 01CV - Civils | Cxxx-NCR-001068 | NCR | Fisher Street - Underspray of headwall in Westbound binocular |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2014-09-09 | 2014-09-12 10:55 | 3 | 2014-07-08 15:41 | Tunnelling - Linings - Sprayed Concrete | 2000 |  | Supervision/Management | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Headwall of Westbound binocular located at chainage 8.5/9.0 shows some areas with under spray of approx. 100mm resulting in under thickness. Design thickness in that area is 500mm. Attached are the as builds and proof drilling results. Minimum thickness of 300mm, as required in KT20 for approx. 2 weeks, is in place.
| 01CV - Civils | Cxxx-NCR-001069 | NCR | Lack of Monitoring Data from CB6 at RMS 0.70 (WBX Part 2/3) due to Damaged Monitoring Target |  | Crossrail | XRL | TUX - Tunnel Drive X (West) |  | 2014-08-19 | 2014-08-21 15:16 | 2 | 2014-07-15 23:25 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Damaged | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Monitoring results from Target CB6 in the RMS located at Ch0.70 was not presented since it has repeatedly been damaged. This has meant that the readings of this point have been reset and this does not reflect the actual deflection of the point (and therefore, the tunnel).
| 01CV - Civils | Cxxx-NCR-001070 | NCR | CP4a -SCL Advance 3 Overspray |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2014-09-30 | 2014-09-30 08:03 | 0 | 2014-07-21 12:06 | Civil - Tunnelling | 2000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Overspray of Primary Lining at Approximately 1,3,5,6 and 7 o'clock on Survey Profile. (Attached)
| 01CV - Civils | Cxxx-NCR-001071 | NCR | Circumferential Joint Not Properly Cleaned at CH5.5 CP1 WTH BOS |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2014-08-20 | 2014-08-08 09:56 | -12 | 2014-07-21 12:23 | Tunnelling - Linings - Sprayed Concrete | 3000 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During the spraying operations to advance 2 of CP1 some shotcrete was sprayed up to the face and not left 250-300mm back to form a leading edge. Once the excavation of advance 3 commenced muck that was covered by this shotcrete was left hidden and not mucked to profile. As a result only 50mm of shotcrete was sprayed along the leading edge
| 01CV - Civils | Cxxx-NCR-001072 | NCR | FIS Panel-28 Days Residual Flexural Strength Failures (June monthly testing) |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2015-01-31 | 2015-02-03 12:55 | 3 | 2014-07-22 11:32 | Tunnelling - Tunnelling General | 500 |  | Testing and Commissioning | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | Sample FIS0142.36, sprayed on 04/06/14 failed on the 28 Day D3S1.4 criteria, achieving 1.19N/mm2 vs. 1.4N/mm2 target. Samples FIS0142.34+35 both passed the 28 + 90 Day criterion.
| 01CV - Civils | Cxxx-NCR-001073 | NCR | FIS WBX - Missing Water Penetration and Drying Shrinkage results ( May + June monthly testing) |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2014-09-04 | 2014-09-04 14:04 | 0 | 2014-07-22 12:37 | Tunnelling - Tunnelling General | 500 |  | Testing and Commissioning | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | __ is unable to report the drying shrinkage and water penetration results for the monthly testing for May and June. The results appear to have been lost
| 01CV - Civils | Cxxx-NCR-001074 | NCR | Levels of Kerbs West of Paddington in Eastbound Tunnel |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2014-10-16 | 2014-11-05 10:21 | 20 | 2014-09-01 09:26 | Civil - Tunnelling | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Levels of kerbs are out of tolerance on LHS and RHS in the Eastbound tunnel to the west of Paddington. Information provided on As Built Survey Cxxx--C4-LRC-CRT00_ST005-50420.
| 01CV - Civils | Cxxx-NCR-001075 | NCR | NCR - Major spalling Damage to CL segment in ring No. 3360 of the Westbound tunnel. |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2014-10-08 | 2014-10-14 08:41 | 6 | 2014-07-25 09:22 | Civil - Tunnelling | 1000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During the crack repairs survey ring number 3360 was discovered to have some major spalling on the CL segment. Note that the gasket was not damaged. The defective material was removed which was quite a sizeable amount of the structural concrete. It roughly measures 400mm x 600mm x 125mm deep. No damage observed to the gasket.
| 01CV - Civils | Cxxx-NCR-001076 | NCR | Use of wrong link in HAS section |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2014-09-05 | 2014-08-15 16:59 | -21 | 2014-07-29 08:15 | Civil - Tunnelling | 2000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The use of the wrong link (attachment illustarates what is use) but the cover is still acheived on both sides. This is the case on the LHS inbye from rings 3500-3479. On the RHS inbye (rings 3500-3473) , the same link is used and no cover is achieved there. This section will be removed and drilled again and installed correctly with the new links.
| 01CV - Civils | Cxxx-NCR-001077 | NCR | Eastbound Tunnel LHS kerb pour area at ring 381 untidy before pour |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2014-09-25 | 2014-09-25 13:39 | 0 | 2014-08-03 12:26 | Civil - Tunnelling | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | Before pouring kerbs in the eastbound, CRL inspected the pour area and found it untidy. Pre pour checks were not done sufficiently. CRL stopped pour until tidied. This took place at ring 381 LHS in the Eastbound tunnel.
| 01CV - Civils | Cxxx-NCR-001078 | NCR | No monthly tests completed for Crosspassage CP1 |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2014-09-15 | 2014-09-12 17:22 | -3 | 2014-07-30 10:44 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Planning | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | According to RFI Cxxx 1127 monthly test results could be used from BOS SCL for CP 2, 3 & 4. This meant that for CP1 separate tests should have happened. This did not happen. Which means monthly tests should have occurred in June and July for CP1. Tests that have not occureed are, B3.4 Depth of water penetration B3.5 Flexural strength B3.6 Fibre content and compressive strength of sprayed concrete for beam tests 1 set per month B3.7 Concrete drying shrinkage 1 set per month B3.8 Rebound test 1 test every 2 months
| 01CV - Civils | Cxxx-NCR-001079 | NCR | Incorrect Setting Out CP1 WBP Running Tunnels |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2014-08-29 | 2014-08-08 09:50 | -21 | 2014-07-30 15:53 | Tunnelling - Linings - Sprayed Concrete | 2000 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Due to setting out error the profile has been sprayed incorrectly
| 01CV - Civils | Cxxx-NCR-001080 | NCR | Damage to Permanent Running Tunnel Precast Concrete Segments at FIS |  | Crossrail | XRL | TUX - Tunnel Drive X (West) |  | 2015-09-15 | 2015-09-22 11:38 | 7 | 2014-08-01 08:11 | Tunnelling - Linings - Precast | 10000 |  | Damaged | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Insufficient information made available to the worker. | Completed |  | The permanent precast concrete segments in the vicinity of Cross passage No. 5 have been cored through for depressurisation purposes. Some of the cores have been taken through the joints of the segments thereby damaging the gaskets of the segments which compromised the water-tightness of the remaining structure. KH11.3112 states the ‘Fabrication and Workmanship’ requirements for gaskets and coring through them has compromised this.
| 01CV - Civils | Cxxx-NCR-001083 | NCR | Time of flow not included for primary linig on CP1 advance 11 |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2014-09-10 | 2014-09-04 14:47 | -6 | 2014-08-01 15:02 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During a surveillance on the spraying of advance 11 of CP1 it has been noticed that the time the flow was taken has not been detailed on the from 50. This means cannot prove that the flow has been taken immediately prior to spraying. Which is a requirement of the ITP.
| 01CV - Civils | Cxxx-NCR-001084 | NCR | A pipe (90mm?) was left in the formwork when casting the concrete kerb resulting in a void in the vertical face of the kerb at R211 L/H kerb. |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2014-09-05 | 2014-09-05 11:35 | 0 | 2014-08-03 12:16 | Civil - Tunnelling | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Contamination | Completed |  | A pipe (90mm?) was left in the formwork when casting the concrete kerb resulting in a void in the vertical face of the kerb at R211 L/H kerb.
| 01CV - Civils | Cxxx-NCR-001085 | NCR | A footprint was left in the finish on top of the L/H kerb at R166 |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2014-09-24 | 2014-09-15 14:35 | -9 | 2014-08-03 12:21 | Civil - Tunnelling | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Contamination | Completed |  | A footpring was left in top of the kerb on the LHS at R 1666
| 01CV - Civils | Cxxx-NCR-001086 | NCR | BFK 050 not completed properly on CP4a Primary Lining Works -Missing Lead Miner Signatures |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2014-09-05 | 2014-08-28 11:45 | -8 | 2014-08-05 12:06 | Civil - Tunnelling | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | During CP4a Primary Lining works, a number 050 forms (Section E -Confirmation of Primary Linings strengh Confirmation) was not completed and signed off by lead miner- this was only picked up after works had been completed.
| 01CV - Civils | Cxxx-NCR-001087 | NCR | Missing UTX in FTS Slab |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2014-09-05 | 2014-08-28 11:48 | -8 | 2014-08-05 15:40 | Tunnelling - Linings - In-situ Concrete | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | FTS slab poured without casting in 2 no. of UTX ducts on Eastbound Tunnel (Location - Ring 2487 and Ring 2486)
| 01CV - Civils | Cxxx-NCR-001088 | NCR | Holes left behind in tunnel lining rings due to drilling for FTS kerb rebar |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2014-09-30 | 2014-10-07 11:51 | 7 | 2014-08-05 16:20 | Civil - Civil Engineering General | 3000 |  | Design | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Whilst drilling for the kerb reinforcement installation in the tunnel lining rings there were excess holes drilled for a number of reasons: 1. The holes were incomplete due to clashes with existing rebar in the segments. 2. The setting out information changed after drilling had commenced.
| 01CV - Civils | Cxxx-NCR-001089 | NCR | Damaged UTX in Floating Track Slab Area |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2015-01-31 | 2015-01-20 17:57 | -11 | 2014-08-05 16:29 | Civil - Civil Engineering General | 4000 |  | Damaged | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Worker not correctly instructed | Completed |  | Following the completion of the invert pour in the running tunnel Floating Track Slabs theses slabs have been used as a roadway for vehicles. Whilst driving on the slab these vehicles have damaged the UTX ducts.
| 01CV - Civils | Cxxx-NCR-001090 | NCR | Cores made in CP01 (running tunnels) primary lining above 2.5 grade |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2014-11-27 | 2014-11-20 15:47 | -7 | 2014-08-05 22:10 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Cores taken in CP01 lining as instructed and witnessed by CRL and Cxxx were above the 2.5 grade required Please find attached lab results for shotcrete core compressive strength, depth of water penetration and flexural tensile test for the months of June and July 2014 for mix 17.2. The same mix was used for CP1 running tunnel. The lab tests show good results. Two additional cores have already been taken in the affected area showing grade 2 & 3 (Please see attached). The mean result is 2.75 for the cores at Ch 4.5 and 3.25 for cores at CH10.6. There is no engineering requirement to take additional cores as there was no settlement prior to excavation of sump and no settlement afterwards. Drilling additional cores is therefore not required as there is no indication that the shell is not performing as it should do. propose to use as is and close this NCR Also find attached is grading procedure + plus the cores sample check sheets As per agreement with Andy Kendal CRL/Stephan 10/10/14. are going to take 6 No cores in CP1 3 No in Adv 4 clock position 10/2/4 and 3 No in Adv 9 clock position 10/2/6. These cores will be taken in presence of Cxxx inspector on Saturday 11/10/14. 5 additional cores have been taken in the effected area. propose to close this NCR as we think the defect is localised and the extent would not compromise the tunnel’s integrity. The core sample check sheets are attached and show good encapsulation around the rebar. The check sheets are signed by both /Cxxx. Please find attach clear pictures for the previous cores when this NCR was raised
| 01CV - Civils | Cxxx-NCR-001091 | NCR | FIS - EBX - Advance 16 Insufficient Compressive Strength |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2014-09-24 | 2014-09-26 04:47 | 2 | 2014-08-06 10:55 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | The shotcrete core compressive strength test report of Advance 16 - EBX - Panel shows insufficient values .Please find attached result
| 01CV - Civils | Cxxx-NCR-001093 | NCR | Advance 1 in CP5 not sealed for 3 hours after completion of excavation |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2014-09-30 | 2014-09-03 21:35 | -27 | 2014-08-06 14:51 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | After completion of excavation of advance 1 in CP5, the concrete on site presented a flow of 470mm. As the advance was only temporary, concrete was going to be used to seal the face. As pumping started it was realized that it was not possible to pump. For this reason and due to waiting time for shotcrete to arrive on site, the face was opened and unsealed for 3 hours
| 01CV - Civils | Cxxx-NCR-001094 | NCR | Primary Lining Profile WB Binocular - Fisher Street |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2014-11-27 | 2014-10-03 16:27 | -55 | 2014-08-06 18:11 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | A small area of the primary lining in the first section of the WB Binocular (right shoulder looking inbye) protruded into the design tunnel profile (a tight spot) to a maximum of 39mm. Additionally there is evidence of residual concrete spray on the surface.
| 01CV - Civils | Cxxx-NCR-001097 | NCR | Fisher Street - Incomplete F50 forms for IA1 and IA2 |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2014-09-10 | 2014-09-12 07:39 | 2 | 2014-08-11 16:10 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | A number of the Form 50s for the IA1 and IA2 have not been fully completed This includes; 1.Most of the Form 50s are not witnessed by CRL and Cxxx( IA1 and IA2) 2. IA2 - no form 50s presented for Advance 5,6 & 8a 3.For IA2 Advance 8b,9,10 & 12 , missing information on Form 50s such as ; concrete records, volume used, consistency checks ,approval to spray records, post spray checks
| 01CV - Civils | Cxxx-NCR-001098 | NCR | First Stage Concrete - FTS Kerb BOS - TCR WB holes drilled through full depth of segment |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2015-01-31 | 2015-01-29 11:45 | -2 | 2014-08-13 13:19 | Civil - Tunnelling | 1000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | WB R2502, 2501 and 2505 rings have been drilled 300mm i.e. through the segment. therefore this will need to be repaired by . (specified max depth is 225mm)
| 01CV - Civils | Cxxx-NCR-001099 | NCR | Additional Catchpit required at BOS to TCR |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2015-01-31 | 2015-02-04 15:45 | 4 | 2014-08-14 14:43 | Civil - Tunnelling | 6000 |  | Design | Repair | 3 (3-6k) | Complete | Design Problem - Conflicting information on drawings | Completed |  | Drainage drawing Cxxx-OVE-D-DDE-CR001_Z-56674 shows a catch pit in the First Stage Concrete at Ch. 4053 but this catch pit was not included in the catchpit schedule on drawing Cxxx-OVE-D-DDD-CR001_Z-53016 for this reason construction teams did not construct catchpit as required. The last catch pit in the westbound tunnel towards Bond Street was at Ch. 4080 in the STS track slab.
| 01CV - Civils | Cxxx-NCR-001100 | NCR | UTX blocked at rings 72, 241 WB tunnel |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2014-09-25 | 2014-09-26 14:30 | 1 | 2014-08-22 17:33 | Tunnelling - Tunnelling General | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | During the jointly inspection with CRL of the UTX between ROP and PAD WB tunnel, two of them were founded blocked. Cobra was used for the inspection. Nozzles will be used to attempt this.
| 01CV - Civils | Cxxx-NCR-001101 | NCR | Masterseal Repairs - WB Binocular - FIS |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2014-10-15 | 2014-10-15 15:56 | 0 | 2014-08-21 13:01 | Tunnelling - Linings - In-situ Concrete | 5000 |  | Incorrect Installation | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Following application of Masterseal 345 on 19/8/14, a __ trained engineer together with a __ inspector inspected the finish of the sprayed invert in the WB Binocular. Some minor areas were identified as having pinprick voids. Rather than respraying the invert patch repairs were brush applied to the affected areas ensuring the appropriate 300mm laps. This is not in line with the Activity Plan.
| 01CV - Civils | Cxxx-NCR-001102 | NCR | Spiral Survey not carried out for Inclinometer Boreholes (Hanover Square) |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2014-09-29 | 2014-09-26 14:13 | -3 | 2014-08-22 13:37 | Surveying - Instrumentation and Monitoring | 0 |  | Equipment Breakdown | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Due to issues with the spiral probe at the time of installations, there was no spiral survey carried out for the inclinometer boreholes.
| 01CV - Civils | Cxxx-NCR-001103 | NCR | Improper Spraying of Primary on Adv 19 CP4A |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2014-10-01 | 2014-10-03 08:35 | 2 | 2014-08-27 17:22 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Full Face Adv 19 CP4A commenced spraying of top heading prior to invert causing possible build up of rebound in invert
| 01CV - Civils | Cxxx-NCR-001104 | NCR | Early Age Strength Adv 19 CP4A |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2014-09-26 | 2014-09-03 18:14 | -23 | 2014-08-27 17:28 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | No early age strength panel sprayed for Adv 19 CP4A (First advance of back excavation)
| 01CV - Civils | Cxxx-NCR-001107 | NCR | Use of Reader Spraycrete in Permanent Works - FIS - WB Crossover Cavern |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2015-02-15 | 2015-02-17 16:20 | 2 | 2014-08-28 18:25 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Use of unapproved materials | Completed |  | Revision 2 of the MCR for Spraycrete 50A (Cxxx--C-LRC-CRT00_ST005-50297) that was submitted with the intent of incorporating Spraycrete (Reader) into the regulating layer has not been approved yet but has been used on a 16m2 area at the mouth to the WB Binocular at Fisher St.
| 01CV - Civils | Cxxx-NCR-001109 | NCR | Concrete Testing Failure - WB Binocular Slab BN3 |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2014-11-30 | 2014-10-23 23:05 | -38 | 2014-09-01 16:50 | Tunnelling - Linings - In-situ Concrete | 500 |  | Testing and Commissioning | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | KF10.2207 specifies that concrete shall be tested for compliance with characteristic compressive strength in accordance with BS 8500-1, BS 8500-2 and BS EN 206-1. Concrete cubes were not taken for the the slab pour in the WB Binocular BN3. A sample cube 1m x 1m (on plan) and 0.5m deep was prepared in place with the intent that the sample be cored.
| 01CV - Civils | Cxxx-NCR-001110 | NCR | Concrete Curing Failure - WB Binocular Slab BN3 |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2015-08-13 | 2015-08-23 13:43 | 10 | 2014-09-01 17:12 | Tunnelling - Linings - In-situ Concrete | 2500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | KF10.3206 says concrete shall be cured to prevent loss of moisture from the concrete. The first two days after the slab concerned was poured there was no curing facility provided.
| 01CV - Civils | Cxxx-NCR-001111 | NCR | FIS - EBX Advance 34 Insufficient thickness |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2014-10-31 | 2014-11-01 10:50 | 1 | 2014-09-02 16:32 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The profiles and proof drilling of chainage 22 of Advance 34 ,EBX - Fisher Street, have revealed an insufficient thickness for the primary lining. The thickness profile and proof drilling as per attached .
| 01CV - Civils | Cxxx-NCR-001112 | NCR | Headwall Primary Lining Delamination |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2014-09-16 | 2014-09-27 22:29 | 11 | 2014-09-02 15:57 | Tunnelling - Linings - Sprayed Concrete | 1000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | A wedge shaped (0-100mm thick) 2m2 area of the headwall to the WB Crossover Cavern delaminated during excavation for the secondary lining works. Probe drilling within the area revealled a depth of 500-520mm which is short of the designed 600mm.
| 01CV - Civils | Cxxx-NCR-001113 | NCR | Slab Level Out of Tollerance BN3 WB Binocular FIS |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2014-10-16 | 2014-10-16 07:25 | 0 | 2014-09-03 17:29 | Tunnelling - Linings - In-situ Concrete | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Specified tollerance for this concrete is +50/-0. Slab level of the BN3 slab is +70 (LOW) all over (20mm beyond tollerance). Slab Survey (E,N,RL) SLAB4 80991.81 36415.5 96.997 SLAB2 80985.24 36413.93 97.069 SLAB3 80986.87 36411.87 97.070 SLAB1 80990.18 36417.57 96.993
| 01CV - Civils | Cxxx-NCR-001115 | NCR | FIS_SMM_Red Lion Sq IPI08 |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2014-10-10 | 2014-10-31 16:40 | 21 | 2014-09-08 09:36 | Surveying - Instrumentation and Monitoring | 1000 |  | Equipment Breakdown | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Red Lion Sq IPI08 is not giving reliable and consistent data in relation to the excavation works for EBX. Following this, a serie of problems have been found: 1. Conversion setup to output using wrong units (ArcDec instead of mm/m) 2. Conversion settings had calibration factors inverted (shallowest to deepest) instead of the other way around 3. Conversion settings had 2 incorrect beam lengths (3 meters instead of 2) 4. Manual testing of each sensor revealed 2 malfunctioning mux channels (and confirmed their functionality) 5. Site inspection found that the IPI string is not suspended anymore and loose at the top
| 01CV - Civils | Cxxx-NCR-001116 | NCR | EBX - Advance 44 early age strength testing |  | Crossrail | PDP | TUX - Tunnel Drive X (West) |  | 2014-09-30 | 2014-10-01 16:10 | 1 | 2014-09-09 19:29 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | EAS test for Adv 44 in EBX @ 1hr and 2 hr was lower than the J2 curve. No tests were carried out at 3 or 4 hours.
| 01CV - Civils | Cxxx-NCR-001118 | NCR | Discrepancy in the coordinates between UCIMS/Gtc and the Installation Reports |  | Crossrail | XRL | TUX - Tunnel Drive X (West) |  | 2014-10-31 | 2014-11-04 11:44 | 4 | 2014-09-10 17:02 | Geotechnical Engineering - Geotechnical Monitoring | 5000 |  | Documentation and Records | Repair | 3 (3-6k) | Complete | Personnel Error - Other human error | Completed |  | During a review of the I&M coordinates reported in the Installation Reports and UCIMS/GTC, it was noted that there are inconsistences in the data: •BOS - TCR Area: levelling I&M group A08: Installation Report No. Cxxx--C4-RGN-CRT00_ST005-50749 rev 1 matches GTC data but doesn’t match UCIMS coordinates with variable differences of more than 2m in places (see attachment). •FIS - FARR Area: levelling I&M group E09: Installation report compared to GTC/UCIMS data have a variable difference of more than 7m in places (see attachment). Please note that it is an important part of the specification to present accurate coordinates of the I&M installed.
| 01CV - Civils | Cxxx-NCR-001119 | NCR | Levelling points not added to UCIMS |  | Crossrail | XRL | TUX - Tunnel Drive X (West) |  | 2014-10-30 | 2014-11-04 16:51 | 5 | 2014-09-10 17:07 | Geotechnical Engineering - Geotechnical Monitoring | 10000 |  | Software | Rework | 2 (6-60k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | The following precision levelling points do not appear on UCIMs: -PLPs belonging to levelling I&M group A08, on Berwick Street and Wardour Street (Between BOS and TCR) -PLPs belonging to levelling I&M group F09, between Saffron Hill and Gray’s Inn Road (Between Holborn and Farringdon) Please see attachment for a map of the sections missing from UCIMS.
| 01CV - Civils | Cxxx-NCR-001120 | NCR | Erroneous data provided for IPIs 07 and 08 at Red Lion Square |  | Crossrail | XRL | TUX - Tunnel Drive X (West) |  | 2014-10-24 | 2014-10-13 09:13 | -11 | 2014-09-10 17:47 | Geotechnical Engineering - Geotechnical Monitoring | 15000 |  | Incorrect Installation | Use As-Is | 2 (6-60k) | Complete | Personnel Error - Inattention to detail | Completed |  | The contractor has been providing incorrect data to CRL from deep instruments (IP07 & IPI08 - Ext7 is under investigation) in the Red Lion Square Area. The contractor has informed the FIS CTC – 10.9.14 that significant and reiterative errors have been made in all the stages of the processing of the data since the instruments were installed, meaning that all of the data provided has been erroneous. Additionally, today we were informed that IP08 is not fixed from the top since the end of 2013, therefore rendering the instrument completely unreliable. It is unacceptable that such error was not reported before. The PM considers this to be a defect and may seek to Disallow Costs.
| 01CV - Civils | Cxxx-NCR-001121 | NCR | UTX blocked at WB Tunnel ring 72 Chainage 624.35 |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2014-10-16 | 2014-12-04 20:19 | 49 | 2014-09-15 13:32 | Tunnelling - Tunnelling General | 500 |  | Damaged | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During the jointly inspection with CRL of the UTX between ROP and PAD WB tunnel, the UTX at ring 72 was found blocked. Cobra was used for the inspection.
| 01CV - Civils | Cxxx-NCR-001122 | NCR | Cracks located locally at Catchpits in FSC slabs |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2015-01-31 | 2015-01-13 16:59 | -18 | 2014-09-15 15:38 | Civil - Civil Engineering General | 500 |  | Design | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | and Crossrail have noticed a bit of a pattern with cracks appearing in the STS invert slabs located at the catchpits. The obvious reasoning for this would be that the catchpit intern reduces the amount of concrete in the slab at this area, hence making it the weaker part of the slab and allowing cracks to form.
| 01CV - Civils | Cxxx-NCR-001123 | NCR | FIS-Missing early age strenght results for Advance 86 EBX part 1 |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2015-01-30 | 2015-02-03 21:03 | 4 | 2014-09-16 09:49 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Testing and Commissioning | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | Missing data for early age strength results of 10 min. and 6 hrs. for advance 86 (Top Heading).
| 01CV - Civils | Cxxx-NCR-001124 | NCR | FIS - Installation of monitoring points in EBX chainage 0.7 of sidewall drift |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2014-10-30 | 2014-10-16 17:29 | -14 | 2014-09-16 10:22 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | According to RESS EBX037, monitoring points were to be installed in chainage 0.7 of EBX, sidewall part. Monitoring points were not installed immediately after spraying of advance. They were installed approx. 20hours after spraying.
| 01CV - Civils | Cxxx-NCR-001125 | NCR | BFK Form 101H not in place between rings 3325 and 3279 for drill holes |  | Crossrail | XRL | TUX - Tunnel Drive X (West) |  | 2014-11-20 | 2014-11-24 15:05 | 4 | 2014-09-16 15:18 | Civil - Tunnelling | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | During Crossrail surveillance dated 28th August 2014 it was noted that the documented method statement states a requirement for repairing any defects in the invert of the concrete segments where FSC will take place. On review of the segment repair procedure for the running tunnel invert it states that ‘segment repair report form 101h’ will be used to repair all 12mm or 110mm holes using PCC mortar referenced as a CAT H repair; this is also documented in the FSC ITP as a requirement. During the site visit, the setting out for the kerb was reviewed in the westbound tunnel between rings 3325 and 3279 which was stated as planned to be poured night shift 28/08/14. On review it was highlighted that there were a large number of drill holes in the pre-cast segments at kerb level between rings 3325 and 3279. Materials and Workmanship Specification Bored Tunnels KT10.4238 b states “all necessary repairs shall be performed and water ingress into the tunnel controlled…” A post surveillance request was made to produce form 101h for the repair of the 12mm drill holes between rings 3325 and 3279 before pouring the kerb concrete. No documentation was provided and as such it could not be confirmed that the deviations in the concrete segments were repaired as defined in the repair procedure and as required by the documented ITP.
| 01CV - Civils | Cxxx-NCR-001126 | NCR | 12mm reinforcement bars being used for FSC work were being stored incorrectly in direct contact with the ground |  | Crossrail | XRL | TUX - Tunnel Drive X (West) |  | 2014-10-14 | 2014-10-15 15:12 | 1 | 2014-09-16 15:22 | Civil - Tunnelling | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | During Crossrail surveillance dated 28th August 2014 it was identified that a large quantity of 12mm reinforcement bars for the FSC works were being stored in direct contact with the ground in the westbound tunnel causing potential for contamination which could affect the bond between the reinforcement and the concrete. Materials and Workmanship Specification In-Situ Concrete KF10.3241’Stroage of Reinforcement’ states “a) Reinforcement shall be stored in such a way as to avoid contamination …… c) Steel reinforcing bars and fabric reinforcement shall be kept clean and shall be free from pitting, loose rush, mill scale, oil, grease, earth, paint, chlorides or any other material which may impair the bond between the concrete and the reinforcement”. This NCR was raised to ensure all reinforcement is stored appropriately to avoid potential for contamination.
| 01CV - Civils | Cxxx-NCR-001127 | NCR | Constituent material records for concrete being used in FSC works are not being maintained as required |  | Crossrail | XRL | TUX - Tunnel Drive X (West) |  | 2014-10-14 | 2014-10-28 14:41 | 14 | 2014-09-16 15:25 | Civil - Tunnelling | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | During Crossrail surveillance dated 28th August 2014 a review of the Contractors ITP was carried out. Under point B18 ‘Constituent Material Testing’ it states a frequency of ‘monthly’ for obtaining supplier constituent material results for the concrete mix design being used in the FSC construction. Cxxx--C4-LRC-CRT00_ST005-50375 Rev 1 Code 4 (supplier records) was produced during the surveillance, however on review it was noted that only one set of aggregate grading results existed which dated back to supplier testing carried out in October 2013. No other grading results were present for the 0/4mm and 4/10mm aggregates being used in the concrete mix design. Therefore the aggregates compliance against the performance requirements detailed under KF10.1406 ‘Aggregates’ could not be demonstrated, where weekly and monthly testing is required. Works Information Vol 2B part 13.1 states “the provision and maintenance of records”.
| 01CV - Civils | Cxxx-NCR-001128 | NCR | ITP check sheets for FSC works missing required sign off information/ incorrect; as such pre pour inspection could not be verified as done |  | Crossrail | XRL | TUX - Tunnel Drive X (West) |  | 2014-10-14 | 2014-10-13 10:58 | -1 | 2014-09-16 15:30 | Civil - Tunnelling | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | During Crossrail surveillance dated 28th August 2014 a review of Forms 099 a-d was carried out. It was noted that forms 099 c and d included a requirement for pre pour inspection and cleanliness however nothing existed on forms 099a and b for pre pour inspection of the Standard and HAS invert works. It could therefore not be demonstrated that appropriate checks had been carried out by the nominated person prior to pouring the invert works as required by ITP Point B4 ‘clean out pour area’, which requires a check to ensure the pour area is clean and caulking groove free from debris. Additionally on review of form 099b it states in diagram format that the top of the kerb should have a U3 unformed finish, however on review of form 099d it states that the top of the kerb shall have a brush finish. Works Information Vol 2B part 13.1 states “the provision and maintenance of records”.
| 01CV - Civils | Cxxx-NCR-001130 | NCR | Drill holes cored the entire way through the ring segments BOS to TCR Westbound - West of TCR Ring 2680 to 2743 |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2014-01-31 | 2015-01-13 17:05 | 347 | 2014-09-17 12:34 | Civil - Civil Engineering General | 5000 |  | Damaged | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Whilst drilling the holes in the ring segments for the kerb rebinforcement some of the holes have been drilled the full depth of the segment.
| 01CV - Civils | Cxxx-NCR-001131 | NCR | Green Lane Sewer - MH4-5 Tunnel Annulus 28day Grout Strength Not Achieved |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2014-10-09 | 2014-10-02 17:36 | -7 | 2014-09-25 10:02 | Civil - Sewage/Water services | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Grout is pumped under pressure into the tunnel annulus to 3 bar to close the annulus. The ITP requires 7 day grout strength 3N/mm2 this was achieved, the ITP requires a 28day grout strength 8N/mm2 this was not achieved. Further cube tests were carried out at 56 days and did not achieve 8N/mm2, a minimum of 5N/mm2 was achieved at 56 days. See attached cube test results.
| 01CV - Civils | Cxxx-NCR-001132 | NCR | CP1 (RT) proof drilling records show localised depth less than design depth |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2014-10-18 | 2014-10-03 08:46 | -15 | 2014-09-18 17:44 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Proof drilling records sheets show localised areas with depth less than design depth of 250mm. Proof drilling records with chainages attached
| 01CV - Civils | Cxxx-NCR-001133 | NCR | CP4a - Concrete quality issues between chainage 7.6 to 8.2. Remedial works required |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2014-10-08 | 2014-10-09 16:50 | 1 | 2014-09-20 16:33 | Tunnelling - Tunnelling General | 10000 |  | Workmanship | Use As-Is | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Whilst carrying out the milling works in preparation for the regulating layer, an area was found with poor quality concrete. After removal of all the rebound there was no sufficient thickeness on the lining (see picture attached). Remedial actions were carried out on the following area: * CP4a - Chainage - between 7.6 & 8.2; - Invert - between 4 o'clock & 7 o'clock; - Remedial actions - break out primary lining, excavate to right profile, install bars to ensure good connection between joints & spray up to the right profile (see RESS attached)
| 01CV - Civils | Cxxx-NCR-001135 | NCR | Cross Passage 1: Overbreak of Primary lining concrete in sump for directional drilling |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2014-10-06 | 2014-10-15 15:41 | 9 | 2014-09-22 09:07 | Tunnelling - Linings - Sprayed Concrete | 1000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Procedure Problem - Defective or inadequate procedure | Completed |  | To complete the directional drilling from the sump at cross passage 1, it was necessary to break out a proportion of the sumps primary lining to a size of 750*750. These works were carried out without a RESS. Checksheet attached. However for general repair work e.g. backfilling of core holes, do not require the necessity of photographic evidence and unfortunately this is the case of backfilling around the 400mm OD pipe. propose to close this NCR
| 01CV - Civils | Cxxx-NCR-001136 | NCR | CP4a Thickening Steel Reinforcement |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2014-10-07 | 2014-10-09 16:56 | 2 | 2014-09-23 09:09 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | The primary lining thickening reinforcement for CP4a has not been installed as shown on drawing Cxxx-MMD-C4-DDD-CR001-06030. The drawing indicates the TBM rings to the south showing the westbound running tunnel and eastbound to the north. The steel to the north (eastbound) side of the sump was installed first, witnessed by Cxxx and CRL and sprayed in. On commencing installation of the steel to the south (westbound) side, it became apparent that there wasn't room to fit 14 number BM05 bars as indicated. There was only room to install nine bars as per the north (eastbound) side. The bars were therefore installed as per the north side and the BM04 bars cut to suit (equivalent to BM03). This again was witnessed and signed off by CRL and Cxxx. See attached sketch of changes,
| 01CV - Civils | Cxxx-NCR-001137 | NCR | EBX Fisher Street - Encapsulation of reinforcement in advances 85 in the crown of sidewall drift |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2014-12-15 | 2014-12-17 09:59 | 2 | 2014-09-25 10:51 | Tunnelling - Linings - Sprayed Concrete | 10000 |  | Workmanship | Repair | 2 (6-60k) | Complete | Material/Preservation Problems - Other | Completed |  | One of the cores taken in the crown of EBX sidewall drift advances 85 shows poor encapsulation. Encapsulation of reinforcement in the far face (FF) is not according to requirements – Bar mark 14 and 18. Remaining lining has good quality, . Area has been identified has being up to 700mm of the joint (area of congestion reinforcement).
| 01CV - Civils | Cxxx-NCR-001138 | NCR | Commencement of work to running tunnels mini sumps at CP1 without a code 1 decal sheet for RAMS and ITP |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2014-10-30 | 2014-10-22 08:46 | -8 | 2014-09-25 13:52 | Tunnelling - Linings - In-situ Concrete | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Defective or inadequate procedure | Completed |  | Rebar was fixed within westbound running tunnel sump at CP01 without a Code 1 RAMS or ITP
| 01CV - Civils | Cxxx-NCR-001140 | NCR | Invert base pour to westbound collar at Cross passage 01 |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2014-10-30 | 2014-11-02 16:07 | 3 | 2014-09-28 12:21 | Tunnelling - Linings - In-situ Concrete | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Upon striking the formwork to the invert base pour to westbound collar the following defects were observed. 1. The concrete should have been cast with a downward 1:80 slope from inside the cross passage to the running tunnel. A fall of approximately 18mm. During concreting the operatives ignored the falls and the concrete was cast flat. see photograph. 2. Two of the five 100mm diameter HDPE ducts have shifted during concreting. See photograph.
| 01CV - Civils | Cxxx-NCR-001141 | NCR | Cross Passage 1: Over-excavation of tunnel profile |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2014-11-09 | 2014-11-24 14:20 | 15 | 2014-09-29 12:05 | Tunnelling - Linings - Sprayed Concrete | 5000 |  | Incorrect Installation | Use As-Is | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During the excavation of CP1, advances 2,3,8 and 9 were over excavated past the allowable tolerances. Due to this there is the potential for a clash with the vitrified clay pipe directly below the invert of the tunnel.
| 01CV - Civils | Cxxx-NCR-001142 | NCR | EBX- Fisher Street / Monitoring targets CB5 and CB6 at RMS 34.0 and RMS 43.0 has not been done as per required frequency |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2014-10-14 | 2014-10-16 17:21 | 2 | 2014-09-30 19:02 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | Monitoring targets CB5 and CB6 at RMS 34.0 and RMS 43.0 were not read and results presented as per required frequency
| 01CV - Civils | Cxxx-NCR-001143 | NCR | Overscabbling on FTS Breaking Blocks at rings 3080/3081 & 3083/3084 (on both sides) in the westbound tunnel |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2014-10-22 | 2014-10-22 08:44 | 0 | 2014-10-03 18:26 | Civil - Tunnelling | 1000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Where the scabbling machine has come through to scabbler the kerb line, the breaking block (which should remain smooth) was scabbled at the rings 3083/3084 3080/3081 in the westbound tunnel.
| 01CV - Civils | Cxxx-NCR-001147 | NCR | Holes filled in Paddington Box West in Westbound tunnel between rings 495-457 |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2014-11-21 | 2014-11-25 14:06 | 4 | 2014-10-06 13:59 | Civil - Tunnelling | 1000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Holes within rings 495 and 457 were filled up with __ Hit when they should have been empty.
| 01CV - Civils | Cxxx-NCR-001148 | NCR | Holes filled in the east of the Paddington Box in the westbound between rings 660-692 |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2015-04-23 | 2015-04-20 17:44 | -3 | 2014-10-06 14:03 | Civil - Tunnelling | 1000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Holes were filled with Hilit Hit on the east side of paddington Box in the westbound between rings 660-692
| 01CV - Civils | Cxxx-NCR-001149 | NCR | Holes were filled in the West of Paddington Box on the eastbound between rings 470-502 |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2014-11-21 | 2014-11-24 14:24 | 3 | 2014-10-06 14:05 | Civil - Tunnelling | 1000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Holes were filled in the west of Paddington Box in the eastbound tunnel with __ hit between rings 470-502.
| 01CV - Civils | Cxxx-NCR-001150 | NCR | Holes filled with __ Hit in East of Paddington Box in the eastbound Tunnel between rings 667-699 |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2015-04-30 | 2015-05-05 08:04 | 5 | 2014-10-06 14:11 | Civil - Tunnelling | 3000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Holes were filled with __ hit between rings 667-699 in the eastbound tunnel.
| 01CV - Civils | Cxxx-NCR-001153 | NCR | CP2 (running tunnel) Adv 4 was oversprayed |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2014-11-29 | 2014-11-19 12:03 | -10 | 2014-10-08 22:20 | Tunnelling - Linings - Sprayed Concrete | 2000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Advance 4 primary lining was oversprayed up to 230mm
| 01CV - Civils | Cxxx-NCR-001154 | NCR | U-bars installed at incorrect position of thickening at CP2 |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2014-11-29 | 2014-11-19 12:05 | -10 | 2014-10-09 04:22 | Tunnelling - Tunnelling General | 1000 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | On commencement of the NF steel it was realised the survey chainages(5m and 11.4m) given had incorrectly positioned the U-bars 400mm closer than needed. The 25mm diam NF steel was installed correctly as per drawing Cxxx-MMD-C4-DDD-C4001-06010, however, the U-bars had already been sprayed in with the mesh using fibre shotcrete.
| 01CV - Civils | Cxxx-NCR-001155 | NCR | Cracking in tunnel segments WB rings 2598, 2595, 2593, 2591, 2589 and 2587 |  | Contr | KIR | TUX - Tunnel Drive X (West) |  | 2015-02-09 | 2015-02-20 08:25 | 11 | 2014-10-09 09:52 | Civil - Tunnelling | 5000 |  | Damaged | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Other | Completed |  | A number of cracks have been observed at approx 1 o'clock position looking inbye in the rings listed above. Relevant cracks only at rings 2587, 2589 and 2591.
| 01CV - Civils | Cxxx-NCR-001158 | NCR | Kerb falling backwards on Eastbound between rings 460-438 |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2014-10-24 | 2014-11-09 09:58 | 16 | 2014-10-10 17:12 | Civil - Tunnelling | 1000 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The Kerb is currently falling back into the ring as opposed towards to the track. This is between rings 460-438 on the eastbound tunnel.
| 01CV - Civils | Cxxx-NCR-001159 | NCR | FIS - EBX Binocular 1 , Early age strenght results below modified J2 curve in Advance 4 and Missing early age strenght results for advance 7 |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2014-11-30 | 2014-10-31 02:40 | -30 | 2014-10-13 10:50 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Testing and Commissioning | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | EBX Binocular 1; 1- Advance 4 -early age strength test failed to meet the specified strengths of 0.78 Mpa at 2 hrs old respectively, also no tests were carried out at 4 hours. 2- Advance 7 - Missing early age strength result at 6 hours and 12 hours
| 01CV - Civils | Cxxx-NCR-001160 | NCR | Number of reinforcement bars installed in EBX between chainages 36.77 and 44.20 |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2014-12-11 | 2014-12-11 17:45 | 0 | 2014-10-13 17:41 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Personnel Error - Inattention to detail | Completed |  | During excavation and primary lining of Eastbound cavern (EBX); between chainages 36.77 and 44.20, in advances 52, 56, 60, 64, 68, 72, 75 and 77; some of the reinforcement bars were installed in inferior number to the required in the design/drawings. Due to leadings edges of advances and spacing between the bars, the number of bars missing are as follows: Bar Mark from drawing Cxxx-MMD-C4-DDD-CR086_SH003_5-01010 No. of bars missing Bar Mark 4 - 6 bar missing Bar Mark 5 - 4 bar missing Bar Mark 6 - 3 bar missing Bar Mark 7 - 3 bar missing Bar Mark 8 - 3 bar missing This is equivalent to 4% less reinforcement installed, or to a spacing of extra 8mm between bars. All advances have been inspected by /CRL/Cxxx and respective reinforcement checksheets signed by all parties, as ok to spray
| 01CV - Civils | Cxxx-NCR-001161 | NCR | Advance 7 EB Binocular (invert) not sprayed in layers;faced not sealed prior to commencing primary layer |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2015-03-31 | 2015-03-05 19:29 | -26 | 2014-10-13 18:24 | Civil - Tunnelling | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | When spraying Advance 7 EB Binocular (invert) initial and pimary lining were sprayed simultanously without the face being supported. This was not done in layers.
| 01CV - Civils | Cxxx-NCR-001162 | NCR | FIS-EBX Binocular 1 - Missing early age strenght results for Advance 10 |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2015-01-14 | 2014-12-19 23:51 | -26 | 2014-10-14 10:54 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Testing and Commissioning | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | Missing data for early age strength results of 2,6 and 12 hours for FIS EBX Binocular Part 1 Advance 10
| 01CV - Civils | Cxxx-NCR-001163 | NCR | 5 No. UTX ducts missing at CP1 interface EB & WB Tunnels |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2014-10-28 | 2014-11-10 09:26 | 13 | 2014-10-14 15:30 | Tunnelling - Tunnelling General | 2000 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Conflicting information on drawings | Completed |  | According to drawing Cxxx-OVE-C4-DDD-CR001_Z-23129, 5 No. UTX ducts should be installed at CP1 interface EB & WB Tunnels.
| 01CV - Civils | Cxxx-NCR-001164 | NCR | Overscabbling on eastbound tunnel at ring 3029 on the FTS Breaking Block section |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2014-10-29 | 2014-10-28 14:48 | -1 | 2014-10-15 12:49 | Civil - Tunnelling | 1000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Overscabbling on eastbound tunnel at ring 3029 on the FTS Breaking Block section. This resulted in the smooth concrete finish being left rough.
| 01CV - Civils | Cxxx-NCR-001165 | NCR | When FSC poured the invert Floating slab, the invert was over poured to chainage 4018.120 in eastbound tunnel which prevents Cxxx to complete their overlap zone in the correct location. The kerb section is to design. |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2015-03-18 | 2015-03-26 22:55 | 8 | 2014-10-15 16:56 | Civil - Tunnelling | 5000 |  | Incorrect Installation | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Drawing Cxxx-OVE-C4-DDA-CR001_Z-81051 stipulates that FSC will be cast upto chainage 4018.120 +/- 500 mm at BOS WTH. An overlap zone of 1.3 m is stipulated beyond chainage 4018.120 (+/- 500 mm) which is to contain only the steel for the FSC. As per note 7 the section of tunnel within the overlap zone (in this case 4018.120 – 4019.720) should be cast by Cxxx. Please see the attached sketch and photo which shows Cxxx have cast upto chainage 4018.120 and therefore not left the correct lap (1.3 m) for the follow on contractor (Cxxx).
| 01CV - Civils | Cxxx-NCR-001167 | NCR | Breaking blocks within FTS not achieving the required cover on the EB FIS-TCR (rings 3006, 3007, 3009, 3010, 3029, 3030, 3032,3033 (All LHS and RHS)) |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2014-12-17 | 2014-12-19 13:30 | 2 | 2014-10-17 11:37 | Civil - Tunnelling | 10000 |  | Incorrect Installation | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | In the FTS on the EB at FIS-TCR (rings 3006, 3007, 3009, 3010, 3029, 3030, 3032,3033 (All LHS and RHS)), where a breaking block is, there are issues with the cover with the dowel bar, side u bar and link bar having either too much cover or not enough.
| 01CV - Civils | Cxxx-NCR-001168 | NCR | Breaking blocks within FTS not achieving the required cover on the WB FIS-TCR (rings 3080,3081, 3083,3084, 3111,3112,3114,3115 (ALl LHS and RHS)) |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2014-12-17 | 2014-12-19 13:32 | 2 | 2014-10-17 11:52 | Civil - Tunnelling | 10000 |  | Incorrect Installation | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | In the FTS on the WB at FIS-TCR (rings 3080,3081, 3083,3084, 3111,3112,3114,3115 (All LHS and RHS)), where a breaking block is, there are issues with the cover with the dowel bar, side u bar and link bar having either too much cover or not enough.
| 01CV - Civils | Cxxx-NCR-001169 | NCR | Incorrect installation of UTX collar between ROP to PAD Eastbound at Ring 260 |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2014-10-31 | 2014-10-29 11:46 | -2 | 2014-10-17 17:02 | Civil - Tunnelling | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The UTX Collar has no or required cover. The Collar should have been cast in with at least 75mm minimum cover as per Cxxx-RFI-001146.
| 01CV - Civils | Cxxx-NCR-001170 | NCR | Position of WB Binocular Central Pillar Wall cast outside tollerance - FIS |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2014-11-04 | 2014-10-27 17:59 | -8 | 2014-10-21 17:41 | Tunnelling - Linings - In-situ Concrete | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The wall offsets to the tunnel centre from the WB Binocular central dividing pillar should be: West End - Ch 6022.42 -2.661m Middle - Ch 6025.28 -2.850m East End - Ch 6029.20 -3.109m The first 3.6m (in height) of the wall have been poured. Asbuilt survey shows the south face of the wall to have been built too far south (the tunnel is small): West End - Ch 6022.42 -2.630m Middle - Ch 6025.28 -2.813m East End - Ch 6029.20 -3.061m
| 01CV - Civils | Cxxx-NCR-001171 | NCR | EB tunnel TCR-BOS Cold joint in kerbs at ring No 2597 north side |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2015-01-31 | 2015-01-16 13:09 | -15 | 2014-10-27 10:34 | Tunnelling - Linings - In-situ Concrete | 2000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Cold joint present in ring No 2507 at the edge of breaking block, due to lack of available concrete on site at the time.
| 01CV - Civils | Cxxx-NCR-001172 | NCR | Fisher Street, Westbound Binocular - Missing Bars from Headwall |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2015-08-20 | 2015-10-02 10:56 | 43 | 2014-10-27 18:25 | Tunnelling - Linings - In-situ Concrete | 5000 |  | Incorrect Installation | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Fisher Street, Westbound Binocular Headwall - Secondary Lining Headwall to Westbound Binocular was cast with Bar Marks 85 and 89 not installed.
| 01CV - Civils | Cxxx-NCR-001173 | NCR | Filling Quality core holes in Primary lining of EBX and CP5 Fisher Street |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2015-04-30 | 2015-05-01 01:50 | 1 | 2014-10-29 14:08 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During the operation of filling some of the quality core holes in the tunnel lining, the activity plan for the activity requires that the core hole is filled in 100 to 150mm layers, tamping each layer 15 to 20 times to ensure good compaction and prevent entrainment of air. The activity was not performed in that way. The grout produced was sufficient fluid to be poured into the core holes in a way that did not required tamping. The activity plan was not followed but sufficient compaction has been achieved. Location as per observation of Cxxx and CRL inspectors/engineers at 13:56 of 19/10/2014 during 1.5 hour site inspection: a) Two cores at CH 6.04-CH 7.03 advance 13 (bench) of EBX binocular (these are already covered by secondary lining). b) One core at approximately CH 31 of EBX ( on left side of the bench facing the headwall)
| 01CV - Civils | Cxxx-NCR-001174 | NCR | CP4a - Remedial works between chainage 5 and 7,5 |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2014-11-28 | 2014-11-27 08:15 | -1 | 2014-10-31 17:48 | Tunnelling - Tunnelling General | 20000 |  | Incorrect Installation | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | After thorough examination of the primary lining works, it was noticed that there were issues with the thickness of the lining between chainage 5 to 7.5. The location is shown on the activity plan attached. The profile was out of tolerance and the lining had under thickness issues.
| 01CV - Civils | Cxxx-NCR-001175 | NCR | Cores made in CP02 (running tunnels) primary lining above 2.5 grade |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2015-01-31 | 2015-02-04 16:16 | 4 | 2014-11-04 00:37 | Tunnelling - Linings - Sprayed Concrete | 10000 |  | Workmanship | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Three cores taken in CP02 lining as instructed by CRL and Cxxx were above the 2.5 grade required showing a value of 2.8 Additional cores were taken at the time of the first coring showing similar value of 3 which were not presented or logged. Two additional cores have already been taken on 31/10/14 in the affected area showing grade also above 2.5. The cores were taken at the location of the U-bars, L-Bars and 25mm longitudinal bar. The first three check sheets are signed by both /Cxxx.
| 01CV - Civils | Cxxx-NCR-001176 | NCR | FIS Secondary Lining - Mis-Positioned Couplers in WBX Binocular Headwall |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2014-11-18 | 2014-11-27 20:11 | 9 | 2014-11-04 15:06 | Civil - Tunnelling | 10000 |  | Incorrect Installation | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | It has been identified that the cast in couplers in the WBX Binocular Headwall are in the wrong location and are unsuitable for use to connect the reinforcement from the adjoining crown structure.
| 01CV - Civils | Cxxx-NCR-001177 | NCR | FIS Secondary Lining - Sheet Waterproofing installed at incorrect level - WBX Binocular Wall |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2014-11-18 | 2014-11-27 20:18 | 9 | 2014-11-04 18:08 | Civil - Tunnelling | 15000 |  | Incorrect Installation | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The sheet waterproofing intended for between the top of the WBX binocular wall and primary lining was installed at the incorrect level.
| 01CV - Civils | Cxxx-NCR-001178 | NCR | Fisher Street, Westbound Binocular - Profile to WB Binocular Headwall Crown |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2014-11-26 | 2014-11-28 15:27 | 2 | 2014-11-05 12:25 | Tunnelling - Linings - In-situ Concrete | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Fisher Street, Westbound Binocular Headwall - Please find attached profiles for the crown pour of the Binocular Headwall. Small section of the crown section of the headwall is outside allowable tolerance (maximum 18mm).
| 01CV - Civils | Cxxx-NCR-001179 | NCR | CP5 - Primary lining quality cores from advances 3,5 & 8 |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2014-12-02 | 2014-12-01 09:21 | -1 | 2014-11-06 10:16 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | Quality cores from the CP5 tunnel lining were taken from advances 3, 5 and 8 for the 28 day compressive testing, as per ITP. Concerns were raised due to poor grading and the high number of band layers present in the cores. Extra cores were taken. Sketch with the section of the tunnel with the location of all cores and a core register are attached to the NCR. When considering all the cores, the average of the grades is below 2.5. Although, recognises that some localized areas of advance 5 and 8, specially invert at knee level (4o’clock and 8oo’clock), have an extraordinary number of voids and band layers.
| 01CV - Civils | Cxxx-NCR-001180 | NCR | Missing Form50 for CP4a Sump- advance 25 |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2014-12-04 | 2014-12-02 08:52 | -2 | 2014-11-06 15:46 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | Missing Form50 for CP4a Sump advance 25
| 01CV - Civils | Cxxx-NCR-001181 | NCR | Fisher Street - Repairs done to secondary lining cast in situ surface without approved method/procedure - Binocular Westbound |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2015-05-28 | 2015-05-30 11:13 | 2 | 2014-11-06 18:14 | Tunnelling - Linings - Sprayed Concrete | 5000 |  | Supervision/Management | Repair | 3 (3-6k) | Complete | Procedure Problem - Other | Completed |  | Fisher Street - Repairs were undertaken in the surface of the cast in situ concrete in the binocular Westbound without an approved procedure. Material used is approved under MCR Cxxx--C-LRC-CRT00_ST005-50224
| 01CV - Civils | Cxxx-NCR-001182 | NCR | Fisher Street - Sheet waterproofing system installed for cast in situ headwall in binocular Westbound |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2015-09-15 | 2015-08-24 12:11 | -22 | 2014-11-06 18:34 | Tunnelling - Linings - In-situ Concrete | 10000 |  | Incorrect Installation | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Fisher Street - Sheet waterproofing detail installed in for the cast in situ headwall in the binocular Westbound appears to be below the required level as per drawing Cxxx-MMD-C4-DDD-CR086_SH003-04065. Due to the fact the sheet is now concreted in, proposes to wait until the primary lining is broken from the crossover side for full investigation and agreeing in repair procedure. 14/05/2015 - Membrane exposed and problems found in the membrane are the same as in the rest of the wall.
| 01CV - Civils | Cxxx-NCR-001183 | NCR | Fisher Street, Westbound Binocular Wall - Bars missing during pre-pour inspection |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2014-11-24 | 2014-11-24 14:40 | 0 | 2014-11-10 09:01 | Tunnelling - Linings - In-situ Concrete | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Other | Completed |  | During the Pre-Pour inspection with CRL and Cxxx of Binocular pour 2 it was noticed taht 4 bars (Bar Mark 38) were not yet intalled. These were installed prior to pouring the wall.
| 01CV - Civils | Cxxx-NCR-001184 | NCR | First Stage Concrete Cubes results did not achieve the required density of 2300kg/m3 |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2014-12-04 | 2014-12-04 21:05 | 0 | 2014-11-10 10:13 | Civil - Tunnelling | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | 23 cubes in 16 sets did not acheive the required density of 2300 kg/m3 at 28 days. Range betwen 2250-2290 kg/m3. 16 sets had low density cubes at 28 days. 7 sets had low density cubes in both 28 days. 9 sets had 1 low density cube 28 day results. 7 days and 56 days cubes results are not applicable and are for information only and are not required to meet specifications. Excel Spreadsheet has been attached- results highlighted yellow.
| 01CV - Civils | Cxxx-NCR-001185 | NCR | First Stage Concrete Cubes damaged. |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2014-12-04 | 2014-12-04 21:08 | 0 | 2014-11-10 11:19 | Tunnelling - Linings - In-situ Concrete | 500 |  | Damaged | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | During transportation/sampling of cubes, 5 no. cubes were damaged- No effect on Concrete cube results Analysis. Excel Sheet attached. Red hightlight indicating damaged cubes.
| 01CV - Civils | Cxxx-NCR-001187 | NCR | Missing accelerator dosing pump calibration check sheets |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2015-02-12 | 2015-02-12 14:53 | 0 | 2014-11-14 12:44 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | Although regular accelerator dosage checks are carried out using Form -082 as per the ITP, there are some missing check sheets. Missing weeks as per below ; Week Ending -Sunday 22/12/13, 12/01/14, 15/02/2014, 23/02/2014, 02/03/2014, 09/03/2014, 20/04/2014, 27/04/2014, 04/05/2014, 11/05/2014, 18/05/2014, 25/05/2014, 01/06/2014, 08/06/2014,15/06/2014,22/06/2014, 29/06/2014, 06/07/2014
| 01CV - Civils | Cxxx-NCR-001188 | NCR | Tunnel - SGI Installation CP3 - Eastbound - Space for SGI Fire Protection layer |  | Crossrail | XRL | TUX - Tunnel Drive X (West) |  | 2015-03-30 | 2015-03-04 22:56 | -26 | 2014-11-11 14:18 | Tunnelling - Linings - SGI Rings | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | As a result of the SGI ring (R1325) at CP3 in the Eastbound tunnel being built out of tolerance there is insufficient space on the intrados of the SGI segments to appy the required 50mm fire protection layer which is to be finished flush to the inside profile of the concrete segments as shown on drawing Cxxx-OVE-C4-DDD-CR001_Z-23093.
| 01CV - Civils | Cxxx-NCR-001189 | NCR | EB Binocular Regulating Layer - Defects identified after BFK sign off |  | Crossrail | PDP | TUX - Tunnel Drive X (West) |  | 2014-12-19 | 2014-12-19 23:37 | 0 | 2014-11-11 15:11 | Civil - Tunnelling | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Other | Completed |  | An 'Approval to spray' sheet (Form 117) was presented to CRL and Cxxx (11/11/2014 7am - attached) , already signed off by for the application of Regulating layer in the EB Binocular. There were several issues preventing the application of regulating layer, that had not been captured by through their ITP procedure (Cxxx--C4-ITP-CRT00_ST005-50139) 1) Profiles were not presented to accurately show the whole tunnel. Resulting survey showed that the transition headwall was tight requiring further milling/rework 2) Core holes had not been filled 3) Monitoring points not removed 4) Leak at headwall not fully sealed The 'approval to spray' form was not signed by CRL, and the rest of the shift was spent re working the area. This NCR is for the defective items above that were not picked up or addressed prior to seeking CRL and Cxxx sign off.
| 01CV - Civils | Cxxx-NCR-001190 | NCR | Fisher Street - EB Binocular Headwall Oversprayed |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2014-11-25 | 2014-11-18 15:26 | -7 | 2014-11-11 15:32 | Tunnelling - Linings - Sprayed Concrete | 2000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Fisher Street SCL Overspray EB Binocular Headwall 1 and 2 (Attached As builts)
| 01CV - Civils | Cxxx-NCR-001191 | NCR | Fisher Street - Missing 2 reinforcement bar mark 26 in the Cast in situ binocular wall |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2014-12-18 | 2014-12-16 02:53 | -2 | 2014-11-11 17:10 | Tunnelling - Linings - In-situ Concrete | 1000 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | It was found, after the second pour of the binocular wall, that 2 of the starter bars (bar mark 26 Cxxx-MMD-C4-DDD-CR086_SH003_5-02051) bars are missing.
| 01CV - Civils | Cxxx-NCR-001192 | NCR | Missing information from BFK 048 Forms for Royal Oak Portal to Paddington Westbound ITP Records |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2014-11-26 | 2014-11-17 09:03 | -9 | 2014-11-12 10:06 | Civil - Tunnelling | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | A number of 048 forms are missing information and should have been completed during pour. Items missing - Concrete temperature and Slump Test Results. Dates missing from 048 forms - 10/05/2014 , 06/05/2014 , 22/04/2014
| 01CV - Civils | Cxxx-NCR-001193 | NCR | EB Binocular Part 3 regulating layer |  | Crossrail | PDP | TUX - Tunnel Drive X (West) |  | 2014-12-19 | 2014-12-22 14:53 | 3 | 2014-11-11 19:07 | Civil - Tunnelling | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Other | Completed |  | The regulating layer in EB Binocular Part 3 was sprayed between 1400hrs and 1600hrs on 11.11.2014. The corresponding 'Approval to Spray' form 117 had not been signed by CRL or Cxxx at this time as it was not signed until approximately 1630hrs. It had been presented to CRL and Cxxx at approximately 7.00am but was not signed due to missing documents - this is the subject of NCR 001189. Thus the regulating layer was sprayed without closure of all relating NCRs, in contravention of ITP Cxxx--C4-ITP-CRT00_ST005-50139 line A1.
| 01CV - Civils | Cxxx-NCR-001194 | NCR | CP4a - Running tunnel mini sumps under excavated |  | Crossrail | XRL | TUX - Tunnel Drive X (West) |  | 2015-01-21 | 2015-01-16 13:02 | -5 | 2014-11-12 09:02 | Tunnelling - Excavation - Hand | 2000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | *NCR raised by CRL - to add additional information* Mini sumps for first stage concrete drainage, outfalling to CP4a main sump, was under excavated 8/9/11. This was not discovered until 7/11/14 when RC concrete works were to commence.
| 01CV - Civils | Cxxx-NCR-001195 | NCR | Missing QA forms for First Stage Concrete ROP to PAD Eastbound |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2014-11-26 | 2014-11-27 20:56 | 1 | 2014-11-12 17:09 | Civil - Tunnelling | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | NCR raised due to missing QA 099a forms for the following locations Rings 13-32, 131-132, 182-183, 204-205, 211-224, 267-283, 344-359, 425-437, 478-489. 099e forms- A number of ring numbers overlap, so it would appear that there has been some confusion on what is left and right channel when kerbs were checked.
| 01CV - Civils | Cxxx-NCR-001196 | NCR | FSC - ROP-PAD - WB & EB - As built position of catchpits |  | Crossrail | XRL | TUX - Tunnel Drive X (West) |  | 2015-02-20 | 2015-02-20 15:05 | 0 | 2014-11-17 10:12 | Tunnelling - Tunnelling General | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | A number of the catchpits in the standard track slab between ROP and PAD in the Westbound & Eastbound Tunnnels have not been installed vertically below the Track SOP as shown on drawings 53204 & 73957.
| 01CV - Civils | Cxxx-NCR-001197 | NCR | CP1 Secondary Lining Profile |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2014-11-27 | 2014-11-20 16:58 | -7 | 2014-11-13 19:21 | Tunnelling - Linings - Sprayed Concrete | 10000 |  | Incorrect Installation | Use As-Is | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | There is ambiguity over the secondary lining profile of CP1. The survey system (provided by __) shows that in all four corners, adjacent to the collars, the final end product (fireproofing layer) will be tight.
| 01CV - Civils | Cxxx-NCR-001198 | NCR | Missing Checks from BFK 099a forms for ROP to PAD Eastbound |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2014-11-27 | 2014-11-27 21:31 | 0 | 2014-11-13 17:26 | Civil - Tunnelling | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | A good percentage of forms are missing minor checks, i.e Engineer have failed to circle yes/no or state not applicable at the time of pour. The 099a forms at the time of completion were earlier revision and later checksheets were revised to show a better representation of the works- ie Aluminium Caps were never used, or draw cords would not have been installed prior to pour taken place and surface area scabbled would not have been checked on those forms. Attached are the checksheets where the engineer have failed to check the pipe has been inspected, tested and passed off, Line and level checked, backing rods flash with Ring, Collars pushed in fully, and O'rings in place.
| 01CV - Civils | Cxxx-NCR-001200 | NCR | Fire Protection for SGI Plate |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2014-11-28 | 2015-01-06 08:49 | 39 | 2014-11-14 09:09 | Tunnelling - Linings - SGI Rings | 5000 |  | Damaged | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | In two locations in the westbound running tunnel by CP1 the fireproofing layer applied to the SGI plate has been damaged. In one area to the western end of the SGI plate, the 50x50mm mesh has been exposed (photos attached) over an area of roughly 2m2. At the eastern end of the plate there is a 'gash' in the lining (most likely from the tooth of an excavator bucket) of size 200x100mmx40mm (photo also attached).
| 01CV - Civils | Cxxx-NCR-001201 | NCR | CP4a - Under thickness of Waterproofing |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2014-11-29 | 2014-12-02 08:57 | 3 | 2014-11-15 19:04 | Tunnelling - Tunnelling General | 2000 |  | Incomplete Works | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | After inspection on site, it was noticed that some areas didn't have enough thickness of waterproofing in CP4a. These areas are above the invert.
| 01CV - Civils | Cxxx-NCR-001202 | NCR | Fisher Street EB1 and EB2 Overspray Regulating layer |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2014-12-31 | 2015-01-08 13:34 | 8 | 2014-11-17 17:20 | Tunnelling - Linings - Sprayed Concrete | 10000 |  | Workmanship | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | Overspray of regulating layer EB1 and EB2 (Attached As-Builts)
| 01CV - Civils | Cxxx-NCR-001203 | NCR | CP1 (RT) Secondary Lining Steel Reinforcement NF |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2014-11-26 | 2014-11-27 21:00 | 1 | 2014-11-19 13:33 | Tunnelling - Linings - Sprayed Concrete | 20000 |  | Incorrect Installation | Use As-Is | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | As part of CP1 (RT) NF steel reinforcement, installed BM04 (labelled as bar 01 in attached sketch) as per drawing Cxxx-MMD-C4-DDD-CR001-06020 Rev C02. BM02 (labelled as bar 02 in sketch) was then subsequently installed with a lap of 760mm to BM04 as per the design. However, the issue arose that due to the slight over excavation (and subsequent spraying of the primary lining) of CP1 the reinforcement specified in the bending schedule Cxxx-MMD-C4-DDJ-CR001-06020 Rev C01 did not reach the required level of 2350mm radially above the SSL, which was brought to the designers attention in Cxxx-RFI-1258 (and Cxxx-NCR-1204); the answer to which was that the bars must reach the intended design level. As a result the site team cut back BM02 towards the invert (leaving 760mm protruding out of the cast invert slab) to avoid having to spray through the NF steel when spraying in the FF reinforcement. Once the FF had been sprayed in an additional 16mm bar (labelled 03 in sketch) was then lapped to BM02 by 760mm to bring the NF reinforcement up to the required level of 2350mm radially above SSL. This resulted in the 'triple lap' splice reinforcement arrangement shown in the attached sketch and photograph.
| 01CV - Civils | Cxxx-NCR-001204 | NCR | Cross passages CP1 Secondary Lining NF Rebar Length |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2014-11-26 | 2014-11-27 21:04 | 1 | 2014-11-19 14:47 | Tunnelling - Linings - Sprayed Concrete | 20000 |  | Incorrect Installation | Use As-Is | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Drawing Cxxx-MMD-C4-DDD-CR001-06020 rev C02 Section B-B indicates BM 02 (shown as bar 02 on the attached sketch) commencing from SSL and of 2350mm in length. would therefore expect the reinforcement to stop 2350mm from SSL measuring radially. The rebar has been tied and spliced to BM04 (shown as bar 01 on the attached sketch) as per the design drawing, but due to the slight over excavation (and subsequent underlations in the spraying of the primary lining - as expected with SCL works) the bar does not reach the required position. To overcome this added an additional 16mm bar, spliced at 760mm, in order that the required design level be reached (refer to Cxxx-FCD-000989, Cxxx-RFI-001258 and Cxxx-NCR-001203). This has resulted in the 'triple lap splice' as shown in the photograph attached, thus creating the buildability issues discussed in Cxxx-FCD-000989 and Cxxx-NCR-001203.
| 01CV - Civils | Cxxx-NCR-001205 | NCR | Galvanised B385 mesh has reduced cover at door jamb on LHS at CP3 EB |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2015-02-15 | 2015-02-24 17:02 | 9 | 2014-11-20 05:23 | Tunnelling - Linings - In-situ Concrete | 500 |  | System Defect | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The galvanised mesh has been installed with less than 30mm cover at CP3 EB on the LHS at the highest section at 200-300mm of the opening. This is due to the door opening being plumb level and the tunnel alignment askew. RFI-001226 instructed "With future collars set the rebar correctly to 50mm cover but install the B385 galvanized mesh to maintain this detail." The rebar was set correctly, however the mesh was unable to fit at the top most point of the jamb due to the steel sets being askew and forcing a reduction in cover at this point for approx 200-300mm.
| 01CV - Civils | Cxxx-NCR-001206 | NCR | Tunnel - FSC: repair of leaking segment joints ROP - PAD Westbound and Eastbound Tunnels |  | Crossrail | XRL | TUX - Tunnel Drive X (West) |  | 2014-12-22 | 2014-12-19 13:29 | -3 | 2014-11-24 10:57 | Tunnelling - Tunnelling General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Not Defined | Completed |  | Trials with CRL/Cxxx/ were undertaken to select the most suitable method of repair for leaking joints (Category E repairs), the current method statement Rev05 of Cxxx--C4-GMS-CRT00_ST005-50200 states that there are two possbile repair methods which are dependent on trials to be undertaken. Category E gasket repairs were carried out in the WB & EB tunnels between ROP-PAD on the rings listed in the attached spreadsheet. The current method statement has not been updated to include this selected method of repair.
| 01CV - Civils | Cxxx-NCR-001207 | NCR | CP1 (RT) Secondary Lining Thickness |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2014-11-25 | 2014-12-11 17:46 | 16 | 2014-11-24 15:43 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Incomplete Works | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | In CP1 (RT) there is one area where the secondary lining is below the required thickness of 200mm (see the attached scans for the as-built information and drawing Cxxx-MMD-C4-DDB-CR001-02021 Cross Passages Cross Sections for the design thickness). The maximum deviation from the minimum thickness is 7mm (i.e. the thickness is 193mm).
| 01CV - Civils | Cxxx-NCR-001208 | NCR | CP1 (RT) Fireproofing Final As-Built Profile |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2015-03-11 | 2015-03-04 17:31 | -7 | 2014-11-26 16:59 | Tunnelling - Linings - Sprayed Concrete | 5000 |  | Incorrect Installation | Use As-Is | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The final as-built profile of CP1 (RT) is tighter, in places, than the revised profile agreed as per Cxxx-NCR-001197 by up to 50mm. This is due to being unable to push the NF steel back as far they had hoped at roughly axis level. This coupled with an average fireproofing thickness of 70mm has left the final profile tighter than intended.
| 01CV - Civils | Cxxx-NCR-001209 | NCR | Missing deliverable records from ITP ‘Sprayed Concrete Testing’ package June and no process identified for formally submitting outstanding deliverable documents |  | Crossrail | XRL | TUX - Tunnel Drive X (West) |  | 2015-04-23 | 2015-04-05 23:43 | -18 | 2014-11-25 15:47 | Tunnelling - Tunnelling General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Other | Completed |  | During a planned Crossrail surveillance dated 11th November 2014 a review was carried out on the June SCL ITP material records handover package which had been submitted to Crossrail. During the review it was highlighted that no process was in place for how follow up submitted packages to ensure ‘outstanding’ documentation (results) is attached once received, i.e. 90 days. This is prevalent from review of the packages content as detailed below; Under section ‘Flexural Beam’, 28 day test results were included with one test sample showing a non conformance on the D3 criteria which was recorded under Cxxx-NCR-001072. As the sample failed to meet the 28 day performance requirements, 90 day test samples were taken by . On review, the Materials Technician made available the 90 day test results, which were received in September 2014, however the results were not included in the certification package. Under section ‘Drying Shrinkage’ no records were present, however an NCR reference number existed (Cxxx-NCR-001073). On review of the NCR, it detailed that the laboratory had lost the test samples and could not undertake testing, however of further reading under ‘actual answer’, it was detailed that the samples had been found and the testing carried out. The Materials Technician had readily available the drying shrinkage results for June, which were received in September but not included in the submission. NCR was raised to ensure a review is carried out on all other submissions, and a process identified for capturing outstanding results.
| 01CV - Civils | Cxxx-NCR-001210 | NCR | CP4a - Installing steel dowels (instead of GRP dowels) into the waterproofing membrane |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2014-12-10 | 2014-12-02 09:00 | -8 | 2014-11-26 09:43 | Tunnelling - Tunnelling General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During the installation of the reinforcement steel for the secondary lining works of the base of the sump, some steel dowels were installed into the waterproofing membrane to tie the reinforcement instead of grp dowels.
| 01CV - Civils | Cxxx-NCR-001211 | NCR | North Audley Street Inclinometer Cxxx-IM600002 Installed 3 meters Short |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2014-12-10 | 2014-12-04 22:11 | -6 | 2014-11-26 16:42 | Surveying - Instrumentation and Monitoring | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | On North Audley Street monitoring instrumentation installation, inclinometer Cxxx-IM600002 was installed 3 meters short. That due to the boreholefor the inclinometer Cxxx-IM600002 was installed in partially collapsed during installation and the inclinometer was installed three meters too shallow.
| 01CV - Civils | Cxxx-NCR-001212 | NCR | Missing Spiral Survey Results for Inclinometer (Earnshaw Street) |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2014-12-10 | 2014-12-04 22:12 | -6 | 2014-11-26 17:03 | Surveying - Instrumentation and Monitoring | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Information not detailed | Completed |  | No Spiral Test Results available for Inclinometer installed at Earnshaw Street.
| 01CV - Civils | Cxxx-NCR-001213 | NCR | Repair to ring 284WB tunnel |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2014-12-03 | 2014-12-10 18:02 | 7 | 2014-11-27 18:49 | Civil - Tunnelling | 2000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | During the Ring Repairs Survey for the second review of the ROP-PAD WB package, ring number 284 WB Tunnel was discovered to have some major cracks.
| 01CV - Civils | Cxxx-NCR-001214 | NCR | FIS Secondary Lining - WBX Binocular - Concrete Repairs |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2015-10-16 | 2015-11-18 11:42 | 33 | 2014-11-28 09:29 | Civil - Tunnelling | 5000 |  | Workmanship | Repair | 3 (3-6k) | Complete | Material/Preservation Problems - Other | Completed |  | Following Cast In Situ concrete works to the WBX Binocular, a number of areas require remedial works to achieve a high quality finish. Works include rubbing up concrete, removing fins and matching in joints.
| 01CV - Civils | Cxxx-NCR-001215 | NCR | SCL flexural beam test failure - Fisher Street (June 2014) |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2015-01-31 | 2015-02-02 10:35 | 2 | 2014-11-28 13:08 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | 90 day beam test failure (KT20) - abrupt failure. See attached report containing copies of the beam test results and technical narrative on the results, plus a detailed justification for why this is considered to be acceptable "leave as is".
| 01CV - Civils | Cxxx-NCR-001216 | NCR | Minor honeycombing in CP3 EB collar soffit |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2015-02-19 | 2015-02-25 16:55 | 6 | 2014-11-30 18:32 | Tunnelling - Linings - In-situ Concrete | 1000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | When the CP3 soffit shutter on the EB was struck, there was found to be some minor honeycombing in the crown.
| 01CV - Civils | Cxxx-NCR-001217 | NCR | CP4a - Width of the recess at the WB collar |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2014-12-15 | 2014-12-15 08:51 | 0 | 2014-12-01 13:23 | Tunnelling - Tunnelling General | 1000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | According to drawing Cxxx-OVE-C4-DDD-CR001_Z-23101, a recess 260x100 deep in floor for door should have been formed on the Westbound and on the Eastbound Collar. Due to setting out issues, the recess on the WB collar was casted in the wrong location and it didn’t have the width required as per design.
| 01CV - Civils | Cxxx-NCR-001218 | NCR | Cable ducts have lifted on the inside of the EB collar of CP2 |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2015-02-15 | 2015-02-17 13:25 | 2 | 2014-12-01 17:32 | Tunnelling - Linings - In-situ Concrete | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Contamination | Completed |  | The internal end of the cable ducts that were cast into the invert pour of CP2 EB have risen up to 100mm. Concrete has also penetrated the ducts from the internal side partially. The ducts have been cleared out since
| 01CV - Civils | Cxxx-NCR-001219 | NCR | CP4a - 40 mm step in the fireproofing of the EB collar |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2014-12-16 | 2014-12-11 14:02 | -5 | 2014-12-02 20:11 | Tunnelling - Tunnelling General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | As per KN20, the SGI openings are to be sprayed with a 50mm layer of fireproofing. On the EB collar of CP4a, the collar was casted following drawings Cxxx-OVE-C4-DDD-CR001_Z-23101 and 23102, leaving an opening of 2.4m. However, due to a misalignment of the SGI rings and to ensure a minimum of 50 mm of fireproofing, when spraying the SGI ring we ended up with a 40 mm step. See attached pictures showing the following: * Opening of 2.36m where the SGI's were sprayed; * 40 mm step in the fireproofing. Before approval to spray the SGIs, this was discussed and agreed with Cxxx (__) on site as it was inevitable to avoid the step.
| 01CV - Civils | Cxxx-NCR-001220 | NCR | CP4a - Duct pipes at the wrong level on the WB Collar |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2015-01-17 | 2015-01-14 17:16 | -3 | 2014-12-02 20:30 | Tunnelling - Tunnelling General | 2000 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Following Cxxx-RFI-001253, have poured the invert slab in conjuction with the slab of the WB Collar. In order to do that the duct pipes and steel pipe described on drawing Cxxx-OVE-C4-DDD-CR001_Z-23102 were installed prior to the pour and tyed up using dowels and steel bars. See attached picture 1 showing the duct, steel pipe and rebar prior to the commencement of the pour. After pouring the invert it was noticed that two of the pipes ended up in the wrong position. (see pic 4451 attached) It was agreed between , CRL & Cxxx to break out the slab, fix the ductpipes into the right position and grout back to the FFL. These works have been carried out shown in the pictures 3 & 4attached.
| 01CV - Civils | Cxxx-NCR-001221 | NCR | Overspray Fireproofing CP4a ch 5.5 - 17.50 |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2014-12-17 | 2014-12-11 17:48 | -6 | 2014-12-03 18:09 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | After spraying the fireproofing in CP4a between ch. 5.5- 17.50, the profiles have been assessed by __ () and presented to __ (Cxxx) and Dan Callaghan (CRL).It was concluded that there are overspray areas between 10mm up to a maximum of 30mm.The 30mm overspray is in a localised area which coincide with the flare (see attached plan view and profiles)
| 01CV - Civils | Cxxx-NCR-001222 | NCR | CP4a - Exposing Rebar while milling of secondary lining was carried out |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2014-12-17 | 2014-12-17 16:26 | 0 | 2014-12-03 18:38 | Tunnelling - Tunnelling General | 0 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | After obtaining the as-built survey of the Secondary Lining on CP4a it was noticed that there were some tight areas and that milling was required to get at least 50 mm of fireproofing layer. During the milling works some rebar was exposed locally. It was agreed with Cxxx to use the fireproofing layer as cover to the steel since it is only required 35 mm of cover and there was at least 50 mm of fireproofing to spray. In attachment it is provided the following documentation: *approval to spray fireproofing signed off by all parties; *as built profiles of secondary lining showing enough room for 50 mm of fireproofing layer.
| 01CV - Civils | Cxxx-NCR-001223 | NCR | CP4a - Mesh used in the WB Collar opening |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2014-12-17 | 2014-12-17 16:34 | 0 | 2014-12-03 20:07 | Tunnelling - Tunnelling General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Use of unapproved materials | Completed |  | As per KN20.3301 the fire protection to the SGI Linings should include a 50mm x 50mm x 1.5mm grade 316 stainless steel mesh to the face of the shotcrete infill and supported at approximately mid-depth of the fire protection mortar. At the WB collar of CP4a it was used a Stainless steel B385 mesh. This was discussed with Cxxx & CRL prior to the approval to spray the fireproofing. It was agreed to leave the mesh in place. See attached reinforcement checksheet signed off and pictures showing the mesh installed.
| 01CV - Civils | Cxxx-NCR-001224 | NCR | Fisher Street Westbound binocular secondary lining - High results of weekly fresh washout count of polyfibres mix 24 |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2015-01-23 | 2015-02-05 09:48 | 13 | 2014-12-08 18:02 | Tunnelling - Linings - In-situ Concrete | 500 |  | Testing and Commissioning | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | Fresh fibre washout test performed on the 30/10/2014, samples EX-892.1/2/3, shows results between 6-9 kg/m3, the specified in the mix design is 2Kg/m3. These results are very high considering the mix design.
| 01CV - Civils | Cxxx-NCR-001225 | NCR | FIS-Insufficient Early age strenght results for advance 8,12 and 16 - Crossover |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2015-04-08 | 2015-04-09 09:33 | 1 | 2014-12-12 16:48 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Testing and Commissioning | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | FIS Crossover -Insufficient Early age strength results from ; Advance 8 - below than modified J2 curve at 1 hr and 2 hrs, Advance 12 -below than modified J2 curve at 2 hrs . Advance 16 -below than modified J2 curve at 1 hr and 2 hrs.
| 01CV - Civils | Cxxx-NCR-001226 | NCR | Green Lane Sewer - Detailed Design |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2015-02-16 | 2015-02-04 13:08 | -12 | 2015-01-06 10:20 | Civil - Sewage/Water services | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Green Lane Sewer scheme design in the Works Information, adopted as the Employers Design as agreed in Green Lane Sewer Permanent Works Design Management document (Cxxx--U-RGN-CRT00_ST005-50007), in some locations was un-buildable and in others Crossrail/__ required different items. In conjunction with Crossrail and __, an alternative solution has been arrived at through many meetings and RFI's to the satisfaction of Crossrail and __. This solution has been issued on eB and accepted by __ and Crossrail for construction. This NCR is to formally record that the submitted design is non-conforming to the original Works Information scheme design. There is no requirement for any corrective actions. The changes can be seen in the differences between the original Works and Site information CRL1-THW-U-XWI-CRG03-50017 rev 3.0 and the final design drawings listed in the design register Cxxx--U-LRG-CRT00_ST005-50001.
| 01CV - Civils | Cxxx-NCR-001227 | NCR | FSC BOS-PAD Pipe lifted in concrete slba between rings 1331-1341 |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2015-04-14 | 2015-04-17 09:17 | 3 | 2014-12-11 09:22 | Civil - Tunnelling | 5000 |  | Workmanship | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During the concrete pour, a section of concrete pipe lifted when struck by the concrete train ladder. As a result the pipe lost its fitting with the slab and after concreting it, the pipe began to rise from its fixed position. This section was between ring 1331-1341.
| 01CV - Civils | Cxxx-NCR-001228 | NCR | Discrepancies between HLCs and other instrumentations in Davies Mews-North side South Molton Street |  | Crossrail | XRL | TUX - Tunnel Drive X (West) |  | 2015-01-16 | 2015-01-13 12:08 | -3 | 2014-12-11 11:43 | Geotechnical Engineering - Geotechnical Monitoring | 500 |  | Equipment Breakdown | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | Between 22/02/14 and 17/07/14, the data from HLCs SM2301M to SM2314M experienced a heave of approximately 10 mm in total. This apparent movement was not reflected neither by the __s nor the prisms in the same location, which were actually showing a settlement trend. The implication is that the HLCs system experienced some malfunction that wasn't corrected until July, when the data's trend reverts to settlement, matching the surrounding instrumentation's. The exact nature of the problem and the correction used have not been stated.
| 01CV - Civils | Cxxx-NCR-001229 | NCR | Incorrect Installation of Sheet Membrane in EBX Binocular Central Pillar Wall and Headwall |  | Crossrail | XRL | TUX - Tunnel Drive X (West) |  | 2015-09-24 | 2015-09-28 12:56 | 4 | 2014-12-17 23:25 | Tunnelling - Tunnelling General | 20000 |  | Incorrect Installation | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | In the cavern section of the Eastbound tunnels, at the interface between the EBX and E__ tunnels, the sheet waterproof membrane at the junction between the E__ tunnel and the EBX Cavern has been incorrectly installed. As installed while carrying out the WBX works, the sheet waterproof membrane should have been brought around the headwall prior to casting the invert (of the headwall section). Due to the incorrect installation, a termination bar has been installed up the side of the invert in E__ (this is not compliant with design drawings).
| 01CV - Civils | Cxxx-NCR-001230 | NCR | FSC_BOS to TCR_Westbound_Catchpits installed in FTS slab |  | Crossrail | XRL | TUX - Tunnel Drive X (West) |  | 2015-01-30 | 2015-02-05 12:24 | 6 | 2014-12-12 10:26 | Civil - Tunnelling | 10000 |  | Incorrect Installation | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Insufficient information made available to the worker. | Completed |  | The Type 3 catch pit installed at the interface between STS and FTS (WB Ring 2442) first stage concrete was installed within FTS section instead of the STS section as shown on catchpit detail drawing Cxxx-OVE-D-DDD-CR001-Z-53206.
| 01CV - Civils | Cxxx-NCR-001231 | NCR | FSC_BOS to TCR_Eastbound_Catchpits installed in FTS slab |  | Crossrail | XRL | TUX - Tunnel Drive X (West) |  | 2015-01-30 | 2015-02-05 12:30 | 6 | 2014-12-12 10:47 | Civil - Tunnelling | 10000 |  | Incorrect Installation | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Insufficient information made available to the worker. | Completed |  | The Type 3 catch pits installed at the interfaces between STS and FTS (EB Rings 2313/2314 and EB Rings 2397/2398) first stage concrete wer installed within FTS section instead of the STS section as shown on catchpit detail drawing Cxxx-OVE-D-DDD-CR001-Z-53206.
| 01CV - Civils | Cxxx-NCR-001232 | NCR | Fisher Street - Testing of fresh concrete before use (advance 31 crossover) |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2015-02-19 | 2015-02-05 10:02 | -14 | 2014-12-15 09:17 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Testing and Commissioning | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | Stand by load was used to spray the initial lining of advance 31 without being tested immediately before use. The load was tested last time at 10:20am and used approx. at 11:50am. The values at the last testing were 520 mm and 17.4 degrees. Load was only used to spray the initial.
| 01CV - Civils | Cxxx-NCR-001233 | NCR | Holes at Rings 2301 and 2350 EB Tunnel |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2015-01-21 | 2015-01-19 17:19 | -2 | 2014-12-16 12:40 | Civil - Tunnelling | 3000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Resin has been injected in two holes between BOS-TCR EB Tunnel at Rings 2301 and 2350 but the holes should have been repaired as per Category H according to the RAMS Cxxx--C4-GMS-CRT00_ST005-50200.
| 01CV - Civils | Cxxx-NCR-001234 | NCR | Crack at ring 2441 EB Tunnel |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2015-01-20 | 2015-01-20 17:52 | 0 | 2014-12-16 13:17 | Civil - Tunnelling | 5000 |  | Damaged | Repair | 3 (3-6k) | Complete | External Phenomenon - Other | Completed |  | A dry crack with a width of more than 4 mm has been observed in segment KL at Ring 2441 EB has a crack with a width > 4mm.
| 01CV - Civils | Cxxx-NCR-001235 | NCR | Royal Oak Head house holding down bolts |  | Contr | KIR | TUX - Tunnel Drive X (West) |  | 2015-02-27 | 2015-02-27 10:29 | 0 | 2014-12-19 10:28 | Civil - Structural Engineering | 5000 |  | Damaged | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Worker not correctly instructed | Completed |  | Some of the type 1 head house holding down bolts installed by C330 on the portal structure have been cut off at finished concrete level. See attached repair procedure for locations.
| 01CV - Civils | Cxxx-NCR-001236 | NCR | FSC - TCR to FIS WB - UTX filled with water |  | Crossrail | XRL | TUX - Tunnel Drive X (West) |  | 2015-01-31 | 2015-02-05 09:49 | 5 | 2014-12-17 16:15 | Tunnelling - Linings - In-situ Concrete | 5000 |  | Damaged | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Other | Completed |  | * NCR raised by CRL - to review* UTX duct between TCR - FIS WB filled with water (3352 WB)
| 01CV - Civils | Cxxx-NCR-001237 | NCR | BOS-TCR EB Tunnel Pressure relief drains |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2015-01-22 | 2015-02-05 12:32 | 14 | 2014-12-18 07:48 | Civil - Tunnelling | 5000 |  | Damaged | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Insufficient information made available to the worker. | Completed |  | Resin was found inside the some pressure relief drains due to failed injections and resin coming from the crown injections. Between BOS-TCR EB Tunnel, between rings: •2704 •2695 •2690 •2688 •2681 •2645 •2641 •2624 •2545 •2531 •2503 •2493 •2474 •2475 •2469 Low amount of resin has been used (average of 0.1 litres per ring).
| 01CV - Civils | Cxxx-NCR-001241 | NCR | 200mm steel duct for discharge pipe at CP2 WB collar has risen on running tunnel side |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2015-02-05 | 2015-02-12 15:12 | 7 | 2015-01-06 06:29 | Tunnelling - Linings - In-situ Concrete | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The cast in steel duct at CP2 WB collar has risen approximately 100mm at the the external side of the CP2 WB collar. The internal side has remained in the correct position
| 01CV - Civils | Cxxx-NCR-001242 | NCR | Damage to 3rd Party Monitoring prisims installed under Cxxx-PMI-01378_WB tunnel Rings 1794 and 1851 |  | Crossrail | XRL | TUX - Tunnel Drive X (West) |  | 2015-05-15 | 2015-05-15 08:50 | 0 | 2015-01-06 14:43 | Civil - Tunnelling | 2000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Improper preservation of material after installation | Completed |  | The 3rd Party monitoring prisims installed by under Cxxx-PMI-01378 in the Westbound tunnel between rings 1794 and 1851 have been damaged by traffic in the tunnel during the Cross Passage works. Attached is the findings from an inspection carried out on the 11/12/2014.
| 01CV - Civils | Cxxx-NCR-001243 | NCR | Cross Passages Drainage pipe |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2015-01-29 | 2015-02-10 09:24 | 12 | 2015-01-07 09:09 | Civil - Tunnelling | 3000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The drainage pipe on the Westbound of CP3 and CP4 has been cast in using PVC pipe.
| 01CV - Civils | Cxxx-NCR-001245 | NCR | ROP-PAD Westbound Tunnel. Sections out of extended tolerance. Vertical Measurement on kerb. |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2015-02-20 | 2015-02-19 21:25 | -1 | 2015-01-16 17:36 | Civil - Tunnelling | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Some points on kerbs were found out of vertical tolerance after the As built survey. Accuracy of the total station +/-3mm. Please See columm Y diff (2-6) in the attached document. + Noth & Up -South and Down
| 01CV - Civils | Cxxx-NCR-001247 | NCR | ROP-PAD Westbound Tunnel. Sections out of extended tolerance. Horizontal deviation. |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2015-02-20 | 2015-02-20 12:40 | 0 | 2015-01-16 18:09 | Civil - Tunnelling | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Some points were found out of extended horizontal tolerance between ROP-PAD STS slab after the As built Survey. See attached document column "X Diff".
| 01CV - Civils | Cxxx-NCR-001248 | NCR | FSC BOS-TCR EB FTS braking block reinforcement cover |  | Crossrail | XRL | TUX - Tunnel Drive X (West) |  | 2015-01-21 | 2015-01-27 18:25 | 6 | 2015-01-07 14:23 | Tunnelling - Tunnelling General | 5000 |  | Incorrect Installation | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Similar to NCR 1167 and 1168, the braking blocks have been constructed with excessive concrete cover to the reinforcement.
| 01CV - Civils | Cxxx-NCR-001249 | NCR | FSC_TCR to KTT_WB_Catchpits_Temporary M16 bars not removed from permanent works |  | Crossrail | XRL | TUX - Tunnel Drive X (West) |  | 2015-03-11 | 2015-03-07 23:44 | -4 | 2015-01-08 17:16 | Civil - Tunnelling | 1000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The RAMS for the FSC states that 4 M16 threaded bars are dirlled into tunnel lining to temporarily support the formwork for the catchpits. Once the FSC has been cast the M16 bars are to be unscrewed and the holes filled with grout. In the westbound tunnel between TCR and KTT tunnel at FIS (Rings 3130 to 3527) the M16 bars have been cut flush with the invert of catchpit making it not possible to unscrew the M16 bars.
| 01CV - Civils | Cxxx-NCR-001250 | NCR | FSC_TCR to KTT_E_Catchpits_Temporary M16 bars not removed from permanent works |  | Crossrail | XRL | TUX - Tunnel Drive X (West) |  | 2015-02-26 | 2015-02-26 19:57 | 0 | 2015-01-08 17:22 | Civil - Tunnelling | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The RAMS for the FSC states that 4 M16 threaded bars are dirlled into tunnel lining to temporarily support the formwork for the catchpits. Once the FSC has been cast the M16 bars are to be unscrewed and the holes filled with grout. In the Eastbound tunnel between TCR and KTT tunnel at FIS (Rings 3050 to 3466) the M16 bars have been cut flush with the invert of catchpit making it not possible to unscrew the M16 bars.
| 01CV - Civils | Cxxx-NCR-001251 | NCR | Damaged Segments at Rings 3291 and 3436 EB Tunnel. |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2015-01-26 | 2015-01-27 18:07 | 1 | 2015-01-12 11:33 | Civil - Tunnelling | 1000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | During the joint survey with CRL two rings were found damaged at Rings 3291 and 3436 EB.
| 01CV - Civils | Cxxx-NCR-001252 | NCR | 185-190mm thickness of secondary lining in CP4 (rt) in localised area (10-15mm under design) |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2015-01-26 | 2015-02-11 13:15 | 16 | 2015-01-12 13:32 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | After completion of secondary lining an area shown (as per attached) was shown to be short thickness in a localised area. This was discussed and identified with the CRL team and it was agreed to use as is and to proceed with fireproofing.
| 01CV - Civils | Cxxx-NCR-001253 | NCR | FSC BOS-TCR WB FTS braking block reinforcement cover |  | Crossrail | XRL | TUX - Tunnel Drive X (West) |  | 2015-02-05 | 2015-02-11 08:32 | 6 | 2015-01-13 10:26 | Tunnelling - Tunnelling General | 5000 |  | Incorrect Installation | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Similar to NCR 1167, 1168 and 1248, the braking blocks have been constructed with excessive concrete cover to the reinforcement.
| 01CV - Civils | Cxxx-NCR-001254 | NCR | FSC reinforcement cover BOS - TCR WB 2644 RHS |  | Crossrail | XRL | TUX - Tunnel Drive X (West) |  | 2015-01-27 | 2015-02-11 09:00 | 15 | 2015-01-13 12:37 | Tunnelling - Tunnelling General | 1000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During braking block inspection by A Alchin and A Albu it was discovered that a reinforcment bar has 15mm cover at the point where it protrudes from the concrete kerb into the exposed reinforcement cage of the breaking block.
| 01CV - Civils | Cxxx-NCR-001255 | NCR | ROP-PAD Westbound tunnel. Sections within allowable extended Tolerance as per RFI. |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2015-02-20 | 2015-02-19 21:34 | -1 | 2015-01-16 18:12 | Civil - Tunnelling | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Some points were found within extended tolerance according to RFI 1297 between ROP-PAD on the WB Tunnel. See attached document for details STS-HAS 1.
| 01CV - Civils | Cxxx-NCR-001257 | NCR | ROP-PAD Eastbound Tunnel. FSC As Built Sections out of tolerance. Vertical Measurement on kerb. |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2015-02-20 | 2015-02-19 21:39 | -1 | 2015-01-16 17:31 | Civil - Tunnelling | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Some points out of tolerance were found after the As built survey in the EB Tunnel ROP-PAD Section.
| 01CV - Civils | Cxxx-NCR-001258 | NCR | ROP-PAD Eastbound Tunnel. FSC As Built Sections out of tolerance. Slope on Kerb. |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2015-02-20 | 2015-02-19 21:43 | -1 | 2015-01-16 18:23 | Civil - Tunnelling | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Some points out of tolerance in the solpe on the kerbs were found after the As built survey of the STS section between ROP-PAD.
| 01CV - Civils | Cxxx-NCR-001259 | NCR | ROP-PAD Eastbound Tunnel. FSC As Built Sections out of extended tolerance. Horizontal deviation. |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2015-02-20 | 2015-02-20 12:49 | 0 | 2015-01-16 18:28 | Civil - Tunnelling | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Some points out of horizontal tolerance were found after the As built survey of the STS section between ROP-PAD.
| 01CV - Civils | Cxxx-NCR-001260 | NCR | ROP-PAD Eastbound tunnel. Sections within allowable extended Tolerance as per RFI. |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2015-02-20 | 2015-02-19 21:47 | -1 | 2015-01-16 18:29 | Civil - Tunnelling | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | See "NCR UAI" values in attached excel file on EB Document: Cxxx--C4-LRC-CRT00_ST005-50420.
| 01CV - Civils | Cxxx-NCR-001261 | NCR | Fisher Street - Lack of curing in reinforced primary lining thickening layer |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2015-03-31 | 2015-03-26 08:18 | -5 | 2015-01-14 15:31 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | KT20.3225 a) requires that secondary sprayed concrete linings and primary linings that contain structural steel reinforcement (e.g. Junctions) shall be cured in accordance with BS EN 14487-2 unless otherwise accepted by the Project Manager. Details of the Contractors curing methods shall be submitted to the Project Manager with the mix design details 9 weeks before commencement of the works. Some parts of the primary lining thickening layer for CP1 breakout have reinforcement and have not been cured as required.
| 01CV - Civils | Cxxx-NCR-001262 | NCR | Blocked UTX at ring No 2699 CH 4651.8 |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2015-01-28 | 2015-02-11 17:46 | 14 | 2015-01-14 16:12 | Tunnelling - Tunnelling General | 1000 |  | Damaged | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Contamination | Completed |  | UTX duct have been accidentally filled by resin used by caulker to repair cracks in the concrete lining in nearby area. Inspection rod entered from opposite end of UTX proves that UTX filled up to half way (up to underneath of drainage channel)
| 01CV - Civils | Cxxx-NCR-001263 | NCR | Fisher Street Damaged to Crossover thickening reinforcement during mucking out at CP1 Junction |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2015-03-26 | 2015-03-24 09:27 | -2 | 2015-01-15 12:05 | Tunnelling - Linings - Sprayed Concrete | 5000 |  | Workmanship | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During mucking out operations in CP1 reinforcement bar mark 30 and bar mark 21 in Crossover thickening area were damaged.
| 01CV - Civils | Cxxx-NCR-001264 | NCR | Localised thickness areas underthickness primary lining CP3 RT |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2015-02-14 | 2015-02-04 11:08 | -10 | 2015-01-15 16:59 | Tunnelling - Linings - In-situ Concrete | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | NCR details - “During review of asbuilt records Cxxx--C4-LRC-CRT00_ST005-50675 for the excavation and primary lining of CP3, it was discovered that some sections of tunnel lining were not constructed to the required thicknesses. These were not discovered during the time of construction or addressed in the SRG meetings.” Cause corrective actions - “Discussions between CRL, Cxxx and have agreed at the following location:- Chainage 4, 375mm of 400mm required – RC concrete collars now constructed therefore primary lining is redundant. Use as is. Chainage 5.5, 222mm of 250mm required – small localised area. Settlement monitoring proved no convergence during construction. Secondary lining complete. Use as is. Chainage 12.5, 386 of 400mm required – RC concrete collars now constructed therefore primary lining is redundant. Use as is.”
| 01CV - Civils | Cxxx-NCR-001265 | NCR | Concrete Pour Records Sheet BFK-048 Not Filled in as per CP1 SL ITP for Collars |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2015-03-19 | 2015-03-18 15:04 | -1 | 2015-01-19 18:37 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Not Defined | Completed |  | Item B22 (-form 048) is missing from the ITP records for reinforced concrete works cross passages collars. believes it is a mistake on the ITP. The ITP used is attached with this NCR. Following discussion between and CRL does not intend to revise the said ITP. The reason for that is crosspassage works are finished. propose to close this NCR as the evidence attached is sufficient to prove that we are compliant.
| 01CV - Civils | Cxxx-NCR-001266 | NCR | Concrete Pour Records Sheet BFK-048 Not Filled in as per CP1 SL ITP for Sumps |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2015-03-20 | 2015-03-19 13:30 | -1 | 2015-01-19 18:33 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | Item B22 (-form 048) is missing from the ITP records for CP1 Secondary lining ITP for sumps. believes it is a mistake on the ITP. propose to up rev the existing ITP The ITP used is attached with this NCR.
| 01CV - Civils | Cxxx-NCR-001267 | NCR | Damaged UTX in WB TCR-BOS |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2015-02-03 | 2015-02-11 08:35 | 8 | 2015-01-20 18:43 | Tunnelling - Tunnelling General | 6000 |  | Damaged | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | Installed by FSC team UTXs were damaged by vehichles driving from/to CP4A works area. Inspection on 16/01/15 identified outstanding repairs at rings 2478, 2476, 2471, 2468, 2452, 2530, 2601, 2648, 2686, 2693, 2696 and 2714
| 01CV - Civils | Cxxx-NCR-001268 | NCR | FSC BOS Unsatisfactory quality of STS kerb (north side) Ring No 2322-2326 TCR-BOS westbound |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2015-02-09 | 2015-02-05 12:44 | -4 | 2015-01-23 12:37 | Tunnelling - Linings - In-situ Concrete | 2000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | While striking off formwork of newly built kerbs at North side ring No 2322-2326(which was cast on Sunday 18th Jan day-time), quality of concrete observed to be unsatisfactory by section engineer Khalid Zegmou. This was the area from where pour has started. understand that the concrete pump's primer have been incorporated into the works.
| 01CV - Civils | Cxxx-NCR-001269 | NCR | Fisher Street - Breach of max advance rate in crossover between SOP0432 & SOP0433 |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2015-03-26 | 2015-03-23 22:27 | -3 | 2015-01-26 17:41 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Excavation of advance 68 took place less than 24hours after the start of the previous ring (advance 65). This took place within an area where the max advance rate is 2m/24hours. Advance 65 was started at 10am of 25/01/2015, ring closed with invert 67, and then top heading 68 started at 2am of 26/01/2015, only 16h after.
| 01CV - Civils | Cxxx-NCR-001271 | NCR | Fisher Street - Clash between CP1 primary lining and WB binocular headwall lining |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2015-03-26 | 2015-02-04 15:56 | -50 | 2015-01-26 18:34 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Design | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Information not detailed | Completed |  | During excavation of CP1 in the Fisher Street Crossover, it was noticed that the headwall in the end of the Westbound binocular clashes with the position of the primary lining of CP1. During excavation of advance 3, the primary lining of the headwall was protruding in the theoretical line of excavation of CP1, as per attached as builds of CP1 excavation. The over excavation and the tolerances used to build the WB binocular wall increased the problem of the clash. Also, during the excavation of advance 3, whilst trying to break some of the concrete from the headwall, the lining thickness of the headwall was compromised and a hole was created through the primary lining. This was re sprayed to the correct thickness during the installation of the lining in CP1
| 01CV - Civils | Cxxx-NCR-001272 | NCR | In september 2014 the fibre content from fresh sample was from 3 samples and not 6 at Fisher Street |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2015-03-19 | 2015-03-26 21:29 | 7 | 2015-01-27 11:50 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | In september 2014 the fibre content was taken from 3 samples and not the required 6 samples from the ITP Cxxx--C4-ITP-CRT00_ST005-50073. Line B3.3.1
| 01CV - Civils | Cxxx-NCR-001273 | NCR | Concrete Pour Records Sheet BFK-048 Not Filled in as per RC Collars to Cross Passages ITP - CP4a |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2015-02-17 | 2015-02-17 14:25 | 0 | 2015-01-27 16:31 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Verification Problems - Other | Completed |  | Item B11 and B22 (-form 048) is missing from the ITP records for reinforced concrete works cross passages collars. believes it is a mistake on the ITP. propose to up rev the existing ITP The ITP used is attached with this NCR.
| 01CV - Civils | Cxxx-NCR-001274 | NCR | FIS Secondary Lining - EBX Binocular Construction - Compaction Issue with Binocular Wall Pour 2 |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2015-08-13 | 2015-08-27 14:22 | 14 | 2015-01-27 13:39 | Civil - Tunnelling | 10000 |  | Manufacturing Defect | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | Following removal of the shutter from the Binocular Wall pour 2 (EBX), a section of poorly compacted concrete was visible within the wall. Before the issue could was discussed with CRL, the site team carried out a repair on the concrete. Therefore, the compaction of concrete and the unplanned repair constitute a Non Conformance.
| 01CV - Civils | Cxxx-NCR-001275 | NCR | Rebound test not done every two months between August and December 2014 Fisher street |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2015-02-17 | 2015-02-17 16:32 | 0 | 2015-01-27 15:29 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | Rebound test was not done every two months as is the requirement from KT 20 and the ITP. Rebound was should have been done in October 2014 but was not.
| 01CV - Civils | Cxxx-NCR-001276 | NCR | Regulating mix has not had dry shrinkage test done FIS |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2015-02-17 | 2015-02-17 16:43 | 0 | 2015-01-27 16:30 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | Regualting started in fisher street in august 2014 and although not much volume has been sprayed, estimated to be 40m^3, KT20 and the ITP state that dry shrinkage needs to be taken every month and it has not been. In fact the first sample taken for regulating has been taken in January 2015.
| 01CV - Civils | Cxxx-NCR-001277 | NCR | Fireproofing layer final profile |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2015-02-20 | 2015-02-26 08:13 | 6 | 2015-01-27 18:59 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The scan performed to the fireproofing layer of Cross Passages 3 shows enough thickness for the full length of the tunnel. The scan performed to the fireproofing layer of Cross Passages 4 shows generally enough thickness for the full length of the tunnel. There is very localised areas (under 0.250m2) with thickness 40-50mm (see profiles). The scan performed to the fireproofing layer of Cross Passages 3 shows the lining constructed generally within tolerance. There is very localised areas (under 0.250m2) where profile is 10 mm tight (10 mm red) (see profiles). The scan performed to the fireproofing layer of Cross Passages 4 shows the lining constructed generally within tolerance. There is some areas localised areas where profile is up to 30 mm tight (30 mm red) (see profiles).
| 01CV - Civils | Cxxx-NCR-001278 | NCR | Fibre washouts from cast secondary lining not done once a week. FIS |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2015-03-18 | 2015-03-23 21:26 | 5 | 2015-01-28 11:47 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | For mix 24 & 24a 3 samples once a week have not been taken for fibre washouts. with 4 weeks missed for mix 24 and 1 week missed for mix 24a. This is a requirement from KF10.2208 and the ITP Cxxx--C-ITP-CRT00_ST005-50186.
| 01CV - Civils | Cxxx-NCR-001279 | NCR | Drying shrinkage not taken at required frequency for cast secondary lining mixes FIS |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2015-02-18 | 2015-02-25 15:01 | 7 | 2015-01-28 12:10 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | Only one drying shrinkage has been taken for 24a so far with no test done for 24. The requirement is from Table KF10-01
| 01CV - Civils | Cxxx-NCR-001280 | NCR | Fisher Street Crossover unable to achieve domed shape temporary head-wall SOP.0419 |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2015-03-31 | 2015-03-25 14:19 | -6 | 2015-01-29 14:07 | Civil - Tunnelling | 2000 |  | Manufacturing Defect | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Shape of domed temporary head-wall at SOP 0419 not done in accordance with the design. Please see attached as builts and proof drillings. Minimum thickness generally achieved.
| 01CV - Civils | Cxxx-NCR-001281 | NCR | ROP-PAD Westbound Tunnel. Sections out of tolerance. Slope on kerb. |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2015-02-20 | 2015-02-19 21:54 | -1 | 2015-01-28 17:40 | Civil - Tunnelling | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Some points out of extended tolerance on the slope of the kerbs STS Section WB Tunnel ROP-PAD.
| 01CV - Civils | Cxxx-NCR-001282 | NCR | ROP-PAD Westbound Tunnel. Sections out of extended tolerance. Invert As built. |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2015-02-20 | 2015-02-20 12:26 | 0 | 2015-01-28 17:50 | Civil - Tunnelling | 5000 |  | Workmanship | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Some points were found out of extended tolerance 0/-30mm in the invert slab after the As built survey.
| 01CV - Civils | Cxxx-NCR-001283 | NCR | ROP-PAD Eastbound Tunnel. Sections out of extended tolerance. Invert Slab. |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2015-02-20 | 2015-02-20 12:35 | 0 | 2015-01-28 17:57 | Civil - Tunnelling | 5000 |  | Workmanship | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Some points out of extended tolerance 0/-30mm in the invert slab between ROP-PAD Eastbound Tunnel.
| 01CV - Civils | Cxxx-NCR-001284 | NCR | Non stainless steel treaded bars installed into the permanent lining at west end of BOS-TCR WB running tunnel |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2015-02-12 | 2015-02-13 08:09 | 1 | 2015-01-29 16:17 | Tunnelling - Tunnelling General | 1000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Insufficient information made available to the worker. | Completed |  | To erect a needle beams at the most western two rings at BOS side of TCR-BOS WB running tunnel a stainless steel treaded bars were suppposed to be used for temporary support. For unkown reason gang/team who installed the beams (part of BOS SCL team) did not use stainless steel treaded bars, but a standart steel bars This area is now falls into the scope of FSC team (who is to handover this section of tunnel on the week commenceing 2nd Feb 2015). FSC team propose to cut the bars flash with lining and use as is.
| 01CV - Civils | Cxxx-NCR-001286 | NCR | Underthickness of profiles in CP2(RT) Primary Lining |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2015-03-04 | 2015-02-09 16:39 | -23 | 2015-02-02 18:15 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | Please see attached detailed NCR Details. Also find attached scans for the effected areas
| 01CV - Civils | Cxxx-NCR-001287 | NCR | CP2 (RT) As-Built Waterproofing Layer to Fireproofing Layer Design Line Survey |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2015-03-04 | 2015-03-05 11:43 | 1 | 2015-02-03 09:48 | Tunnelling - Linings - Sprayed Concrete | 5000 |  | Incorrect Installation | Use As-Is | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | In CP2 (RT) the current as-built postiion of the waterproofing layer means that the final end product (fireproofing layer) will be tight in the corners where the SCL lining intersects with the collars. The worst case is currently 70mm tight (see attached sketches) however note that due to the nature of SCL work these will increase (though not singicantly).
| 01CV - Civils | Cxxx-NCR-001288 | NCR | Hollow area in fireproofing 300mm x 500mm found at CP3 (rt) |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2015-03-03 | 2015-02-20 12:31 | -11 | 2015-02-03 12:33 | Tunnelling - Linings - Sprayed Concrete | 1000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | On completion of testing of CP4 and CP3 an area of 300mm x 500mm was found to be hollow in CP3 near where the fireproofing meets the floor slab
| 01CV - Civils | Cxxx-NCR-001289 | NCR | BOS-PAD Westbound HAS south kerbs setout incorrectly from ring 743 -ring 770 |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2015-04-17 | 2015-05-05 10:31 | 18 | 2015-02-10 07:40 | Civil - Tunnelling | 5000 |  | Incorrect Installation | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The south HAS kerbs between Paddington and CP2 in the westbound tunnel were incorrectly setout by the shift surveyor. Currently the 12mm U-bar is outside the final position of the the FSC kerb face. intend to cut out a section of the 12mm U bar and replace it with another 12mm bar.
| 01CV - Civils | Cxxx-NCR-001290 | NCR | BOS-PAD Westbound North Kerb rings 767 and ring 771 insuffucient cover on HAS steel |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2015-03-31 | 2015-03-25 17:39 | -6 | 2015-02-10 09:30 | Civil - Tunnelling | 1000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During Shuttering the north HAS kerbs in the westbound tunnel. On an inspection, it was discovered there was less than 40mm cover achieved from the kerb steel to the shutter at rings 767 - 771.
| 01CV - Civils | Cxxx-NCR-001291 | NCR | Crosspassage 2 running tunnels Only 2 cured film thickenss were taken |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2015-03-11 | 2015-03-05 19:04 | -6 | 2015-02-11 15:57 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | ITP 50112 states that for cured film thickness patches minimum 4 per 500 square meters. If tunnel < 500m2, frequency per tunnel. In CP2 only 2 cured film tests have been done for the entire tunnel. Please note area of tunnel is roughly 210m^2.
| 01CV - Civils | Cxxx-NCR-001292 | NCR | Poor finish to regulating repairs resulted in poor waterproofing in CP2 invert |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2015-02-26 | 2015-02-27 17:20 | 1 | 2015-02-12 13:42 | Tunnelling - Linings - Sprayed Concrete | 5000 |  | Incorrect Installation | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Areas of masterseal were cut out in the invert around the CP2 sump and resprayed with regulating. On completion of the regulating and waterproofing, it was discovered the waterproofing had not been sprayed on a clean surface and substrate was not of good standard
| 01CV - Civils | Cxxx-NCR-001294 | NCR | SMM_FIS_12/02/15 Nightshift SRG report |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2015-02-27 | 2015-03-13 15:16 | 14 | 2015-02-13 14:38 | Surveying - Instrumentation and Monitoring | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Information not detailed | Completed |  | During 12/02/15 Night SRG, the Amber trigger breach for PLP D09LP338 has been reported, but the specific graph showing the point has not been included in the report. The point was showing -44.9mm on the previous reading during the dayshift (Amber Trigger at 45mm) and moved to -45.2mm. Discussion of the breach has been done during 13/02/15 day SRG as there was no sudden movement or imminent danger. During this it has been agreed that no emergency CTC was necessary. No slopes or deflection ratio Alerts have been breached.
| 01CV - Civils | Cxxx-NCR-001295 | NCR | FIS CP5 Invert Leakage |  | Crossrail | PDP | TUX - Tunnel Drive X (West) |  | 2015-03-31 | 2015-03-25 17:26 | -6 | 2015-02-13 15:51 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | On dayshift 08th Feb 2015 CRL/Cxxx were invited to do final pre-pour inspection of the Masterseal. Leak in the invert along the cast EB collar was found which wasn't picked up by the . Dayshift then carried out the repairs. On nightshift of 08th Feb 2015, CRL/Cxxx were invited for a second time and another damp patch and a water blister forming underneath the Masterseal adjacent to the repaired section was observed. Defective section was removed and repairs carried out. (picture showing the defect attached) On both these occassions inspection and testing regime failed to identify the defect.
| 01CV - Civils | Cxxx-NCR-001296 | NCR | FSC As built. BOS-TCR EB Tunnel. STS Sections out of PMI 1288 tolerances. Kerbs slope. |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2015-04-15 | 2015-04-01 16:24 | -14 | 2015-02-15 11:33 | Civil - Tunnelling | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | In the FSC As built survey between BOS-TCR EB Tunnel Some points were found out of the 1:20/1:60 Tolerance for STS Section.
| 01CV - Civils | Cxxx-NCR-001297 | NCR | FIS - Crossover Insufficient Early Age Strength Results for Advance 82 |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2015-04-17 | 2015-04-24 07:29 | 7 | 2015-02-16 10:12 | Tunnelling - Linings - Sprayed Concrete | 5000 |  | Testing and Commissioning | Use As-Is | 3 (3-6k) | Complete | Material/Preservation Problems - Other | Completed |  | FIS Crossover Advance 82-Early age strength test results below than modified J2 Curve at 30min., 1,2 and 6 hrs.Also no tests were carried out at 4 hours.
| 01CV - Civils | Cxxx-NCR-001298 | NCR | Fisher Street - Incorrect installation of primary lining reinforcement in thickening layer of crossover |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2015-03-31 | 2015-03-26 21:47 | -5 | 2015-02-17 09:29 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The primary lining thickening layer of the crossover is being installed in 2 stages. The first part was installed for the breakout of CP1 and it is now completed. The extension of the thickening layer already built is clashing with the installation of bar mark 17 and 18 for Niche 1. Bar mark 17 and 18 should have been partially installed together with the CP1 thickening layer. Attached drawing shows extension of thickening layer already installed and the clash with the bars still to be installed. Bar mark 17 will be short by 1.0m and bar mark 18 by 3.0m
| 01CV - Civils | Cxxx-NCR-001299 | NCR | CP4 WB SGI fireproofing thickness is below 50mm in some areas |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2015-03-10 | 2015-03-06 12:59 | -4 | 2015-02-17 14:51 | Tunnelling - Linings - Sprayed Concrete | 2000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Area of fireproofing sprayed on SGI's showed local areas that were below 50mm and after proof drilling at the corners showed points of 35mm. See attached
| 01CV - Civils | Cxxx-NCR-001300 | NCR | Floor level at CP4 WB collar was poured 20mm lower than it should be |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2015-03-10 | 2015-03-05 19:15 | -5 | 2015-02-17 15:51 | Tunnelling - Linings - In-situ Concrete | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The floor level where it meets the door recess at the CP4 WB collar was poured 20mm lower than the required level
| 01CV - Civils | Cxxx-NCR-001301 | NCR | Rendering of inside collars with ST05 at CP4 and CP3 |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2015-03-04 | 2015-03-03 16:58 | -1 | 2015-02-18 08:54 | Tunnelling - Linings - In-situ Concrete | 4000 |  | Incorrect Installation | Use As-Is | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Due to honeycombing in CP3 and minor honeycombing in other areas, NCR 1216 was raised and rendering with ST05 was proposed. This was accepted and the rendering was made using a procedure of scabbling, damping down with a sponge and then application of the __ St05 The rendering was completed to inside collars at CP4 and CP3 and a skim coat made to areas without honeycombing to ensure continuity and aesthetic finish. This was not agreed upon with the client
| 01CV - Civils | Cxxx-NCR-001302 | NCR | Rendering carried out in the crown of the CP2 EB running tunnel SGI segments |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2015-03-04 | 2015-02-27 17:08 | -5 | 2015-02-18 19:36 | Tunnelling - Linings - Sprayed Concrete | 1000 |  | Supervision/Management | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Rendering of fireproofing sprayed to the CP2 SGI EB segments was performed in the running tunnel
| 01CV - Civils | Cxxx-NCR-001303 | NCR | FSC As Built Survey. BOS-TCR EB Section. STS Slab out of Horizontal tolerance. |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2015-07-10 | 2015-07-08 23:35 | -2 | 2015-02-19 11:28 | Civil - Tunnelling | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Some points were found out of Horizontal tolerance in the FSC As Built Survey for BOS-TCR Easbound Tunnel STS Slab Section.
| 01CV - Civils | Cxxx-NCR-001304 | NCR | FSC As built. BOS-TCR EB Tunnel. STS Sections out of tolerances. Vertical deviation on Kerbs. |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2015-07-16 | 2015-07-14 14:14 | -2 | 2015-02-19 11:44 | Civil - Tunnelling | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During the FSC As built survey at BOS-TCR EB Tunnel some points were found out of tolerance in the vertical position of kerbs.
| 01CV - Civils | Cxxx-NCR-001305 | NCR | FSC As built. BOS-TCR EB Tunnel. STS Sections within extended tolerances. |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2015-07-10 | 2015-07-08 23:39 | -2 | 2015-02-19 11:53 | Civil - Tunnelling | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During the FSC As built survey at BOS-TCR EB Tunnel some points in the STS Slab were found out of tolerance as per Cxxx-PMI-01688 and within extended tolerances as per Cxxx-RFI-001297.
| 01CV - Civils | Cxxx-NCR-001306 | NCR | FSC As built. BOS-TCR EB Tunnel. FTS Sections out of tolerance. |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2015-10-30 | 2015-10-06 11:19 | -24 | 2015-02-19 11:59 | Civil - Tunnelling | 30000 |  | Workmanship | Use As-Is | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During the FSC As built survey at BOS-TCR EB Tunnel some points were found out of tolerance in the FTS slab.
| 01CV - Civils | Cxxx-NCR-001307 | NCR | FSC As built. BOS-TCR WB Tunnel. STS Sections out tolerances. Kerbs slope. |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2015-04-15 | 2015-04-01 16:18 | -14 | 2015-02-20 10:22 | Civil - Tunnelling | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During the FSC As built survey at BOS-TCR WB Tunnel some points were found out of tolerance in the vertical position of kerbs.
| 01CV - Civils | Cxxx-NCR-001308 | NCR | FSC As Built Survey. BOS-TCR WB Section. Points out of horizontal tolerance. |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2015-04-15 | 2015-04-05 23:23 | -10 | 2015-02-20 10:30 | Civil - Tunnelling | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During the FSC As built survey at BOS-TCR WB Tunnel some points were found out of horizontal tolerance.
| 01CV - Civils | Cxxx-NCR-001309 | NCR | FSC As built. BOS-TCR WB Tunnel. STS Sections out of tolerances. Vertical deviation. |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2015-04-15 | 2015-04-15 10:09 | 0 | 2015-02-20 10:48 | Civil - Tunnelling | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During the FSC As built survey at BOS-TCR WB Tunnel some points were found out of tolerance in the vertical position of kerbs.
| 01CV - Civils | Cxxx-NCR-001310 | NCR | FSC As built. BOS-TCR WB Tunnel. STS Sections within extended tolerances. |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2015-04-15 | 2015-04-15 10:14 | 0 | 2015-02-20 11:33 | Civil - Tunnelling | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During the FSC As built survey at BOS-TCR WB Tunnel some points in the STS Section were found out of tolerance as per Cxxx-PMI-01688 and within extended tolerances as per Cxxx-RFI-001297.
| 01CV - Civils | Cxxx-NCR-001311 | NCR | FSC As built. BOS-TCR WB Tunnel. FTS Sections out of tolerance. |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2015-10-30 | 2015-10-09 23:25 | -21 | 2015-03-16 16:12 | Civil - Tunnelling | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During the FSC As built survey at BOS-TCR WB Tunnel some points were found out of tolerance in the FTS Slab as per Cxxx-PMI-01688.
| 01CV - Civils | Cxxx-NCR-001312 | NCR | CP2 minor underthickness in fireproofing and secondary lining in localised area |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2015-03-10 | 2015-03-09 11:07 | -1 | 2015-02-24 17:19 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | It was identified before spraying fireproofing that localised areas of the secondary lining in CP2 had not achieved 200mm thickness (2 areas were 40mm shy and less than 1m²) It was agreed in the comment section of Form 125 that “Some minor shy spots in the crown to be made up with fireproofing as per NCR-001252” This can be seen in Approval to spray fireproofing CP2 running tunnels.pdf After the completion of fireproofing it was found that a small area (.25m²) at CH9m in the crown was 40-50mm thick with fireproofing as shown in Fireproofing thickness.pdf Due to the reduced thickness, this reduced the combined thickness of the fireproofing and secondary lining at this area in the crown at CH9m. The thickness of the fireproofing and secondary lining (40-45mm + 190mm) resulted in the total thickness being 235-250mm in this area as shown in the Secondary and Fireproofing combined thickness.pdf
| 01CV - Civils | Cxxx-NCR-001313 | NCR | FIS-Missing fresh fibre content and cube compressive strenght results -EBX Advance 21 |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2015-03-11 | 2015-03-05 19:05 | -6 | 2015-02-25 11:52 | Materials - General | 500 |  | Testing and Commissioning | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | Fisher Street EBX Advance 21 - No sample of cubes taken from monthly test panel for cube compressive strength and fresh fiber content on 18/08/2014
| 01CV - Civils | Cxxx-NCR-001315 | NCR | FSC - Missing flow sampling due to Eurotest Consult UK Technician Error |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2015-03-11 | 2015-03-05 19:07 | -6 | 2015-02-25 16:51 | Tunnelling - Linings - In-situ Concrete | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Worker not correctly instructed | Completed |  | technicians failed to present flow testing on Certificates for first stage concrete works. Cube samples were taken but no flow was recorded due to 'Technician Error' Missing flow from INV 023,112,278,281,289 certificates. INV 281 - Slump was taken but not flow.
| 01CV - Civils | Cxxx-NCR-001316 | NCR | FIS-EBX 28 and 90 days core compressive strenght failures |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2015-03-31 | 2015-03-13 10:44 | -18 | 2015-02-26 16:49 | Materials - General | 500 |  | Testing and Commissioning | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | 28 days average of compressive strength below requirements of target for continuous production according to EN 14487-1 in EBX and EB 5 samples have failed to meet criteria 1 of Table 13 on EN 14487-1:2005 at 28 days. More cores were taken for 90 days and the results indicate that 4 samples still failed criteria 1 on the target strength Sample numbers; at 28 days ;FIS0210 -FIS0214-FIS0216-FIS0220-FIS0222 at 90 days ;FIS0210-FIS0214-FIS0216-FIS0222
| 01CV - Civils | Cxxx-NCR-001317 | NCR | FIS EBX - Reinforcement Exposed during milling works |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2015-04-30 | 2015-04-16 22:26 | -14 | 2015-02-26 17:42 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During the milling works of EBX, reinforcement was exposed at the crown of the tunnel at chaingae 45 and 49.
| 01CV - Civils | Cxxx-NCR-001318 | NCR | FIS EBX - EBX Exposed Core Holes |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2015-04-24 | 2015-04-23 13:02 | -1 | 2015-02-26 17:52 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During the milling works in EBX, three core holes were exposed that were not filled at Chainage 44.7 and 54 (at 3 o'clock) and Chainage 47 in the crown.
| 01CV - Civils | Cxxx-NCR-001319 | NCR | FIS CP5 - Concrete Pipe cast into Collar Crown |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2015-05-28 | 2015-05-25 23:21 | -3 | 2015-02-26 18:21 | Tunnelling - Linings - In-situ Concrete | 4000 |  | Supervision/Management | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | To pour the crown of the collars in CP5, the concrete delivery pipe was cast from the soffit of the crown. The concrete delivery pipe was cast into the pour.
| 01CV - Civils | Cxxx-NCR-001320 | NCR | FIS EBX regulating layer sprayed without approval |  | Crossrail | PDP | TUX - Tunnel Drive X (West) |  | 2015-06-04 | 2015-06-12 14:38 | 8 | 2015-03-01 06:09 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | form 117 (Approval to spray regulating spray) for the remaining 10m of EBX between Ch 42 to 52 was not signed-off by Cxxx and CRL. ordered the concrete and decided to proceed with the spray. Crack sealing was rushed in the section and regulating layer sprayed on top of the wet repairs.
| 01CV - Civils | Cxxx-NCR-001321 | NCR | FIS EBX - Exposed Kwikastrip |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2015-04-08 | 2015-04-07 08:37 | -1 | 2015-03-02 09:41 | Tunnelling - Tunnelling General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Following milling works in EBX, some Kwikastip between the heading and bench has been exposed.
| 01CV - Civils | Cxxx-NCR-001322 | NCR | FIS -WBX /EBX and CP5 Some test cores tested outside the required dates as per the ITP( August ) |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2015-04-17 | 2015-04-16 15:42 | -1 | 2015-03-03 10:15 | Materials - General | 500 |  | Testing and Commissioning | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | The cores from the lining for 28 days core compressive strength test was delayed due to inaccessible section of the tunnel. Sample numbers; FIS0172 CP5 Advance 3-4 tested on 57 days FIS0179 EBX Advance 23 tested on 42 days FIS0187 EBX Advance 41 tested on 44 days FIS0194 EBX Advance 56 tested on 34 days FIS0148 EBX Advance 68 tested on 30days FIS209 EBX Advance 101 tested on 30 days FIS210 EBX Advance 104 tested 32 days FIS221 EB Advance 19 (90 days core compressive) tested on 126 days
| 01CV - Civils | Cxxx-NCR-001323 | NCR | Fisher Street EBX - Missing information on Form 50s |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2015-03-31 | 2015-03-26 21:48 | -5 | 2015-03-03 11:52 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Other | Completed |  | EBX Sprayed Concrete Checklist Form 50 sheets for Advance 32,87,92,94,104 and 106 are missing nozzleman signatures.
| 01CV - Civils | Cxxx-NCR-001325 | NCR | Fisher Street CP2 - EB binocular headwall connection |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2015-03-18 | 2015-03-26 23:12 | 8 | 2015-03-04 13:31 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | As raised in Cxxx-NCR-001271, there is an issue requiring resolution due to a clash between CP2 Primary and Eastbound binocular. Binocular headwall is protruding into the CP2 primary lining section and even into the secondary lining profile.
| 01CV - Civils | Cxxx-NCR-001326 | NCR | Fisher Street Niche 2 Under-excavation of domed headwall |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2015-03-31 | 2015-04-05 14:10 | 5 | 2015-03-11 09:59 | Tunnelling - Linings - Sprayed Concrete | 10000 |  | Supervision/Management | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Domed Headwall in Niche 2 was not excavated to the required chainage and minimum thickness was not achieved.
| 01CV - Civils | Cxxx-NCR-001327 | NCR | Fisher Street Crossover Damaged to thickening reinforcement during mucking out at Niche 1 |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2015-04-08 | 2015-04-08 08:45 | 0 | 2015-03-11 10:00 | Tunnelling - Linings - Sprayed Concrete | 10000 |  | Damaged | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Whilst cleaning debris arising from the breaking out of niche 1 eye some of the reinforcement bars were damaged by the excavator bucket.
| 01CV - Civils | Cxxx-NCR-001328 | NCR | FIS CP1 - Leak in invert prior to casting |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2015-04-24 | 2015-04-23 13:13 | -1 | 2015-03-11 10:54 | Tunnelling - Linings - In-situ Concrete | 500 |  | Supervision/Management | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During the prepour inspection CRL identified a leak in the invert of CP1. The leak was sealed prior to casting of invert.
| 01CV - Civils | Cxxx-NCR-001329 | NCR | FSC As built. TCR-FIS WB Tunnel. HAS Sections out tolerances. Kerbs slope. |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2015-07-30 | 2015-08-11 11:38 | 12 | 2015-03-16 13:13 | Civil - Tunnelling | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | In the FSC As built survey between TCR-FIS WB Tunnel Some points of the Kerbs slope were found out of the tolerance according to PMI 1288 for STS Section.
| 01CV - Civils | Cxxx-NCR-001330 | NCR | FSC As Built Survey. TCR-FIS WB Section. HAS Slab out of Horizontal tolerance. |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2015-07-30 | 2015-08-17 09:24 | 18 | 2015-03-16 13:21 | Civil - Tunnelling | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During the FSC As built survey at TCR-FIS WB Tunnel some points were found out of horizontal tolerance.
| 01CV - Civils | Cxxx-NCR-001331 | NCR | FSC As built. TCR-FIS WB Tunnel. HAS Sections out of tolerances. Vertical deviation. |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2015-07-30 | 2015-08-17 09:28 | 18 | 2015-03-16 14:41 | Civil - Tunnelling | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During the FSC As built survey at TCR-FIS WB Tunnel some points were found out of tolerance in the vertical position of the slab.
| 01CV - Civils | Cxxx-NCR-001332 | NCR | FSC As built. TCR-FIS WB Tunnel. HAS Sections within extended tolerances. |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2015-07-30 | 2015-08-17 09:38 | 18 | 2015-03-16 14:49 | Civil - Tunnelling | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During the FSC As built survey at TCR-FIS WB Tunnel some points in the STS Slab were found out of tolerance as per Cxxx-PMI-01688 and within extended tolerances as per Cxxx-RFI-001297.
| 01CV - Civils | Cxxx-NCR-001333 | NCR | FSC As built. TCR-FIS WB Tunnel. FTS Sections out of tolerance. |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2015-07-30 | 2015-10-08 16:38 | 70 | 2015-03-16 14:54 | Civil - Tunnelling | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During the FSC As built survey at TCR-FIS WB Tunnel some points were found out of tolerance in the FTS slab.
| 01CV - Civils | Cxxx-NCR-001339 | NCR | FSC - BOS-TCR - WB & EB - As built position of catchpits |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2015-08-14 | 2015-09-29 11:09 | 46 | 2015-03-17 12:53 | Civil - Tunnelling | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During the FSC As built survey at BOS-TCR EB & WB Tunnels some points in the catchpits corners were found with up to 55mm of deviation from the horizontal position.
| 01CV - Civils | Cxxx-NCR-001340 | NCR | NCR - SMM - unsurveyed Obstructed Points |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2015-04-03 | 2015-03-25 17:43 | -9 | 2015-03-17 12:19 | Surveying - Instrumentation and Monitoring | 500 |  | Planning | Use As-Is | 4 (0.5-3k) | Complete | Subcontractor Problems - Insufficient surveillance of subcontractors | Completed |  | Points D09LB174 and D09LB192 had not been read due to access issue on Tuesday (10/03/15) and Wednesday 11/03/15. The location of these point is in a gated access that requires daily request. only got contact details for access Monday evening and was only able to establish contact with the details given on Tuesday (pm). These Point was not read on Wednesday 11/03/15 as the surveyors were told that the person who had the key was unavailable and were told to check back later in the day (pm) at which point survey could not be available for 1100hrs SRG on wednesday (11/03/15). The Surveyor were however instructed to survey as early as possible on Thursday morning so as to present in the 1100hrs 12/03/15. These point was read and presented in the SRG, and no breaches have been reported to these points.
| 01CV - Civils | Cxxx-NCR-001350 | NCR | Tamcrete Topshot testing not carried out @ BOS |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2015-04-17 | 2015-03-25 17:04 | -23 | 2015-03-18 17:00 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | Tamcrete Topshot not being tested @ BOS,
| 01CV - Civils | Cxxx-NCR-001351 | NCR | Fisher Street Niche 1 L-bar reinforcement Exposed during milling |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2015-04-02 | 2015-04-07 07:43 | 5 | 2015-03-19 11:19 | Tunnelling - Tunnelling General | 500 |  | Damaged | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During milling operations in Niche 1, 2 x L-bar reinforcement was exposed. The length of the L-bars (bar number 27 in schedule Cxxx-MMD-C4-DDJ-CR086_SH003-04009 P03) exposed is approximately 300mm and is at the point where the bend is in the bar.
| 01CV - Civils | Cxxx-NCR-001352 | NCR | Fisher Street CP2 - During Milling extrados of tunnel segments was damaged |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2015-05-31 | 2015-06-05 09:25 | 5 | 2015-03-20 09:46 | Tunnelling - Tunnelling General | 2500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Fisher Street CP2 - During Milling of CP2 profile the estrados of a precast segment was damaged (milled). This was because the roadheader was rubbing in the SCL lining and the extrados of the lining at the same time. The operator was not aware the wheel was rubbing in the segment as it was in his blind side.
| 01CV - Civils | Cxxx-NCR-001353 | NCR | Fisher Street Muck Inclusion in the crown and invert area of the connection between EB binocular and Crossover |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2015-04-23 | 2015-04-28 14:55 | 5 | 2015-03-20 10:14 | Tunnelling - Linings - Sprayed Concrete | 20000 |  | Damaged | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During Excavation of the Crossover the joint between the EB binocular wall and Crossover was found to contain clay inclusion.
| 01CV - Civils | Cxxx-NCR-001355 | NCR | Fisher Street Muck Inclusion in the crown and invert area of the connection between WB binocular and Crossover |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2015-04-17 | 2015-04-16 18:07 | -1 | 2015-03-25 13:04 | Tunnelling - Linings - Sprayed Concrete | 15000 |  | Workmanship | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During Excavation of the Crossover the joint between the WB binocular wall and Crossover was found to contain clay inclusion.
| 01CV - Civils | Cxxx-NCR-001357 | NCR | FIS CP5 - Collar Profiles out of tolerance |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2015-04-30 | 2015-04-30 14:29 | 0 | 2015-03-24 15:44 | Tunnelling - Linings - In-situ Concrete | 1000 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The Collars to CP5 have been cast out of tolerance. Two profiles of EB collar (intrados profile and profile to EB Running Tunnel) and two profiles of WB collar (intrados profile and profile to WB Running tunnel) are provided.
| 01CV - Civils | Cxxx-NCR-001358 | NCR | The two sumps in the running tunnels adjacent to CP4a have not had the correct QA as the correct ITP was not followed for the works. |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2015-05-04 | 2015-05-01 16:43 | -3 | 2015-03-24 16:05 | Civil - Tunnelling | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Lack of procedure | Completed |  | The works were being carried out by the TCR team who were following ITP Cxxx--C4-ITP-CRT00_ST005-50162. Due to program and logistics reasons the works were completed by the FSC team who carried out the RC works following the ITP for their own RC works. They were unaware that the correct ITP had more stringent requirements for CRL to inspect waterproofing, reinforcement and the submission of 83 – reinforcement check sheets. As a result, the following QA has not been gathered for :- Items B6 & B7 - Recorded inspection of waterproofing by CRL (countersigned check sheet) Item B8 - Recorded inspection of reinforcement by CRL (countersigned check sheet 83)
| 01CV - Civils | Cxxx-NCR-001359 | NCR | FIS EBX - Waterproofing lap length to Binocular Tunnels |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2015-04-14 | 2015-04-16 22:24 | 2 | 2015-03-24 20:37 | Tunnelling - Linings - Sprayed Concrete | 1000 |  | Material | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Following excavation of the temporary invert to EBX the sprayed waterproofing membrane that was extending beyond the Binocular cast invert was damaged. This prevents the the appropriate lap length being provided to the EBX invert waterproofing membrane.
| 01CV - Civils | Cxxx-NCR-001360 | NCR | FIS CP5 - Location of Reinjectable Tubes |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2015-04-15 | 2015-04-17 02:31 | 2 | 2015-03-25 15:30 | Tunnelling - Linings - In-situ Concrete | 1000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | In each of the cast walls of CP5 the reinjectable tubes (that are located in the construction joints between the invert and walls) have a spare end located centrally to the collar. These will not be able to reach the termination boxes unless in open space.
| 01CV - Civils | Cxxx-NCR-001361 | NCR | FIS CP1 - Bar Splicing instead of Coupling |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2015-04-17 | 2015-04-28 14:46 | 11 | 2015-03-27 17:32 | Tunnelling - Linings - In-situ Concrete | 1000 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Drawing number Cxxx-OVE-C4-DDD-CR001_Z-03035 shows that BM 13 is to be installed as a coupler bar. did not install as a coupler due to not being on site. spliced bars ensuring 1.58m splice throughout.
| 01CV - Civils | Cxxx-NCR-001362 | NCR | Concrete Pour Records Sheet BFK-048 Not Filled in as per CP3 SL ITP for Collars |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2015-04-30 | 2015-04-30 16:09 | 0 | 2015-03-27 14:41 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Verification Problems - Other | Completed |  | Item B11 (-form 048) is missing from the ITP records for reinforced concrete works cross passages collars. believes it is a mistake on the ITP. The ITP used is attached with this NCR. Following discussion between and CRL, does not intend to revise the said ITP. The reason for that is crosspassage works are finished. propose to close this NCR as the evidence attached is sufficient to prove that we are compliant.
| 01CV - Civils | Cxxx-NCR-001363 | NCR | Concrete Pour Records Sheet BFK-048 Not Filled in as per CP4 SL ITP for Collars |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2015-04-26 | 2015-04-24 08:10 | -2 | 2015-03-27 14:49 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Other | Completed |  | Item B11 (-form 048) is missing from the ITP records for reinforced concrete works cross passages collars. believes it is a mistake on the ITP. The ITP used is attached with this NCR. Following discussion between and CRL, does not intend to revise the said ITP. The reason for that is crosspassage works are finished. propose to close this NCR as the evidence attached is sufficient to prove that we are compliant.
| 01CV - Civils | Cxxx-NCR-001364 | NCR | FIS WBX - Milling clashing with Primary Lining Reinforcement |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2015-04-30 | 2015-04-30 20:38 | 0 | 2015-03-31 10:30 | Tunnelling - Linings - Sprayed Concrete | 5000 |  | Incorrect Installation | Repair | 3 (3-6k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | During Milling of the Primary Lining for Secondary Lining works steel reinforcement was exposed at Chainage 45, 46.5, 48.35 and 50.6.
| 01CV - Civils | Cxxx-NCR-001366 | NCR | Exposed Reinforcement to beginning of EBX |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2015-04-30 | 2015-04-30 20:45 | 0 | 2015-04-02 12:09 | Tunnelling - Linings - In-situ Concrete | 5000 |  | Workmanship | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During Casting of Bay 1 of EBX the section beneath the running tunnel segments has some exposed reinforcement.
| 01CV - Civils | Cxxx-NCR-001367 | NCR | FIS Binocular Wall/Crossover - Sheet Waterproofing Lapping |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2015-08-13 | 2015-09-01 14:02 | 19 | 2015-04-02 12:36 | Tunnelling - Linings - In-situ Concrete | 10000 |  | Damaged | Repair | 2 (6-60k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | The Sheet waterproofing ,that was to lap down from the Binocular Wall, has a overlapping coming into the Crossover which will lead to waterpaths and has been damaged from removal of the primary lining during the excavation of the crossover. The damage cannot be repaired as there is insufficient lapping available.
| 01CV - Civils | Cxxx-NCR-001368 | NCR | Green Lane Sewer - MH2 base concrete |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2015-05-29 | 2015-05-30 11:24 | 1 | 2015-04-08 16:34 | Civil - Utilities Engineering | 5000 |  | Incorrect Installation | Use As-Is | 3 (3-6k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | The concrete used at the base of MH2 was different as the one specified in the drawing Cxxx--U-DWG-CRT00_ST005-51008. Donaldson has been consulted and justification on the durability of the concrete base has been attached: Documentation attached: 1) 454-TW-WI-99-04 Great Western Road WSI Vol2 Rev4 for tender 05-04-2013 - abstract p139 - p170 2) Cxxx--U-RGN-CRT00_ST005-51001 - Geotechnical Interpretative Report 3) - email Green Lane JL131 Concrete Durability Justification 4) JL131 - Green Lane Sewer Diversion - MH02 Base Slab Check 01.05.2015 calculations 5) - email JL131 - Green Lane Sewer Diversion MH02 Base Slab Durability Review 6) excavation Records
| 01CV - Civils | Cxxx-NCR-001369 | NCR | FIS WBX - Waterproofing lap length from Binocular Tunnel |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2015-05-21 | 2015-05-14 08:15 | -7 | 2015-04-13 18:04 | Tunnelling - Linings - Sprayed Concrete | 10000 |  | Material | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Following excavation of the temporary invert to WBX the sprayed waterproofing membrane that was extending beyond the Binocular cast invert was damaged. This prevents the appropriate lap length being provided to the WBX invert waterproofing membrane. This NCR is identical to Cxxx-NCR-1359 raised for EBX. Solution is the same, see attached sketch
| 01CV - Civils | Cxxx-NCR-001370 | NCR | Low Single Concrete Cube Strenght Results |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2015-04-29 | 2015-04-17 07:38 | -12 | 2015-04-15 10:09 | Tunnelling - Linings - In-situ Concrete | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | External Phenomenon - Other | Completed |  | Cube testing results INV 390 carried out on the 09/03/15 at Bond Street shows that the mean strength falls below the require strength of a single result. The mean strength at 28 days is 35.7N/mm3 at 28 days. (36 N/mm3 is required for single result)
| 01CV - Civils | Cxxx-NCR-001373 | NCR | FSC - Crack at Ring 1297 Eastbound |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2015-05-14 | 2015-05-15 08:45 | 1 | 2015-04-25 14:51 | Tunnelling - Linings - Precast | 2000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | In Eastbound running tunnel at the ring 1297 segment crack has been repaired, but this crack generated a spall representing substantial risk of falling.
| 01CV - Civils | Cxxx-NCR-001375 | NCR | FIS EBX - Invert Slab Profiles |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2015-06-09 | 2015-05-25 23:17 | -15 | 2015-04-20 19:37 | Tunnelling - Linings - In-situ Concrete | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Please find attached profiles for cast in-situ inverts to EBX. Some profiles are not within the tolerance outlined in the general notes drawings, note G33.
| 01CV - Civils | Cxxx-NCR-001376 | NCR | FIS CP1 - Collar As-Built |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2015-05-25 | 2015-05-18 21:45 | -7 | 2015-04-21 10:27 | Tunnelling - Linings - In-situ Concrete | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Please find enclosed the as-builts for the CP1 collar. Some areas in the profiles indicate that the collar has been constructed out of tolerance.
| 01CV - Civils | Cxxx-NCR-001377 | NCR | Crossover Bay 1 and 2 contraction joint |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2015-05-06 | 2015-05-07 05:35 | 1 | 2015-04-22 16:05 | Tunnelling - Linings - In-situ Concrete | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During the pour of the crossover invert, Bays 1 to 4, the contraction joint to the top of the joint between Bays 1 and 2 was missed.
| 01CV - Civils | Cxxx-NCR-001378 | NCR | FIS Crossover Invert Slab Profiles |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2015-06-18 | 2015-05-25 23:16 | -24 | 2015-04-22 16:13 | Tunnelling - Alignment | 1000 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Please find enclosed profiles for the Crossover Invert Slabs - Bay 1, 2, 3 and 4. Some profiles are out of tolerance.
| 01CV - Civils | Cxxx-NCR-001382 | NCR | Damaged Couplers in Eastbound Binocular |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2015-08-14 | 2015-08-18 21:48 | 4 | 2015-04-28 10:12 | Tunnelling - Linings - In-situ Concrete | 2000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | BM32 and BM33 couplers were cast into the Binocular invert slab but during the construction of the rest of the binocular and the EBX, 9 no. couplers have been damaged. Refer to attached photos – couplers highlighted in Red are damaged and yellow shows the couplers that are intact.
| 01CV - Civils | Cxxx-NCR-001383 | NCR | Missing information from BFK 048 Forms for Paddington to Bond Street Westbound ITP Records |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2015-05-07 | 2015-05-11 08:29 | 4 | 2015-04-23 15:16 | Tunnelling - Linings - In-situ Concrete | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Information not detailed | Completed |  | A number of 048 forms are missing information and should have been completed during pour. Items missing - Concrete temperature, time of test, and Slump Test Results.
| 01CV - Civils | Cxxx-NCR-001384 | NCR | Concrete Pour Records Sheet BFK-048 Not Filled in as per CP2 SL ITP for Collars |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2015-05-24 | 2015-05-15 08:53 | -9 | 2015-04-24 09:57 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Other | Completed |  | Item B11 (-form 048) is missing from the ITP records for reinforced concrete works cross passages collars. believes it is a mistake on the ITP. The ITP used is attached with this NCR. Following discussion between and CRL, does not intend to revise the said ITP. The reason for that is crosspassage works are finished. propose to close this NCR as the evidence attached is sufficient to prove that we are compliant.
| 01CV - Civils | Cxxx-NCR-001385 | NCR | Concrete Pour Records Sheet BFK-048 Not Filled in as per CP2(RT) SL ITP for Sumps |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2015-05-24 | 2015-05-15 08:55 | -9 | 2015-04-24 10:10 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Other | Completed |  | Item B13 (-form 048) is missing from the ITP records for reinforced concrete works cross passages sumps. believes it is a mistake on the ITP. The ITP used is attached with this NCR. Following discussion between and CRL, does not intend to revise the said ITP. The reason for that is crosspassage works are finished. propose to close this NCR as the evidence attached is sufficient to prove that we are compliant.
| 01CV - Civils | Cxxx-NCR-001387 | NCR | Cover on CP1 ducts - Fisher St |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2015-06-30 | 2015-06-30 08:04 | 0 | 2015-04-30 16:35 | Tunnelling - Linings - In-situ Concrete | 4000 |  | Workmanship | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | 2 no. ducts in CP1 collar rose during pouring of the collar and therefore have less than 70mm cover. Please refer to attached pdf for the cover on all five ducts at CP1.
| 01CV - Civils | Cxxx-NCR-001389 | NCR | FIS IA2 - Localised underthickness of Primary Lining |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2015-06-18 | 2015-06-12 23:44 | -6 | 2015-05-07 08:45 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Localised underthickness found in primary lining of IA2. Lining thickness design is 400mm. Proof Drilling carried out and found two points with less than 400mm thickness.
| 01CV - Civils | Cxxx-NCR-001392 | NCR | FIS- E/B Enlargement Invert Part 1-2, 28 day compressive cube strength |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2015-05-28 | 2015-05-18 22:11 | -10 | 2015-05-07 14:53 | Tunnelling - Linings - In-situ Concrete | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | FIS- E/B Enlargement invert Part 1&2, sample EX1011, 28 day cubes failed to reach at least 36mpa
| 01CV - Civils | Cxxx-NCR-001393 | NCR | FSC EBRT Drainage Pipe Blockage ( BOS-PAD Between Ring 1428 to Ring 1433) |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2015-06-24 | 2015-06-25 14:53 | 1 | 2015-05-26 14:05 | Tunnelling - Linings - Precast | 5000 |  | Workmanship | Use As-Is | 3 (3-6k) | Complete | Discipline/Workmanship - Other | Completed |  | During drainage pipe inspection in the eastbound tunnel section BOS- PAD between ring 1428 and 1433 we discovered that the drain was blocked due to the ingress grout into the drain pipe
| 01CV - Civils | Cxxx-NCR-001396 | NCR | FIS IA2 - Exposure of Clay during milling of IA2 |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2015-06-06 | 2015-06-15 22:49 | 9 | 2015-05-12 08:56 | Tunnelling - Tunnelling General | 5000 |  | Incorrect Installation | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During milling of IA2 at chainage 11.5, clay was exposed. Proof drilling was undertaken around the exposed clay (See attached)
| 01CV - Civils | Cxxx-NCR-001398 | NCR | Form BFK-089 not filled in correctly CP4(RT) Ch14.5 to Ch2 |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2015-06-12 | 2015-05-26 18:57 | -17 | 2015-05-13 15:21 | Tunnelling - Linings - Sprayed Concrete | 5000 |  | Workmanship | Use As-Is | 3 (3-6k) | Complete | Procedure Problem - Other | Completed |  | The attached (Waterproofing membrane checksheet) -089 shows one point with 3mm spray. Although it shows a second layer was sprayed in the said area. The check sheet does not specify clearly if that particular point 4 had been re-sprayed as part of 2nd layer
| 01CV - Civils | Cxxx-NCR-001399 | NCR | Fisher Street IA2 L-bar reinforcement Exposed during millining |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2015-06-10 | 2015-06-11 10:09 | 1 | 2015-05-14 09:01 | Tunnelling - Linings - Sprayed Concrete | 2000 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Whilst milling IA2 some of the L-bars were exposed.
| 01CV - Civils | Cxxx-NCR-001400 | NCR | FIS - FAR WB Blocked UTX at ring 4110 |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2015-08-21 | 2015-09-29 13:47 | 39 | 2015-05-15 14:01 | Civil - Tunnelling | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Contamination | Completed |  | During an inspection of the UTX ducts in the westbound tunnel from Fisher Street to Farringdon. It was discovered the UTX at ring 4110 is blocked.
| 01CV - Civils | Cxxx-NCR-001401 | NCR | BOS-PAD WB Missing UTX at ring 992 |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2015-08-21 | 2015-09-29 17:12 | 39 | 2015-05-15 14:26 | Civil - Tunnelling | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During the UTX asbuilt survey it was discovered there is a missing UTX at ring 992. There is a UTX at ring 973 and another UTX at ring 1010. (59.2 metres apart). The ITP Plan Cxxx--C4-ITP-CRT00_ST005-51802 requires UTX ducting to be positioned every 30 metres.
| 01CV - Civils | Cxxx-NCR-001402 | NCR | Milling in FIS shaft around ADIT IA2 without approval |  | Crossrail | XRL | TUX - Tunnel Drive X (West) |  | 2015-06-05 | 2015-06-12 18:01 | 7 | 2015-05-15 15:24 | Civil - Tunnelling | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Other | Completed |  | Milliing of the primary lining in Fisher street shaft around adit IA2 commenced prior to obtaining authorisation from CRL and Cxxx on Form 123. During the daily secondary lining meeting on Friday 15th May it was discussed that the primary lining profiles would be presented with Form123 for approval to mill. Following the meeting it was found that milling had already commenced during the previous night shift without approval.
| 01CV - Civils | Cxxx-NCR-001403 | NCR | Fisher Street - Intervention Adit 2 under thickness of primary lining after milling |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2015-07-10 | 2015-07-08 23:46 | -2 | 2015-05-18 16:06 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Profiles of primary lining in intervention adit 2 after milling show some areas where design thickness (<400mm) has not been achieved
| 01CV - Civils | Cxxx-NCR-001404 | NCR | FIS WBX - Cavern Headwall Starter Bars Damaged |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2015-06-30 | 2015-06-19 23:06 | -11 | 2015-05-19 22:29 | Tunnelling - Tunnelling General | 5000 |  | Damaged | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | 2 No. starter Bars from Binocular Invert, Bar Mark 16, have been damaged and cannot be connected using couplers.
| 01CV - Civils | Cxxx-NCR-001405 | NCR | Fisher Street IA2 Crown Milling Sheet missing signature of the Senior SCL Engineer Prior To Commencing Works. |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2015-06-11 | 2015-06-15 22:56 | 4 | 2015-05-21 12:55 | Tunnelling - Linings - Sprayed Concrete | 10000 |  | Documentation and Records | Use As-Is | 2 (6-60k) | Complete | Procedure Problem - Other | Completed |  | Fisher Street IA2 Crown Milling Sheet missing signature of the Senior SCL Engineer Prior To Commencing Works.
| 01CV - Civils | Cxxx-NCR-001406 | NCR | FIS IA2 - Missing Excavation Profiles |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2015-06-26 | 2015-06-23 17:54 | -3 | 2015-05-27 08:19 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Excavation profiles to Advance 1, 2, 3, 4 and 5 were missed during excavation works of initial advances of tunneling.
| 01CV - Civils | Cxxx-NCR-001407 | NCR | 1 day cores tested late |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2015-07-15 | 2015-07-22 22:34 | 7 | 2015-06-24 14:38 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Planning | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | FIS, EBX Bay 1C, Fireproofing, Ch 8.15-11.52 - 1-3 day cores were tested at 7 days
| 01CV - Civils | Cxxx-NCR-001409 | NCR | Fisher Street EBX Cavern bay 1 grouting tubes missing in connection from kerbs to crown |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2015-07-10 | 2015-07-17 10:36 | 7 | 2015-06-02 16:48 | Tunnelling - Tunnelling General | 10000 |  | Incorrect Installation | Use As-Is | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Re-injectable grout tubes were not installed in the construction joints between secondary lining kerbs and crown in EBX bays 1A,1B,1C.
| 01CV - Civils | Cxxx-NCR-001410 | NCR | FSC FIS - Crack at Ring 3742 WB |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2015-08-31 | 2015-09-01 20:59 | 1 | 2015-06-02 18:22 | Civil - Tunnelling | 1000 |  | Damaged | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Not Defined | Completed |  | A dry crack with a width of more than 4 mm has been observed in segment ER at Ring 3742 WB.
| 01CV - Civils | Cxxx-NCR-001411 | NCR | FSC FIS - Crack at ring 3740 WB Tunnel |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2015-06-25 | 2015-06-25 17:52 | 0 | 2015-06-02 18:25 | Civil - Tunnelling | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | A dry crack with a width of more than 4 mm has been observed in segment ER at Ring 3740 WB.
| 01CV - Civils | Cxxx-NCR-001412 | NCR | No evidence of inspection / checks on installed dowels before spraying / casting secondary lining concrete |  | Crossrail | XRL | TUX - Tunnel Drive X (West) |  | 2015-07-23 | 2015-07-23 21:09 | 0 | 2015-06-04 08:26 | Civil - Tunnelling | 500 |  | Documentation and Records | Repair | 4 (0.5-3k) | Complete | Procedure Problem - Lack of procedure | Completed |  | During a planned Crossrail surveillance undertaken on 19th May 2015 which looked at TAM sprayed waterproofing it was noticed that the dowels being used to support the secondary lining reinforcement did not have 300mm overlap and 50mm dowel encapsulation as required by the documented activity plan and manufacturers instructions. This was rectified during the site visit. However, as the secondary lining concrete had been cast in WBX bays 1-5 invert, a request was made for the Contractor to provide evidence through checks/ inspections that the embedded dowels in the invert had been checked to ensure sufficient overlap as detailed previously. Following review of the waterproof and secondary lining check sheets and on review of ITP’s ‘FIS Sprayed Waterproofing’ Cxxx--C-ITP-CRT00_ST005-50194 (Rev 1) Code 1 and ‘FIS Works Secondary Lining’ Cxxx--C4-ITP-CRT00_ST005-50138 (Rev 4) Code 1, it was noted that no check item exists for the inspection of sufficient dowel coverage/repairs before spraying secondary lining concrete, as such it could not be verified whether the dowels installed in the invert had been sufficiently repaired. Works Information Volume 2B Part 13.2 ‘Assurance’ details a requirement for the generation of contemporaneous records. To ensure the relevant ITP is amended this NCR was raised.
| 01CV - Civils | Cxxx-NCR-001413 | NCR | ROP - foam backing rod not coverved with mastic sealant |  | Crossrail | XRL | TUX - Tunnel Drive X (West) |  | 2015-08-14 | 2015-08-17 13:32 | 3 | 2015-06-04 14:38 | Tunnelling - Linings - Precast | 5000 |  | Incorrect Installation | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Drawing Cxxx-OVE-C4-DDD-CR001_Z-23080 Detail 3 shows that the void in the channel drain between the first ring and cast in-situ headwall is to be filled with a foam backing rod and covered over with a mastic sealant. The void has been filled with a polystyrene void former as can be seen on the attached photo. During review of the asbuilt drawings, it was noted that the drawing has been marked up identifying Cxxx-RFI-00955 which is confirmation that the foam does not need to be covered up with mastic in areas beneath the first stage concrete. It is believed that this was mis-interpreted to apply to this location as well, and subsequently there is no mastic on the foam void filler at the ROP headwall connection.
| 01CV - Civils | Cxxx-NCR-001414 | NCR | Incorrect Grouting details in Installation Reports |  | Crossrail | XRL | TUX - Tunnel Drive X (West) |  | 2015-07-16 | 2015-07-09 16:35 | -7 | 2015-06-08 11:07 | Geotechnical Engineering - Geotechnical Monitoring | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The grouting mix reported in some Installation Reports for deep instrumentation doesn't match the description of the composition of the grout reported in the Grout Report Cxxx--C4-RGN-CRT00_ST005-51941 Rev 3.0. Specifically, the cement-bentonite ratio and the water-cement one have been mixed up.
| 01CV - Civils | Cxxx-NCR-001415 | NCR | Incorrect grout testing |  | Crossrail | XRL | TUX - Tunnel Drive X (West) |  | 2015-07-17 | 2015-07-23 21:17 | 6 | 2015-06-09 16:48 | Geotechnical Engineering - Geotechnical Monitoring | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The four triaxial tests carried out to determine the compressive strengths of the grout used during the installations show results abnormally low. Also, it is not clear how the samples were taken and there is no information available as to whether the results were for 7 or 28 days.
| 01CV - Civils | Cxxx-NCR-001416 | NCR | FIS - No 90 day Shrinkage - February Mix 18 |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2015-07-21 | 2015-07-22 23:09 | 1 | 2015-06-30 19:31 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | No 90 shrinkage test was completed for Mix 18 in February 2015.
| 01CV - Civils | Cxxx-NCR-001417 | NCR | FIS WBX - South Bay 3 Kerb |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2015-06-30 | 2015-07-03 10:36 | 3 | 2015-06-12 12:59 | Tunnelling - Linings - In-situ Concrete | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Bay 3 Kerb of the WBX was not adequately filled during casting and has been cast with a slope running longitudinally.
| 01CV - Civils | Cxxx-NCR-001418 | NCR | As Built Profiles Not taken for secondary lining main sump CP2(RT) BOS |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2015-07-02 | 2015-07-03 10:44 | 1 | 2015-06-17 12:22 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | failed to take the asbuilt records for the main sump in CP2(RT) secondary lining
| 01CV - Civils | Cxxx-NCR-001419 | NCR | FIS Monthly Beams Mix 17.2 - February 2015 |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2015-07-20 | 2015-07-22 22:51 | 2 | 2015-06-22 16:47 | Tunnelling - Linings - Sprayed Concrete | 500 |  | System Defect | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | February monthly beams mix 17.2, sample FIS0263 Crossover-XO-Advance 75 Of the 3 beams tested at 28 days, beams 1&2 did not achieve the minimum D3 value of 1.4.
| 01CV - Civils | Cxxx-NCR-001420 | NCR | Rebound Test - January/February 2015 |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2015-07-20 | 2015-07-22 22:59 | 2 | 2015-06-22 16:46 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Planning | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | No rebound test performed during January and February 2015
| 01CV - Civils | Cxxx-NCR-001421 | NCR | No 1 day cores for Regulating in January - April 2015 |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2015-07-20 | 2015-07-22 23:04 | 2 | 2015-06-22 13:09 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Planning | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | No 1 day cores were tested between January & April 2015. Samples FIS256, FIS270, FIS0272, FIS272 & FIS0278 were only tested at 28 days.
| 01CV - Civils | Cxxx-NCR-001422 | NCR | STS type FSC as-built data for EB PAD-BOS out of tolerance |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2015-08-14 | 2015-09-16 15:29 | 33 | 2015-06-19 09:48 | Civil - Tunnelling | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | All high spots have been removed after scabbling works. Low points are within extended tolerances. Please find detailed As built survey data in the Eb Document: Cxxx--C4-LRC-CRT00_ST005-50762 Revision 2.
| 01CV - Civils | Cxxx-NCR-001423 | NCR | STS type FSC as-built data for WB PAD-BOS out of tolerance |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2015-08-14 | 2015-09-16 15:38 | 33 | 2015-06-19 10:06 | Civil - Tunnelling | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | All high spots have been removed after scabbling works. Low points are within extended tolerances. Please find detailed As built survey data in the eB Document: Cxxx--C4-LRC-CRT00_ST005-50762 Revision 2.
| 01CV - Civils | Cxxx-NCR-001424 | NCR | HAS type FSC as-built data for EB PAD-BOS out of tolerance |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2015-08-14 | 2015-09-16 15:32 | 33 | 2015-06-19 10:09 | Civil - Tunnelling | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | All high spots have been removed after scabbling works. Low points are within extended tolerances. Please find detailed As built survey data in the eB Document: Cxxx--C4-LRC-CRT00_ST005-50762 Revision 2.
| 01CV - Civils | Cxxx-NCR-001425 | NCR | HAS type FSC as-built data for WB PAD-BOS out of tolerance |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2015-09-30 | 2015-10-02 09:31 | 2 | 2015-06-19 10:12 | Civil - Tunnelling | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | All high spots have been removed after scabbling works. Low points are within extended tolerances. Please find detailed As built survey data in the eB Document: Cxxx--C4-LRC-CRT00_ST005-50762
| 01CV - Civils | Cxxx-NCR-001426 | NCR | STS type FSC catchpit as-built data for EB & WB PAD-BOS out of tolerance |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2015-09-30 | 2015-10-07 14:56 | 7 | 2015-06-19 10:23 | Civil - Tunnelling | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Please find detailed As built survey data for catchpits in the eB Document: Cxxx--C4-LRC-CRT00_ST005-50762
| 01CV - Civils | Cxxx-NCR-001427 | NCR | HAS type FSC catchpit as-built data for EB & WB PAD-BOS out of tolerance |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2015-09-30 | 2015-10-02 09:37 | 2 | 2015-06-19 10:35 | Civil - Tunnelling | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Please find detailed As built survey data for catchpits in the eB Document: Cxxx--C4-LRC-CRT00_ST005-50762
| 01CV - Civils | Cxxx-NCR-001428 | NCR | Washout Tests |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2015-08-14 | 2015-08-18 23:28 | 4 | 2015-06-30 18:32 | Tunnelling - Linings - In-situ Concrete | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | Samples EX1094, EX1179 both had results less than 80% of design content.
| 01CV - Civils | Cxxx-NCR-001429 | NCR | STS type FSC as-built data for EB FIS-FAR out of tolerance |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2015-10-30 | 2015-10-13 15:24 | -17 | 2015-06-22 08:17 | Civil - Tunnelling | 1500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | No high spots detected. Low points are within extended tolerances. Please find detailed As built survey data in the Eb Document: Cxxx--C4-LRC-CRT00_ST005-50763
| 01CV - Civils | Cxxx-NCR-001430 | NCR | HAS type FSC as-built data for EB FIS-FAR out of tolerance |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2015-10-30 | 2015-10-13 15:31 | -17 | 2015-06-22 08:19 | Civil - Tunnelling | 6000 |  | Workmanship | Use As-Is | 3 (3-6k) | Complete | Discipline/Workmanship - Other | Completed |  | No high spots detected. Low points are within extended tolerances. Please find detailed As built survey data in the Eb Document: Cxxx--C4-LRC-CRT00_ST005-50763
| 01CV - Civils | Cxxx-NCR-001431 | NCR | STS type FSC as-built data for WB FIS-FAR out of tolerance |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2015-10-30 | 2015-10-19 12:20 | -11 | 2015-06-22 08:19 | Civil - Tunnelling | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | All high spots removed by scabbling works. Low points are within extended tolerances. Please find detailed As built survey data in the Eb Document: Cxxx--C4-LRC-CRT00_ST005-50763
| 01CV - Civils | Cxxx-NCR-001432 | NCR | SATEBA 312 type FSC as-built data for WB FIS-FAR out of tolerance |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2015-10-30 | 2015-10-19 10:23 | -11 | 2015-06-22 08:20 | Civil - Tunnelling | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | All high spots removed by scabbling methods. Low points are within extended tolerances. Please find detailed As built survey data in the Eb Document: Cxxx--C4-LRC-CRT00_ST005-50763
| 01CV - Civils | Cxxx-NCR-001433 | NCR | STS type catchpit as-built data for EB and WB FIS-FAR out of tolerance |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2015-10-30 | 2015-10-19 10:38 | -11 | 2015-06-22 08:20 | Civil - Tunnelling | 1500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Please find detailed As built survey data in the Eb Document: Cxxx--C4-LRC-CRT00_ST005-50763
| 01CV - Civils | Cxxx-NCR-001434 | NCR | HAS type catchpit as-built data for EB and WB FIS-FAR out of tolerance |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2015-10-30 | 2015-10-19 10:43 | -11 | 2015-06-22 08:21 | Civil - Tunnelling | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Please find detailed As built survey data in the Eb Document: Cxxx--C4-LRC-CRT00_ST005-50763
| 01CV - Civils | Cxxx-NCR-001435 | NCR | STS type FSC as-built data for EB TCR-KTT out of tolerance |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2015-08-14 | 2015-08-17 21:33 | 3 | 2015-06-22 09:30 | Civil - Tunnelling | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | High spots corrected by scabbling works. Low points are within extended tolerances. Please find detailed As built survey data in eB Document Cxxx--C4-LRC-CRT00_ST005-50754 Rev2
| 01CV - Civils | Cxxx-NCR-001436 | NCR | HAS type FSC as-built data for EB TCR-KTT out of tolerance |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2015-09-10 | 2015-10-02 09:41 | 22 | 2015-06-22 09:34 | Civil - Tunnelling | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | High spots corrected by scabbling works. Low points are within extended tolerances. Please find detailed As built survey data in eB Document Cxxx--C4-LRC-CRT00_ST005-50754
| 01CV - Civils | Cxxx-NCR-001437 | NCR | FTS type FSC as-built data for EB TCR-KTT out of tolerance |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2015-08-31 | 2015-10-19 21:38 | 49 | 2015-06-22 09:35 | Civil - Tunnelling | 5000 |  | Workmanship | Use As-Is | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | High spots corrected by scabbling works. Exiting low points remain. Please find detailed As built survey data in eB Document Cxxx--C4-LRC-CRT00_ST005-50754
| 01CV - Civils | Cxxx-NCR-001438 | NCR | STS type catchpit as-built data for EB TCR-KTT out of tolerance |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2015-08-14 | 2015-09-08 13:09 | 25 | 2015-06-22 09:36 | Civil - Tunnelling | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Some catchpits out of tolerances. Please find detailed As built survey data in eB Document Cxxx--C4-LRC-CRT00_ST005-50754 Rev2
| 01CV - Civils | Cxxx-NCR-001439 | NCR | HAS type catchpit as-built data for EB TCR-KTT out of tolerance |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2015-10-30 | 2015-10-02 10:03 | -28 | 2015-06-22 09:36 | Civil - Tunnelling | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Some catchpits out of tolerances. Please find detailed As built survey data in eB Document Cxxx--C4-LRC-CRT00_ST005-50754
| 01CV - Civils | Cxxx-NCR-001440 | NCR | HAS type catchpit as-built data for WB TCR-KTT out of tolerance |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2015-08-27 | 2015-10-27 16:42 | 61 | 2015-06-22 09:37 | Civil - Tunnelling | 50000 |  | Workmanship | Use As-Is | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Some catchpits out of tolerances. Please find detailed As built survey data in eB Document Cxxx--C4-LRC-CRT00_ST005-50754
| 01CV - Civils | Cxxx-NCR-001441 | NCR | FIS-TCR Eastbound HAS kerb steel damaged from ring 3470 - 3462 |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2015-09-11 | 2015-08-27 14:25 | -15 | 2015-06-25 09:41 | Civil - Tunnelling | 10000 |  | Damaged | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Other | Completed |  | The HAS kerbs in the eastbound tunnel from ring 3470-3462 were steel fixed but where have not been cast with concrete. The steel was covered over with a temporary ramp onto the FSC slab. The ramp has now been removed. During this activity a number of HAS bars have been damaged. wish to repair the steel using a previously approved method from Cxxx-NCR-001289 (BOS-PAD Westbound HAS south kerbs setout incorrectly from ring 743-770)
| 01CV - Civils | Cxxx-NCR-001442 | NCR | Low construction joint in bay 4N of Crossover Wall |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2015-07-30 | 2015-08-18 23:29 | 19 | 2015-06-30 12:15 | Tunnelling - Linings - In-situ Concrete | 1000 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Bay 4N wall was cast 300mm low.
| 01CV - Civils | Cxxx-NCR-001443 | NCR | FIS-FAR __ 130 used on category D1 cracks |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2015-08-14 | 2015-08-18 23:26 | 4 | 2015-07-03 08:38 | Tunnelling - Linings - Precast | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Tam 130 has been used in a number of category D1 cracks. The current segment repair matrix shows the use of TAM 130 on category D2 cracks (Cxxx--C-LRG-CRT00_ST005-50008). would like to update the segment repair matrix to accommodate the use of TAM 130 on D1 cracks.
| 01CV - Civils | Cxxx-NCR-001444 | NCR | FSC - FTS BOS-TCR use of upto 30mm chamfer on the kerbs in the west and eastbound tunnel |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2015-09-27 | 2015-10-07 14:01 | 10 | 2015-07-02 15:57 | Civil - Tunnelling | 1500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | During FTS casting kerb operations, upto 30mm chamfer have been used instead of 10 mm chamfer. 30mm chamfer have been used in Floating Track Slab project wise
| 01CV - Civils | Cxxx-NCR-001446 | NCR | Insufficient lap in CP2 collars FIS |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2015-08-12 | 2015-08-18 21:46 | 6 | 2015-07-07 18:03 | Tunnelling - Linings - In-situ Concrete | 1000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Lack of splice available from invert for BM17 and BM24
| 01CV - Civils | Cxxx-NCR-001447 | NCR | Lack of available splice on BM20 and BM36 Far Face WBX FIS |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2015-07-29 | 2015-08-17 11:55 | 19 | 2015-07-07 18:22 | Tunnelling - Linings - In-situ Concrete | 2000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Lack of available splice from the kerbs in WBX on FF BM20 and 36.
| 01CV - Civils | Cxxx-NCR-001448 | NCR | Fans used to cure masterseal in FIS EB stub tunnel invert |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2015-07-29 | 2015-08-17 09:41 | 19 | 2015-07-15 13:19 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Counterfeit Items | Completed |  | Fans were put in place on a nightshift to cure the masterseal in the invert of EB stub tunnel. The ITP states that ventilation should not be directed on the masterseal.
| 01CV - Civils | Cxxx-NCR-001449 | NCR | FIS EB Binocular Headwall Crown - Contact Grouting carried out using a pump without a gauge |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2015-10-21 | 2015-10-13 17:42 | -8 | 2015-07-23 15:31 | Tunnelling - Linings - In-situ Concrete | 5000 |  | Planning | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Contact grouting of EB Binocular headwall crown was carried out on night shift of 22/07/15 however there are no records of grout mix used or grout take available. Grout cubes have been taken and will be tested as per ITP. There was no pressure gauge fitted to the grout line at point of injection. After completion of grouting, ingress water was observed from the crown of the binocular tunnel at the change in profile and at the junction with the EBX cavern headwall. It is unclear if there are any remaining cavities behind the secondary lining.
| 01CV - Civils | Cxxx-NCR-001450 | NCR | Fisher Street WB Stub Invert MasterSeal Overlap |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2015-08-27 | 2015-10-02 10:07 | 36 | 2015-07-27 18:17 | Tunnelling - Linings - In-situ Concrete | 5000 |  | Damaged | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Whilst Breaking Out a temporary base slab in the running tunnel the 300mm waterproofing membrane slab was damaged.
| 01CV - Civils | Cxxx-NCR-001451 | NCR | EB Stub tunnel Fisher St Overspray Secondary Lining |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2015-08-27 | 2015-08-27 14:20 | 0 | 2015-08-04 12:48 | Tunnelling - Linings - Sprayed Concrete | 5000 |  | Workmanship | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Near face secondary lining was over sprayed in EB Stub tunnel Fisher St.
| 01CV - Civils | Cxxx-NCR-001452 | NCR | Fisher St EB BN/XO Wall out of tolerance |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2015-08-18 | 2015-08-17 22:42 | -1 | 2015-08-04 12:23 | Tunnelling - Linings - In-situ Concrete | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Crossover/East bound Binocular wall has been cast out of tolerance Ch. 52.0 - 58.0. Profiles have been provided for these areas.
| 01CV - Civils | Cxxx-NCR-001454 | NCR | WB Stub tunnel Fisher St Overspray Regulating Layer |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2015-08-24 | 2015-08-18 22:23 | -6 | 2015-08-07 16:08 | Tunnelling - Linings - Sprayed Concrete | 5000 |  | Workmanship | Use As-Is | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Regulating layer was oversprayed in WB Stub tunnel Fisher St.
| 01CV - Civils | Cxxx-NCR-001456 | NCR | Repair of M16 holes in the EBX / WBX slab (Cxxx) from FSC formwork |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2015-08-24 | 2015-08-19 18:07 | -5 | 2015-08-10 15:48 | Tunnelling - Linings - In-situ Concrete | 2000 |  | Material | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | In order to setup RMD formwork for the FSC slab in EBX / WBX. AN anchor plate is fixed to the Cxxx slab using 2no. M16 x 150 JCP Anchor bolts spaced every 1500mm approximately. When the centre pour is cast, RMD will be removed. The JCP anchor bolts will be removed and the holes will be plugged using Tam Crete Polyplug.
| 01CV - Civils | Cxxx-NCR-001458 | NCR | Fisher Street - IA1 Clay inclusion in the primary lining |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2015-08-31 | 2015-08-23 22:57 | -8 | 2015-08-17 17:29 | Tunnelling - Linings - Sprayed Concrete | 8000 |  | Incorrect Installation | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During preparation works for secondary lining in IA1 clay was found within the primary lining shell. Proof drilling was undertaken around the exposed clay (See attached) and area found to be approx. 900mm by 400mm. In this area the design thickness of primary lining was not installed.
| 01CV - Civils | Cxxx-NCR-001459 | NCR | Fisher Street - Shaft and IA1 primary lining for breakout |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2015-08-31 | 2015-09-28 13:59 | 28 | 2015-08-17 17:43 | Tunnelling - Linings - Sprayed Concrete | 5000 |  | Incorrect Installation | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During preparation works for secondary lining in IA1 it was found that most of the near face ‘L’ bars for primary lining were installed outside tolerance in during the breaking out of IA1 from the Fisher Street shaft. The bars do not allow for the installation of the secondary lining in accordance with the design thickness. This is particularly bad in the crown (approx. 3m) and in the RHS at below axis. As builds, after milling, of areas outside tolerance attached.
| 01CV - Civils | Cxxx-NCR-001460 | NCR | Water ingress in contraction joint Bay 1/1a and top of BN wall in the Crossover |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2015-11-13 | 2015-12-08 15:19 | 25 | 2015-08-19 17:22 | Tunnelling - Linings - In-situ Concrete | 50000 |  | Damaged | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | After casting the final crossover wall, it was noticed that there was water collecting in the channel of the contraction joint between bay 1 and 1a in the invert just behind the WBX binocular wall. After casting the crown Ch. 8.2 - 4.5m, water started to appear from the joint of the BN wall and the XO crown. After casting the crown Ch. 4.5-0.0m the water remained in the crown joint.
| 01CV - Civils | Cxxx-NCR-001462 | NCR | Inadequate curing on Bay 4a and 4 crown in Crossover |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2015-09-02 | 2015-09-01 21:33 | -1 | 2015-08-19 17:17 | Tunnelling - Linings - In-situ Concrete | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | After striking the Crossover Crown shutter, a curing agent was not applied straight away.
| 01CV - Civils | Cxxx-NCR-001463 | NCR | TCR-FIS FTS Non compliance with U3/F3 finish on invert in the westbound Tunnel between rings 3049-3128 (CH 5031.31-5157.69) |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2015-09-25 | 2015-10-02 10:10 | 7 | 2015-08-19 13:40 | Civil - Tunnelling | 1000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | In the section of FTS between Rings 3049-3128, there are some section of the invert slab that required gridning down to reach tolerance. This resulted in the slab not achieving the U3/F3 finish required.
| 01CV - Civils | Cxxx-NCR-001464 | NCR | Fisher Street - IA1 localized under thickness of primary lining |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2015-09-02 | 2015-09-01 21:35 | -1 | 2015-08-19 14:34 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Upon completion of the milling works it was noticed that, in some areas, the full 400mm design thickness of primary lining was reduced up to 350mm. Proof drilling attached proves that the as builds are accurate.
| 01CV - Civils | Cxxx-NCR-001465 | NCR | FIS - Flag 19mm pipe used without an approved MCR |  | Crossrail | PDP | TUX - Tunnel Drive X (West) |  | 2015-09-17 | 2015-11-23 14:58 | 67 | 2015-08-21 08:55 | Tunnelling - Linings - In-situ Concrete | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Flagon Predimax Flag 19 re-injected pipe was used in cast in-situ works for contact grouting purposes in Cross Passages 1, 2 & 5 and Crossover crown pour between Ch 45 - 58 without an approved MCR in place. This material was not approved to be used in the above mentioned 'Location of works' and not known to show conformance to KF10.3221. Please note this was raised earlier with reference Cxxx-NCR-001453 but cancelled the NCR.
| 01CV - Civils | Cxxx-NCR-001466 | NCR | FIS - Adit IA1 regulating layer sprayed without inspection |  | Crossrail | PDP | TUX - Tunnel Drive X (West) |  | 2015-09-17 | 2015-09-25 12:07 | 8 | 2015-08-27 13:07 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | On the nightshift of 26/08/2015 Adit IA1 invert and shaft wall was sprayed with regulating layer without Crossrail and Cxxx inspection and approval. As per ITP Cxxx--C4-ITP-CRT00_ST005-50139 item B2.2 requires inspection of the substrate and was a hold point for , CRL and Cxxx. Also, forms 91(a) and 117(b) to be signed off prior to commencing the works. It is to be noted that as part of the closure of NCR 1320 hold point was introduced for the substrate check in the ITP and that has not been followed. Notification of defect to be raised.
| 01CV - Civils | Cxxx-NCR-001468 | NCR | FIS - Secondary Lining - Sheet Waterproofing Detail - Binocular/Cavern Headwall Upper |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2015-09-23 | 2015-10-08 15:46 | 15 | 2015-09-02 17:04 | Civil - Tunnelling | 5000 |  | Damaged | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | has not been able to achieve the Sheet Waterproofing detail as per Cxxx-MMD-C4-DDD-CR086_SH003-04065 at the junction between the binocular wall and the Cavern Headwall upper in both WBX and EBX.
| 01CV - Civils | Cxxx-NCR-001469 | NCR | FIS - Secondary Lining - IA1 Collar Invert Steel |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2015-09-05 | 2015-10-30 14:46 | 55 | 2015-09-04 16:12 | Civil - Tunnelling | 500 |  | Supervision/Management | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During fixing of the IA1 Collar Invert, CRL Field Engineer instructed to change the steel from the design in Cxxx-OVE-C4-DDD-CR001_Z-03022 (C03) as there was an error in the drawing. Bar Mark 2x2-B32-02 is shown as being installed on the NF, though CRL Field Engineer asked for these bars to be installed on the FF. CRL Field Engineer would not sign off the steel inspection form until the amendment was made. Once changed, CRL Field Engineer signed off the check sheet and the pour commenced. In order to confirm the design change, raised Cxxx-RFI-001405. Though the response has not yet been received, has been told that this will say that the steel must be installed in accordance with the original design (Cxxx-OVE-C4-DDD-CR001_Z-03022 (C03)). This means that the instructions given by the CRL Field Engineer were incorrect and that remedial work must be done. The bars affected are Bark Mark 2, as highlighted on the attached detail (1).
| 01CV - Civils | Cxxx-NCR-001470 | NCR | Bolt holes drilled though FF sprayed secondary lining Fisher St WBX |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2015-09-21 | 2015-10-24 09:47 | 33 | 2015-09-07 13:36 | Tunnelling - Linings - Sprayed Concrete | 5000 |  | Workmanship | Repair | 3 (3-6k) | Complete | Management Problem - Inadequate supervision | Completed |  | In Bay 5B WBX, bolt holes that have been drilled for temporary works have been drilled between 250mm and 320mm. This means that some holes have been drilled through the waterproof membrane.
| 01CV - Civils | Cxxx-NCR-001471 | NCR | CP1 FIS out of tolerance |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2015-09-22 | 2015-11-02 09:03 | 41 | 2015-09-08 12:17 | Tunnelling - Linings - In-situ Concrete | 1500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The central section of CP1 has been cast out of tolerance and profiles have been provided for these areas.
| 01CV - Civils | Cxxx-NCR-001472 | NCR | Crack inducer not installed on contraction joint in IA1 invert collar to central section |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2015-09-22 | 2015-11-04 11:42 | 43 | 2015-09-08 15:10 | Tunnelling - Linings - In-situ Concrete | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Cxxx-FCD-001043 states: Collar and adit invert can be build together. Contraction joint to be achieved with a crack inducer. Please note that contraction joint type B requires a reinjectable tube in both the far face and near face. No grout tubes or crack inducer has been installed in this location.
| 01CV - Civils | Cxxx-NCR-001473 | NCR | WB tunnel out of tolerance ch 6445_6465 |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2015-10-07 | 2015-10-08 16:10 | 1 | 2015-09-23 15:51 | Tunnelling - Alignment | 1500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Further scan work and comparision to the design has highlighted a small area of tunnel inside the 100mm envelope. The area is approximately 4m by 3m located in the crown between chainages 6445 and 6465. This area was between profiles in the submitted wriggle survey and may have been subject to further movement due to its close proximity to CP5. Attached is a folder containing further wriggle analysis at 500mm centres through the area.
| 01CV - Civils | Cxxx-NCR-001474 | NCR | BOS-TCR FSC Incorrect installation of a ramp instead of a step at R2751 WB |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2015-09-25 | 2015-09-18 16:31 | -7 | 2015-09-11 07:38 | Civil - Tunnelling | 2000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Within the WB Tunnel of BOS-TCR, reworks were required on R2751 LHS where a ramp was put in the wrong position. This was broken out and made into a ramp at the correct position but was meant to be a step.
| 01CV - Civils | Cxxx-NCR-001475 | NCR | Non-stainless steel fixings installed in the invert of Crossover and Binocualr FIS |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2015-09-25 | 2015-10-09 23:30 | 14 | 2015-09-11 16:04 | Tunnelling - Linings - In-situ Concrete | 500 |  | Material | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | Non-stainless steel threaded bar has been installed in the invert of the Crossover and EB and WB binocular for the installation of side wall shutters. They have been drilled 100mm deep average.
| 01CV - Civils | Cxxx-NCR-001476 | NCR | FIS CP1 - Collar Profiles out of tolerance |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2015-09-28 | 2015-10-13 17:37 | 15 | 2015-09-14 14:10 | Tunnelling - Linings - In-situ Concrete | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | The Collar to CP1 has been cast out of tolerance. The profile of the collar is provided.
| 01CV - Civils | Cxxx-NCR-001477 | NCR | MASS POUR STS type FSC as-built data for WB TCR-BOS PTW out of tolerance |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2015-10-14 | 2015-09-22 15:03 | -22 | 2015-09-14 17:48 | Civil - Tunnelling | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | No high spots on the slab only some low points but within extended tolerances. Some slopes out of tolerance. Please find detailed as built survey data in file titled "BOS-TCR EB & WB Asbuilt Final Survey Rev.6" included in eB document: Cxxx--C4-LRC-CRT00_ST005-50753
| 01CV - Civils | Cxxx-NCR-001478 | NCR | FIS- Lack of Early Age Compressive Strength testing of Secondary Lining |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2015-10-09 | 2015-10-19 09:14 | 10 | 2015-09-18 14:50 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Planning | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Whilst spraying the secondary lining of EBX, CP5 and WBX not many early age compressive strength tests were completed. The requirement as per FCD 1141 is that an early age strength panel should be sprayed every 24hrs.
| 01CV - Civils | Cxxx-NCR-001479 | NCR | Not installed UTXs TCR-BOS section Eastbound |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2015-10-01 | 2015-10-02 10:14 | 1 | 2015-09-17 09:38 | Civil - Tunnelling | 50000 |  | Workmanship | Use As-Is | 2 (6-60k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | UTXs not installed in Eastbound Tunnel TCR-BOS section. Locations: chainages 4+358.0, 4+555.6 and 4+753.2
| 01CV - Civils | Cxxx-NCR-001481 | NCR | Fisher street - Damages to the SGI segments in CP2 |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2015-10-02 | 2015-10-09 23:33 | 7 | 2015-09-18 08:33 | Tunnelling - Linings - SGI Rings | 1500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | During the breaking out of the temporary concrete infil of the SGI segments to support the temporary proping, some damages were made in the SGI segments in the crown of CP2. Pictures and marked up drawing attached
| 01CV - Civils | Cxxx-NCR-001482 | NCR | SL- Approval To Spray Waterproofing In The Eastbound Binocular Stub Tunnel (Form 117c) |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2015-10-02 | 2015-10-02 10:18 | 0 | 2015-09-18 11:58 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | Approval to spray waterproofing in the eastbound stub tunnel ( Form 117c) cannot be found/missing.
| 01CV - Civils | Cxxx-NCR-001483 | NCR | FIS CP1 & CP2 Cracks on cast in situ concrete |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2015-10-06 | 2015-11-22 20:10 | 47 | 2015-09-22 08:52 | Tunnelling - Linings - In-situ Concrete | 1500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Cracks have been observed in cast in situ CP1 & CP2 shoulder in the Crossover side. They have been measured as follows: CP1 East side 0.6mm & CP1 West side 0.5mm, CP2 East side 0.6mm & CP2 West side 0.7mm. As the cracks are above 0.3mm in width, remedial works will be required.
| 01CV - Civils | Cxxx-NCR-001484 | NCR | Adit 2. Invert contraction joint |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2015-10-13 | 2015-10-16 16:27 | 3 | 2015-09-29 12:13 | Tunnelling - Linings - In-situ Concrete | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | During the cast of the invert slab in the Adit 2, the contraction joint (type F) was built parallel to the shaft instead of parallel to the westbound running tunnel as the drawing showed
| 01CV - Civils | Cxxx-NCR-001485 | NCR | Westbound catchpit at chainage 5916. No box out for Cxxx drainage pipe |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2015-10-05 | 2015-10-06 15:57 | 1 | 2015-09-21 18:21 | Civil - Drainage | 2000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Drawing Cxxx-OVE-D-DDD-CR001_Z-53016 and Cxxx-RFI-001403 show details of a catchpit at chainage 5916 in the westbound tunnel. The catchpit in question was to be boxed out to allow for Cxxx to install a drainage pipe on the north side of the catchpit. The box out was never installed and have cast the catchpit in FSC. The catchpit is located between IA2 and WBX.
| 01CV - Civils | Cxxx-NCR-001486 | NCR | Lips and Steps out of agreed tolerances in Running Tunnels between ROP-FAR (16mm-20mm) |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2015-10-06 | 2015-10-09 23:46 | 3 | 2015-09-22 17:44 | Civil - Tunnelling | 1500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Following the Lips and Steps survey within the tunnels between ROP and FAR, it was determined that some of the lips and steps fall beyond the agreed tolerances stated in RFI 001342. Many of the steps found out of the agreed tolerances, are within the range of 16-20mm. The attached table shows the areas where the lips and steps exceed the 16mm tolerance.
| 01CV - Civils | Cxxx-NCR-001487 | NCR | Lips and Steps out of agreed tolerances in Running Tunnels between ROP-FAR (Greater than 20mm) |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2015-10-06 | 2015-10-16 16:59 | 10 | 2015-09-22 17:45 | Civil - Tunnelling | 6000 |  | Incorrect Installation | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Following the Lips and Steps survey within the tunnels between ROP and FAR, it was determined that some of the lips and steps fall beyond the agreed tolerances stated in RFI 001342. In three places between FIS-FAR Westbound Tunnel, the lips and stps were found to be greater than 20mm. At CH 6093.7 the lip/step is 27mm, CH6095.3 the lip/step is 27mm and at CH 6696.7 the lip/step is 30mm. Table attached.
| 01CV - Civils | Cxxx-NCR-001488 | NCR | Damage to Permanent Running Tunnel Precast Concrete Segments at CP1 Fisher Street |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2015-10-12 | 2015-10-14 12:06 | 2 | 2015-09-23 14:29 | Tunnelling - Linings - Precast | 1500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | The permanent precast concrete segments in the vicinity of CP1 Fisher Street have been cored through for depressurization purposes. No cores have passed through any segment joints. wish to repair the depressurization holes using the same approved method used at CP5. The approved method for CP5 is outlined in Cxxx-NCR-001080. Please find attached sketch illustrating the repair procedure. Please find attached photo of depressurization holes at CP1
| 01CV - Civils | Cxxx-NCR-001489 | NCR | FSC TCR-FIS Non compliance with U3/F3 finish on invert in the eastbound Tunnel between rings 3004-3046 (CH 5024.28-5091.44) |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2015-10-08 | 2015-10-09 23:37 | 1 | 2015-09-24 09:05 | Civil - Tunnelling | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Polish down where possible to smooth off ridges but to not go too deep otherwise a bowl will be present.
| 01CV - Civils | Cxxx-NCR-001490 | NCR | BFK090b form missing for FIS EBX RHS Kerbs |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2015-10-22 | 2015-10-19 09:07 | -3 | 2015-09-29 10:58 | Tunnelling - Linings - In-situ Concrete | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | 090b form missing for FIS EBX RHS Kerbs Ch 0 - 11.5
| 01CV - Civils | Cxxx-NCR-001491 | NCR | BFK091a Regulating Application forms missing FIS EBX |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2015-10-13 | 2015-10-19 09:02 | 6 | 2015-09-29 11:00 | Tunnelling - Linings - In-situ Concrete | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | 091a missing EBX Invert Ch 36 - 45m Application and Inspection and Crown Ch 0 - 15m & 42.3 - 53m Application. Signature page missing for 091a Ch. 15 - 33m application and 0 - 22m application and inspection.
| 01CV - Civils | Cxxx-NCR-001492 | NCR | Signatures missing from FIS EBX Form BFK090a |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2015-10-12 | 2015-10-19 21:52 | 7 | 2015-09-29 11:06 | Tunnelling - Linings - In-situ Concrete | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | Signatures missing from Form 090 EBX invert Ch 30.1 - 45m and 0 - 30m.
| 01CV - Civils | Cxxx-NCR-001493 | NCR | Form BFK117(b) missing FIS EBX |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2015-10-12 | 2015-11-16 08:58 | 35 | 2015-09-29 11:10 | Tunnelling - Linings - In-situ Concrete | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | Approval to spray 117b missing for EBX invert Ch. 0 - 36m and Crown 0 - 2 & 42 - 44.
| 01CV - Civils | Cxxx-NCR-001494 | NCR | Form BFK088 missing FIS EBX |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2015-10-13 | 2015-10-19 14:02 | 6 | 2015-09-29 13:18 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Form 088 missing for FF Mix018 Ch 1 - 11m and NF Mix021 0 - 1.15m EBX sprayed secondary lining. In addition to this, Engineer signatures are missing from the following forms: NF Ch. 4.89 - 8.11 NF Ch. 8.13 - 11.52 NF Ch. 11.55 - 14.68 FF Ch. 14.71 - 17.81 NF Ch. 14.71 - 17.85 NF Ch. 20.84 - 25.47 NF Ch. 25.5 - 30.1 FF Ch. 34.7 - 39.2 NF Ch. 34.7 - 39.3 FF Ch. 39.33 - 44.25 NF Ch. 39.3 - 44.3 FF Ch. 44.3 - 48.3 FF Ch. 48.3 - 52.83 NF Ch. 48.5 - 52.5 (headwall)
| 01CV - Civils | Cxxx-NCR-001495 | NCR | Dosing pump calibration has not been carried out in accordance with ITP - FIS EBX |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2015-10-13 | 2015-10-19 08:51 | 6 | 2015-09-29 13:37 | Tunnelling - Linings - In-situ Concrete | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | As per the ITP, dosing pump calibration is to be carried out weekly, there are insufficient records to show this.
| 01CV - Civils | Cxxx-NCR-001496 | NCR | Cores tested outside of 1-3 days - June |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2015-10-21 | 2015-10-21 21:20 | 0 | 2015-09-30 15:24 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Planning | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Improper resource allocation | Completed |  | The following sets of cores were tested outside of 1-3 days: Sample FIS140, 09/06/15, EBX, Secondary, Bay 2C FF - tested at 7 days Sample FIS141, 12/06/15, EBX, Secondary, Bay 4A FF - tested at 4 days Sample FIS143, 27/06/15, EBX, Fireproofing, Bay 3B NF, Ch25.5-30.1 - tested at 4days
| 01CV - Civils | Cxxx-NCR-001497 | NCR | Washout test - Mix24A July |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2015-10-26 | 2015-10-19 21:50 | -7 | 2015-10-05 18:14 | Tunnelling - Linings - In-situ Concrete | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | Sample EX1834, one of the samples produced a result of 1.5kg/m which is less than 80% of design content.
| 01CV - Civils | Cxxx-NCR-001498 | NCR | 1 day cores tested late |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2015-10-22 | 2015-10-29 12:10 | 7 | 2015-10-01 15:46 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Planning | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | The following set of cores were tested late: Sample FIS146, WBX Secondary Bay 5A, Ch20.7-25.5 - tested at 5 days Sample FIS147, WBX Secondary Bay 4C, Ch20.7-25.5 - tested at 4 days Sample FIS150, WBX Secondary Bay 3A, Ch20.7-25.5 - tested at 4 days
| 01CV - Civils | Cxxx-NCR-001499 | NCR | FIS IA1 Masterseal overlap damaged |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2015-10-12 | 2015-10-14 17:16 | 2 | 2015-10-01 16:33 | Tunnelling - Tunnelling General | 5000 |  | Damaged | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | In IA1 on the RHS, looking from the shaft, the 300 mm masterseal overlap between the invert and the wall was damaged.
| 01CV - Civils | Cxxx-NCR-001500 | NCR | Insufficient testing of Mix 21 in July |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2015-10-22 | 2015-10-21 20:59 | -1 | 2015-10-01 16:13 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Planning | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | In July, 48m of Mix21 was used but no panels were sprayed for testing.
| 01CV - Civils | Cxxx-NCR-001502 | NCR | FIS Oversprayed secondary lining profiles Niche1 & Niche 2 |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2015-10-12 | 2015-11-15 20:14 | 34 | 2015-10-02 17:33 | Tunnelling - Linings - Sprayed Concrete | 3000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Some areas of the secondary lining profiles in Niche 1 & Niche 2 are not according to the design profile and not compliant with the tolerances
| 01CV - Civils | Cxxx-NCR-001503 | NCR | FIS WBX Contraction Joint between Bay 5B and Cavern Headwall |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2015-10-12 | 2015-11-22 20:14 | 41 | 2015-10-02 18:28 | Tunnelling - Linings - Sprayed Concrete | 2000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | In WBX, the contraction joint between Bay 5B and Cavern Headwall was not built completely straight. For this reason some remedial works are needed.
| 01CV - Civils | Cxxx-NCR-001504 | NCR | Missing BFK090a&b Masterseal and BFK091a Regulating for WB BN 1 & 2 FIS |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2015-10-21 | 2015-10-21 20:48 | 0 | 2015-10-07 16:06 | Tunnelling - Linings - In-situ Concrete | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | The regulating and waterproofing checksheets for the WB BN 1 & 2 are missing from the ITP package. the works have been carried out and all appropriate people witnessed and were satisfied at the hold points from the ITP. The approval to regulate and spray waterproofing (117) has been attached to show that all parties were happy to continue with the works at the time. Checksheets 090 and 091 have been back dated to contain the correct information and a stamp has been used (similar to NCR1097) to state that all checks have been carried out in accordance with the ITP.
| 01CV - Civils | Cxxx-NCR-001505 | NCR | Missing Hammer Testing form BFK116 for Primary lining Crown WB BN 1 & 2 |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2015-10-21 | 2015-11-16 09:01 | 26 | 2015-10-07 13:50 | Tunnelling - Linings - In-situ Concrete | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | The Hammer testing Form 116 for the WB BN 1 & 2 crown Ch. 1-10 has been lost. This is a hold point on the ITP and the works have been carried out, we have a signed approval to regulate form for the Binocular section and the hammer testing has been completed - see attached.
| 01CV - Civils | Cxxx-NCR-001506 | NCR | Hammer Testing form BFK116 missing for WB BN 1 & 2 post regulating Invert |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2015-10-21 | 2015-11-16 09:04 | 26 | 2015-10-07 14:48 | Tunnelling - Linings - In-situ Concrete | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Hammer testing form 116 WB BN 1 & 2 Invert post regulating has been lost, testing was carried out at the time of the works. The approval to spray waterproofing has been attached and states that hammer testing has been carried out.
| 01CV - Civils | Cxxx-NCR-001507 | NCR | Category H2 hole positioned in the crown at ring 3634 westbound |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2015-10-21 | 2015-11-02 14:58 | 12 | 2015-10-07 15:08 | Tunnelling - Linings - Precast | 4000 |  | Damaged | Repair | 3 (3-6k) | Complete | Management Problem - Other | Completed |  | The permanent precast concrete segments west of WBX (ring 3634) have been cored for depressurization. No cores have passed through any segment joints. wish to repair the depressurization holes using the same approved method used at CP5. The approved method for CP5 is outlined in Cxxx-NCR-001080. Please find attached sketch illustrating the repair procedure. Please find attached photo of repair location and proposed solution. Please find attached segment repair matrix which contains material for category H2 repairs: Cxxx--C-LRG-CRT00_ST005-50008
| 01CV - Civils | Cxxx-NCR-001508 | NCR | As builts missing from EB BN 3 invert |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2015-10-22 | 2015-11-16 09:09 | 25 | 2015-10-08 08:56 | Tunnelling - Linings - In-situ Concrete | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | The asbuilt from the EB BN 3 invert is missing. We have the invert of BN 1 & 2 and the profile of BN3.
| 01CV - Civils | Cxxx-NCR-001509 | NCR | Approval to spray regulating and waterproofing incomplete for CP5 FIS |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2015-10-22 | 2015-11-16 09:16 | 25 | 2015-10-08 11:31 | Tunnelling - Linings - In-situ Concrete | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | The CRL and Cxxx signatures are missing from 117b and 117c. has signed. This is a hold point on the ITP (50139). See attached for 091 stating that CRL & Cxxx was happy with the pre spray checks and substrate prior to regulating and also 090b stating that Cxxx was happy with pre spray checks and substrate.
| 01CV - Civils | Cxxx-NCR-001510 | NCR | FIS CP5 Small area of fireproofing layer removed |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2015-10-12 | 2015-11-16 09:29 | 35 | 2015-10-08 15:30 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Damaged | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | In CP5 tunnel, a small hollow area was found close to the collar (Eastbound side) at the shoulder level between Ch. 4.7 and Ch. 5.0.
| 01CV - Civils | Cxxx-NCR-001511 | NCR | Imcomplete BFK117 approval to waterproof and regulate EB BN 1 and 2 |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2015-10-22 | 2015-11-16 09:39 | 25 | 2015-10-08 16:58 | Tunnelling - Linings - In-situ Concrete | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | There are CRL and Cxxx signatures missing from the Approval to regulate the EB BN 1 and 2 crown Ch. 0 - 10 and approval to waterproof the EB BN 1 and 2. See attached for 091a for BN 1 and 2 crown and also 090a for the EB BN - all pre spray checked have been signed by and/or CRL and Cxxx.
| 01CV - Civils | Cxxx-NCR-001513 | NCR | Fisher Street - WB binocular stub tunnel secondary lining hollow spot |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2015-10-26 | 2015-11-04 14:52 | 9 | 2015-10-12 10:02 | Tunnelling - Linings - Sprayed Concrete | 1500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | During the hammer test of the sprayed near face secondary lining in the WB binocular, an area of 1.5mx2.0m was found to be hollow. As builds with the location and the thickness of the layer attached to the NCR 5 quality cores were taken and show good quality and evidences of a min thickness of 150mm of the layer and the A393 mesh installed
| 01CV - Civils | Cxxx-NCR-001514 | NCR | Incomplete as builts FIS WBX invert slab |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2015-10-28 | 2015-11-22 20:20 | 25 | 2015-10-14 17:05 | Tunnelling - Linings - In-situ Concrete | 1500 |  | Planning | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | There are incomplete as builts taken on the secondary lining WBX invert slab. Ch 30 - 53 only has half the width of the slab - ITP states every 1m is required. First stage concrete has been cast over the slab. See attached for as builts taken.
| 01CV - Civils | Cxxx-NCR-001515 | NCR | CP5 invert slab out of tolerence |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2015-10-29 | 2015-10-29 11:34 | 0 | 2015-10-15 17:05 | Tunnelling - Linings - In-situ Concrete | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | CP5 invert slab out of tolerance. See attached for asbuilt of slab and I have also attached a dwg stating in Note 9 that there will be a 75mm screed over the slab.
| 01CV - Civils | Cxxx-NCR-001526 | NCR | FIS Crossover out of tolerance |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2015-10-30 | 2015-12-08 13:56 | 39 | 2015-10-16 09:43 | Tunnelling - Linings - In-situ Concrete | 1500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The last section in the Crossover tunnel between chainage. 58.9 and 60.3 (Eastbound side) has been cast out of tolerance. Profiles have been provided for these areas
| 01CV - Civils | Cxxx-NCR-001527 | NCR | FIS WBX Exposed re-injectable tubes |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2015-11-02 | 2015-10-30 14:37 | -3 | 2015-10-19 09:06 | Tunnelling - Grouting | 1500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | In the WBX, in the connection between Bay 5B and the Cavern Headwall the re-injectable tubes were exposed. A picture of the area is attached
| 01CV - Civils | Cxxx-NCR-001528 | NCR | Depressurisation holes through PCC Segmennts to be repaired in the vicinity of IA1 Eastbound and IA2 Westbound |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2015-11-02 | 2015-10-27 15:47 | -6 | 2015-10-19 11:36 | Tunnelling - Linings - Precast | 3000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The permanent precast concrete segments in the vicinity of IA1 and IA2 have been cored through for depressurization purposes. The depressurization holes are positioned at rings 3510 and 3514 in the eastbound tunnel. The depressurization holes are positioned at ring 3594 and 3598 in the westbound tunnel. Attached are photographs showing the position of each hole, its ring number, and tunnel location
| 01CV - Civils | Cxxx-NCR-001529 | NCR | Fisher Street - IA1 collar out of tolerance |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2015-11-30 | 2016-12-07 21:22 | 373 | 2015-10-19 12:24 | Tunnelling - Linings - In-situ Concrete | 3000 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During the construction of IA1 collar, the vertical walls of the collar were built out of tolerance, reducing the opening size to a max of 30mm
| 01CV - Civils | Cxxx-NCR-001532 | NCR | KTT EB and WB Running Tunnels. Sections out of tolerance |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2015-11-21 | 2015-11-02 09:27 | -19 | 2015-10-22 17:57 | Civil - Tunnelling | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Several sections of running tunnels detected as out of tolerance. Slab: no high spots detected. A few spots out of tolerance but within extended tolerance. Kerbs: no critical spots but a few within extended tolerance Catchpits: no critical spots but a few within extended tolerance
| 01CV - Civils | Cxxx-NCR-001533 | NCR | Crossover - WBX - EBX. Sections out of tolerance |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2015-11-21 | 2015-11-17 10:22 | -4 | 2015-10-22 17:58 | Civil - Tunnelling | 10000 |  | Workmanship | Use As-Is | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Several sections of Crossover, EBX or/and WBX detected as out of tolerance. Slab: no high spots detected. A few spots out of tolerance but within extended tolerance. Kerbs: no critical spots but a few within extended tolerance Catchpits: no critical spots but a few within extended tolerance
| 01CV - Civils | Cxxx-NCR-001534 | NCR | Invert Slab profiles missing FIS EBX Ch. 49-55 |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2015-10-23 | 2015-11-16 09:42 | 24 | 2015-10-22 10:57 | Tunnelling - Linings - In-situ Concrete | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Invert slab profiles missing for EBX Ch 49 - 55. I have attached the profiles up to Ch. 49. First stage concrete has been cast over this area now therefore no as built can be taken.
| 01CV - Civils | Cxxx-NCR-001535 | NCR | BFK Form 090b missing for EBX Kerbs |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2015-10-23 | 2015-11-22 20:27 | 30 | 2015-10-22 15:15 | Tunnelling - Linings - In-situ Concrete | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | North side 44-53 South side 20.8 - 30.1 missing Masterseal inspection form. I have attached the cast insitu checksheet and it has been signed by CRL and Cxxx in each occasion. In addition, the EB BN LHS Headwall Form 090b has not been signed by CRL/Cxxx and this is a hold point on the ITP. All checks have been carried out by and see attached for the application checksheet for this area with checks carried out by , CRL and Cxxx.
| 01CV - Civils | Cxxx-NCR-001536 | NCR | Localised under thickness of primary lining EBX |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2015-10-23 | 2016-08-16 14:50 | 298 | 2015-10-23 08:40 | Tunnelling - Linings - In-situ Concrete | 1500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Ch. 1.995 and 10.212 show localised areas of below design thickness. I have attached 123 milling sheet stating that the minimum thickness will be 330mm and also the thickness as builts.
| 01CV - Civils | Cxxx-NCR-001537 | NCR | Missing BFK117b, 117c and regulating layer comb tests Fisher St Crossover |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2015-10-30 | 2015-12-07 17:01 | 38 | 2015-10-26 13:10 | Tunnelling - Linings - In-situ Concrete | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | Approval spray regulating layer form 117b is missing for CP1, N1, N2, XO crown 16-59 and XO invert 0-9 and 22-25. I have attached the first sheet of the regulating layer checksheet 091a that makes reference to primary lining checks. Comb testing of the regulating layer is a hold point on the ITP and there are some areas that are missing, the areas that we do have witnessed by CRL/Cxxx are: N2, CP2, invert Ch. 9-22 and Crown 0-58. All other areas are missing, I have attached the approval to spray waterproofing in all areas to show that all parties were happy with the substrate before spraying waterproofing. The approval to spray waterproofing check sheet is also not signed by CRL/Cxxx for CP1 - I have attached the Masterseal application check sheet 090a with makes reference to the regulating layer substrate checks. Additional Notes: There is hammer testing missing for Niche 2 and CP1 - see attached form 091a for N2 and CP1 (under folder 'NCR 1537 117b evidence') all checks on primary lining prior to regulating have been carried out.
| 01CV - Civils | Cxxx-NCR-001538 | NCR | Cover to NF steel profiles missing FIS EBX |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2015-10-27 | 2015-11-22 20:31 | 26 | 2015-10-26 16:12 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Ch. 31-39 missing steel cover profiles. See attached for available steel cover profiles with summary and final profile. Wagon wheels have been used during spraying in EBX to ensure that there is 60mm minimum cover - no wagon wheels are visible post spraying therefore cover has been achieved.
| 01CV - Civils | Cxxx-NCR-001539 | NCR | Mix 24A Flow results |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2015-11-12 | 2015-11-22 20:37 | 10 | 2015-10-29 16:11 | Tunnelling - Linings - In-situ Concrete | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Subcontractor Problems - Other | Completed |  | During May to October 2015, the flow results recorded on arrival to site were outside the specified range. In addition, on 17/12/14 there was one load of concrete mix 24A out of spec. the slump flow recorded was 730 however, this could be due to the fact that this mix uses different test procedures and operatives were not aware and performed a flow test on the mix. This note is to be included in the Cxxx--C4-LRC-CRT00_ST005-50851 ITP records for EB BN 1&2.
| 01CV - Civils | Cxxx-NCR-001540 | NCR | FIS - Batching Tolerance for Microsilica August 2015 |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2015-11-12 | 2015-11-22 20:40 | 10 | 2015-10-29 13:05 | Tunnelling - Linings - In-situ Concrete | 500 |  | Equipment Breakdown | Use As-Is | 4 (0.5-3k) | Complete | Subcontractor Problems - Other | Completed |  | There was one batch during August 2015 that was underdosed with microsilica.
| 01CV - Civils | Cxxx-NCR-001541 | NCR | FIS CP5 thickness of invert primary lining after milling |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2015-11-03 | 2015-11-22 20:44 | 19 | 2015-11-02 13:41 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | At chainage 6.6m in CP5 invert there is no excavation profile to determine primary lining thickness, therefore proof drilling was carried out in this area. The results of the proof drilling showed that the lining thickness was >250mm. On the milling sheet it states that a minimum thickness of 218mm is permitted, however some milling has been undertaken in the localized area and therefore the exact thickness can not be determined. This area has since had concrete cast over so further proof drilling is not practical. I have attached the milling sheet for this area, the after milling profile for CP5 and after milling thickness of primary lining.
| 01CV - Civils | Cxxx-NCR-001542 | NCR | Crosover out of tolerance |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2015-11-05 | 2015-11-22 20:51 | 17 | 2015-11-03 09:30 | Tunnelling - Linings - In-situ Concrete | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Areas in the Crossover at the knees are out of tolerance, the max is 24mm at chainage 37.0m in a localized area. The first stage concrete has been marked on to show its location.
| 01CV - Civils | Cxxx-NCR-001544 | NCR | FIS WB BN wall out of tolerance |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2015-11-13 | 2015-11-22 20:54 | 9 | 2015-11-10 16:53 | Tunnelling - Linings - In-situ Concrete | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | The WB BN Wall lift 2 has been cast out of tolerance. NCR 1170 was raised for the lower section.
| 01CV - Civils | Cxxx-NCR-001545 | NCR | Missing signatures on Form 091b and missing 117c - WB Stub tunnel |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2015-11-13 | 2015-12-07 17:09 | 24 | 2015-11-12 09:36 | Tunnelling - Linings - SGI Rings | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | on Form 091b regulating of WB Stub tunnel there are CRL/Cxxx signatures missing and this is a hold point on the ITP. All checks were carried out at the time of works and I have attached the Regulating and Masterseal sheets to prove this. There are also missing new Form 117c for sprayed waterproofing after some milling was carried out. please refer to masterseal checksheet to see that all checks were carried out at the time of works.
| 01CV - Civils | Cxxx-NCR-001546 | NCR | Localised underthickness of secondary lining WB stub tunnel FIS |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2015-11-13 | 2016-05-06 07:27 | 175 | 2015-11-13 11:47 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | There is localized underthickness of the sprayed secondary lining in the WB stub tunnel. The combined thickness of the lining (primary + secondary) exceeds the design and the thickness of the fireproofing has not been compromised in any area. See attached for the thickness of lining, thickness of secondary lining and thickness of fireproofing.
| 01CV - Civils | Cxxx-NCR-001547 | NCR | WBX FIS Invert Slab profiles |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2015-11-20 | 2015-11-22 20:58 | 2 | 2015-11-19 11:07 | Tunnelling - Linings - In-situ Concrete | 3000 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Worker not correctly instructed | Completed |  | Please find attached profiles for cast in-situ inverts to EBX. Some profiles are not within the tolerance outlined in the general notes drawings. This relates to Cxxx-NCR-001514.
| 01CV - Civils | Cxxx-NCR-001548 | NCR | FIS WBX Missing forms and signatures for regualting and waterproofing |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2015-11-20 | 2015-12-08 14:05 | 18 | 2015-11-19 13:27 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | There are missing forms and signatures for CRL/Cxxx hold points. Areas missing for Regulating checksheet 091A: Ch. 33-35 missing comb test/signatures for RHS crown Ch. 44-41 missing comb tests/signatures for LHS crown Ch. 45-53 missing comb test/signatures for LHS crown Areas missing for Tamseal Application 138A: Ch. 30-50 missing shore hardness test Ch. 0-13 missing CRL/Cxxx signature Area missing for Hammer testing of Primary lining 116: Ch. 30-35 crown Area missing for Approval to spray waterproofing 117c: Ch. 30-53 crown. All checks have been carried out at the time of works. See attached checksheets for regulating and waterproof application of WBX as evidence.
| 01CV - Civils | Cxxx-NCR-001549 | NCR | Profile missing from FIS Shaft wall IA2 |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2015-12-04 | 2015-12-21 09:22 | 17 | 2015-11-20 16:14 | Tunnelling - Linings - In-situ Concrete | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | In the first pour of IA2/shaft wall only one as built was taken for a two metre pour, this is at 100.9. The first pour is between 99.2 and 101.14, therefore one profile is missing. All shutters were installed vertical and plumb therefore it is right to assume that the asbuilts above the area are a fair representation of the lower section. The Shaft wall cast with the adit is cast to match in line with the secondary lining of the shaft.
| 01CV - Civils | Cxxx-NCR-001550 | NCR | FIS IA2 collar inside profile |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2015-11-24 | 2015-11-30 11:08 | 6 | 2015-11-20 16:34 | Tunnelling - Linings - In-situ Concrete | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During the construction of IA2 collar, the vertical walls of the collar were built out of tolerance, reducing the opening size to a max of 25mm
| 01CV - Civils | Cxxx-NCR-001551 | NCR | Compressive strength of Contact grouting cubes not achieved in 28 days - FIS |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2015-11-27 | 2015-11-30 10:25 | 3 | 2015-11-24 15:40 | Tunnelling - Linings - In-situ Concrete | 500 |  | Testing and Commissioning | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | The compressive strength of contact grout tubes for Crossover crown bay 4, 5 & 7 have not achieved 28 day strength in 28 days. The compressive strength has been reached in tests at 41, 40 and 36 days respectively. Testing for IA1 and IA2 crown was not undertaken at 7 and 28 days as per ITP but at 12 and 21. Strength was achieved. See attached for compressive strength reports and results summary.
| 01CV - Civils | Cxxx-NCR-001553 | NCR | No serial numbers provided for tilt sensors at Paddington Station |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2015-12-24 | 2015-12-30 11:11 | 6 | 2015-12-10 10:42 | Geotechnical Engineering - Compensation Grouting | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | Report Cxxx--C4-RGN-CRT00_ST005-50637 7.0 Installation Report for Paddington Station Track has been rejected due to lack of certificate for the batch of track tilmeters installed on Paddington Station.
| 01CV - Civils | Cxxx-NCR-001554 | NCR | Cracks To First Stage Concrete - WB Running Tunnel West of Paddington Station Box |  | Crossrail | XRL | TUX - Tunnel Drive X (West) |  | 2016-05-27 | 2017-04-22 06:44 | 330 | 2016-05-13 10:49 | Tunnelling - Linings - In-situ Concrete | 1500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Not Defined | Completed |  | Crossrail have identified a number of cracks in the First Stage Concrete in the WB Running Tunnel to the west of Paddington Station Box. The cracks have been identified in the kerb and the invert and are located between ring number 480 to 492 for the kerb and between ring number 490 and 491. The cracks located in the kerb are in the both the north kerb location and south kerb location. The cracks in the invert extend to the north and south of the invert. The crack widths for both the kerbs and the invert vary in size between 5mm to 6.7.
| 01CV - Civils | Cxxx-NCR-001555 | NCR | Defect - TWUL Great Western Road Sewer |  | Contr | BFK | TUX - Tunnel Drive X (West) |  | 2016-08-05 | 2017-01-18 09:41 | 166 | 2016-07-22 14:29 | Civil - Utilities Engineering | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | External Phenomenon - Other | Completed |  | A defect notice has been raised by the WCC Highway Authority, for works completed by Crossrail at the Great West Road back in November 2014. The notice was raised by TW’s street works team who have been chasing this since April 2015, however the representative that they were contacting (James Carden) had already left the Cxxx/xxx project by then and hence the remediation works did not go ahead on a timely manner. TW finally contacted CRL (__) on 22/06/2016 who immediately made contact with (__, Peter Bimson) on the 23/06/16 and a site visit was arranged by WCC / TW/ CRL / for verification of the situation. The visit took place on Tuesday 05/07/16 however the extent of the defect was not clearly confirmed by WCC. WCC suggested during this meeting that the defect notice would affect mainly the trench excavated at 56 Great Western Road in order to pump from the existing manhole on east side of the bridge over to the old sewer south of MH1. The asphalt on the trench is showing cracks and holes and sliding areas due to lack of chipping. In addition, a wrong tone of yellow had been applied to the traffic lines over the trench and nearby areas. WCC stated that the defect extent needed to be confirmed in a further site visit. The current situation is that a remedial works permit must be issued by TW before WCC can arrange the coordination meeting where the scope of the repairs will be agreed. Please find attached pre-condition and current condition pictures of the trench.
| 01CV - Civils | Cxxx-NCR-000151 | NCR | Limmo Diaphgram Walls: Panel 1 Stop Ends Setting Out |  | Contr |  | TUY - Tunnel Drive Y (Central) |  | 2011-09-30 | 2011-11-04 16:24 | 35 | 2011-09-14 | Structural Engineering - Diaphragm Walls | 500 |  | Supervision/Management | Rework |  | Complete |  | Completed |  | An incorrect drawing was used by the setting out engineer for marking the positions of the ends of the panel 1. The guidewall construction joint positions were set out instead of precast stopend positions. A survey of Panel 1 was carried out to determine it's as-built location. The steel cages were installed at the design offset to the stopends and as such the central gap between the two cages had increased from 200mm to 600mm. See attached sketch indicating the as-built position of the stopends compared to the design position. The incorrect positioning of the stop ends on Panel 1 have resulted in the cages for Panel 1 being located in a different location in respect to plan to that required in the design detailing drawings. The attached sketch: "Limmo __ - attachment to NCR - Panel_1_asbuilt.pdf" indicates the actual asbuilt condition, for which it is requested that the Cxxx Jacobs review. It is noted that there will be an affect on the corbel design positioned at this location which will need to be reviewed as a consequence.
| 01CV - Civils | Cxxx-NCR-000165 | NCR | Contractors witness interventions |  | Contr |  | TUY - Tunnel Drive Y (Central) |  | 2011-10-21 | 2011-11-16 11:18 | 26 | 2011-09-22 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | Records were available to demonstrate that only one of the interventions points had been implemented.
| 01CV - Civils | Cxxx-NCR-000201 | NCR | Limmo Diaphragm Wall: Panel 14 |  | Contr |  | TUY - Tunnel Drive Y (Central) |  | 2011-10-07 | 2011-11-30 15:35 | 54 | 2011-10-05 | Structural Engineering - Diaphragm Walls | 500 |  | Design | Rework |  | Complete |  | Completed |  | The final panel excavation profile is insufficient to accomodate the reinforcement cages. During installation, the cage sections snagged against each other during the lowering operation resulting in the abandonment of the operation. This is related to NCR Number 152, where the Panel 1 stop-end was placed 200mm oversize to the design, which reduced the plan length of Panel 14. The contractors proposal to alter the detailing of the cages for panels 2,3,4,5,7,8,9,11,12,13,14 has been discussed. However the wording of the NCR needs to be revised to clarify exactly what is proposed. In order that this can be forwarded to the designer for consideration and acceptance. MBush 06/10/11. The proposal of the NCR is considerd acceptable and is to be reviewed by the designer Cxxx Jacobs.
| 01CV - Civils | Cxxx-NCR-000202 | NCR | Limmo Diaphgram Walls: Panel 2 Reinforcement |  | Contr |  | TUY - Tunnel Drive Y (Central) |  | 2011-10-20 | 2011-11-28 14:22 | 39 | 2011-10-06 | Structural Engineering - Reinforcement | 500 |  | Design | Rework |  | Complete |  | Completed |  | Panel 2 - Following installation issues encountered at Panel 9 and Panel 14 (see RFI 201 and 204), a review of the reinforcing cage dimension highlighted a lack of provision for installation tolerances for Panel 2 cage sections. The cages have been fabricated in accordance with approved construction drawings Cxxx-DSJ-S-DWG-CR144_SH011-50009 rev. C02 and Cxxx-DSJ-S-DWG-CR144_SH011-50010 rev. C02.
| 01CV - Civils | Cxxx-NCR-000203 | NCR | Limmo Diaphgram Walls: Panel 11 Reinforcement |  | Contr |  | TUY - Tunnel Drive Y (Central) |  | 2011-10-20 | 2011-12-20 16:27 | 61 | 2011-10-06 | Structural Engineering - Reinforcement | 500 |  | Design | Rework |  | Complete |  | Completed |  | Panel 11 - Following installation issues encountered at Panel 9 and Panel 14 (see RFI 201 and 204), a review of the reinforcing cage dimension highlighted a lack of provision for installation tolerances for Panel 11 cage sections. The cages have been fabricated in accordance with approved construction drawings Cxxx-DSJ-S-DWG-CR144_SH011-50013 rev.C02 and Cxxx-DSJ-S-DWG-CR144_SH011-50014 rev.C02.
| 01CV - Civils | Cxxx-NCR-000204 | NCR | PANEL 9 - Diaphragm Walls Reinforcement |  | Contr |  | TUY - Tunnel Drive Y (Central) |  | 2011-10-09 | 2011-12-20 16:44 | 72 | 2011-10-06 | Structural Engineering - Reinforcement | 500 |  | Design | Rework |  | Complete |  | Completed |  | Panel 9 - Problems with cage sections snagging against each other during reinforcing cage sections installation for Panel 9. The installation had to be abandoned as the cage sections would not fit into the gap excavated.
| 01CV - Civils | Cxxx-NCR-000205 | NCR | PANELS 3, 5, 7, 13, 4, 8 and 12 - Diaphragm Walls Reinforcement |  | Contr |  | TUY - Tunnel Drive Y (Central) |  | 2011-09-10 | 2011-12-21 16:06 | 102 | 2011-10-06 | Structural Engineering - Reinforcement | 500 |  | Design | Rework |  | Complete |  | Completed |  | Panel 3, 5, 7, 13, 4, 8 and 12 - Following installation issues encountered at panel 9 and panel 14 (see NCR 201 and 204), a review of the reinforcing cage dimension highlighted a lack of provision for installation tolerances for Panel 11 cage sections. The cages have been fabricated in accordance with approved construction drawings (Panel 5 - Cxxx-DSJ-S-DWG-CR144_SH011-50015 rev. C02 and Cxxx-DSJ-S-DWG-CR144_SH011-50016 rev. C02; Panel 7 - Cxxx-DSJ-S-DWG-CR144_SH011-50017 rev. C02 and Cxxx-DSJ-S-DWG-CR144_SH011-50018 rev. C02; Panel 13 Cxxx-DSJ-S-DWG-CR144_SH011-50019 rev. C02 and Cxxx-DSJ-S-DWG-CR144_SH011-50020 rev. C02; Panel 3 - Cxxx-DSJ-S-DWG-CR144_SH011-50021 rev. C02 and Cxxx-DSJ-S-DWG-CR144_SH011-50022 rev. C02; Panel 12 - Cxxx-DSJ-S-DWG-CR144_SH011-50023 rev. C02 and Cxxx-DSJ-S-DWG-CR144_SH011-50024 rev. C02; Panel 8 - Cxxx-DSJ-S-DWG-CR144_SH011-50025 rev. C02 and Cxxx-DSJ-S-DWG-CR144_SH011-50026 rev. C02; Panel 4 - Cxxx-DSJ-S-DWG-CR144_SH011-50027 rev. C02 and Cxxx-DSJ-S-DWG-CR144_SH011-50028 rev. C02)
| 01CV - Civils | Cxxx-NCR-000207 | NCR | Panel 18 Cast out of plan tolerance. |  | Contr |  | TUY - Tunnel Drive Y (Central) |  | 2011-10-25 | 2011-12-19 12:59 | 55 | 2011-10-11 | Civil - Structural Engineering | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | The stopend of diaphragm wall panel 18 has been cast out of position as shown in the attached sketch. The reinforcement cage was installed such that the spacing between the two cages is correct within the panel. The cover to the external faces of the panel (between panels) is also within tolerance.
| 01CV - Civils | Cxxx-NCR-000212 | NCR | Limmo Diaphragm Wall: Panel 14 Stop End |  | Contr |  | TUY - Tunnel Drive Y (Central) |  | 2011-10-14 | 2011-11-16 08:31 | 33 | 2011-10-13 | Structural Engineering - Joints | 500 |  | Damaged | Repair |  | Complete |  | Completed |  | Following removal from Panel 14 (see RFI 201), several pullout bars were pulled off the precast concrete stopend by the reinforcement cage as it was removed. This arose due to insufficient clearance allowed for from the stopend to the steel prior to installation.
| 01CV - Civils | Cxxx-NCR-000219 | NCR | Calibration of bentonite testing equipment |  | Contr |  | TUY - Tunnel Drive Y (Central) |  | 2011-11-02 | 2011-11-16 13:42 | 14 | 2011-10-26 | Shafts - Shafts General | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | The supplier of the laboratory equipment used to test the bentonite support fluid for the Stepney Green D-Walls has been unable to provide a calibration certificate or a certificate of conformity.
| 01CV - Civils | Cxxx-NCR-000234 | NCR | Panel 24 28 Compressive Strength Results |  | Contr |  | TUY - Tunnel Drive Y (Central) |  | 2011-11-30 | 2012-01-10 15:25 | 41 | 2011-10-27 | Shafts - Shafts General | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | Please refer to DRY-CRLNCR-Cxxx-00243 for details of the root cause, system failure. 28 day compressive strength tests have been found to be below the design strength. The average for panel number 24 is 53 N/mm2. Files containing the test results are attached.
| 01CV - Civils | Cxxx-NCR-000236 | NCR | Panel 18- 28 day compressive strength |  | Contr |  | TUY - Tunnel Drive Y (Central) |  | 2011-11-11 | 2011-12-21 10:49 | 40 | 2011-10-28 | Shafts - Shafts General | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | Please refer to DRY-CRLNCR-Cxxx-00243 for details of the root cause, system failure. 28 day compressive strength tests have been found to be below the design strength. The average for panel number 18 is 58 N/mm2. Files containing the test results are attached.
| 01CV - Civils | Cxxx-NCR-000237 | NCR | Limmo Diaphragm Walls: Panel 6 - Inclinometer tube blocked |  | Contr |  | TUY - Tunnel Drive Y (Central) |  | 2011-11-04 | 2012-01-13 17:00 | 70 | 2011-11-01 | Shafts - Shafts General | 500 |  | System Defect | Use As-Is |  | Complete |  | Completed |  | Following concreting of Panel 6, it is apparent that the inclinometer tube IE00004 is blocked at a depth of 41.5m below platform level (+107.0 mOD). See attached survey for further details. The void former tubes included in the prefabricated reinforcement cages have failed to align and form a sealed joint, thus material infiltrated the void during concreting and blocked the tube.
| 01CV - Civils | Cxxx-NCR-000243 | NCR | D-Wall Concrete Mix |  | Contr |  | TUY - Tunnel Drive Y (Central) |  | 2011-11-18 | 2011-12-09 12:57 | 21 | 2011-11-07 | Shafts - Shafts General | 500 |  | System Defect | Use As-Is |  | Complete |  | Completed |  | Erroneously the mix design inputted to the batch computer at the __ plant at Canning Town was for a 60N mix with a 50% PFA cement replacement. Therefore concrete with a 50% PFA content was delivered and placed on site in panels 24, 23, 19, 18 and 12 in the period commencing 22/09/2011 to 12/10/2011. This issue was raised on review of the 28 day compressive strength for panels 18 and 24, which were found to be lower than the specified design strength. This has been raised in two NCRs; 234 and 236. Further NCRs will be raised for further panels should subsequent 28 day cube results fail to meet the design strength.
| 01CV - Civils | Cxxx-NCR-000252 | NCR | Panel 12 28 day compressive strength |  | Contr |  | TUY - Tunnel Drive Y (Central) |  | 2011-11-30 | 2012-01-03 14:55 | 34 | 2011-11-16 | Shafts - Shafts General | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | Please refer to DRY-CRLNCR-Cxxx-00243 for details of the root cause, system failure. 28 day compressive strength tests have been found to be below the design strength. The average for panel number 12 is 58.9 N/mm2. Files containing the test results are attached.
| 01CV - Civils | Cxxx-NCR-000253 | NCR | Panel 19 28 day compressive strength |  | Contr |  | TUY - Tunnel Drive Y (Central) |  | 2011-11-30 | 2011-12-21 10:53 | 21 | 2011-11-16 | Shafts - Shafts General | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | Please refer to DRY-CRLNCR-Cxxx-00243 for details of the root cause, system failure. 28 day compressive strength tests have been found to be below the design strength. The average for panel number 19 is 57.9 N/mm2. Files containing the test results are attached.
| 01CV - Civils | Cxxx-NCR-000257 | NCR | Limmo D-Walls: Panels 1, 6 and 10 sonic tubes blockages |  | Contr |  | TUY - Tunnel Drive Y (Central) |  | 2011-11-24 | 2011-12-12 17:08 | 18 | 2011-11-17 | Shafts - Shafts General | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | During the casting of panels 1,6 and 10, it was found when the clearance check was made post concreting, that several of the tubes were blocked at varying levels within each panel. Please refer attached sketches and tabular schedule for panels 1,6 and 10 that detail the location of the blocked tubes and the depth of the blockage.
| 01CV - Civils | Cxxx-NCR-000258 | NCR | Limmo D-Walls: Integrity Testing |  | Contr |  | TUY - Tunnel Drive Y (Central) |  | 2011-12-08 | 2011-12-14 09:44 | 6 | 2011-11-17 | Shafts - Shafts General | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | Panels 1,10,6, and 14 have all been tested after the 21day reccomendation stated in the specification:- 1-Panel 1 tested 09th Nov 2011, due date was 21st Sept 2011 2-Panel10 tested 09th Nov 2011, due date was 30th Sept 2011 3- Panel 6 tested 09th Nov 2011, due date was 07th Oct 2011 4- Panel14 tested 15th Nov 2011, due date was 03rd Nov 2011
| 01CV - Civils | Cxxx-NCR-000270 | NCR | Limmo Piezometer for monitoring ground water |  | Contr |  | TUY - Tunnel Drive Y (Central) |  | 2011-12-09 | 2012-03-05 16:51 | 87 | 2011-11-29 | Shafts - Shafts General | 500 |  | Supervision/Management | Rework |  | Complete |  | Completed |  | Due to materials stored in proposed location it was decided to move the location rather than stand the borehole team and rig, and adversely affect the installation programme. However upon double checking the new location (2.5mE, 1.6N) after it fully completed, it was determined there would be a clash with the proposed SCL constuction parameters. This clash presents an unacceptable risk to the success of the SCL works.
| 01CV - Civils | Cxxx-NCR-000271 | NCR | Document and Drawing Control |  | Contr |  | TUY - Tunnel Drive Y (Central) |  | 2011-12-16 | 2012-06-18 15:21 | 185 | 2011-11-30 | Shafts - Shafts General | 500 |  | System Defect | Use As-Is |  | Complete |  | Completed |  | An unsigned drawing was produced by the sub-contractor at the surveillance visit, althogh this was the correct revision number that was in existence on both the Eb and DSJV systems.
| 01CV - Civils | Cxxx-NCR-000273 | NCR | Panel 22 28 day compressive strength |  | Contr |  | TUY - Tunnel Drive Y (Central) |  | 2011-12-16 | 2012-01-11 11:43 | 26 | 2011-12-02 | Shafts - Shafts General | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | 28 day compressive strength tests have been found to be below the design strength. The average for panel number 22 is 56.8 N/mm2. Files containing the test results are attached.
| 01CV - Civils | Cxxx-NCR-000289 | NCR | Panel 20 Compressive Strength |  | Contr |  | TUY - Tunnel Drive Y (Central) |  | 2012-01-13 | 2012-01-25 16:23 | 12 | 2011-12-22 | Shafts - Shafts General | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | 28 day compressive strength tests have been found to be below the design strength. The average for panel number 20 is 60.7 N/mm2. Summary of the test results are attached.
| 01CV - Civils | Cxxx-NCR-000290 | NCR | Panel 13 Compressive Strength |  | Contr |  | TUY - Tunnel Drive Y (Central) |  | 2012-01-13 | 2012-01-25 16:29 | 12 | 2011-12-22 | Shafts - Shafts General | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | 28 day compressive strength tests have been found to be below the design strength. The average for panel number 13 is 59.8 N/mm2. Summary of the test results are attached.
| 01CV - Civils | Cxxx-NCR-000292 | NCR | Panel 07 Compressive strength |  | Contr |  | TUY - Tunnel Drive Y (Central) |  | 2012-01-26 | 2012-02-21 09:25 | 26 | 2012-01-12 | Shafts - Shafts General | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | 28 day compressive strength tests have been found to be below the design strength. The average for panel number 07 is 59.7 N/mm2. Summary of the test results are attached.
| 01CV - Civils | Cxxx-NCR-000295 | NCR | Panel 10 compressive strength |  | Contr |  | TUY - Tunnel Drive Y (Central) |  | 2012-01-31 | 2012-02-21 09:32 | 21 | 2012-01-17 | Shafts - Shafts General | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | 28 day compressive strength tests have been found to be below the design strength. The average for panel number 10 is 56.3 N/mm2. Summary of the test results are attached.
| 01CV - Civils | Cxxx-NCR-000296 | NCR | Panel 2 compressive strength |  | Contr |  | TUY - Tunnel Drive Y (Central) |  | 2012-01-31 | 2012-02-21 09:35 | 21 | 2012-01-17 | Shafts - Shafts General | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | 28 day compressive strength tests have been found to be below the design strength. The average for panel number 02 is 59.1 N/mm2. Summary of the test results are attached.
| 01CV - Civils | Cxxx-NCR-000297 | NCR | Limmo Peninsular Shaft. Panel 5. D-Wall |  | Contr |  | TUY - Tunnel Drive Y (Central) |  | 2012-01-31 | 2012-03-26 12:59 | 55 | 2012-01-17 | Shafts - Shafts General | 500 |  | Design | Use As-Is |  | Complete |  | Completed |  | a starter bar coming out of the D-Wall was removed at the cut of level to form the capping beam. this was due to a human error. the position of the removed reinforcement bar was located at the far face of panel 5 on the lefthand side cage. (see attached pictures) the level at which the bar was cut has been noted at 104.950m
| 01CV - Civils | Cxxx-NCR-000298 | NCR | Limmo Peninsula Diaphragm Walling |  | Contr |  | TUY - Tunnel Drive Y (Central) |  | 2012-05-31 | 2012-06-15 16:00 | 15 | 2012-01-19 | Shafts - Shafts General | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | Due to a breakdown at __'s GGBS supplier on the 18th November 2011 it was confirmed that the concrete could not be sourced locally. there was a delay in the supply of discharge between loads. the waiting time was two hours and two minutes. this does not comply with the tecnical specifications outlined in BS EN 1538:2010 Cl8.8.3.13
| 01CV - Civils | Cxxx-NCR-000300 | NCR | Limmo Peninsula - Instrumentation and Monitoring |  | Contr |  | TUY - Tunnel Drive Y (Central) |  | 2012-02-02 | 2012-02-15 12:50 | 13 | 2012-01-19 | Shafts - Shafts General | 500 |  | Supervision/Management | Rework |  | Complete |  | Completed |  | LIP 1 has been located on the footprint of the Auxiliary Shaft. the original setting out co-ordinates are 89838.163 E 35489.106 N the reason for this is because the Auxiliary Shaft has increased in diameter and there was an issue wih the original setting out co-ordinates.
| 01CV - Civils | Cxxx-NCR-000302 | NCR | Inclinometer tube blocked in D-Wall panel 9 |  | Contr |  | TUY - Tunnel Drive Y (Central) |  | 2012-01-25 | 2012-03-13 16:16 | 48 | 2012-01-23 | Shafts - Shafts General | 500 |  | Damaged | Rework |  | Complete |  | Completed |  | Following the concreting of panel 09 the tube was checked and was found to be blocked at approximately 30m deep.
| 01CV - Civils | Cxxx-NCR-000311 | NCR | Panel 21 Compressive Strength |  | Contr |  | TUY - Tunnel Drive Y (Central) |  | 2012-02-06 | 2012-02-21 09:38 | 15 | 2012-01-27 | Shafts - Shafts General | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | 28 day compressive strength tests have been found to be below the design strength. The average for panel number 21 is 60.8 N/mm2. Test result certificates are attached.
| 01CV - Civils | Cxxx-NCR-000319 | NCR | Limmo Main Shaft Capping beam non - compliance |  | Contr |  | TUY - Tunnel Drive Y (Central) |  | 2012-02-20 | 2012-03-26 13:22 | 35 | 2012-02-06 | Shafts - Shafts General | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | During the placing of concrete on the first quadrant of the capping beam additional water was added to the concrete mix for the final three loads delivered to site. This was due to the mix (S3 Slump) being too dry to pump. The concrete was ok to pump once the slump fell in the range of 170-180mm. Below this, the mix was found to be non-flowing and difficult to place during the concrete pour. Water was added to the mix by the wagon driver under the supervision of the DSJV Materials Engineer to mitigate cold joint formation and also ensure that the concrete slump was in the range of 170-180mm. the quantities of water added were recorded by the Materials Engineer
| 01CV - Civils | Cxxx-NCR-000333 | NCR | Main Shaft Capping Beam Concrete Pour - Cold weather working |  | Contr |  | TUY - Tunnel Drive Y (Central) |  | 2012-03-02 | 2012-03-27 17:00 | 25 | 2012-02-13 | Shafts - Shafts General | 500 |  | Planning | Use As-Is |  | Complete |  | Completed |  | No calibrated thermometer was available during the pour to demonstrate that the method statement minimum ambient air temperature was maintained. A non-calibrated thermometer gave the air temperature to be between 1.7 and 2.2 ºC. No method of measuring the temperature of the placed concrete during the pour was available. Concrete was placed into proprietary ply wood & steel backed formwork, which was not entirely free from ice on the outside. Insulating blankets were placed at the end of the pour, however, no space heaters were available. Arrangements were not in place to: provide space heaters; monitor the temperature of the placed concrete; and measure the ambient air temperature with a calibrated thermometer.
| 01CV - Civils | Cxxx-NCR-000334 | NCR | In Situ Concrete |  | Contr |  | TUY - Tunnel Drive Y (Central) |  | 2015-05-14 | 2012-08-10 13:25 | -1007 | 2012-02-13 | Shafts - Shafts General | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | The Angle Chamfer is missing. A 50mm x 50mm angle fillet should have been cast in the concrete pour.
| 01CV - Civils | Cxxx-NCR-000335 | NCR | Workmanship of In Situ Concrete |  | Contr |  | TUY - Tunnel Drive Y (Central) |  | 2015-05-14 | 2012-08-10 13:29 | -1007 | 2012-02-13 | Shafts - Shafts General | 500 |  | Planning | Repair |  | Complete |  | Completed |  | The Angle Chamfer is missing. A 50mm x 50mm angle fillet should have been cast in the concrete pour.
| 01CV - Civils | Cxxx-NCR-000336 | NCR | Workmanship In Situ Concrete |  | Contr |  | TUY - Tunnel Drive Y (Central) |  | 2015-05-14 | 2012-08-10 13:32 | -1007 | 2012-02-13 | Shafts - Shafts General | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | The Angle Chamfer is missing. A 50mm x 50mm angle fillet should have been cast in the concrete pour.
| 01CV - Civils | Cxxx-NCR-000337 | NCR | Concrete Finish at Limmo Capping Beam |  | Contr |  | TUY - Tunnel Drive Y (Central) |  | 2015-05-14 | 2012-08-13 09:56 | -1004 | 2012-02-14 | Shafts - Shafts General | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | at gridline 5, North of the shaft. the precast beam boxout has 800mm long honeycombe
| 01CV - Civils | Cxxx-NCR-000338 | NCR | Concrete Finish at Limmo Capping beam |  | Contr |  | TUY - Tunnel Drive Y (Central) |  | 2015-05-14 | 2012-08-13 10:03 | -1004 | 2012-02-14 | Shafts - Shafts General | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | Precast Beam Boxout at Gridline 6 North of the Shaft shows 600mm honeycomb. and also 250mm honeycombon the west side of the boxout
| 01CV - Civils | Cxxx-NCR-000339 | NCR | Concrete Finish at Limmo Capping beam |  | Contr |  | TUY - Tunnel Drive Y (Central) |  | 2015-05-14 | 2012-08-13 10:16 | -1004 | 2012-02-14 | Shafts - Shafts General | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | Precast Beam Boxout Gridline 4, East Side of the Boxout, North Side of the Shaft 200mm Honeycomb. Precast Beam Boxout Gridline 4, West Side of the Boxout, North Side of the Shaft 200mm Honeycomb
| 01CV - Civils | Cxxx-NCR-000341 | NCR | Limmo Site: Reinforcement steel traceability |  | Contr |  | TUY - Tunnel Drive Y (Central) |  | 2012-03-30 | 2012-03-26 16:12 | -4 | 2012-02-15 | Structural Engineering - Reinforcement | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | Reinforcement steel records were not available on site for inspection
| 01CV - Civils | Cxxx-NCR-000344 | NCR | Inclinometer Tube Blocked in Panel 08 |  | Contr |  | TUY - Tunnel Drive Y (Central) |  | 2012-03-30 | 2012-04-19 11:03 | 20 | 2012-02-15 | Shafts - Shafts General | 500 |  | Damaged | Use As-Is |  | Complete |  | Completed |  | Following the concreting of panel 08 the tube was checked and was found to be blocked at approximately 25m deep. It is suspected that the tube has been crushed.
| 01CV - Civils | Cxxx-NCR-000345 | NCR | Limmo- Temporary Auxiliary Shaft, Ring Beams ITP |  | Contr |  | TUY - Tunnel Drive Y (Central) |  | 2012-03-07 | 2012-03-26 12:38 | 19 | 2012-02-22 | Shafts - Shafts General | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | ITP for Construction of Ring Beams at the Axuliary Shaft, document number Cxxx-DSJ-C-ITP-CR144_WS155-50010, submitted to CRL and in approval process by the time the works started on the ring beams. The actual element of the works that had commenced was the installation of the reinforcement for the top ring beam (Level 1)
| 01CV - Civils | Cxxx-NCR-000346 | NCR | Diaphragm Wall Panel 5- Incorrect Mix Design |  | Contr |  | TUY - Tunnel Drive Y (Central) |  | 2012-03-30 | 2012-04-13 14:44 | 14 | 2012-02-15 | Shafts - Shafts General | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | Concrete with a cement content was delivered to site with a cement content of 465kg. The ticket accurately stated the cement content.
| 01CV - Civils | Cxxx-NCR-000347 | NCR | Diaphragm Wall Panel 6- Incorrect Concrete Ticket |  | Contr |  | TUY - Tunnel Drive Y (Central) |  | 2012-03-30 | 2012-04-13 14:49 | 14 | 2012-02-15 | Shafts - Shafts General | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | Concrete tickets incorrectly stated that the concrete had a cement content of 465kg. Concrete actually had a cement content of 500kg as described in revision 5 of the MCR
| 01CV - Civils | Cxxx-NCR-000350 | NCR | Limmo Main Shaft - Patch West Lift 1 Concrete Repairs. |  | Contr |  | TUY - Tunnel Drive Y (Central) |  | 2012-09-30 | 2012-10-04 16:16 | 4 | 2012-05-28 | Shafts - Shafts General | 500 |  | System Defect | Repair |  | Complete |  | Completed |  | On the Main Shaft, West Patch, Lift 1 section, poured the 18/05/12, two concrete defects have appeared beneath the tunnel eye. (see sketch and pictures attached) The details of the repairs with appropriate check sheets will be collated and presented with evidence as part of the Implementation section of the NCR.
| 01CV - Civils | Cxxx-NCR-000352 | NCR | Concrete sampling methodologies |  | Contr |  | TUY - Tunnel Drive Y (Central) |  | 2012-03-19 | 2012-03-26 12:32 | 7 | 2012-02-20 | Civil - Civil Engineering General | 500 |  | Planning | Use As-Is |  | Complete |  | Completed |  | The test methodology did not fully meet the requirements of the above referenced Works Information clause with respect to recording air temperature and alternative arrangements had not been agreed in writing by the Project Manager.
| 01CV - Civils | Cxxx-NCR-000353 | NCR | not recording NCRs in PTR |  | Contr |  | TUY - Tunnel Drive Y (Central) |  | 2012-04-20 | 2012-04-11 11:58 | -9 | 2012-02-20 | Civil - Civil Engineering General | 500 |  | System Defect | Use As-Is |  | Complete |  | Completed |  | The contractor is not recording all NCRs in accordance with the above requirement
| 01CV - Civils | Cxxx-NCR-000354 | NCR | Structural Concrete - Temporary Works |  | Contr |  | TUY - Tunnel Drive Y (Central) |  | 2012-02-24 | 2012-03-26 10:29 | 31 | 2012-02-20 | Shafts - Shafts General | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | During the pouring of the 1st ring beam of Limmo Auxiliary Shaft on 17th Feb 2012, the 4th load of concrete was tested for slump by __ and found to be out of tolerance. (found value 210mm, permitted range 80mm to 180mm). The load was placed in the works upon the advice of DSJVs materials engineer
| 01CV - Civils | Cxxx-NCR-000359 | NCR | Limmo Main Shaft. D-Walls Concrete Void on Panel 6 |  | Contr |  | TUY - Tunnel Drive Y (Central) |  | 2012-05-31 | 2012-05-30 08:51 | -1 | 2012-02-22 | Shafts - Shafts General | 500 |  | Supervision/Management | Repair |  | Complete |  | Completed |  | On excavation of the diaphragm wall a void has become apparent between panel 6 and 7 at a level of approximately 102m od. The void has been formed because the cobble backfill material (used to fill the overdig area) breached around the stopend during concreting and prevented the concrete from forming a competent panel in this location. The defect is triangular in shape measuring approximately 700mm high and 600mm wide at its widest point. A section of the reinforcement cage is visible but the void does not apparently penetrate to the earth side of the panel. The reparation will be achieved by breaking out the stone/cobble fill to sound concrete and filling up with a high flow self compacting concrete whos largest aggregatedoes not exceed 10mm. A plywood shutter will be used to retain the concrete in place.
| 01CV - Civils | Cxxx-NCR-000360 | NCR | Gantry Foundation CFA Pile 9 |  | Contr |  | TUY - Tunnel Drive Y (Central) |  | 2012-03-05 | 2012-04-24 17:00 | 50 | 2012-02-22 | Shafts - Shafts General | 500 |  | Equipment Breakdown | Rework |  | Complete |  | Completed |  | Due to a mechanical failure at the concrete batching plant the concrete did not have sufficient workability to install the pile reinforcement. In addition to this the piling rig had a hydraulic fault which resulted in the concrete being left in the ground.
| 01CV - Civils | Cxxx-NCR-000361 | NCR | Blocked Inclinometer Tube- Panel 15 |  | Contr |  | TUY - Tunnel Drive Y (Central) |  | 2012-03-08 | 2012-05-04 09:38 | 57 | 2012-02-23 | Shafts - Shafts General | 500 |  | Damaged | Use As-Is |  | Complete |  | Completed |  | Following the concreting of panel 15 the tube was checked and was found to be blocked at approximately 30m deep.
| 01CV - Civils | Cxxx-NCR-000376 | NCR | Sonic Logging Anomalies Panels 2, 18 and 22 |  | Contr |  | TUY - Tunnel Drive Y (Central) |  | 2012-12-15 | 2012-12-05 08:45 | -10 | 2012-02-24 | Shafts - Shafts General | 500 |  | Damaged | Use As-Is |  | Complete |  | Completed |  | In accordance with the Technical Requirements above several anomalies arose. These were all classified as ‘Observations’ except one which was classified as a ‘Flaw’. All anomalies highlighted have been summarised in the attached Table.
| 01CV - Civils | Cxxx-NCR-000385 | NCR | Blocked Inclinometer Tube- Panel 3 |  | Contr |  | TUY - Tunnel Drive Y (Central) |  | 2012-03-30 | 2012-04-24 17:16 | 25 | 2012-02-28 | Shafts - Shafts General | 500 |  | Damaged | Use As-Is |  | Complete |  | Completed |  | Following the concreting of panel 3 the tube was checked and was found to be blocked at approximately 38.3m deep.
| 01CV - Civils | Cxxx-NCR-000387 | NCR | Limmo Main Shaft. D-Walls Concrete Void 2 on Panel 6 |  | Contr |  | TUY - Tunnel Drive Y (Central) |  | 2012-05-31 | 2012-05-30 08:56 | -1 | 2012-03-01 | Shafts - Shafts General | 500 |  | Supervision/Management | Repair |  | Complete |  | Completed |  | On excavation of the diaphragm wall a void has become apparent between panel 6 and 7 at a level of approximately 99m od. The void has been formed because the cobble backfill material (used to fill the overdig area) breached around the stopend during concreting and prevented the concrete from forming a competent panel in this location. The defect is triangualr in shape measuring approximately 1300mm high and 1600mm wide at its widest point. A section of the reinforcement cage is visible but the void does not apparently penetrate to the earth side of the panel.
| 01CV - Civils | Cxxx-NCR-000388 | NCR | Blocked piezometer tubes Panels 5 and 16 |  | Contr |  | TUY - Tunnel Drive Y (Central) |  | 2012-03-30 | 2012-04-25 15:06 | 26 | 2012-03-02 | Shafts - Shafts General | 500 |  | Damaged | Use As-Is |  | Complete |  | Completed |  | Following the concreting of panel 5 and 16 the tubes were checked and was found to be blocked at approximately 13m and 26.5m deep.
| 01CV - Civils | Cxxx-NCR-000397 | NCR | Limmo Main Shaft. D-Walls Concrete Void 3 on Panel 6 |  | Contr |  | TUY - Tunnel Drive Y (Central) |  | 2012-05-31 | 2012-05-30 08:57 | -1 | 2012-03-07 | Shafts - Shafts General | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | On excavation of the diaphragm wall a void has become apparent on the right hand side of panel 6 beside the stopend at a level of approximately 95.000m od to 96.400m od. The void has been formed because the cobble backfill material (used to fill the overdig area) breached around the stopend during concreting and prevented the concrete from forming a competent panel in this location. The defect is triangular in shape measuring approximately 950mm high and 1100mm wide at its widest point.
| 01CV - Civils | Cxxx-NCR-000400 | NCR | Coupler Positions- Basement roof |  | Contr |  | TUY - Tunnel Drive Y (Central) |  | 2012-03-23 | 2012-04-24 17:03 | 32 | 2012-03-12 | Shafts - Shafts General | 500 |  | Planning | Repair |  | Complete |  | Completed |  | Coupler positions exposed to date are included in the attached table. Figures shown in red are out of the specified tolerance.
| 01CV - Civils | Cxxx-NCR-000404 | NCR | Limmo Main Shaft. D-Walls Concrete Void on Panel 14 |  | Contr |  | TUY - Tunnel Drive Y (Central) |  | 2012-05-31 | 2012-05-30 08:59 | -1 | 2012-03-13 | Shafts - Shafts General | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | On excavation of the diaphragm wall a void has become apparent on the right hand side of the panel 14 at a level of approximately 94.200m . The void has been formed because the of a collapse in the dig during construction of Panel 14. The defect is rectangular in shape measuring approximately 1500mm high and 1300mm wide at its widest point.
| 01CV - Civils | Cxxx-NCR-000406 | NCR | Limmo Main Shaft - Panel 14 Protrusion |  | Contr |  | TUY - Tunnel Drive Y (Central) |  | 2012-03-28 | 2012-04-23 15:46 | 26 | 2012-03-14 | Shafts - Shafts General | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | On excavation of the diaphragm wall a protrusion has become apparent on the right hand side of the panel 14 at a level of approximately 94.62 mTD. The protrusion has been formed because of a collapse in the dig during construction of Panel 14. The protrusion is aroun 6800 mm wide, 2500 mm on the thickness area. The bottom level of the protrusion has not been yet cleared as the excavation is ongoing. See sketch attached.
| 01CV - Civils | Cxxx-NCR-000411 | NCR | Limmo Main Shaft. D-Walls Concrete Void on Panel 7 |  | Contr |  | TUY - Tunnel Drive Y (Central) |  | 2012-05-31 | 2012-05-30 09:01 | -1 | 2012-03-14 | Shafts - Shafts General | 500 |  | Supervision/Management | Repair |  | Complete |  | Completed |  | On excavation of the diaphragm wall a void has become apparent on the right hand side of the panel 7 between the levels of 95.000m and 91.500m. The defect is rectangular in shape measuring approximately 3500mm high and 400mm wide at its widest point. the depth of the void was noted at 150-200mm.
| 01CV - Civils | Cxxx-NCR-000420 | NCR | Construction of gantry crane beam without Accepted ITP |  | Contr |  | TUY - Tunnel Drive Y (Central) |  | 2012-07-11 | 2012-07-02 11:15 | -9 | 2012-05-08 | Shafts - Shafts General | 500 |  | Planning | Rework |  | Complete |  | Completed |  | The ITP for the Gantry Crane Foundation had been submitted to CRL and had received comments. DSJV decided to commence construction of the beams at risk.
| 01CV - Civils | Cxxx-NCR-000443 | NCR | STG Detailing errors for Basement Roof |  | Contr |  | TUY - Tunnel Drive Y (Central) |  | 2012-04-20 | 2012-05-04 09:53 | 14 | 2012-03-29 | Structural Engineering - Reinforcement | 500 |  | Design | Rework |  | Complete |  | Completed |  | Stepney Green Basement Roof detailing errors on drawings and schedules for Cxxx design. Refer to the following RFI for specific examples. DRY-CRL RFI-Cxxx-00403 Information Requested: Bar mark 23 of the referenced schedule would appear to have been scheduled incorrectly. Dimension D at 450mm is inconsistent with the required site dimension. Please revise. Impact: New bar required to be bent. DRY-CRL RFI-Cxxx-00426 Requested information: The graded links in the prop along gridline 11 on drawing 02604 have been incorrectly scheduled. Bar mark 09 and 10 are too wide for the prop. Please confirm the correct bar dimensions. It has been discussed on site that the C dimension of Bar Mark 09 is to reduce by 40mm. Impact: New links along full length of prop required to be bent. DRY-CRL RFI-Cxxx-00429 Requested information: Section C-C on drawing 02602 shows three layers capping links (BM 45) along the waler (W5). The bending schedule shows only 11 bars within this waler as does the plan drawing. 11 bars will only be sufficent for the top layer. Please confirm that an additional 22 links will be required for this waler as shown in the section. Impact: Additional bars required to be bent as not scheduled correctly. DRY-CRL RFI-Cxxx-00431 Requested information: The following bar marks from drawing 02602 appear to have an incorrect D dimension; 06, 08, 40, 49. Please review and advise the correct dimension. Impact: New bars required to be bent.
| 01CV - Civils | Cxxx-NCR-000451 | NCR | STG Basement Roof P1 links incorrectly scheduled |  | Contr |  | TUY - Tunnel Drive Y (Central) |  | 2012-04-17 | 2012-05-02 16:54 | 15 | 2012-04-03 | Structural Engineering - Reinforcement | 500 |  | Design | Rework |  | Complete |  | Completed |  | The scheduled outer links, bar marks 32 and 33, for the P1 prop at Basement Roof level are smaller than required.
| 01CV - Civils | Cxxx-NCR-000455 | NCR | Construction of Stepney Farm Buildings without accepted ITP |  | Contr |  | TUY - Tunnel Drive Y (Central) |  | 2012-07-11 | 2012-07-26 09:06 | 15 | 2012-05-08 | Architectural - General | 500 |  | Supervision/Management | Rework |  | Complete |  | Completed |  | The ITP for the Stepney Farm Construction had been submitted to CRL and had received comments. DSJV decided to commence construction works at risk.
| 01CV - Civils | Cxxx-NCR-000457 | NCR | STG - Links not scheduled in Basement Roof prop haunches |  | Contr |  | TUY - Tunnel Drive Y (Central) |  | 2012-04-30 | 2012-05-02 16:57 | 2 | 2012-04-10 | Structural Engineering - Reinforcement | 500 |  | Design | Rework |  | Complete |  | Completed |  | It has been identified that the construction information issued for the following locations in the Basement Roof detail an inadequate number of shear links. P1 East haunch P1 West haunch P2 East haunch P2 West haunch P4 East haunch P5 East haunch
| 01CV - Civils | Cxxx-NCR-000472 | NCR | Limmo Main Shaft Inclinometers |  | Contr |  | TUY - Tunnel Drive Y (Central) |  | 2012-12-21 | 2012-12-14 16:33 | -7 | 2012-09-11 | Surveying - Instrumentation and Monitoring | 500 |  | Equipment Breakdown | Use As-Is |  | Complete |  | Completed |  | Inclinometers suffered equipment breakdown and at 20-Apr-12 were not providing useful readings. Alternative manual (torpedo) readings had been taken only once but the results had not been processed and presented. As such DSJV were not complying with the Cxxx I&M requirements.
| 01CV - Civils | Cxxx-NCR-000477 | NCR | Limmo Main Shaft - Diaphragm Wall Panel 2 Concrete Remedial Works |  | Contr |  | TUY - Tunnel Drive Y (Central) |  | 2012-08-31 | 2012-09-13 10:27 | 13 | 2012-05-18 | Shafts - Shafts General | 500 |  | System Defect | Repair |  | Complete |  | Completed |  | Various concrete defects. Added by MB (21/05/12): This NCR has been raised to capture all D-wall concrete defects requiring repair for Panel No. 2, with the proposed answer providing the appropriate repair method and material. It is confirmed that due to the quantity of repairs required that these will be inspected and repaired with a check sheet signed off for each individual repair. The details of all the repairs with appropriate check sheets are to be collated and presented with evidence as part of the Implementation section of the NCR.
| 01CV - Civils | Cxxx-NCR-000478 | NCR | Limmo Main Shaft - Diaphragm Wall Panel 3 Concrete Remedial Works |  | Contr |  | TUY - Tunnel Drive Y (Central) |  | 2012-08-31 | 2012-09-13 10:32 | 13 | 2012-05-18 | Shafts - Shafts General | 500 |  | Supervision/Management | Repair |  | Complete |  | Completed |  | Various concrete defects. Added comments Marc Bush (21/05/12): This NCR has been raised to capture all D-wall concrete defects requiring repair for Panel No. 3, with the proposed answer providing the appropriate repair method and material. It is confirmed that due to the quantity of repairs required that these will be inspected and repaired with a check sheet signed off for each individual repair. The details of all the repairs with appropriate check sheets are to be collated and presented with evidence as part of the Implementation section of the NCR.
| 01CV - Civils | Cxxx-NCR-000479 | NCR | Limmo Main Shaft - Diaphragm Wall Panel 4 Concrete Remedial Works |  | Contr |  | TUY - Tunnel Drive Y (Central) |  | 2012-08-31 | 2012-09-13 10:39 | 13 | 2012-05-18 | Shafts - Shafts General | 500 |  | Supervision/Management | Repair |  | Complete |  | Completed |  | Various concrete defects. Added comments Marc Bush (21/05/12): This NCR has been raised to capture all D-wall concrete defects requiring repair for Panel No. 4, with the proposed answer providing the appropriate repair method and material. It is confirmed that due to the quantity of repairs required that these will be inspected and repaired with a check sheet signed off for each individual repair. The details of all the repairs with appropriate check sheets are to be collated and presented with evidence as part of the Implementation section of the NCR.
| 01CV - Civils | Cxxx-NCR-000481 | NCR | Limmo Main Shaft - Diaphragm Wall Panel 6 Concrete Remedial Works |  | Contr |  | TUY - Tunnel Drive Y (Central) |  | 2012-08-31 | 2012-09-14 12:30 | 14 | 2012-05-18 | Shafts - Shafts General | 500 |  | Supervision/Management | Repair |  | Complete |  | Completed |  | Various concrete defects. Added comments Marc Bush (21/05/12): This NCR has been raised to capture all D-wall concrete defects requiring repair for Panel No. 6, with the proposed answer providing the appropriate repair method and material. This NCR superceeds NCRCxxx-00359, 00387, 00397 which are now included as part of this NCR and hence allow closed out. It is confirmed that due to the quantity of repairs required that these will be inspected and repaired with a check sheet signed off for each individual repair. The details of all the repairs with appropriate check sheets are to be collated and presented with evidence as part of the Implementation section of the NCR.
| 01CV - Civils | Cxxx-NCR-000482 | NCR | Limmo Main Shaft - Diaphragm Wall Panel 7 Concrete Remedial Works |  | Contr |  | TUY - Tunnel Drive Y (Central) |  | 2012-08-31 | 2012-09-13 11:01 | 13 | 2012-05-17 | Shafts - Shafts General | 500 |  | Supervision/Management | Repair |  | Complete |  | Completed |  | Various concrete defects. Added comments Marc Bush (21/05/12): This NCR has been raised to capture all D-wall concrete defects requiring repair for Panel No. 7, with the proposed answer providing the appropriate repair method and material. This superceeds previous NCR Cxxx-00411 for which the details will be now be covered fully under this NCR allowing 411 to be closed out. It is confirmed that due to the quantity of repairs required that these will be inspected and repaired with a check sheet signed off for each individual repair. The details of all the repairs with appropriate check sheets are to be collated and presented with evidence as part of the Implementation section of the NCR.
| 01CV - Civils | Cxxx-NCR-000483 | NCR | Limmo Main Shaft - Diaphragm WallPanel 9 Concrete Remedial Works |  | Contr |  | TUY - Tunnel Drive Y (Central) |  | 2012-08-31 | 2012-09-13 11:06 | 13 | 2012-05-18 | Shafts - Shafts General | 500 |  | Supervision/Management | Repair |  | Complete |  | Completed |  | Various concrete defects. Added comments Marc Bush (21/05/12): This NCR has been raised to capture all D-wall concrete defects requiring repair for Panel No. 9, with the proposed answer providing the appropriate repair method and material. It is confirmed that due to the quantity of repairs required that these will be inspected and repaired with a check sheet signed off for each individual repair. The details of all the repairs with appropriate check sheets are to be collated and presented with evidence as part of the Implementation section of the NCR.
| 01CV - Civils | Cxxx-NCR-000484 | NCR | Limmo Main Shaft - Diaphragm Wall Panel 10 Concrete Remedial Works |  | Contr |  | TUY - Tunnel Drive Y (Central) |  | 2012-08-31 | 2012-09-13 11:23 | 13 | 2012-05-18 | Shafts - Shafts General | 500 |  | Supervision/Management | Repair |  | Complete |  | Completed |  | Various concrete defects. Added comments Marc Bush (21/05/12): This NCR has been raised to capture all D-wall concrete defects requiring repair for Panel No.10, with the proposed answer providing the appropriate repair method and material. It is confirmed that due to the quantity of repairs required that these will be inspected and repaired with a check sheet signed off for each individual repair. The details of all the repairs with appropriate check sheets are to be collated and presented with evidence as part of the Implementation section of the NCR.
| 01CV - Civils | Cxxx-NCR-000485 | NCR | Limmo Main Shaft - Panel 11 Concrete Remedial Works |  | Contr |  | TUY - Tunnel Drive Y (Central) |  | 2012-08-31 | 2012-09-13 11:29 | 13 | 2012-05-18 | Shafts - Shafts General | 500 |  | Supervision/Management | Repair |  | Complete |  | Completed |  | Various concrete defects. Added comments Marc Bush (21/05/12): This NCR has been raised to capture all D-wall concrete defects requiring repair for Panel No.11, with the proposed answer providing the appropriate repair method and material. It is confirmed that due to the quantity of repairs required that these will be inspected and repaired with a check sheet signed off for each individual repair. The details of all the repairs with appropriate check sheets are to be collated and presented with evidence as part of the Implementation section of the NCR.
| 01CV - Civils | Cxxx-NCR-000486 | NCR | Limmo Main Shaft - Diaphragm Wall Panel 12 Concrete Remedial Works |  | Contr |  | TUY - Tunnel Drive Y (Central) |  | 2012-08-31 | 2012-09-13 11:39 | 13 | 2012-05-18 | Shafts - Shafts General | 500 |  | Supervision/Management | Repair |  | Complete |  | Completed |  | Various concrete defects. Added comments Marc Bush (21/05/12): This NCR has been raised to capture all D-wall concrete defects requiring repair for Panel No.12, with the proposed answer providing the appropriate repair method and material. It is confirmed that due to the quantity of repairs required that these will be inspected and repaired with a check sheet signed off for each individual repair. The details of all the repairs with appropriate check sheets are to be collated and presented with evidence as part of the Implementation section of the NCR.
| 01CV - Civils | Cxxx-NCR-000487 | NCR | Limmo Main Shaft - Diaphragm Wall Panel 13 Concrete Remedial Works |  | Contr |  | TUY - Tunnel Drive Y (Central) |  | 2012-08-31 | 2012-09-13 11:42 | 13 | 2012-05-18 | Shafts - Shafts General | 500 |  | Supervision/Management | Repair |  | Complete |  | Completed |  | Various concrete defects. Added comments Marc Bush (21/05/12): This NCR has been raised to capture all D-wall concrete defects requiring repair for Panel No.13, with the proposed answer providing the appropriate repair method and material. It is confirmed that due to the quantity of repairs required that these will be inspected and repaired with a check sheet signed off for each individual repair. The details of all the repairs with appropriate check sheets are to be collated and presented with evidence as part of the Implementation section of the NCR.
| 01CV - Civils | Cxxx-NCR-000488 | NCR | Limmo Main Shaft - Diaphragm Wall Panel 14 Concrete Remedial Works |  | Contr |  | TUY - Tunnel Drive Y (Central) |  | 2012-08-31 | 2012-09-13 11:49 | 13 | 2012-05-18 | Shafts - Shafts General | 500 |  | Supervision/Management | Repair |  | Complete |  | Completed |  | Various concrete defects. Added comments Marc Bush (21/05/12): This NCR has been raised to capture all D-wall concrete defects requiring repair for Panel No.14, with the proposed answer providing the appropriate repair method and material. This NCR also superceeds NCR No Cxxx-00404 for which the details are to be fully transferred and incorporated into this NCR allowing 404 to be closed out. It is confirmed that due to the quantity of repairs required that these will be inspected and repaired with a check sheet signed off for each individual repair. The details of all the repairs with appropriate check sheets are to be collated and presented with evidence as part of the Implementation section of the NCR.
| 01CV - Civils | Cxxx-NCR-000489 | NCR | Limmo Main Shaft - Diaphragm Wall Panel 5 Concrete Remedial Works |  | Contr |  | TUY - Tunnel Drive Y (Central) |  | 2012-08-31 | 2012-09-13 11:55 | 13 | 2012-05-18 | Shafts - Shafts General | 500 |  | Supervision/Management | Repair |  | Complete |  | Completed |  | Various concrete defects. Added comments Marc Bush (21/05/12): This NCR has been raised to capture all D-wall concrete defects requiring repair for Panel No.5, with the proposed answer providing the appropriate repair method and material. It is confirmed that due to the quantity of repairs required that these will be inspected and repaired with a check sheet signed off for each individual repair. The details of all the repairs with appropriate check sheets are to be collated and presented with evidence as part of the Implementation section of the NCR.
| 01CV - Civils | Cxxx-NCR-000505 | NCR | B1 Level- Diaphragm wall verticality |  | Contr |  | TUY - Tunnel Drive Y (Central) |  | 2012-07-13 | 2012-07-04 15:05 | -9 | 2012-05-10 | Shafts - Shafts General | 500 |  |  | Rework |  | Complete |  | Completed |  | The position of the couplers and steel plates have been checked as a reference point. At some locations the diaphragm walls have been found to exceed the +/-84mm tolerance at the B1 level. The attached drawing show the location of the panels which are out of tolerance.
| 01CV - Civils | Cxxx-NCR-000514 | NCR | Welded L bars within concrete encased steel beams |  | Contr |  | TUY - Tunnel Drive Y (Central) |  | 2012-07-11 | 2012-05-23 17:00 | -49 | 2012-05-08 | Shafts - Shafts General | 500 |  | Workmanship | Rework |  | Complete |  | Completed |  | Due to the alignment of the diaphragm walls it is nescessary to bend these bars on site. In fabricating these bars a former of an incorrect size was used to bend the bars resulting in a radius less than that required by BS8666.
| 01CV - Civils | Cxxx-NCR-000515 | NCR | Incorrect couplers in panel 13 |  | Contr |  | TUY - Tunnel Drive Y (Central) |  | 2012-07-11 | 2012-07-06 13:24 | -5 | 2012-05-08 | Shafts - Shafts General | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | Once the couplers were exposed the thread in the couplers at the B1 level of panel 13 were found to have a different thread. Further investigation found that 'Griptech' couplers had been supplied instead of __.
| 01CV - Civils | Cxxx-NCR-000526 | NCR | Planned arrangements for temporary works |  | Contr |  | TUY - Tunnel Drive Y (Central) |  | 2012-06-14 | 2012-07-31 17:09 | 47 | 2012-05-14 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | Inspection and Test plan not available for gallows’ brackets, and calculations for gallows brackets not included in the Method Statement
| 01CV - Civils | Cxxx-NCR-000527 | NCR | Method Statement acceptance |  | Contr |  | TUY - Tunnel Drive Y (Central) |  | 2012-07-20 | 2012-07-02 11:35 | -18 | 2012-05-14 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | The accepted method statement did not include the gallows brackets
| 01CV - Civils | Cxxx-NCR-000537 | NCR | STG Welding of anchor bars to embedded plates at B1 level |  | Contr |  | TUY - Tunnel Drive Y (Central) |  | 2012-07-20 | 2012-10-23 13:53 | 95 | 2012-05-15 | Structural Engineering - Welding | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | Site welding for the B1 level slab carried out without Welding Procedure Specification (WPS) and Welding Procedure Qualification Record (WPQR) in place in accordance with the Specification.
| 01CV - Civils | Cxxx-NCR-000549 | NCR | Installation of Auxiliary Shaft sheet Piles |  | Contr |  | TUY - Tunnel Drive Y (Central) |  | 2012-06-01 | 2012-06-19 14:50 | 18 | 2012-05-18 | Shafts - Shafts General | 500 |  | Workmanship | Rework |  | Complete |  | Completed |  | During the bulk excavation of the Auxiliary Shaft it was discovered that pile number 64 was out of design position by 216mm, between 2nd and 3rd ring beam level
| 01CV - Civils | Cxxx-NCR-000550 | NCR | Gantry Crane 1 - CFA Piles as-built positions |  | Contr |  | TUY - Tunnel Drive Y (Central) |  | 2012-07-01 | 2012-08-02 15:48 | 32 | 2012-05-18 | Civil - Civil Engineering General | 500 |  | Design | Rework |  | Complete |  | Completed |  | Pile moved 1.5m east due to water main in ground (pile no. AB04) Pile moved 1.5m west due to cables in the ground. (pile no. AB08)
| 01CV - Civils | Cxxx-NCR-000551 | NCR | Gantry Crane 2 - CFA Piles as-built positions |  | Contr |  | TUY - Tunnel Drive Y (Central) |  | 2012-07-01 | 2012-09-12 09:46 | 73 | 2012-05-18 | Civil - Civil Engineering General | 500 |  | Design | Rework |  | Complete |  | Completed |  | please see attached excel sheet showing piles out of tolerance
| 01CV - Civils | Cxxx-NCR-000555 | NCR | D-Wall verticality |  | Contr |  | TUY - Tunnel Drive Y (Central) |  | 2012-07-23 | 2012-08-08 16:54 | 16 | 2012-05-21 | Shafts - Shafts General | 500 |  | Workmanship | Rework |  | Complete |  | Completed |  | Further to NCR 505 the attached drawing shows there are a number of locations which exceed this tolerance specifically panel 6/7 and panel 22.
| 01CV - Civils | Cxxx-NCR-000558 | NCR | Batching of SFR sprayed concrete |  | Contr |  | TUY - Tunnel Drive Y (Central) |  | 2012-07-01 | 2012-08-02 15:14 | 32 | 2012-05-21 | Shafts -Sprayed Concrete | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | A 7.5 cu m load, batched at 06.18 on 21st May 2012, ticket no 315437, was reported as being difficult to pump and spray. Visually, the concrete was more fluid than usual, with a large number of balls of dry concrete. A discussion with 's batcherman and a check on the autographic batch record for this load determined that the Glenium Sky 901 Super plasticizer tank had become empty during batching, and a 2nd tank had to be used. Somehow, it is thought that the load was overdosed with Glenium Sky 901
| 01CV - Civils | Cxxx-NCR-000559 | NCR | Aggregates for sprayed concrete |  | Contr |  | TUY - Tunnel Drive Y (Central) |  | 2012-06-29 | 2012-08-02 09:28 | 34 | 2012-05-21 | Shafts -Sprayed Concrete | 500 |  | Material | Rework |  | Complete |  | Completed |  | Oversize material up to 40mm has been found in the 0/4mm washed limestone grit delivered to 's batching plant at Limmo
| 01CV - Civils | Cxxx-NCR-000560 | NCR | Gantry Piles Cast Out of Plan Tolerance |  | Contr |  | TUY - Tunnel Drive Y (Central) |  | 2012-06-21 | 2012-06-25 15:48 | 4 | 2012-05-21 | Shafts - Shafts General | 500 |  | Workmanship | Rework |  | Complete |  | Completed |  | The following piles have been cast out of plan tolerance; 7,8,9A, 10 and 14 as shown on the attached sketch.
| 01CV - Civils | Cxxx-NCR-000561 | NCR | Defective Strain Gauges in Basement Roof Level |  | Contr |  | TUY - Tunnel Drive Y (Central) |  | 2012-07-21 | 2012-08-09 15:45 | 19 | 2012-05-21 | Surveying - Instrumentation and Monitoring | 500 |  | Damaged | Use As-Is |  | Complete |  | Completed |  | Prop P8- Strain gauges 1 and 2 are not taking automatic readings.
| 01CV - Civils | Cxxx-NCR-000569 | NCR | STG - Welding of cross bars at Basement Roof level |  | Contr |  | TUY - Tunnel Drive Y (Central) |  | 2012-11-30 | 2012-11-20 09:22 | -10 | 2012-05-24 | Structural Engineering - Welding | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | Basement Roof Slab - Welds carried out without weld procedure testing to qualify the weld procedure. Welds carried out without weld production tests for each welder.
| 01CV - Civils | Cxxx-NCR-000571 | NCR | Limmo Main Shaft: Panel 11-12 out of vertical tollerance |  | Contr |  | TUY - Tunnel Drive Y (Central) |  | 2012-08-29 | 2012-10-08 16:42 | 40 | 2012-05-25 | Shafts - Shafts General | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | Surface level is 107m ATD. Panel 11 to 12 interface at "68.5m ATD" measured as 620mm. The maximum specified out of position allowed between two panels is 552mm (25mm+251mm per panel) at this level. Therefore out of tollerance.
| 01CV - Civils | Cxxx-NCR-000575 | NCR | Batcher maintenance records |  | Contr |  | TUY - Tunnel Drive Y (Central) |  | 2012-07-20 | 2012-08-17 13:55 | 28 | 2012-05-28 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | Planned maintenance records for April do not record that the planned maintenance was undertaken and records for May were incoplete yet signed as verified and dated 17th May 2012
| 01CV - Civils | Cxxx-NCR-000576 | NCR | ITP intervention records |  | Contr |  | TUY - Tunnel Drive Y (Central) |  | 2012-08-17 | 2012-08-17 16:19 | 0 | 2012-05-28 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | Records were not available to demonstrate implementation of ITP interventions for concrete flow table and temperature testing.
| 01CV - Civils | Cxxx-NCR-000580 | NCR | BM14 omitted from P3 |  | Contr |  | TUY - Tunnel Drive Y (Central) |  | 2012-07-26 | 2012-08-06 17:23 | 11 | 2012-05-28 | Shafts - Shafts General | 500 |  | Supervision/Management | Repair |  | Complete |  | Completed |  | 3No Bar mark 14 have been omitted from the prop. 1No from the B4 level and 2No from the T4 level.
| 01CV - Civils | Cxxx-NCR-000581 | NCR | B1 Level Central Section- Concrete out of slump tolerance |  | Contr |  | TUY - Tunnel Drive Y (Central) |  | 2012-08-31 | 2012-09-04 11:38 | 4 | 2012-06-12 | Shafts - Shafts General | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | Four loads at the start of the central section concrete pour were found to be out of slump tolerance (please refer to attached sheets). Due to the high temperatures expected it was decided to incorporate the concrete into the works to avoid a joint forming once the lorries had gone out of circulation.
| 01CV - Civils | Cxxx-NCR-000582 | NCR | Limmo Main Shaft - Patch East Lift 1 Concrete Repair. |  | Contr |  | TUY - Tunnel Drive Y (Central) |  | 2012-08-19 | 2012-08-16 15:41 | -3 | 2012-05-29 | Shafts - Shafts General | 500 |  | System Defect | Repair |  | Complete |  | Completed |  | On the Main Shaft, East Patch, Lift 1 section, poured the 24/05/12, a concrete defect has appeared beneath the tunnel eye, (see sketch and pictures attached). The details of the repairs with appropiate check sheets will be collated and presented with evidence as part of the Implementation section of the NCR.
| 01CV - Civils | Cxxx-NCR-000585 | NCR | Rebound not removed |  | Contr |  | TUY - Tunnel Drive Y (Central) |  | 2012-07-20 | 2012-09-12 10:08 | 54 | 2012-05-30 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Rework |  | Complete |  | Completed |  | – Following completion of spraying to form the primary lining for advance 22, quadrant3, the nightshift team failed to remove the accumulated rebound. The activity was completed by the Saturday day shift team, by which time additional effort was required to remove the set concrete.
| 01CV - Civils | Cxxx-NCR-000589 | NCR | Kwikastrips Not Installed in Q1 at Advance 24 |  | Contr |  | TUY - Tunnel Drive Y (Central) |  | 2012-07-20 | 2012-09-12 12:32 | 54 | 2012-05-30 | Shafts -Sprayed Concrete | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | Following completion of spraying the primary lining for advance 24, quadrant 1, the nightshift team failed to install 2no. Kwikastrips.
| 01CV - Civils | Cxxx-NCR-000590 | NCR | Sprayed Concrete Materials - Aggregates |  | Contr |  | TUY - Tunnel Drive Y (Central) |  | 2012-07-20 | 2012-08-02 09:18 | 13 | 2012-05-31 | Shafts -Sprayed Concrete | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | During a site inspection of the batcher and overhead storage bins it was noted that there is cross contamination of the 0/4mm marine sand and 0/4mm washed limestone grit. This is because the bins are being overfilled
| 01CV - Civils | Cxxx-NCR-000592 | NCR | STG - Welding of cross bars B1 level central sector |  | Contr |  | TUY - Tunnel Drive Y (Central) |  | 2012-07-20 | 2012-09-12 10:05 | 54 | 2012-06-01 | Structural Engineering - Welding | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | B1 central sector - Welds carried out without full weld procedure testing (tensile tests for 40mm bar, tensile tests for 25mm bar and shear tests for welded connection) to qualify the weld procedure. Welds carried out without full weld production tests for each welder.
| 01CV - Civils | Cxxx-NCR-000593 | NCR | STG - Welding of cross bars B1 level south sector |  | Contr |  | TUY - Tunnel Drive Y (Central) |  | 2012-07-20 | 2012-08-08 17:05 | 19 | 2012-06-01 | Structural Engineering - Welding | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | B1 south sector - Welds carried out without full weld procedure testing (tensile tests for 40mm bar, tensile tests for 25mm bar and shear tests for welded connection) to qualify the weld procedure. Welds carried out without the full weld production tests for each welder.
| 01CV - Civils | Cxxx-NCR-000599 | NCR | Reduced Splice Length on Intrados Rebar Due to Over-spraying SCL |  | Contr |  | TUY - Tunnel Drive Y (Central) |  | 2012-07-20 | 2012-09-12 12:50 | 54 | 2012-06-11 | Shafts -Sprayed Concrete | 500 |  | Workmanship | Rework |  | Complete |  | Completed |  | In certain areas, the splice length of the vertical intrados reinforcement between phase 1 and phase 2, has been reduced due to over-spraying of the SCL. Please see attached photos showing areas where over-spraying has occurred.
| 01CV - Civils | Cxxx-NCR-000602 | NCR | STG - B2 Level Welding Nth Section |  | Contr |  | TUY - Tunnel Drive Y (Central) |  | 2012-07-20 | 2012-09-17 10:52 | 59 | 2012-06-07 | Structural Engineering - Welding | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | B2 North Section - Bar on plate welds carried out without approved weld procedure
| 01CV - Civils | Cxxx-NCR-000616 | NCR | B1 Level south Section- Concrete out of slump tolerance |  | Contr |  | TUY - Tunnel Drive Y (Central) |  | 2012-08-31 | 2012-09-20 16:59 | 20 | 2012-06-15 | Shafts - Shafts General | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | Four loads at the start of the south section concrete pour (B1 level) were found to be out of slump tolerance (please refer to attached sheets). Due to the high temperatures expected it was decided to incorporate the concrete into the works to avoid a joint forming once the lorries had gone out of circulation.
| 01CV - Civils | Cxxx-NCR-000622 | NCR | Concrete Blinding - GL2-6.5 - STG Internal Shaft |  | Contr |  | TUY - Tunnel Drive Y (Central) |  | 2012-07-20 | 2012-08-07 16:57 | 18 | 2012-06-18 | Shafts - Shafts General | 500 |  | Design | Rework |  | Complete |  | Completed |  | Due to a level error, concrete blinding on level B2, from grid line 2-6.5 is out of the tolerance specified in ITP Cxxx-DSJ-C4-ITP-CR094_SH005-50001 - Rev 5 - inspection number 19. The blinding levels range 2mm - 15mm out of specification.
| 01CV - Civils | Cxxx-NCR-000624 | NCR | TP4A- Damaged raker connection |  | Contr |  | TUY - Tunnel Drive Y (Central) |  | 2012-11-15 | 2012-11-05 08:42 | -10 | 2012-10-02 | Shafts - Shafts General | 500 |  | Supervision/Management | Repair |  | Complete |  | Completed |  | The shear connectors on the raker connections were damaged during installation due to an unauthorised change.
| 01CV - Civils | Cxxx-NCR-000626 | NCR | Panel 13-installation of grip tech couplers |  | Contr |  | TUY - Tunnel Drive Y (Central) |  | 2012-06-29 | 2012-08-02 08:54 | 34 | 2012-06-19 | Shafts - Shafts General | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | Once the couplers were exposed the thread in the couplers at the B1 level of panel 13 and now at B2 level were found to have a different thread. Further investigation found that 'Griptech' couplers had been supplied instead of __. It appears this will be the same for levels B3,B4 and B5 of panel 13 The
| 01CV - Civils | Cxxx-NCR-000636 | NCR | LIMMO GANTRY CRANES 1- BEAMS 1&2, CRANE 2- BEAM 2- HD BOLT Assemblies |  | Contr |  | TUY - Tunnel Drive Y (Central) |  | 2012-08-20 | 2012-09-12 13:22 | 23 | 2012-07-31 | Structural Engineering - Concrete Member | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | Gantry Crane 2 - Rail 2 - Pour between piles 25 and 31 - The plates were all levelled into place, however during the pour the HD assemblies moved within the formwork. Five of the plates were installed on an angle with a difference of greater than 5mm from one side to the other. Gantry Crane 1 - Rail 1 and 2 - Insufficient concrete cover under and around 5 of the plates on segment storage 1, resulting in voids being created.
| 01CV - Civils | Cxxx-NCR-000639 | NCR | B2 level; diaphragm wall couplers out of tolerance |  | Contr |  | TUY - Tunnel Drive Y (Central) |  | 2012-07-20 | 2012-08-03 09:16 | 14 | 2012-06-22 | Shafts - Shafts General | 500 |  | Workmanship | Rework |  | Complete |  | Completed |  | see attached table relating to out of tolerance couplers, hightlighted items within table are out of toleranace
| 01CV - Civils | Cxxx-NCR-000640 | NCR | D-Wall verticality |  | Contr |  | TUY - Tunnel Drive Y (Central) |  | 2012-08-31 | 2012-08-14 12:53 | -17 | 2012-06-21 | Shafts - Shafts General | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | The attached drawing shows there are a number of locations which exceed the tolerance specifically panel 8/9 and panel 10/11. Req
| 01CV - Civils | Cxxx-NCR-000655 | NCR | B1 Coupler Level Tolerance - STG Internal Shaft |  | Contr |  | TUY - Tunnel Drive Y (Central) |  | 2012-08-03 | 2012-08-02 08:45 | -1 | 2012-06-27 | Shafts - Shafts General | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | Coupler positions exposed to date are included in the attached table. Figures shown in red are out of the specified tolerance.
| 01CV - Civils | Cxxx-NCR-000657 | NCR | B2 P4 South Recess - STG |  | Contr |  | TUY - Tunnel Drive Y (Central) |  | 2012-08-03 | 2012-08-06 09:11 | 3 | 2012-06-27 | Shafts - Shafts General | 500 |  | Supervision/Management | Rework |  | Complete |  | Completed |  | Recess in P4 south installed is 75mm wide x 350mm deep meaning recess is 100mm longer in depth and 100mm below structural slab soffit.
| 01CV - Civils | Cxxx-NCR-000674 | NCR | Concrete drying shrinkage |  | Contr |  | TUY - Tunnel Drive Y (Central) |  | 2012-09-17 | 2012-10-29 13:19 | 42 | 2012-07-03 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | Drying shrinkage tests were carried out on specimens prepared from 's Steel Fibre Reinforced mix on 11th April. The results from these specimens gave a marginally non-compliant mean value of 0.0375%.
| 01CV - Civils | Cxxx-NCR-000675 | NCR | Concrete drying shrinkage |  | Contr |  | TUY - Tunnel Drive Y (Central) |  | 2012-09-17 | 2012-08-10 11:01 | -38 | 2012-07-03 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | Drying shrinkage tests were carried out on specimens prepared from 's plain (no steel fibres) mix on 23rd February. The results from thes specimens do not comply with the above specification. Mean value as found was 0.066%
| 01CV - Civils | Cxxx-NCR-000677 | NCR | B2 level; Bmk 352 issue due to diffirence in blinding |  | Contr |  | TUY - Tunnel Drive Y (Central) |  | 2012-07-13 | 2012-08-01 09:07 | 19 | 2012-07-03 | Shafts - Shafts General | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | With reference to DRY-CRL-RFI-Cxxx-00649,due to the blinding in W5 being 22mm high and the blinding in W3 being 10mm low, the top of the reinforcement cage has been adjusted to keep the top of steel heights in tolerance. This has not been a problem as the links in both W3 and W5 are capping links and can be adjust to suit. However Bmk 352 within the splay of P3 is not a capping link and cannot be adjusted
| 01CV - Civils | Cxxx-NCR-000679 | NCR | NCR for Limmo Monitoring |  | Contr |  | TUY - Tunnel Drive Y (Central) |  | 2012-09-28 | 2012-09-12 12:20 | -16 | 2012-07-05 | Surveying - Instrumentation and Monitoring | 500 |  | System Defect | Rework |  | Complete |  | Completed |  | Surveying was not linked back to deep datum on Limmo site only. It was assumed linking back to the reference points would be suitable. However, an analysis has proved this is not the case.
| 01CV - Civils | Cxxx-NCR-000680 | NCR | Lower Lea Crossing I&M |  | Contr |  | TUY - Tunnel Drive Y (Central) |  | 2012-08-31 | 2012-09-12 13:53 | 12 | 2012-07-05 | Surveying - Instrumentation and Monitoring | 500 |  | Design | Use As-Is |  | Complete |  | Completed |  | Manual monitoring of 3D prisms continues carried out in accordance with Cxxx drawings. Root cause is that DSJV did not identify that Cxxx’s I&M Plan had more onerous requirements than Cxxx drawings, and that Cxxx’s overall schedules of Cxxx instrumentation are incorrect. NB/ these deliverables were issued in parallel.
| 01CV - Civils | Cxxx-NCR-000696 | NCR | B1-P4 recess depth - STG |  | Contr |  | TUY - Tunnel Drive Y (Central) |  | 2012-08-30 | 2012-08-22 12:37 | -8 | 2012-07-11 | Shafts - Shafts General | 500 |  | Design | Use As-Is |  | Complete |  | Completed |  | Recess in P4 south installed is 75mm wide x 350mm deep meaning recess is 100mm longer in depth and 100mm below structural slab soffit.
| 01CV - Civils | Cxxx-NCR-000712 | NCR | B3 level-diaphragm wall panel 10 out of tolerance |  | Contr |  | TUY - Tunnel Drive Y (Central) |  | 2012-07-24 | 2012-08-09 13:02 | 16 | 2012-07-17 | Shafts - Shafts General | 500 |  | Workmanship | Rework |  | Complete |  | Completed |  | The attached drawing shows there are a number of locations which exceed the tolerance within panel 10
| 01CV - Civils | Cxxx-NCR-000718 | NCR | testing of fresh concrete |  | Contr |  | TUY - Tunnel Drive Y (Central) |  | 2012-08-31 | 2012-09-13 10:01 | 13 | 2012-07-18 | Shafts - Shafts General | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | At the scheduled start time of the pour at Stepney Green shaft on 17th July 2012, due to abnormally high traffic conditions the lab technician had not arrived. However, the first load was allowed to disharge without a test being carried out
| 01CV - Civils | Cxxx-NCR-000724 | NCR | B3 level-Waling 9 cover issue |  | Contr |  | TUY - Tunnel Drive Y (Central) |  | 2012-08-31 | 2012-08-23 17:38 | -8 | 2012-07-19 | Shafts - Shafts General | 500 |  | Workmanship | Rework |  | Complete |  | Completed |  | The attached drawing shows there are a number of locations which exceed the tolerance within panel 08
| 01CV - Civils | Cxxx-NCR-000735 | NCR | Basement roof unistrut channel - STG |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2015-12-05 | 2015-06-15 11:30 | -173 | 2012-09-12 | Shafts - Shafts General | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Personnel Error - Not Defined | Completed |  | __ channel not installed in props as per drawing Cxxx-JUL-S-DDA-CR094-00226 and Cxxx-JUL-S-DDA-CR094-00427.
| 01CV - Civils | Cxxx-NCR-000741 | NCR | Stepney Green Strain Gauges |  | Contr |  | TUY - Tunnel Drive Y (Central) |  | 2012-08-31 | 2012-10-05 14:02 | 35 | 2012-07-26 | Surveying - Instrumentation and Monitoring | 500 |  | Damaged | Rework |  | Complete |  | Completed |  | Some of the strain gauges that were installed to the props have been damaged as a result of concreting works and automatic readings cannot be read. Please see attached summary and proposal.
| 01CV - Civils | Cxxx-NCR-000745 | NCR | E/B launch adit Break out from main shaft - connection details. |  | Contr |  | TUY - Tunnel Drive Y (Central) |  | 2012-08-02 | 2012-09-14 15:58 | 43 | 2012-07-30 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Design | Use As-Is |  | Complete |  | Completed |  | B10 bars installed from crown to top of bench on the left side of the breakout (advance 2). B10 bars not installed from crown to top of bench on the right side (advance 1).
| 01CV - Civils | Cxxx-NCR-000749 | NCR | Limmo Main Shaft: D-Wall Panel 12: Insufficient cover to rebar |  | Contr |  | TUY - Tunnel Drive Y (Central) |  | 2012-10-23 | 2012-10-08 17:00 | -15 | 2012-07-30 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | Upon excavation of the Eastbound Drive Y Launch adit, the break out of the Panel 12 D-wall exposed rebar from the D-wall cage outside of the far face of the D-wall, therefore not meeting the requirement of the design in the drawing.
| 01CV - Civils | Cxxx-NCR-000750 | NCR | STG - Curing of concrete test specimens |  | Contr |  | TUY - Tunnel Drive Y (Central) |  | 2012-09-28 | 2012-09-17 13:09 | -11 | 2012-07-31 | Structural Engineering - Concrete Member | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | Cube samples were removed from site on completion of the concreting operation for the Stepney Green B3 level props 5 and 6. Suitable facilities for storage are available on site.
| 01CV - Civils | Cxxx-NCR-000751 | NCR | Commencement of King John St works without approved ITP |  | Contr |  | TUY - Tunnel Drive Y (Central) |  | 2012-09-21 | 2012-10-08 12:09 | 17 | 2012-07-31 | Utilities Engineering - Utilities General | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | The ITP for the subcontract works has yet to be approved by CRL. DSJV decided to commence construction works at risk.
| 01CV - Civils | Cxxx-NCR-000757 | NCR | Batching & mixing |  | Contr |  | TUY - Tunnel Drive Y (Central) |  | 2012-08-31 | 2012-10-01 12:45 | 31 | 2012-08-01 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Material | Reject |  | Complete |  | Completed |  | A load of Steel Fibre Reinforced Sprayed Concrete delivered to the works at Limmo on 31st july 2012 was found to contain excessive clumps of fibres / microsilica, and fibres / dry concrete. The load was rejected
| 01CV - Civils | Cxxx-NCR-000759 | NCR | Convergence Monitoring - Survey targets |  | Contr |  | TUY - Tunnel Drive Y (Central) |  | 2012-08-10 | 2012-09-17 14:47 | 38 | 2012-08-02 | Surveying - Tunnels/Portal/Shafts surveys | 500 |  | Damaged | Use As-Is |  | Complete |  | Completed |  | Targets C2 and C3 damaged by the excavator, resulting in readings not being available for these points on both the 29th and 30th July.
| 01CV - Civils | Cxxx-NCR-000772 | NCR | pre treatment measures - spiling |  | Contr |  | TUY - Tunnel Drive Y (Central) |  | 2012-09-21 | 2012-09-20 17:46 | -1 | 2012-08-09 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | Spiling to top heading of advance 25 in the Eastbound launch adit. The orientation of the installed spiles did not fully cover the length of arc prescribed in the RESS, leaving part of the left side of the heading short of spile support. RES meeting 129 advised no action required as a result of spile overlap from the previous round.
| 01CV - Civils | Cxxx-NCR-000773 | NCR | SCL initial strength |  | Contr |  | TUY - Tunnel Drive Y (Central) |  | 2012-09-21 | 2012-09-26 08:16 | 5 | 2012-08-09 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | The SCL to the primary lining of advance 37 did not achieve initial set. This prompted an action to seal all open faces and investigate the cause. Later tests demonstrated that the concrete had set and was expected to achive the desired 28 day strength.
| 01CV - Civils | Cxxx-NCR-000775 | NCR | Main Shaft Capping Beam Repairs |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2016-06-30 | 2016-05-13 14:13 | -48 | 2012-08-09 | Shafts - Shafts General | 500 |  | Workmanship | Reject | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | previous NCRs 334 - 336 were raised to cover a 50mm x 50mm chamfer which was required to be cast into the capping beam where the precast concrete beams will sit. the 50mm chamfers were ommitted. NCRs 337 - 339 were raised regarding honeycombing at gridlines 4,5 and 6 on the northern side of the shaft cvapping beam.
| 01CV - Civils | Cxxx-NCR-000781 | NCR | Instone Wharf - Extruded Fender Beams MCR |  | Contr |  | TUY - Tunnel Drive Y (Central) |  | 2012-09-28 | 2012-09-26 08:37 | -2 | 2012-08-13 | Structural Engineering - Steel Member | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | No MCR ("Materials Compliance Record") was in place for the "Trelleborg extruded fender Type DD-500" (see attached drawing) delivered the 26 of July at Instone Wharf, for the berthing facilities impruvement works.
| 01CV - Civils | Cxxx-NCR-000783 | NCR | Limmo Auxiliary Shaft: Westbound Launch: failed to follow RESS |  | Contr |  | TUY - Tunnel Drive Y (Central) |  | 2012-09-21 | 2012-09-26 08:27 | 5 | 2012-08-14 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | Required wedge for face support was not left in place.
| 01CV - Civils | Cxxx-NCR-000786 | NCR | Work not in accordance with the RESS |  | Contr |  | TUY - Tunnel Drive Y (Central) |  | 2012-10-14 | 2012-10-23 09:59 | 9 | 2012-08-14 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | Advance 33 was not executed in accordance with RESS 133. The excavation sequence for the top heading required each step to be excavated and sprayed prior to excavtion of subsequent steps. Steps 1 and 2 were excavated consecutively and sprayed witth a single 75mm initial layer.
| 01CV - Civils | Cxxx-NCR-000787 | NCR | Instone Wharf - Piling works - Welding - ITP |  | Contr |  | TUY - Tunnel Drive Y (Central) |  | 2012-09-28 | 2012-09-26 08:47 | -2 | 2012-08-15 | Structural Engineering - Welding | 500 |  | Supervision/Management | Rework |  | Complete |  | Completed |  | The ITP for the works does not include any reference to welding and weld testing. (see Cxxx-DSJ-C-ITP-CR144_WS155-50018 rev. 1.0) The welding operation has commenced without the updated ITP being in place.
| 01CV - Civils | Cxxx-NCR-000798 | NCR | Foam concrete head walls |  | Contr |  | TUY - Tunnel Drive Y (Central) |  | 2012-10-23 | 2012-10-01 11:43 | -22 | 2012-08-23 | Tunnelling - Linings - In-situ Concrete | 500 |  | Supervision/Management | Rework |  | Complete |  | Completed |  | Work had proceeded with out an accepted ITP. ITP currently under review by Crossrail
| 01CV - Civils | Cxxx-NCR-000799 | NCR | NCR B4 Level Diaphragm wall verticality |  | Contr |  | TUY - Tunnel Drive Y (Central) |  | 2012-09-28 | 2012-09-05 09:47 | -23 | 2012-08-23 | Shafts - Shafts General | 500 |  | Workmanship | Rework |  | Complete |  | Completed |  | The attached drawing shows there are a number of locations which exceed the Tolerance specifically panel 8.
| 01CV - Civils | Cxxx-NCR-000829 | NCR | Coring for inspection of primary lining quality |  | Contr |  | TUY - Tunnel Drive Y (Central) |  | 2013-04-30 | 2013-03-15 12:01 | -46 | 2012-09-17 | Tunnelling - Linings - Sprayed Concrete | 500 |  | System Defect | Use As-Is |  | Complete |  | Completed |  | On 11th September 2012, sets of 2 cores, at 4 locations in the Auxiliary Shaft Westbound Launch adit, at joints between the bench and invert, were bored and recovered for inspection. 2 cores were not taken at joint locations and were subsequently ignored. 5 of the remaining 6 cores exhibited either rebound or clay inclusions although in all cases, the cores were of the minimum primary lining thickness.
| 01CV - Civils | Cxxx-NCR-000857 | NCR | Main Shaft Prisms |  | Contr |  | TUY - Tunnel Drive Y (Central) |  | 2012-11-30 | 2012-11-28 12:29 | -2 | 2012-09-26 | Surveying - Tunnels/Portal/Shafts surveys | 500 |  | Planning | Use As-Is |  | Complete |  | Completed |  | Since 20/09/12 daily readings have not been possible below level 88.5mATD. To compensate for this lack of data DSJV have reviewed surface monitoring and inclinometers for the shaft. Tunnel and shaft excavation works have ceased and 7 daily readings have been taken since formation level of the shaft was reached.
| 01CV - Civils | Cxxx-NCR-000858 | NCR | NCR B5 level diaphragm wall verticality |  | Contr |  | TUY - Tunnel Drive Y (Central) |  | 2012-12-28 | 2012-10-15 11:51 | -74 | 2012-10-05 | Shafts - Shafts General | 500 |  | Workmanship | Rework |  | Complete |  | Completed |  | The attached drawing shows there are a number of locations which exceed the Tolerance specifically panel 10.
| 01CV - Civils | Cxxx-NCR-000859 | NCR | Instone Wharf - Northern end - Support Beam BD3 |  | Contr |  | TUY - Tunnel Drive Y (Central) |  | 2012-11-30 | 2012-10-24 12:09 | -37 | 2012-10-01 | Structural Engineering - Steel Member | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | Support beam BD3 (highlighted on the attached drawing Cxxx-NIC-X-DWG-CR144-0301 rev C01 - Topside Foundations Wharf Northern end, Plan and Sections), at the northern end of the wharf, has been chopped off 500mm on site due to lack of space against the brick wall and before to made aware of the problem and consult to the TWC (decision taken by the subcontractor during the installation). BD3 full length by design should be 9600mm, now is just 9100mm.
| 01CV - Civils | Cxxx-NCR-000884 | NCR | STG-B5-Pour 1-BM17 |  | Contr |  | TUY - Tunnel Drive Y (Central) |  | 2012-11-30 | 2012-10-22 12:04 | -39 | 2012-10-08 | Shafts - Shafts General | 500 |  | Design | Rework |  | Complete |  | Completed |  | Due to BM18 being placed 50mm out of position North, BM17 does not cap the north leg of BM18 as per drawing attached.
| 01CV - Civils | Cxxx-NCR-000886 | NCR | Chatham segment factory concrete mix |  | Contr |  | TUY - Tunnel Drive Y (Central) |  | 2013-02-28 | 2013-03-12 13:42 | 12 | 2012-10-08 | Civil - Civil Engineering General | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | During the period 17-09-2012 (07.30 ) to 24-10-2012 (15.30) , there was a problem with the quality of the concrete mix being produced by Brett's the supplier for the segment factory . In that period there were 143 segments produced , which have been quarintined within the yard at chatham . The problem is suspected to lie with either the reactivity of the cement or contamination of the cement .
| 01CV - Civils | Cxxx-NCR-000889 | NCR | Primary Lining tolerance |  | Contr |  | TUY - Tunnel Drive Y (Central) |  | 2012-12-20 | 2012-12-14 16:56 | -6 | 2012-10-08 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Rework |  | Complete |  | Completed |  | An as-built survey and method statement for this activity were not in place, although the construction team were aware that this section of the primary lining had been previously oversprayed to the extent that the primary lining tolerance had been exceeded.
| 01CV - Civils | Cxxx-NCR-000894 | NCR | In situ structural concrete |  | Contr |  | TUY - Tunnel Drive Y (Central) |  | 2012-10-31 | 2012-11-26 08:37 | 26 | 2012-10-10 | Shafts - Shafts General | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | Although reasonable precautions were taken in the build up to, and during the casting of Limmo main shaft base slab on 28/09/2012, the temperature at the core peaked at 66C. Temperature logs attached
| 01CV - Civils | Cxxx-NCR-000895 | NCR | In situ structural concrete |  | Contr |  | TUY - Tunnel Drive Y (Central) |  | 2012-11-30 | 2012-11-08 15:11 | -22 | 2012-10-10 | Shafts - Shafts General | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | During the casting of Limmo main shaft permanent base slab on the 28th September 2012, a load of concrete (delivery ticket 7756470) was found to have a slump of 250mm. DSJV's materials engineer allowed the load to be placed subject to an extra set of 4 cubes being taken
| 01CV - Civils | Cxxx-NCR-000899 | NCR | Sheet Pile Tolerances |  | Contr |  | TUY - Tunnel Drive Y (Central) |  | 2012-11-30 | 2012-12-03 09:58 | 3 | 2012-10-11 | Civil - Excavation | 500 |  | Material | Reject |  | Complete |  | Completed |  | Sheet Piles delivered to Piling Subcontractor are not straight. This leads to difficulties in installing piles as the clutch line of the pile is not true, which results in difficulties installing the next pile. This will then lead to delays in the shaft construction
| 01CV - Civils | Cxxx-NCR-000900 | NCR | Limmo Main Shaft Base Slab cast-in plates concrete repairs |  | Contr |  | TUY - Tunnel Drive Y (Central) |  | 2012-11-30 | 2012-11-12 12:53 | -18 | 2012-10-23 | Shafts - Shafts General | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | During the pour of the Main Shaft Base Slab, some areas underneath the base plates for the TBM temporary working platfom (see attached drawing Cxxx-DSJ-C-DDL-CR144_SH011_Z-20530) have not been fully covered with the concrete.
| 01CV - Civils | Cxxx-NCR-000904 | NCR | Commening structural welding on Instone loading facility without ITP |  | Contr |  | TUY - Tunnel Drive Y (Central) |  | 2012-11-30 | 2012-11-08 14:35 | -22 | 2012-10-12 | Civil - Civil Engineering General | 500 |  | Planning | Use As-Is |  | Complete |  | Completed |  | Cxxx-DSJ-C-ITP-CR144_WS155-50021 had not been formally accepted and signed off prior to commencement of welding works on the Instone Wharf loading facility.
| 01CV - Civils | Cxxx-NCR-000906 | NCR | Main Shaft: D-wall below Lower Ring Beam: poor D-wall joints |  | Contr |  | TUY - Tunnel Drive Y (Central) |  | 2013-02-28 | 2013-02-15 16:56 | -13 | 2012-10-12 | Shafts - Shafts General | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | Various concrete defects. This NCR has been raised to capture all D-wall concrete defects requiring repair from level 67.9 to 62.7 in Panels 3, 4, 5, 6, 7, 9, 11, 12 and 13, with the proposed answer providing the appropriate repair method and material. It is confirmed that due to the quantity of repairs required that these will be inspected and repaired with a check sheet signed off for each individual repair. The details of all the repairs with appropriate check sheets are to be collated and presented with evidence as part of the Implementation section of the NCR.
| 01CV - Civils | Cxxx-NCR-000918 | NCR | B5 level-Excessive cover to Pour 2 |  | Contr |  | TUY - Tunnel Drive Y (Central) |  | 2012-12-20 | 2012-11-12 17:13 | -38 | 2012-10-22 | Shafts - Shafts General | 500 |  | Workmanship | Rework |  | Complete |  | Completed |  | Cover to the southern end of pour 2 slab had excessive cover of 75mm-80mm in places
| 01CV - Civils | Cxxx-NCR-000933 | NCR | Testing of precast concrete segmental units during production |  | Contr |  | TUY - Tunnel Drive Y (Central) |  | 2013-12-20 | 2013-09-30 13:09 | -81 | 2012-10-19 | Tunnelling - Linings - Precast | 1000 |  | Material | Reject | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Beams cast on the 7th September, do not comply with the requirement above
| 01CV - Civils | Cxxx-NCR-000941 | NCR | Aggregates at Chatham Segment Factory |  | Contr |  | TUY - Tunnel Drive Y (Central) |  | 2012-12-20 | 2012-11-26 09:25 | -24 | 2012-10-24 | Tunnelling - Linings - Precast | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | On the 19th of October 2012 6 over sized particles were noticed in the 20mm aggregate bay at Brett’s Batching Plant. 1 over sized particle was also found in mould DR6 on the same day. Brett , the ready mixed concrete supplier were informed of the matter and they made a visual check of the 20 mm bay along with technicians from __. They found no more oversized aggregate.
| 01CV - Civils | Cxxx-NCR-000943 | NCR | Instone Wharf Conveyors S7 and S8 foundations - ITP |  | Contr |  | TUY - Tunnel Drive Y (Central) |  | 2012-11-23 | 2012-11-02 10:57 | -21 | 2012-10-24 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | Works for the foundations of conveyors S7 and S8 at Instone Wharf, have been started without the CRL formal approval of the ITP Cxxx-DSJ-C-ITP-CR144_WS155-50022.
| 01CV - Civils | Cxxx-NCR-000948 | NCR | Segment Concrete Finishing |  | Contr |  | TUY - Tunnel Drive Y (Central) |  | 2012-11-23 | 2012-11-26 09:03 | 3 | 2012-10-29 | Tunnelling - Linings - SGI Rings | 500 |  | Material | Repair |  | Complete |  | Completed |  | Holes ranging from 11mm to 18mm and 6mm to 9mm deep have been found on these segments 26/10/12 DL3 , CL3 , BL3 , AL3 , TRL3 , TLL3 , EL3 , KL3 , DL2 , CL2 , BL2 , AL2, TRL2, TLL2 , EL2, KL2, DL1 , CL1, BL1,AL1,TRL1,TLL1,EL1,KL1,DR3,CR3,BR3,AR3,TRR3,TLR3,ER3,KR3, AR5,TRR5,BL5,AL6,AR6,25/10/12 DL2,EL3,BL1,TLL1,24/10/12 DR4,AR5,CR6,TRR1,ER2:
| 01CV - Civils | Cxxx-NCR-000955 | NCR | B5 level-north haunch making good of construction joint |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2016-01-31 | 2015-10-12 13:53 | -111 | 2012-12-17 | Shafts - Shafts General | 1000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | On striking formwork to the north haunch there was a section of Construction joint which had a poor finish with a level difference between the kickers and the main haunch. After striking the construction joint was made good using RENDEROC HB45 concrete repair mortar without an approved concrete repair method statement or ITP in place.
| 01CV - Civils | Cxxx-NCR-000957 | NCR | STG EBC1 sidewall incorrectly set out for coring |  | Contr |  | TUY - Tunnel Drive Y (Central) |  | 2012-12-15 | 2012-12-11 11:26 | -4 | 2012-11-07 | Tunnelling - Alignment | 500 |  | Supervision/Management | Rework |  | Complete |  | Completed |  | The profile marked on the diaphragm wall for the side wall of the eastbound tunnel (east side) was set out using a CAD model generated from Cxxx-MMD-C4-DDD-CR094-SH005_2-004 C01 Breakout Sequence. The alignment of the side drift has since been updated and Co-ordinates supplied under RFI 764 have been received but not incorporated into the CAD model for use on the Total Station. The discrepancy was realised after 12no cores were completed on the sidewall. The Engineer compared the correct drawing to the surveyors model which highlighted the discrepancy. The Side-wall was re-set out in the correct position and the 12no cores were backfilled with 40 N/mm2 cementitious non-shrink mortar.
| 01CV - Civils | Cxxx-NCR-000963 | NCR | Main Shaft Access |  | Contr |  | TUY - Tunnel Drive Y (Central) |  | 2013-01-09 | 2013-01-18 15:13 | 9 | 2012-11-07 | Surveying - Tunnels/Portal/Shafts surveys | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | Readings are being taken weekly but not to full depth of shaft since 19/10/12. Readings are being read from 106.5mATD to 90.5/88.5mATD.
| 01CV - Civils | Cxxx-NCR-000964 | NCR | Main Shaft Prism Obstruction |  | Contr |  | TUY - Tunnel Drive Y (Central) |  | 2013-01-31 | 2013-01-29 15:12 | -2 | 2012-11-07 | Surveying - Tunnels/Portal/Shafts surveys | 500 |  | Planning | Rework |  | Complete |  | Completed |  | One complete vertical section of prisms for entire depth of shaft has been obstructed (05/11/12) by the installation of pipework.
| 01CV - Civils | Cxxx-NCR-000970 | NCR | Limmo Main Shaft TBM Support Steelwork |  | Contr |  | TUY - Tunnel Drive Y (Central) |  | 2013-02-28 | 2013-01-16 14:53 | -43 | 2012-11-08 | Civil - Structural Engineering | 500 |  | System Defect | Use As-Is |  | Complete |  | Completed |  | Copies of 3 no. SWTS Inspection Reports were provided which cover the review of the required (NSSS 5th Edition) welding procedural documentation. These clearly state that the Weld Procedure Approval Record to cover the on and off site fillet welding was not in place prior to the commencement of fabrication. Note: This NCR is raised subsequent to the Temporary Works Assurance Surveillance carried out on 11.10.12
| 01CV - Civils | Cxxx-NCR-000972 | NCR | ITP intervention records |  | Contr |  | TUY - Tunnel Drive Y (Central) |  | 2012-12-31 | 2012-12-05 15:25 | -26 | 2012-11-08 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | ITP number Cxxx-DSJ-C-ITP-CRG03-50005 rev 2 identifies Contactor’s interventions for Activity 3.4.1 to 3.4.3 and 3.5.1 to 3.5.4 as 100% during first 2 weeks, 30% for the rest. Non of the verifying documents for the above activities up to 7/11/12 were signed in the designated box to verify that the interventions had been implemented.
| 01CV - Civils | Cxxx-NCR-000973 | NCR | B5 level; pour 4-75mm cover to top mat reinforcement |  | Contr |  | TUY - Tunnel Drive Y (Central) |  | 2012-12-31 | 2012-11-26 09:08 | -35 | 2012-11-08 | Shafts - Shafts General | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | Due to mis-calculation of reinforcement support chairs, cover to top mat of reinforcement within the slab will now be 75mm
| 01CV - Civils | Cxxx-NCR-000974 | NCR | Breaking Ground without complete Permit to Dig |  | Contr |  | TUY - Tunnel Drive Y (Central) |  | 2013-01-15 | 2012-12-14 17:09 | -32 | 2012-11-08 | Civil - Excavation | 500 |  | Supervision/Management | Rework |  | Complete |  | Completed |  | Contractor's Permit to Dig was signed off and breaking ground had commenced. Statatory Undertakers Drawings were not available upon request on 8/11/12.
| 01CV - Civils | Cxxx-NCR-000975 | NCR | Defective sewer lining works at Baldock Street (Cxxx) |  | Contr |  | TUY - Tunnel Drive Y (Central) |  | 2013-06-27 | 2013-06-12 15:43 | -15 | 2012-11-08 | Utilities Engineering - Utilities General | 500 |  | Workmanship | Rework |  | Complete |  | Completed |  | The post cctv survey of the sewer lining work for Baldock Street identified that the lateral connections to the 300mm sewer does not have the required Top Hats in place.
| 01CV - Civils | Cxxx-NCR-000976 | NCR | Defective sewer lining works at Orchard Place (Cxxx) |  | Contr |  | TUY - Tunnel Drive Y (Central) |  | 2013-01-31 | 2013-02-03 21:42 | 3 | 2012-11-08 | Utilities Engineering - Utilities General | 500 |  | Workmanship | Rework |  | Complete |  | Completed |  | Post CCTV survey of the lining that was installed to the Orchard Place sewer identify some defects; No Top Hat installed to lateral connection Lining just passing through manhole and inlet cut out 80mm Connection not bonded
| 01CV - Civils | Cxxx-NCR-000977 | NCR | Defective sewer lining works at Stepney Green (Cxxx) |  | Contr |  | TUY - Tunnel Drive Y (Central) |  | 2013-04-30 | 2013-04-30 00:02 | 0 | 2012-11-08 | Utilities Engineering - Utilities General | 500 |  | Workmanship | Rework |  | Complete |  | Completed |  | Post CCTV survey for teh Stepney Green sewer lining works identifies that some rework is required due to some defects
| 01CV - Civils | Cxxx-NCR-000978 | NCR | Designer Competency |  | Contr |  | TUY - Tunnel Drive Y (Central) |  | 2013-03-08 | 2013-03-04 17:43 | -4 | 2012-11-09 | Civil - Structural Engineering | 500 |  | System Defect | Use As-Is |  | Complete |  | Completed |  | No evidence available that the competency of the Designer of the TBM Conveyor had been verified by DSJV
| 01CV - Civils | Cxxx-NCR-000979 | NCR | Design Calculations |  | Contr |  | TUY - Tunnel Drive Y (Central) |  | 2013-03-15 | 2013-03-06 09:26 | -9 | 2012-11-09 | Civil - Structural Engineering | 500 |  | System Defect | Rework |  | Complete |  | Completed |  | No evidence available that the Design Calculations for the TBM Conveyor had been reviewed and accepted by a competent person
| 01CV - Civils | Cxxx-NCR-000981 | NCR | Temporary Works Design - Independent CAT 2 or 3 check. |  | Contr |  | TUY - Tunnel Drive Y (Central) |  | 2013-03-31 | 2013-03-04 09:03 | -27 | 2012-11-09 | Civil - Structural Engineering | 500 |  | System Defect | Rework |  | Complete |  | Completed |  | No evidence is available of an Independent CAT 2 or 3 check having been carried out on the TBM Conveyor
| 01CV - Civils | Cxxx-NCR-000986 | NCR | Testing of precast concrete segmental units during production |  | Contr |  | TUY - Tunnel Drive Y (Central) |  | 2013-01-31 | 2013-02-01 12:08 | 1 | 2012-11-13 | Tunnelling - Linings - Precast | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | Beams cast on the 11th & 12th October, do not comply with the requirement above
| 01CV - Civils | Cxxx-NCR-000994 | NCR | Dimensional checks for Moulds and segments. |  | Contr |  | TUY - Tunnel Drive Y (Central) |  | 2012-12-31 | 2013-01-11 10:43 | 11 | 2012-11-14 | Tunnelling - Linings - Precast | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | Moulds are not being dimensionally checked on a daily basis and one segment from each day’s production was being dimensionally checked as opposed to the requirement for one ring ie 8 segments.
| 01CV - Civils | Cxxx-NCR-000995 | NCR | Parex Repaired Segments |  | Contr |  | TUY - Tunnel Drive Y (Central) |  | 2012-12-31 | 2013-01-11 12:34 | 11 | 2012-11-14 | Tunnelling - Linings - Precast | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | Segments repaired using Parex Terrapatch , Polyester putty base component and Polyester mortar base component prior to the 5th of October 2012, have not been signed off by the DSJV verification engineer and accepted by CRL as being acceptable to be incorporated within the permanent works. The Segment/ rings affected are;- Rings 24 , 25,26,27,28,29,30,31,32,33,34,35,36,37,38,39,40,41,42,43,44,45,46,47,48,49,50,51,52,53,54,55,56,58,59,60,61,62,63,64,65,66,67,70,71,73,74,75 and 77 from carousel 1 . Rings 2,3,4 and 5 from carousel 2 were repaired using Terrapatch , Polyester putty base component and Polyester mortar base component .
| 01CV - Civils | Cxxx-NCR-001001 | NCR | Calibration of scales |  | Contr |  | TUY - Tunnel Drive Y (Central) |  | 2012-12-28 | 2012-12-04 11:08 | -24 | 2012-11-15 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | Site marked volume line on a container used to measure the addition of bentonite was traced to weight scales for which calibration certification to national standards was not available.
| 01CV - Civils | Cxxx-NCR-001007 | NCR | Protruding thread length of bolts for the S3 trestle foundations |  | Contr |  | TUY - Tunnel Drive Y (Central) |  | 2013-02-28 | 2013-01-16 14:59 | -43 | 2012-11-19 | Structural Engineering - Bolted Connections | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | On inspection of the S3 conveyor route foundations, it was noticed in several locations that the length of thread protruding from the top of the bolt was insufficient.
| 01CV - Civils | Cxxx-NCR-001024 | NCR | B5 level, south west haunch; bar mark 104 |  | Contr |  | TUY - Tunnel Drive Y (Central) |  | 2013-01-31 | 2012-12-17 13:28 | -45 | 2012-11-23 | Shafts - Shafts General | 500 |  | Workmanship | Rework |  | Complete |  | Completed |  | Bar mark 104 appears to have been installed incorrectly as the section of the bar within the south west haunch (eastern face) does not have the required length to tie in with bars opposing barmark 105
| 01CV - Civils | Cxxx-NCR-001026 | NCR | B5 level southern haunches-making good to dywidag bars in kicker |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2016-01-31 | 2015-10-12 13:58 | -111 | 2012-11-26 | Shafts - Shafts General | 1000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | During construction of the southern haunch in the WB pit bottom, dywidag bars used to tie down the shutters did not have the required couplers and sleeves. The couplers and sleeves allow for normal removal of the bars after casting the concrete, which then can be filled in with a non shrink mortar to a smooth finish. The dywidag bars now need to be removed from the haunches by breaking back the concrete by a minimum of 50mm, cut the bars and fill in the area with repair mortar.
| 01CV - Civils | Cxxx-NCR-001045 | NCR | B5 level - south east haunch. concrete finish/making good |  | Contr |  | TUY - Tunnel Drive Y (Central) |  | 2013-12-21 | 2013-12-11 16:45 | -10 | 2012-11-29 | Shafts - Shafts General | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The top of the south west haunch (south end) finish did not comply with the finish detailed in the ITP, seperealty it was made good without specific concrete repair method in place.
| 01CV - Civils | Cxxx-NCR-001055 | NCR | Ham Pump Shaft Piling |  | Contr |  | TUY - Tunnel Drive Y (Central) |  | 2013-01-31 | 2013-01-12 11:26 | -19 | 2012-11-29 | Civil - Excavation | 500 |  | Damaged | Use As-Is |  | Complete |  | Completed |  | Piles on North wall of HAM Sewer Pump Shaft have de-clutched at two locations. This non-conformance has the potential to compromise the structural integrity of the shaft structure
| 01CV - Civils | Cxxx-NCR-001065 | NCR | STG - SCL - Monitoring points |  | Contr |  | TUY - Tunnel Drive Y (Central) |  | 2013-01-31 | 2013-01-25 13:50 | -6 | 2012-12-04 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Damaged | Repair |  | Complete |  | Completed |  | 2 No. conergence monitoring targets in the shoulders of the Eastbound Launch were damaged shortly after being installed.
| 01CV - Civils | Cxxx-NCR-001071 | NCR | SCL batcher back up and dewatering emergency system |  | Contr |  | TUY - Tunnel Drive Y (Central) |  | 2013-02-28 | 2013-02-22 12:51 | -6 | 2012-12-06 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | Records were not made available for post surveillance QS 305-19 review by the agreed date, as such the Contractor did not demonstrated that the generation of contemporaneous records was taking place.
| 01CV - Civils | Cxxx-NCR-001073 | NCR | Aggregates used to manufacture precast concrete segments |  | Contr |  | TUY - Tunnel Drive Y (Central) |  | 2013-02-28 | 2013-03-12 13:28 | 12 | 2012-12-06 | Tunnelling - Linings - Precast | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | As per attached ’s particle size distribution reports for weekly samples of 4/10mm limestone, 3 of the samples do not comply with the specification due to excess material retained on 10mm test sieve.
| 01CV - Civils | Cxxx-NCR-001078 | NCR | STG - SCL - Over excavation |  | Contr |  | TUY - Tunnel Drive Y (Central) |  | 2013-01-31 | 2012-12-13 09:21 | -49 | 2012-12-10 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | Top Heading 6 over excavated by 300mm to Ch.6.300 to introduce a leading edge.
| 01CV - Civils | Cxxx-NCR-001079 | NCR | Kwikastrips not butted together |  | Contr |  | TUY - Tunnel Drive Y (Central) |  | 2013-04-30 | 2013-03-25 08:50 | -36 | 2013-01-16 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | On the 06/12/12 a joint was constructed with out the kwikastrip butt up against the previous round kwikastrip. This was reported and rectified.
| 01CV - Civils | Cxxx-NCR-001081 | NCR | STG - SCL - concrete temperature |  | Contr |  | TUY - Tunnel Drive Y (Central) |  | 2013-02-15 | 2013-01-16 12:35 | -30 | 2012-12-12 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | Concrete ticket number 200129, 2m3, batched at 09:22 on 11/12/12 attained 11°C when tested prior to spraying. The batch was used to complete the spraying of top heading 20 in the E/B launch adit and to spray on the face. The material was subjected to early strength testing in line with KT20 requirements. The results of the early strength testing are attached and show that the sprayed concrete exceeded the modified J2 curve.
| 01CV - Civils | Cxxx-NCR-001087 | NCR | Curing of concrete test specimens |  | Contr |  | TUY - Tunnel Drive Y (Central) |  | 2013-02-15 | 2013-01-22 11:32 | -24 | 2012-12-14 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | Specimens for compression tests for 800m³ concrete pour, located at B5 central section pours 7 &8 were seen during surveillance of 12/12/2012 to be stored without protection from dehydration and the tops of the concrete cubes were seen to be dry.
| 01CV - Civils | Cxxx-NCR-001089 | NCR | SCL rebound from TH 34 |  | Contr |  | TUY - Tunnel Drive Y (Central) |  | 2013-02-28 | 2013-01-17 16:13 | -42 | 2012-12-20 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Rework |  | Complete |  | Completed |  | Due to an incorrect spraying technique, shot crete rebound had allowed to become trapped above the Kwika strip box whilst spraying the footing of the previous top heading, TH 34.
| 01CV - Civils | Cxxx-NCR-001090 | NCR | Missed profiles - East bound Launch Adit |  | Contr |  | TUY - Tunnel Drive Y (Central) |  | 2013-02-28 | 2013-02-05 10:28 | -23 | 2012-12-20 | Surveying - Tunnels/Portal/Shafts surveys | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | The following profiles were not picked up in the TMS Amberg system, so there is no As Built records: - Top Heading Excavation Ch 8, Bench Excavation Ch 3,9,12 & 14, Invert Excavation Ch 8,9,11 & 13, SCL Invert Ch 4, 8, 10 & 12. There was a lack of communication between each shift and assumptions made about which profiles had been picked up already.
| 01CV - Civils | Cxxx-NCR-001093 | NCR | Slumping of concrete on backs of segments |  | Contr |  | TUY - Tunnel Drive Y (Central) |  | 2013-03-15 | 2013-03-15 13:17 | 0 | 2013-01-09 | Tunnelling - Linings - Precast | 500 |  | Workmanship | Reject |  | Complete |  | Completed |  | 16 segments have had the concrete slump to the ends of the mould resulting in the ends of the segment being between +6mm to +12mm and the middle of the segments being -4 mm to -8mm
| 01CV - Civils | Cxxx-NCR-001098 | NCR | Aggregates used to manufacture precast concrete segments |  | Contr |  | TUY - Tunnel Drive Y (Central) |  | 2013-03-15 | 2013-03-12 14:09 | -3 | 2013-01-11 | Tunnelling - Linings - Precast | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | As per attached 's particle size distribution reports for weekly samples of 10/20mm limestone, 3 of the samples do not comply with the specification due to excess material retained on 20mm test sieve
| 01CV - Civils | Cxxx-NCR-001101 | NCR | Off site procurement of HAM SS liner |  | Contr |  | TUY - Tunnel Drive Y (Central) |  | 2013-04-30 | 2013-06-05 18:37 | 36 | 2013-01-12 | Utilities Engineering - Utilities General | 500 |  | System Defect | Use As-Is |  | Complete |  | Completed |  | The SS liner for the HAM sewer was procured without having the necessary documentation (ITP’s, welding procedures and material approvals) in place and/or approved
| 01CV - Civils | Cxxx-NCR-001106 | NCR | Damage to convergence monitoring target - EB Cavern |  | Contr |  | TUY - Tunnel Drive Y (Central) |  | 2013-03-15 | 2013-02-11 13:17 | -32 | 2013-01-24 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Damaged | Repair |  | Complete |  | Completed |  | Convergence monitoring target was damaged at CH 1.8 in the right hand knee during 14/021/13 night shift.
| 01CV - Civils | Cxxx-NCR-001107 | NCR | Lattice girder EB 03 |  | Contr |  | TUY - Tunnel Drive Y (Central) |  | 2013-05-03 | 2013-05-07 12:09 | 4 | 2013-04-05 | Tunnelling - Linings - Sprayed Concrete | 500 |  | System Defect | Use As-Is |  | Complete |  | Completed |  | Lattice girder EB03 delivered to site incorrectly fabricated. A section of EB06 was used to substitute the section. A replacement for the section of EB06 was fabricated on site.
| 01CV - Civils | Cxxx-NCR-001108 | NCR | Using fibres in P2 layer East Bound Cavern |  | Contr |  | TUY - Tunnel Drive Y (Central) |  | 2013-03-29 | 2013-03-05 11:06 | -24 | 2013-02-22 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | On 12/02/13 The final layer of Primary Lining 2 of the invert Ch 3 - 5 was sprayed with fibre reinforced concrete instead of non-fibre reinforced sprayed concrete. Non-fibre SC had already been sprayed covering the reinforment mesh with the fibre SC bringing the thickness of the P2 up to profile. Please refer to attached shift report for record of location.
| 01CV - Civils | Cxxx-NCR-001122 | NCR | slumping on extrados of 2 segments |  | Contr |  | TUY - Tunnel Drive Y (Central) |  | 2013-03-30 | 2013-04-03 14:22 | 4 | 2013-01-19 | Tunnelling - Linings - Precast | 500 |  | Workmanship | Reject |  | Complete |  | Completed |  | On segments TLL1 ring number 562 and AL1 ring number 562 the thickness of the segment is up to 8mm less then 300mm
| 01CV - Civils | Cxxx-NCR-001123 | NCR | SCL - Low temperature concrete EB Cavern TH9 |  | Contr |  | TUY - Tunnel Drive Y (Central) |  | 2013-02-28 | 2013-01-29 08:19 | -30 | 2013-01-21 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | On 18/01/13 at 14.15 the concrete batched and sprayed into TH9 was delivered at 13°C.
| 01CV - Civils | Cxxx-NCR-001125 | NCR | Drive Y EB auxiliary conveyor belt was cut too soon |  | Contr |  | TUY - Tunnel Drive Y (Central) |  | 2013-02-28 | 2013-01-31 08:03 | -28 | 2013-01-22 | Tunnelling - Excavation - TBM | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | The auxiliary belts were repaired, tensioned and tested before excavating the additional 100mm. They will be disassembled afterwards in accordance with Cxxx-DSJ-C4-GMS-CR144_SH011-50062.
| 01CV - Civils | Cxxx-NCR-001128 | NCR | Robeson Street - defective sewer lining |  | Contr |  | TUY - Tunnel Drive Y (Central) |  | 2013-05-31 | 2013-06-12 15:50 | 12 | 2013-01-23 | Utilities Engineering - Water | 500 |  | Workmanship | Rework |  | Complete |  | Completed |  | TQ36829010 to TQ36819904, CH14.7-CH32.0: 1) Installation of the liner appears rutted and scarred along a (approx) 17m length. DSJV have been advised that TWUL will not accept handover of this asset without the condition of the lining in this area being addressed. 2) In addition, 2no. lateral connections (CH32.9 and CH43.1) have been identified as requiring remedial works prior to top hat installation being possible.
| 01CV - Civils | Cxxx-NCR-001143 | NCR | EB Cavern - Core quality |  | Contr |  | TUY - Tunnel Drive Y (Central) |  | 2013-05-31 | 2013-05-07 13:43 | -24 | 2013-01-29 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | Core results from EB Cavern showed evidence of shadowing and voiding. Please refer to photos attached
| 01CV - Civils | Cxxx-NCR-001144 | NCR | Bench excavation - Ch11 P1 layer under sprayed |  | Contr |  | TUY - Tunnel Drive Y (Central) |  | 2013-03-28 | 2013-02-11 13:21 | -45 | 2013-01-31 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Rework |  | Complete |  | Completed |  | Bench at chainage 11m - 12 m SCL P1 thickness undersrayed, please refer to Attachments titled "incorrect".
| 01CV - Civils | Cxxx-NCR-001145 | NCR | Over excavation Top Heading 15 EB Cavern |  | Contr |  | TUY - Tunnel Drive Y (Central) |  | 2013-04-30 | 2013-03-19 15:52 | -42 | 2013-02-01 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Rework |  | Complete |  | Completed |  | Over excavation of Top Heading 15.
| 01CV - Civils | Cxxx-NCR-001163 | NCR | storage temperature of micro silica slurry |  | Contr |  | TUY - Tunnel Drive Y (Central) |  | 2013-04-30 | 2013-02-27 15:51 | -62 | 2013-02-01 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | measured temperature on 16th Jan 2013 was 3 degrees C
| 01CV - Civils | Cxxx-NCR-001164 | NCR | SCL concrete batching plant hot water thermostat calibration |  | Contr |  | TUY - Tunnel Drive Y (Central) |  | 2013-04-30 | 2013-02-28 16:44 | -61 | 2013-02-01 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | SCL concrete batching plant hot water thermostat calibration records have not been made available to demonstrate compliance with the above technical requirement
| 01CV - Civils | Cxxx-NCR-001185 | NCR | STG -SCL - EB Cav 1 Void former in top heading |  | Contr |  | TUY - Tunnel Drive Y (Central) |  | 2013-08-31 | 2013-07-29 12:23 | -33 | 2013-02-07 | Tunnelling - Linings - Sprayed Concrete | 3000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Eastbound Cavern 1 Side drift Expanded polystyrene void formers were installed in front of the top heading lattice girders to maintain a leading edge while constructing the left-hand side drift. The void formers were to be removed prior to spraying the next advance. During the right-hand enlargement excavations at a number of locations the void formers were found still in situ in front of the lattice girder.
| 01CV - Civils | Cxxx-NCR-001186 | NCR | STG - SCL - WB Launch TH2 initial layer duration |  | Contr |  | TUY - Tunnel Drive Y (Central) |  | 2013-04-30 | 2013-03-19 15:24 | -42 | 2013-02-07 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Equipment Breakdown | Use As-Is |  | Complete |  | Completed |  | WB LA TH2: Initial layer was completed at 20:30 04/02/13 then due to problems with the __ the primary lining 1 was left unsprayed for more than 12 hours. The advance was inspected throughout this period and no stability issues were raised. Contingency measures (dry spray Shotcrete 513) were available to deal with stability issues if required. Primary Lining was sprayed at 17:00 05/02/13. Please refer to attached shift reports.
| 01CV - Civils | Cxxx-NCR-001193 | NCR | River Lea Cofferdam Piling |  | Contr |  | TUY - Tunnel Drive Y (Central) |  | 2013-04-30 | 2013-03-21 08:08 | -40 | 2013-02-11 | Civil - Excavation | 500 |  |  | Use As-Is |  | Complete |  | Completed |  | The corner detail on the river Lea cofferdam has not been constructed in accordance with Temporary Works Design Cxxx-DSJ-N2-CER-CR094_PT002-50004
| 01CV - Civils | Cxxx-NCR-001196 | NCR | Uploading Manual Monitoring Results |  | Contr |  | TUY - Tunnel Drive Y (Central) |  | 2013-04-30 | 2013-03-22 08:05 | -39 | 2013-02-12 | Surveying - Instrumentation and Monitoring | 500 |  | Planning | Use As-Is |  | Complete |  | Completed |  | During the planned surveillance of the Contractor's monitoring database (SAI) it became apparent that monitoring results have not been consistently uploaded within the 12 hour target. For example, on Monday 11 February 2013 the following monitoring points were not uploaded for at least 36 hours: Cxxx-PV04201; Cxxx-PV04202; Cxxx-PV04203; Cxxx-PV04204; Cxxx-PV04205; Cxxx-PV04206; Cxxx-IM04010; Cxxx-IM04010, Cxxx-IM04010; and Cxxx-IM04010.
| 01CV - Civils | Cxxx-NCR-001199 | NCR | Concrete Cube Storage |  | Contr |  | TUY - Tunnel Drive Y (Central) |  | 2013-04-30 | 2013-03-18 10:24 | -43 | 2013-02-13 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | Concrete test cubes confirmed by the contractors laboratory personnel as specimens for compressive strength test, identified as cast on 5th February 2013 were stored outside the casting mould, in air at a temperature of 24.5 ºC and were dry
| 01CV - Civils | Cxxx-NCR-001200 | NCR | Storage of Glenium Sky 901 |  | Contr |  | TUY - Tunnel Drive Y (Central) |  | 2013-06-30 | 2013-05-28 13:52 | -33 | 2013-02-13 | Tunnelling - Tunnelling General | 500 |  |  | Use As-Is |  | Complete |  | Completed |  | On the 8th February the CRL site team sampled the temperatures at the batching plant and found ; ambient was 2 ºC, plasticized Glenium sky 901 at 3 ºC. The Glenium Sky 901 manufactures storage requirements are document as ;” ..must be stored in original containers and at temperatures between 5 ºC and 30 ºC
| 01CV - Civils | Cxxx-NCR-001203 | NCR | Chatham Segment Factory Crane Rails |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2013-09-30 | 2013-09-18 13:22 | -12 | 2013-02-14 | Logistics - Logistics - General | 2000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The concrete beams are experiencing cracking / spalling at the plate locations. Some shrinkage cracking is visable through the beams - not structural
| 01CV - Civils | Cxxx-NCR-001209 | NCR | Cat 2 design check for conveyors |  | Contr |  | TUY - Tunnel Drive Y (Central) |  | 2013-06-28 | 2013-06-03 12:21 | -25 | 2013-02-15 | Tunnelling - Excavation - TBM | 500 |  | Design | Rework |  | Complete |  | Completed |  | The DSJV is aware that some of these will not be in place before the Drive Y Easbound TBM resumes excavation, although Cat 2 will be in for critical elements prior to tunnelling (HAC and Tripper).
| 01CV - Civils | Cxxx-NCR-001216 | NCR | Instone wharf trippers |  | Contr |  | TUY - Tunnel Drive Y (Central) |  | 2013-04-15 | 2013-03-04 08:49 | -42 | 2013-02-19 | Structural Engineering - Bracing | 500 |  | Design | Rework |  | Complete |  | Completed |  | Modifications required to the tranverse members of the mobile tripper structure to further increase the stiffness of the base structure to increase stability / robustness and overall factor of safety of the structure of the tripper.
| 01CV - Civils | Cxxx-NCR-001220 | NCR | Compressive strength - cores |  | Contr |  | TUY - Tunnel Drive Y (Central) |  | 2013-04-30 | 2013-04-09 16:48 | -21 | 2013-02-22 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | The requirement for a 1-day test every 20 cubic metres has not been consistently maintained
| 01CV - Civils | Cxxx-NCR-001221 | NCR | SCL Testing |  | Contr |  | TUY - Tunnel Drive Y (Central) |  | 2013-04-30 | 2013-05-07 13:50 | 7 | 2013-02-22 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | Estimated fibre and aggregate rebound testing not implemented in accordance to the above specification. SCL work commenced mid Novemebr 2012 with no results provided to date.
| 01CV - Civils | Cxxx-NCR-001222 | NCR | Missed profiles Ch 3 and 4 EB Cavern |  | Contr |  | TUY - Tunnel Drive Y (Central) |  | 2013-04-30 | 2013-03-22 14:51 | -39 | 2013-02-22 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | East bound cavern top heading chainage 3 and 4 Primary Lining 1 as built survey was missed. There was not a chance to resurvey these locations before Primary Lining 2 was sprayed. The excavation and primary lining 2 was surveyed showing the thicness of the primary lining is withing tollerance at these locations. Please refer to attached thickness profiles.
| 01CV - Civils | Cxxx-NCR-001223 | NCR | Missed invert monitoring Chainage 2 EB Cavern |  | Contr |  | TUY - Tunnel Drive Y (Central) |  | 2013-04-30 | 2013-03-11 11:42 | -50 | 2013-02-22 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | An invert monitoring point was installed at Ch 2, then survey readings were not taken. The monitoring point was then damaged and another monitoring point intalled. Base line readings were taken over 5 days. Reading are being taken weekly presented in a monitoring summary. Please see attached monitoring summary for from Ch 2 and Ch 10.
| 01CV - Civils | Cxxx-NCR-001228 | NCR | Defective Rod XR0401027.00 |  | Contr |  | TUY - Tunnel Drive Y (Central) |  | 2013-04-12 | 2013-03-11 10:06 | -32 | 2013-02-25 | Surveying - Instrumentation and Monitoring | 500 |  | Damaged | Use As-Is |  | Complete |  | Completed |  | During the planned surveillance of the Contractor's monitoring database (SAI) it became apparent that rod XR0401027.00 was defective.
| 01CV - Civils | Cxxx-NCR-001244 | NCR | Westbound Ring 88 Lip |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2015-09-30 | 2013-07-02 11:56 | -820 | 2013-03-05 | Tunnelling - Alignment | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Ring 88 on Drive Y westbound had to be dismantled in order to check the Tailskin Brushes. When the ring was put back in place, it had to be pushed against the Tailskin Brushes and these pushed the bottom segment (A) up causing a lip of 22mm between ring 87 and ring 88 On the vertical Axis only. Alignment issues caused that no dowels could be placed on segments D and E.
| 01CV - Civils | Cxxx-NCR-001245 | NCR | HAM Sewer Shaft |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2013-05-31 | 2013-07-02 15:29 | 32 | 2013-03-06 | Civil - Excavation | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete |  | Completed |  | Kingspost wall not constructed in sequence as per Method Statement. Posts 2,4 and 6 could not be installed from ground level. These will now be retro-fitted out of sequence
| 01CV - Civils | Cxxx-NCR-001248 | NCR | Late submittal of Lattice Girder Drawings |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2013-06-30 | 2013-07-11 14:10 | 11 | 2013-03-06 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Change to drawings not provided on time | Completed |  | Works commenced before approval of drawings by Project Manager.
| 01CV - Civils | Cxxx-NCR-001263 | NCR | Production testing of sprayed concrete - flexural strength |  | Contr |  | TUY - Tunnel Drive Y (Central) |  | 2013-05-31 | 2013-04-22 12:26 | -39 | 2013-03-08 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Damaged | Use As-Is |  | Complete |  | Completed |  | Panels sprayed on 20th February were damaged during removal from Stepney Green shaft. The prepared test specimens were found to be cracked, and since they can no longer give a reliable result, have been declared void
| 01CV - Civils | Cxxx-NCR-001268 | NCR | STG - SCL - Remedial works to EB Cavern 1 Enlargement without an ITP |  | Contr |  | TUY - Tunnel Drive Y (Central) |  | 2013-04-30 | 2013-03-19 15:45 | -42 | 2013-03-13 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | The remedial works to the voids found in the Eastbound Cavern 1 Enlargement Joints commenced prior to an accepted ITP for the works being in place. Remedial works were recorded on a check sheet that was later accepted in the revised ITP.
| 01CV - Civils | Cxxx-NCR-001269 | NCR | STG - SCL - Over excavation of WB Cavern 1 Bench Stage 5 |  | Contr |  | TUY - Tunnel Drive Y (Central) |  | 2013-04-30 | 2013-03-25 08:31 | -36 | 2013-03-13 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | During the Day shift of 08/03/13 in the Westbound Cavern, Bench stage 5 was over excacavated by 500mm. The RESS stated a 500mm advance and a 1000m advance was made instead. The following advance was reduced to bring the excavation back to the required sequence Refer to attached RESS.
| 01CV - Civils | Cxxx-NCR-001270 | NCR | STG - SCL - EB Cavern I26 and 27 Concrete used over 2hrs after batching |  | Contr |  | TUY - Tunnel Drive Y (Central) |  | 2013-04-30 | 2013-03-25 08:40 | -36 | 2013-03-14 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Planning | Use As-Is |  | Complete |  | Completed |  | On 01/03/13 in the EB Cavern the invert at Chainage 26-27 was sprayed with concrete that was batched over 2 hours before. The workability was still acceptable at 3hrs 20mins.
| 01CV - Civils | Cxxx-NCR-001271 | NCR | STG - SCL - Over excavation of profile WB Cavern 1 LHS Ch 4 |  | Contr |  | TUY - Tunnel Drive Y (Central) |  | 2013-04-30 | 2013-03-25 08:44 | -36 | 2013-03-14 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | 12/03/13 the invert Chainage 4 in the Westbound Cavern profile was over excavated refer to attachement 1 for the excavation profile. The primary lining 1 was sprayed to the correct profile.
| 01CV - Civils | Cxxx-NCR-001273 | NCR | Temporary gantry cradle within cut and cover |  | Contr |  | TUY - Tunnel Drive Y (Central) |  | 2013-05-30 | 2013-05-20 10:05 | -10 | 2013-03-18 | Tunnelling - Tunnelling General | 500 |  | Workmanship | Rework |  | Complete |  | Completed |  | A dimension was transposed during setting out and a 35m section of the southern haunch on the eastbound tunnel was cast incorrectly.
| 01CV - Civils | Cxxx-NCR-001278 | NCR | DLR Monitoring |  | Contr |  | TUY - Tunnel Drive Y (Central) |  | 2013-05-31 | 2013-05-17 11:33 | -14 | 2013-03-19 | Surveying - Instrumentation and Monitoring | 500 |  | System Defect | Use As-Is |  | Complete |  | Completed |  | Access for maintenance of the ATS has been requested but is to be facilitated by the Switch House sub-station maintainer.
| 01CV - Civils | Cxxx-NCR-001294 | NCR | STG - SCL - Missed excavation profile Ch 21 EB Launch |  | Contr |  | TUY - Tunnel Drive Y (Central) |  | 2013-05-15 | 2013-03-29 10:49 | -47 | 2013-03-25 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | The excavation profile of the shoulders of the bench at Ch21 in the Eastbound launch adit was is missing from the as-built survey information. Please refer to attachement "Exc Full Ring Ch 21" for location of missing information.
| 01CV - Civils | Cxxx-NCR-001296 | NCR | Off Site Fabrication of TBM Thrust Frames started prior to CRL acceptance of Quality related documentations |  | Contr |  | TUY - Tunnel Drive Y (Central) |  | 2013-05-31 | 2013-06-03 12:17 | 3 | 2013-03-25 | Structural Engineering - Steel Member | 500 |  | System Defect | Use As-Is |  | Complete |  | Completed |  | have started off site fabrication of the TBM steel thrust frame without CRL acceptance of the Method Statement, ITP, Welding Procedure and details of approved welders.
| 01CV - Civils | Cxxx-NCR-001298 | NCR | Commercial Street N__ |  | Contr |  | TUY - Tunnel Drive Y (Central) |  | 2013-08-01 | 2013-06-24 18:05 | -38 | 2013-03-26 | Utilities Engineering - Water | 500 |  | Design | Rework |  | Complete |  | Completed |  | The works instructed under PMI-157 were not able to be completed as per the TWUL specification due to the location of services near by. We were able to complete the N__ to 75% of the main but were unable to complete the remaining 5% as required by the specification due to the location of (assumed) comms ducts running parallel with the main on either side.
| 01CV - Civils | Cxxx-NCR-001312 | NCR | segment breaking |  | Contr |  | TUY - Tunnel Drive Y (Central) |  | 2013-05-31 | 2013-05-28 13:00 | -3 | 2013-04-04 | Tunnelling - Linings - Precast | 500 |  | Damaged | Reject |  | Complete |  | Completed |  | On the 20-3-13 the forklift was asked to remove some segments from the factory due to a build up in the evacuation line area . Through a lack of communication the crane drivers stacked the fresh segments for transporting instead of the one's that had remained in the factory for the required length of time . Because of this as the forklift was traveling outside the factory it ran into a pothole and the bottom segment was cracked through the centre of the segment .
| 01CV - Civils | Cxxx-NCR-001314 | NCR | Testing of precast concrete segmental units during production |  | Contr |  | TUY - Tunnel Drive Y (Central) |  | 2013-07-31 | 2013-05-28 12:27 | -64 | 2013-04-05 | Tunnelling - Linings - Precast | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | Beams cast on the 1st March 2013 do not comply with the above requirement
| 01CV - Civils | Cxxx-NCR-001320 | NCR | Westbound ring 239 crack |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2015-12-31 | 2015-03-24 16:53 | -282 | 2013-04-10 | Tunnelling - Linings - Precast | 5000 |  | Damaged | Rework | 3 (3-6k) | Complete | Discipline/Workmanship - Other | Completed |  | When the installation of the ring 239 (Drive Y Westbound) finished a deep crack appeared on segment B (close to rams 4 and 5 position) Minor water leakage around the key segment and hairline cracks (self healing) on D segment.
| 01CV - Civils | Cxxx-NCR-001323 | NCR | 6m3 concrete used 3 hours 45mins after being batched |  | Contr |  | TUY - Tunnel Drive Y (Central) |  | 2013-06-30 | 2013-05-07 12:27 | -54 | 2013-04-10 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | On 1st March 2013 EB Cavwern, chainage 26&27 invert was sprayed with concrete that was batched over 2 hours before. The workability waqs still acceptable at 3 hours 20mins.
| 01CV - Civils | Cxxx-NCR-001333 | NCR | WBCA Bench 31-32L Girder installation |  | Contr |  | TUY - Tunnel Drive Y (Central) |  | 2013-07-31 | 2013-06-25 16:20 | -36 | 2013-04-12 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | WB Cavern Bench 31-32L kwiks-strip and girder not installed correctly. Muck, not Footblocks used
| 01CV - Civils | Cxxx-NCR-001348 | NCR | Girder damaged while excavating |  | Contr |  | TUY - Tunnel Drive Y (Central) |  | 2013-06-30 | 2013-06-03 10:48 | -27 | 2013-04-15 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Damaged | Repair |  | Complete |  | Completed |  | Girder damaged while excavating.
| 01CV - Civils | Cxxx-NCR-001350 | NCR | Central drift excavated 6m in hight |  | Contr |  | TUY - Tunnel Drive Y (Central) |  | 2013-06-30 | 2013-06-03 11:00 | -27 | 2013-04-15 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | During the first top heading excavation of the enlargement, 6meters of sprayed face came away when only 3 meters were shown on the drawing. This additional 3m was part of the bench. Only top 3 meters was excavated and the other 3 was re-sprayed. Before and after pictures attached
| 01CV - Civils | Cxxx-NCR-001351 | NCR | P2 bars installed in wrong face |  | Contr |  | TUY - Tunnel Drive Y (Central) |  | 2013-06-30 | 2013-06-03 16:05 | -27 | 2013-04-15 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Repair |  | Complete |  | Completed |  | P2 layer of rebar installed in P1 layer. Pictures before and after attched
| 01CV - Civils | Cxxx-NCR-001352 | NCR | RESS not in line with the works |  | Contr |  | TUY - Tunnel Drive Y (Central) |  | 2013-06-30 | 2013-05-21 13:20 | -40 | 2013-04-15 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | Works were carried out that were not clearly indicated in the RESS. The RESS did not include P2 layer which was then installed. The RESS should have been updated there and then by Senior SCL Engineer but this did not happen.
| 01CV - Civils | Cxxx-NCR-001353 | NCR | void repair carried out using grout |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2013-08-31 | 2013-08-12 11:04 | -19 | 2013-04-15 | Tunnelling - Linings - Sprayed Concrete | 1000 |  | Supervision/Management | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Void repair carried out using grout and not as per the approved MS
| 01CV - Civils | Cxxx-NCR-001354 | NCR | B16mm rebar used instead of B12mm - incorrect spacing used for the B12 mm rebar |  | Contr |  | TUY - Tunnel Drive Y (Central) |  | 2013-06-30 | 2013-06-03 11:07 | -27 | 2013-04-15 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | B16mm rebar used instead of B12mm - incorrect spacing used for the B12 mm rebar in Eastbound Cavern invert16 ITP-Checksheet attached
| 01CV - Civils | Cxxx-NCR-001360 | NCR | Excavated aproximately 1.5m into the centre of the invert whilst excavating Bench |  | Contr |  | TUY - Tunnel Drive Y (Central) |  | 2013-06-30 | 2013-05-13 12:31 | -48 | 2013-04-19 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | During the Night shift of 17/04/13 in the Eastbound Cavern, Bench 28/29 was over excacavated approximately 1.5m into the centre of the invert. Once it was spotted another RESS was held (refer attached) and appropriate action taken. (pictures attached) Re-briefing importance of RESS to all gangs: clear communication, operators to follow instructions, SCL Engineers to ensure controls are in place and be more vigilant, Pit Boss to supervise all work activities. (Signed Briefing attached).
| 01CV - Civils | Cxxx-NCR-001363 | NCR | Drive Y, rings 001-100. Minor defects on rings |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2015-12-31 | 2015-10-26 17:16 | -66 | 2013-04-18 | Tunnelling - Tunnelling General | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The following minor defects were detected upon construction on Drive Y Eastbound between ring 001 and ring 100. Minor Spalling (internal), Surface, Shear cone. (R0) 14,16,22,24,34,40,47,55,58,75,78,79,82,83,84,87,90,91,97,98 Minor Spalling (internal), Edge, Circle joint trailing edge. (R1) 15,20,38,45,63,78 Minor Spalling (internal), Corner, trailing edge. (R1) 86,94 Self-healing crack. (R0) 74,76,96 Lips/Steps.(R0) 86
| 01CV - Civils | Cxxx-NCR-001364 | NCR | Eastbound ring 588 crack |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2016-01-31 | 2015-10-26 16:58 | -97 | 2013-04-18 | Tunnelling - Tunnelling General | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During the installation of the ring 588 on the Drive Y Eastbound tunnel a full depth crack appeared on the segment at the invert location (approx. on rams 11)
| 01CV - Civils | Cxxx-NCR-001372 | NCR | Production testing of sprayed concrete - flexural strength |  | Contr |  | TUY - Tunnel Drive Y (Central) |  | 2013-08-31 | 2013-07-15 14:55 | -47 | 2013-04-22 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | As the attached summary sheet demonstrates, __ are failing to deliver flexural strength test reports on time. Reports are frequently late by up to one month in some cases
| 01CV - Civils | Cxxx-NCR-001385 | NCR | Girder installed in the invert prior to spraying |  | Contr |  | TUY - Tunnel Drive Y (Central) |  | 2013-06-30 | 2013-06-03 16:02 | -27 | 2013-04-26 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | The girder was installed in the invert prior to spraying the initial layer on the profile. Initial layer was sprayed on the face. Miss communication between Shift Engineer and PIC & Snr SCL Eng.
| 01CV - Civils | Cxxx-NCR-001393 | NCR | 800mm butterfly valve at Wick lane |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2013-06-28 | 2013-07-12 09:16 | 14 | 2013-04-29 | Utilities Engineering - Water | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete |  | Completed |  | Erhard a member of the Talis group suppliers of the 800mm DIA DFBV,have advised that one of the valves on order has failed a body casting quality control check . They propose as an alternative to meet the required delivery dates and taking cognisance of available stock for an EKB epoxy coated bore rather than enamel lining as originally offered . EKB or Resicoat R4 factory applied epoxy powder coating for use with water up to 85 degree centigrade meets the requirements of BS 6920-1;2000 as to its sutiability as a non metallic product for use in contact with water intended for human consumption and has a WRAS Materials approval.
| 01CV - Civils | Cxxx-NCR-001408 | NCR | Wick Sewer Scour Plate |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2013-06-27 | 2013-07-12 09:07 | 15 | 2013-05-03 | Civil - Drainage | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete |  | Completed |  | The scour plate was fitted but was not extended the requisite 2m beyond the downstream end of the shaft.
| 01CV - Civils | Cxxx-NCR-001413 | NCR | Quality inspections |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2013-12-15 | 2013-12-16 12:43 | 1 | 2013-05-08 | Tunnelling - Linings - Precast | 5000 |  | Material | Use As-Is | 3 (3-6k) | Complete | Discipline/Workmanship - Other | Completed |  | The repair material being used prior to the 5th of October 2012 was found to be not suitable . All repairs were stopped until revision 6 of our repair procedure was code 1 on the 5th of October 2012 . On the 9th of Nov 2012 the segments were inspected by CRL and accepted to be used in the permanent works .
| 01CV - Civils | Cxxx-NCR-001414 | NCR | segment failing during lifting operation |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2013-09-27 | 2013-09-18 13:43 | -9 | 2013-05-08 | Tunnelling - Linings - Precast | 1000 |  | Supervision/Management | Reject | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | This NCR relates to a single segment failure during lifting whilst de-moulding . The NCR is a failure to cure the concrete in accordance with KH11.3206 prior to de-moulding . Segment identification EL5 Ring number 1932 carousel 2.
| 01CV - Civils | Cxxx-NCR-001419 | NCR | Drive Y Eastbound ring 864 crack |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2016-01-31 | 2015-10-26 16:55 | -97 | 2013-05-15 | Tunnelling - Tunnelling General | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During the installation of the ring 864 on the Drive Y Eastbound tunnel a radial crack appeared in 2 segments of the ring (approx. on rams 5-7)
| 01CV - Civils | Cxxx-NCR-001420 | NCR | Production testing of sprayed concrete - compressive strength |  | Contr |  | TUY - Tunnel Drive Y (Central) |  | 2013-07-31 | 2013-06-11 09:37 | -50 | 2013-05-13 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | 28-day compressive strength test results for cores taken from mix P425 SFR from 17/12/12 to 28/01/13 do not comply with Table 13 - group conformity criterion 1 as illustrated by the attached summary
| 01CV - Civils | Cxxx-NCR-001423 | NCR | testing regime non conforming with the spec. |  | Contr |  | TUY - Tunnel Drive Y (Central) |  | 2013-08-16 | 2013-07-08 09:02 | -39 | 2013-05-30 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | Up to 13/12/12 we took seven cores from each panel for testing at: 3 x 1 day, 1 x 7 day, 1 x 28 day, 1 x 56 day, 1 x 90 in accordance with DSJV's approved method statement. We now test to the following: 3 x 3 day, 3 x 28 day, and 3 x 90 day (if required)
| 01CV - Civils | Cxxx-NCR-001425 | NCR | Ring 979 crack on one segment |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2015-12-28 | 2015-10-26 17:00 | -63 | 2013-05-15 | Tunnelling - Tunnelling General | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During the installation of the ring 979 on the Drive Y Eastbound tunnel a crack appeared on the segment located at the crown position.
| 01CV - Civils | Cxxx-NCR-001433 | NCR | Production testing of sprayed concrete - compressive strength |  | Contr |  | TUY - Tunnel Drive Y (Central) |  | 2013-07-31 | 2013-07-08 09:01 | -23 | 2013-05-17 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | 28-day compressive strength test results for cores taken from mix P455 SFR from 01/04/13 to 08/04/13 do not comply with Table 13 - group conformity criterion 1 as illustrated by the attached summary
| 01CV - Civils | Cxxx-NCR-001439 | NCR | Lateral connection alignment |  | Stakeholder - THW | THW | TUY - Tunnel Drive Y (Central) |  | 2013-10-15 | 2013-10-01 15:59 | -14 | 2013-05-21 | Utilities Engineering - Utilities General | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The stainless steel liner has been stitch drilled out of alignment with the incoming 450mm lateral. The contractor has proceeded to weld on the strengthening plate, also out of alignment.
| 01CV - Civils | Cxxx-NCR-001447 | NCR | HAM Sewer - Jacking in advance of Test Results - Weld #1 |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2013-10-04 | 2013-09-06 15:31 | -28 | 2013-05-23 | Civil - Drainage | 500 |  | System Defect | Rework | 4 (0.5-3k) | Complete | Subcontractor Problems - Insufficient surveillance of subcontractors | Completed |  | The stainless steel liner was jacked into position to weld Joint #2 in advance of weld testing being carried out in accordance with the ITP Cxxx-DSJ-C-ITP-CRG03-50015) Rev. 2
| 01CV - Civils | Cxxx-NCR-001458 | NCR | Annulus Grouting surveillance, audit 16-05-13 |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2013-08-31 | 2013-09-06 13:40 | 6 | 2013-05-24 | Tunnelling - Grouting | 500 |  | System Defect | Repair | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | A superseded ITP was tabled during the audit / Surveillance of annulus grouting.
| 01CV - Civils | Cxxx-NCR-001463 | NCR | concrete used in connection detail 2 and 7 |  | Contr |  | TUY - Tunnel Drive Y (Central) |  | 2013-06-13 | 2013-06-13 10:54 | 0 | 2013-05-30 | Utilities Engineering - Water | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | Foundation concrete for thrust restraint at connection detail 2 & 7 is a standard concrete mix: C32/40 Cement type: CIIIB+SR, Admix: Glenium 123 Min Cement content 370kg/m^3 Free water cement ratio of .43
| 01CV - Civils | Cxxx-NCR-001465 | NCR | Proof Drilling + Secondary Grouting records |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2013-09-30 | 2013-09-16 13:49 | -14 | 2013-05-30 | Tunnelling - Grouting | 500 |  | System Defect | Repair | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | Ensure records are compliant with the Method statement + ITP
| 01CV - Civils | Cxxx-NCR-001466 | NCR | Reject segments from between 6-1-13 and 2-2-13 |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2014-04-30 | 2014-03-21 16:20 | -40 | 2013-05-31 | Tunnelling - Linings - Precast | 500 |  | Damaged | Reject | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The following segments have defects ranging from missing T20 sockets to hairline cracks on the conical bolts and will not be used in the permanent works : DATE SHIFT RING No Left /Right Mould No Type Mould Type 07/01/2013 D 492 L 3 S A 09/01/2013 D 505 P 1 P OP 09/01/2013 D 505 P 1 P TRP 11/01/2013 N 526 R 1 B 12/01/2013 D 530 0 R 2 S E 12/01/2013 D 533 1 L 2 S D 16/01/2013 N 550 0 L 1 S E 16/01/2013 N 555 0 R 3 S B 16/01/2013 N 555 0 R 3 S A 16/01/2013 N 555 0 R 3 S TR 17/01/2013 N 562 0 L 1 S A 17/01/2013 N 562 0 L 1 S TL 22/01/2013 D 593 0 L 3 S B 24/01/2013 D 609 0 P 1 P TRP 29/01/2013 D 629 1 L 2 S D 29/01/2013 D 630 1 L 3 S D 29/01/2013 D 630 0 L 3 S A 29/01/2013 D 631 0 P 1 P TRP 30/01/2013 N 646 0 L 1 S E 30/01/2013 N 648 0 L 3 S A 30/01/2013 N 648 0 L 3 S TL 31/01/2013 N 662 0 R 2 S TL 01/02/2013 N 677 0 L 2 S TR 01/02/2013 N 678 1 L 3 S D 07/01/2013 D 409 0 L 4 S B 07/01/2013 D 411 0 L 6 S B 07/01/2013 D 411 0 L 6 S TR 07/01/2013 D 411 0 L 6 S TL 07/01/2013 D 412 1 R 4 S D 07/01/2013 D 412 0 R 4 S C 07/01/2013 D 412 0 R 4 S B 07/01/2013 D 412 0 R 4 S TR 07/01/2013 D 412 0 R 4 S TL 07/01/2013 D 412 0 R 4 S E 07/01/2013 D 412 0 R 4 S K 07/01/2013 D 413 0 R 5 S C 07/01/2013 D 415 0 L 4 S C 07/01/2013 D 415 0 L 4 S A 07/01/2013 D 415 0 L 4 S TR 07/01/2013 D 415 0 L 4 S TL 16/01/2013 D 487 0 L 5 S C 21/01/2013 D 499 0 L 5 S C 22/01/2013 D 505 0 L 5 S C 23/01/2013 D 506 0 L 6 S B 23/01/2013 D 508 0 R 5 S C 24/01/2013 D 519 1 R 4 S D 24/01/2013 N 531 0 R 4 S C 26/01/2013 D 548 0 R 5 S B 26/01/2013 D 548 0 R 5 S A 28/01/2013 D 556 0 L 4 S TL 28/01/2013 N 564 0 L 6 S B 30/01/2013 D 579 0 R 6 S A 30/01/2013 N 589 0 R 4 S A 30/01/2013 N 590 0 R 5 S C 30/01/2013 N 590 0 R 5 S A 31/01/2013 N 602 0 R 5 S C 31/01/2013 N 604 0 L 4 S TR
| 01CV - Civils | Cxxx-NCR-001467 | NCR | Reject segments from between 3-2-13 and 2-3-13 |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2014-04-30 | 2014-03-21 16:21 | -40 | 2013-05-31 | Tunnelling - Linings - Precast | 500 |  | Damaged | Reject | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The following segments have defects ranging from T20 sockets missing to hairline cracks on the conical bolts : Date Cast Shift Ring No Left/Right Mould No Type Mould Type 08/02/2013 N 685 0 R 4 S E 08/02/2013 N 687 0 R 6 S E 06/02/2013 D 715 0 P 1 S TRP 12/02/2013 D 764 1 R 2 R1 D 21/02/2013 N 826 1 L 1 S D 21/02/2013 N 826 0 L 1 S B 21/02/2013 N 826 0 L 1 S A 21/02/2013 N 826 0 L 1 S TR 21/02/2013 N 826 0 L 1 S K 21/02/2013 N 827 1 L 2 S D 21/02/2013 N 827 0 L 2 S C 21/02/2013 N 827 0 L 2 S B 21/02/2013 N 827 0 L 2 S A 11/02/2013 D 688 0 L 4 S E 14/02/2013 D 705 0 R 6 S TL 20/02/2013 D 740 1 R 5 S D 21/02/2013 N 754 1 L 4 S D 21/02/2013 N 755 0 L 5 S K 21/02/2013 N 761 1 L 5 S D 21/02/2013 N 761 0 L 5 S C 22/02/2013 D 761 0 L 5 S E 22/02/2013 D 766 0 L 4 S B 22/02/2013 N 772 0 L 4 S TL 27/02/2013 N 815 0 R 6 S A 1/03/2013 D 852 L 6 S TLL
| 01CV - Civils | Cxxx-NCR-001472 | NCR | STG -SCL - EB Cav 1 Void former in Invert |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2013-08-31 | 2013-07-18 16:10 | -44 | 2013-06-24 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Eastbound Cavern 1 Side drift Expanded polystyrene void formers were installed in front of the invert lattice girders to maintain a leading edge while constructing the left-hand side drift. The void formers were to be removed prior to spraying the next advance. During the right-hand enlargement excavations at a number of locations the void formers were found still in situ in front of the lattice girder.
| 01CV - Civils | Cxxx-NCR-001480 | NCR | WB cavern chainage 34 and 35 overexcavated |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2013-08-31 | 2013-07-11 13:07 | -51 | 2013-06-24 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Overexcavation of chainage 34 by 500mm and Chainage 35 by 289mm
| 01CV - Civils | Cxxx-NCR-001481 | NCR | TH36 oversprayed |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2013-08-31 | 2013-07-29 12:27 | -33 | 2013-06-24 | Tunnelling - Linings - Sprayed Concrete | 2000 |  | Workmanship | Rework | 4 (0.5-3k) | Complete |  | Completed |  | overexcavation by 88mm
| 01CV - Civils | Cxxx-NCR-001488 | NCR | EB Cav Invert 4-5R open P2 layer sprayed with fibres |  | Contr |  | TUY - Tunnel Drive Y (Central) |  | 2013-08-31 | 2013-07-05 13:08 | -57 | 2013-06-13 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Supervision - Other | Completed |  | On the Night shift of the 12th of Feb the Invert P2 was sprayed with SFR. There was a mix up in communication between the batching plant and the Pit Boss and SFR was ordered rather that non-SFR. Neither the Pumpman nor sprayer realised until invert P2 was completed. The batching plant operators have been instructed to confirm with both Pit Boss and Engineer on what SCL is required.
| 01CV - Civils | Cxxx-NCR-001493 | NCR | Eastbound Cavern Headwall repair |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2013-08-31 | 2013-09-03 13:44 | 3 | 2013-06-24 | Tunnelling - Linings - Sprayed Concrete | 1000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Rebound trap, rebound encapsulated by high pressure aplication of concrete by __.
| 01CV - Civils | Cxxx-NCR-001495 | NCR | Excavation data not provided in the SGR report for serveral WB rings |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2013-09-30 | 2013-09-03 08:47 | -27 | 2013-06-17 | Tunnelling - Excavation - TBM | 500 |  | Equipment Breakdown | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | Excavation data was not provided in the SGR report for the following Drive Y Westbound rings: 1- Data for Rings 1080,1081 and 1086. Data was not provided because it was corrupted. When moving the machine along the reception cradle the system was not alternatively switched from mining operation mode to ring building operation mode, consequently the data (strokes length, chainage ring numbers and others )was not possible to be collected due to out of step and none sequential ring building operation. 2- From Rings 1082 – 1085 TBM internal data logging was turned off ( between 11.06.2013 11:02:10 p.m. and 12.06.2013 09:38:41 a.m) backup data has not been logged, therefore it is not possible to restore any data for these rings.
| 01CV - Civils | Cxxx-NCR-001496 | NCR | Overexcavation Bench Chainage 45 |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2013-09-30 | 2013-08-23 15:44 | -38 | 2013-06-18 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Poor workmanship between surveyor and substitute excavator driver caused over-excavation on blind side. Profile to be shown to both surveyor and machine operator. See attached profile
| 01CV - Civils | Cxxx-NCR-001502 | NCR | Missing cores compresive strength |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2013-09-30 | 2013-09-06 12:36 | -24 | 2013-06-21 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | insufficient quantity of insitu cores taken for determination of 28day compressive strength. For the cavern 21 compresive strength test should have been taken and only 17 were done. Due to the average compressive strength of all test are higher than the minimum stength no more test are required
| 01CV - Civils | Cxxx-NCR-001503 | NCR | Invert Chainage 36 overexcavated |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2013-08-12 | 2013-07-11 11:51 | -32 | 2013-06-24 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Overexcavation of up to 426mm at invert Chainage 36.
| 01CV - Civils | Cxxx-NCR-001508 | NCR | Drive Y Eastbound, rings 101-1085. Minor defects on rings |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2016-01-31 | 2015-10-28 10:34 | -95 | 2013-06-24 | Tunnelling - Tunnelling General | 5000 |  | Damaged | Rework | 3 (3-6k) | Complete | Discipline/Workmanship - Not Defined | Completed |  | The following minor defects were detected upon construction on Drive Y Eastbound between ring 101 and ring 1085. Minor Spalling on surface, leading edge. Rings no. : 120 169 224 232 235 237 246 249 257 352 429 456 486 529 605 607 666 853 866 901 Minor Spalling Surface Shear Cone . Rings no. : 113 115 120 131 134 145 155 156 172 174 182 233 236 238 259 260 261 319 320 321 324 350 363 367 368 414 430 433 437 449 450 490 492 509 510 513 515 588 607 608 609 623 638 640 643 644 664 666 678 679 745 830 831 848 852 858 866 870 871 872 874 898 899 902 905 924 927 934 937 963 964 979 997 999 1079 1081 Minor Spalling, shear joint. Ring no. 105 Minor Spalling, circle joint trailing edge. Ring no. 134 Minor Spalling, corner, leading edge Ring no. 122 Major spalling, surface, trailing edge. Ring no. 979 Self healing crack , transverse trailing edge. Ring no.131,855 and 979 Self healing crack , longitudinal, trailing edge. Ring no. 267 854 855 867 928 933 Self healing crack , longitudinal, trailing edge. Ring no. 631 790 934 Self healing crack, longitudinal,full lenght. Ring no. 155 Lips/steps 165 169 970
| 01CV - Civils | Cxxx-NCR-001509 | NCR | Maintaining contemporaneous calibration records |  | Crossrail | PDP | TUY - Tunnel Drive Y (Central) |  | 2013-12-31 | 2013-12-10 11:55 | -21 | 2013-08-09 10:35 | Civil - Tunnelling | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Other management problem | Completed |  | The requirements of Works Information volume 2B part 20.2 are for the Contractor’s quality management system to be capable of demonstrating by Contractor self certification that all the requirements of the contract and all relevant standards, regulations etc. are being met. The Contractor could not demonstrate this with respect to calibration of the grout batching plant and grout injection equipment. The calibration record availability is specified by the Works Information volume 2B part 13.2 (for maintaining contemporaneous records). It was stated by the Contactor during the surveillance on the 13th June 2013 that the records were not available on site, that they were maintained in Canada. The contractor was requested to provide the records for post surveillance review to demonstrate that they were current, hover no records were presented by the 25th June 2013. It therefore remains unknown if the calibration records are contemporaneous.
| 01CV - Civils | Cxxx-NCR-001510 | NCR | Measuring equipment clibration reports |  | Crossrail | PDP | TUY - Tunnel Drive Y (Central) |  | 2013-10-22 | 2013-10-18 14:33 | -4 | 2013-08-09 10:40 | Tunnelling - Grouting | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | The requirement of Works Information volume 2B clause 20.8 is for the Contractor to maintain a schedule of all inspection, measuring and test equipment used for the works that includes records of the calibration of such equipment to nationally recognised standards. The Contractor could not demonstrate compliance with the above for the grout batching plant and the grout injection equipment.
| 01CV - Civils | Cxxx-NCR-001511 | NCR | Canary Wharf - Over-excavation of W/B Tunnel Exit Eye |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2013-08-31 | 2013-07-09 15:11 | -53 | 2013-06-28 10:04 | Civil - Tunnelling | 1000 |  | Damaged | Rework | 4 (0.5-3k) | Complete |  | Completed |  | Existing concrete thickness at the central area of the Westbound Launch seal (220 mm.) not reaching the indicated depth In the TWD (350 mm.). it appears that some clay protrudes into the mass concrete pour at the location of the joint in the pours. During demolition of the concrete the hydraulic breaker struck the weak area and caused the concrete dome to crack locally. Some local cracking occurred within a ~500 x 500mm area in block structure and some section of clay became exposed.
| 01CV - Civils | Cxxx-NCR-001512 | NCR | 30mm Regulating layer Requirement (shotpatch 12) |  | Crossrail | XRL | TUY - Tunnel Drive Y (Central) |  | 2013-09-30 | 2013-08-27 14:41 | -34 | 2013-07-04 09:17 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete |  | Completed |  | The minimum requirement of 30mm was not provided when spraying the regulating layer (shotpatch 12) in the Eastbound cavern. According to KT20.3222, A). Regulating layer of minimum thickness of 30mm should be applied.
| 01CV - Civils | Cxxx-NCR-001513 | NCR | P2 layer at CH 51-52R, wrong bar mark used |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2013-08-31 | 2013-08-22 14:23 | -9 | 2013-07-09 12:31 | Tunnelling - Linings - Sprayed Concrete | 5000 |  | Supervision/Management | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During the installation of the P2 radial bars where install with the incorrect barmark
| 01CV - Civils | Cxxx-NCR-001514 | NCR | Invert P1 not sprayed to correct chainage |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2013-08-30 | 2013-08-07 14:57 | -23 | 2013-07-09 16:45 | Tunnelling - Linings - Sprayed Concrete | 5000 |  | Workmanship | Use As-Is | 3 (3-6k) | Complete | Discipline/Workmanship - Other | Completed |  | During the excavation of the invert stage 2 the excavation face became unstable due to the presence of water. Sheetpiles were used to support the face whilst the profile was excavated. The sheet piles were installed approximately 50-100mm from the excavation chainage. When the P1 was sprayed the sprayer left a 600mm leading edge from the sprayed face in the invert, which created a 1000mm leading edge at the kwikastrip.
| 01CV - Civils | Cxxx-NCR-001515 | NCR | Bench lattice girder missing at ch. 60 right side drift WB Cavern 2 |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2013-08-30 | 2013-08-07 17:54 | -23 | 2013-07-09 16:58 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | The lattice girder was missing from chainage 58 and it was decided that the girder from chainage 60 would be used instead
| 01CV - Civils | Cxxx-NCR-001518 | NCR | UTILITIES- Burdett Road 20" Main Replacement |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2013-08-30 | 2013-09-11 16:52 | 12 | 2013-07-10 12:49 | Utilities Engineering - Water | 500 |  | Design | Rework | 4 (0.5-3k) | Complete |  | Completed |  | During works to install the new main connection on the Southern Connection pit, some reinforcement bars clashed with the pipe due to the fall of existing pipe. Bars had to be cut to suit pipe.
| 01CV - Civils | Cxxx-NCR-001520 | NCR | Rhodesewell Road - Thrust Block Reinforcement |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2013-08-30 | 2013-09-11 17:54 | 12 | 2013-07-16 18:01 | Utilities Engineering - Water | 500 |  | Material | Rework | 4 (0.5-3k) | Complete |  | Completed |  | Rhodeswell Road thrust block reinforcement: A193 mesh (7mm x 200mm) has been used instead of A393 (10mm x 200mm) shown on drawing. Reinforcement has been applied to all 4 sides of the thrust block (not just 2 as per drawing).
| 01CV - Civils | Cxxx-NCR-001522 | NCR | Burdett Rd 20" Main Replacement- South connection, 45 angle branch tee, paint damage |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2013-08-30 | 2013-09-11 18:04 | 12 | 2013-07-16 18:41 | Utilities Engineering - Water | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete |  | Completed |  | Paint damage has ocurred to a section of the 45 angle branch tee, southern connection pit. Photo attached.
| 01CV - Civils | Cxxx-NCR-001523 | NCR | Sheet Waterproofing - Welding equipment calibration records |  | Crossrail | XRL | TUY - Tunnel Drive Y (Central) |  | 2013-09-30 | 2013-09-10 15:26 | -20 | 2013-07-18 09:24 | Tunnelling - Tunnelling General | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Verification Problems - Other | Completed |  | Calibration of waterproof sheet welding equipment is undertaken daily before commencing the welding of the waterproofing sheets. No records were made available to demonstrate that the above process takes place. To ensure welding equipment calibration records meet the requirements of Works Information volume 2B clause 20.8
| 01CV - Civils | Cxxx-NCR-001525 | NCR | Sprayed Concrete Materials - Aggregates |  | Crossrail | XRL | TUY - Tunnel Drive Y (Central) |  | 2013-09-30 | 2013-09-10 15:20 | -20 | 2013-07-18 16:53 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | Samples of 4/10mm aggregate taken from the stock at 's Stepney Green batching plant on the 6th to 8th June 2013 do not comply with the grading requirements of BS EN 12620, due to an excess of material retained on the 10mm test sieve
| 01CV - Civils | Cxxx-NCR-001527 | NCR | Drive Y tunnels ring plane check reports |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2013-09-30 | 2013-09-16 13:52 | -14 | 2013-07-18 19:02 | Tunnelling - Tunnelling General | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | During the excavation of Drive Y tunnels Eastbound and Westbound from Limmo Site to Canary Wharf Station Ring plane check reports were not produced as per the specifications included in Inspection and Test Plan "Cxxx TBM Tunnelling Operations Drive Y" (CRL no. Cxxx-DSJ-C-ITP-CR144 WS155-50027) section 2.10 that states VMT Ring Plane Check Report to be produced every third ring and packers location noted in the ring built report. KT10.4217 Ring plane … b) Check measurements on ring plane shall be carried out every third ring, or more often if plane is such that the maximum permitted packings are required.
| 01CV - Civils | Cxxx-NCR-001528 | NCR | Spalling of soffit to -4 level of CW Station around Eastbound TBM shove frame |  | Crossrail | PDP | TUY - Tunnel Drive Y (Central) |  | 2013-10-15 | 2013-09-19 13:15 | -26 | 2013-07-19 10:01 | Architectural - Ceilings & Soffits | 4000 |  | Damaged | Use As-Is | 3 (3-6k) | Complete | Discipline/Workmanship - Other | Completed |  | Spalling of soffit to -4 level of CW Station around Eastbound TBM shove frame exposing the reinforcing bar at the top RHS of the shove frame caused when removing the wedge.
| 01CV - Civils | Cxxx-NCR-001529 | NCR | Concrete Spalling |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2013-09-30 | 2013-09-18 13:48 | -12 | 2013-07-24 14:51 | Civil - Tunnelling | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | During the removal of the steel packers installed on the thrust frame contact points with Canary Wharf -6 level soffit and bottom slab spalling appeared on the concrete surface. (Note: NCR raised on behalf of Alvaro Garcia)
| 01CV - Civils | Cxxx-NCR-001531 | NCR | Non Conformance to slump - Thrust restraint |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2013-08-30 | 2013-09-03 13:15 | 4 | 2013-07-30 16:12 | Utilities Engineering - Water | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | ITP for the permanent thrust restraint stated concrete to be a slump class 2 50mm-90mm. Concrete strength was designed as C32/40 DC4. Concrete ordered was a dry mix.
| 01CV - Civils | Cxxx-NCR-001534 | NCR | Overexcavation CH43Central by 350mm |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2013-09-30 | 2013-08-27 11:57 | -34 | 2013-07-29 14:33 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Poor workmanship between surveyor and excavator driver caused over-excavation on Top Heading by aproximately 350mm, find attached profile
| 01CV - Civils | Cxxx-NCR-001535 | NCR | EB Invert 4-5R P2 layer sprayed with Fibres |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2013-09-30 | 2013-09-06 13:15 | -24 | 2013-07-29 14:50 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | On the Night shift of the 12th of Feb the Invert 4-5R P2 layer was sprayed with SFR. There was a mix up in communication between the batching plant and the Pit Boss and SFR was ordered rather that non-SFR. Neither the Pumpman nor sprayer realised until invert P2 was completed. The batching plant operators have been instructed to confirm with both Pit Boss and Engineer on what SCL is required.
| 01CV - Civils | Cxxx-NCR-001536 | NCR | Between chainage 42-46m in the westbound cavern, it appears that the minimum 50mm cover to the mesh was not achieved when applying the P2 layer. |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2013-09-30 | 2013-09-06 15:05 | -24 | 2013-07-30 10:52 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Between chainage 42-46m in the westbound cavern, it appears that the minimum 50mm cover to the mesh was not achieved when applying the P2 layer.
| 01CV - Civils | Cxxx-NCR-001537 | NCR | Inadequate projection of holding down bolts for the PML TBM Reaction Frame |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2013-09-30 | 2013-09-03 08:50 | -27 | 2013-08-01 16:00 | Civil - Civil Engineering General | 1000 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | A number of the holding down bolts on connection 2 of the TBM reaction frame do not have sufficient thread beyond the nut when in position. The design stated 3 threads preferably or a minimum of one thread as per KM10.1402 (d)
| 01CV - Civils | Cxxx-NCR-001538 | NCR | Missing cores Eastbound Launch Adit |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2013-09-30 | 2013-09-06 14:57 | -24 | 2013-08-01 15:57 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | 28 days missing cores for compressive strength
| 01CV - Civils | Cxxx-NCR-001539 | NCR | Inadequate projection of holding down bolts for the PML C1 and C2 Tower |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2013-09-30 | 2013-09-30 12:46 | 0 | 2013-08-01 17:29 | Civil - Civil Engineering General | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | 4 holding down anchors on the conveyor belt C1 and C2 towers do not have sufficient thread beyond the nut when in position. The design states 3 threads preferably or a minimum of one thread as per KM10.1402 (d). As you can see from the attached photos 3 of the 4 anchors have been corrected following the Temporary Works Site Design Chance so only one remains to be corrected.
| 01CV - Civils | Cxxx-NCR-001540 | NCR | Inadequate projection of holding down bolts for the PML Belt Storage Loop |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2013-10-30 | 2013-09-19 14:05 | -41 | 2013-08-01 17:25 | Civil - Civil Engineering General | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | 6 holding down anchors on the conveyor belt loop do not have sufficient thread beyond the nut when in position. The design states 3 threads preferably or a minimum of one thread as per KM10.1402 (d)
| 01CV - Civils | Cxxx-NCR-001541 | NCR | WB LA - Primary thickness, less than minimum |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2013-12-22 | 2013-12-02 14:59 | -20 | 2013-08-09 16:35 | Tunnelling - Linings - Sprayed Concrete | 2000 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | In Westbound Launch Adit at chainages 16, 20, 23 and 29, minimum required thickness (350mm) in some points wasn't achieved (see attached profiles).
| 01CV - Civils | Cxxx-NCR-001542 | NCR | SCL Primary Lining thickness |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2013-09-30 | 2013-09-10 15:14 | -20 | 2013-08-12 17:20 | Tunnelling - Linings - Sprayed Concrete | 1000 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Profile plots indicate that 3 points in the Eastbound Launch adit at Chainage 15 do not meet the minimum required thickness
| 01CV - Civils | Cxxx-NCR-001543 | NCR | Non implementation of Surveillance report findings on I&M ITP |  | Crossrail | PDP | TUY - Tunnel Drive Y (Central) |  | 2014-01-31 | 2014-01-28 09:31 | -3 | 2013-08-14 17:05 | Surveying - Instrumentation and Monitoring | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | Cxxx I&M ITP (Cxxx-DSJ-C-ITP-CRG03-50001 Rev 2.0) was reviewed as part of the internal Surveillance by the Contractor in Feb 2013 with changes identified to the ITP and associated ITP check-sheets. In this surveillance report it notes that the ITP is written around the Limmo works and a more generic ITP will be developed by __ for future works. It also notes the lack of materials approvals. The Surveillance was undertaken 6 months ago with no changes implemented and the ITP has been used for all subsequent I&M works.
| 01CV - Civils | Cxxx-NCR-001544 | NCR | Ham Sewer Access shaft - Knee Bracing |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2013-09-06 | 2013-09-09 11:16 | 3 | 2013-08-23 19:08 | Utilities Engineering - Water | 500 |  | Planning | Rework | 4 (0.5-3k) | Complete |  | Completed |  | The Ham Sewer Access shaft sheet piles were being cut without the Waling Frames (Knee Bracing) signed permit to Load Omission included Signed Permit to Load Signed on site welds inspection sheets
| 01CV - Civils | Cxxx-NCR-001545 | NCR | North gas stopple pit |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2013-11-15 | 2013-10-17 08:01 | -29 | 2013-08-23 19:11 | Utilities Engineering - Gas | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | The construction on site does not reflect the subcontractor design that was issued for acceptance. 1. The additional retaining wall propping adjacent to the Northern Gas Stopple pit not included in the revised design Cxxx-DSJ-N2-NOX-CRG03-50143 2. The gas stopple pit was moved to the northern connection pit.
| 01CV - Civils | Cxxx-NCR-001547 | NCR | Water Ingress Sheet Membrane - EBCA - BAY 4 |  | Crossrail | XRL | TUY - Tunnel Drive Y (Central) |  | 2013-09-15 | 2013-09-10 16:46 | -5 | 2013-08-29 09:53 | Civil - Tunnelling | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | During inspection it was established that there was ingress of water under the waterproof sheet membrane. Under KW21.3203 It is the contractors repsonsibilty that water management is maintained throughout the membrane placing and to be arranged that excess water pressure behind the membrane cannot develop.
| 01CV - Civils | Cxxx-NCR-001548 | NCR | Production Testing of Sprayed Concrete |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2013-10-17 | 2013-09-10 14:55 | -37 | 2013-09-03 14:34 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Verification Problems - Other | Completed |  | With reference to water permeability testing, no sample shall display a depth of water penetration greater than 35mm. The mean depth of water penetration (3 samples) shall not exceed 25mm. The 2 sets of 3 cored specimens representing June 2013 and July 2013 production marginally fail to comply with this specification
| 01CV - Civils | Cxxx-NCR-001549 | NCR | Westbound Cavern primary lining crack |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2015-12-05 | 2015-11-30 16:27 | -5 | 2013-09-17 14:42 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | KT20.3221 states ' the concrete cover shall be as per the drawings' Due to insufficient cover to rebar in the P2 layer, a crack of less than 1mm width has appeared between chainage 1 & 19 in the westbound cavern along the single side drift joint.
| 01CV - Civils | Cxxx-NCR-001550 | NCR | Repair of Defective Segments |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2014-03-31 | 2014-03-06 07:49 | -25 | 2013-11-27 15:16 | Tunnelling - Linings - Precast | 4000 |  | Damaged | Repair | 3 (3-6k) | Complete | Material/Preservation Problems - Improper handling of material | Completed |  | Repair of defective segments, i.e. Pin No (Segment factory ID No), 265(TRL3), 273(DR3), 287(DL2), 508(DL1), 626(TRR2), 693(TRR3), 697(TRR4), 751(TRR4), 770(DR2), 871(DL1), 918(DR5), 1052(TRR1), 1053(DL5), 1164(DL2), 1273(DR1), 1279(DR1), 1290(TRL5), 1441(DL6), 1488(DL5), 1516(TRR6), 1532(DR2), 1617(DR3), 1619(DL4), 1698(DL3), 1802(TRR2), 1827(TRR3), 1922(TRR2), 2025(TRR3), 2066(DR4), 2682(TRL3), 2771(DL2), 2879(DL2), 2947(TRR1), 3068(TRR4), 3215(TRL4)
| 01CV - Civils | Cxxx-NCR-001551 | NCR | Production Testing of Sprayed Concrete |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2013-12-15 | 2013-10-29 15:36 | -47 | 2013-10-14 08:42 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | With reference to water permeability testing, no sample shall display a depth of water penetration greater than 35mm. The mean depth of water penetration (3 samples) shall not exceed 25mm. The set of 3 cored specimens representing August 2013 production marginally fail to comply with this specification
| 01CV - Civils | Cxxx-NCR-001552 | NCR | Fibre Optic Remedial Works |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2014-03-15 | 2014-03-06 09:00 | -9 | 2013-10-25 12:54 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Not Defined | Completed |  | During construction of the Westbound cavern, there was a requirement to install Optical Fibre Instrumentation around lattice girders within the double side drift and Enlargement. These fibre optic tables were protected by barrels. These barrels were welded to the lattice girders and protruded out through the primary lining. Some time later it was decided that the fibre optic instrumentation was no longer required therefor all existing barrels embedded into the primary lining would have to be made good. See attached ITP checksheets and photographs.
| 01CV - Civils | Cxxx-NCR-001553 | NCR | Slab out of Tolerance |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2014-02-28 | 2014-02-18 09:12 | -10 | 2013-11-05 17:02 | Tunnelling - Linings - In-situ Concrete | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The design level of the eastbound invert slabs is 81.265. In accordance with RFI 1478 this tolerance should be +25/-0mm As-built level surveys carried out on these slabs indicate some areas to be out of tolerance, worst case being +27/-18mm ( see attached ) As you will see from the attached surveys there are very few areas above the plus 25mm tolerance but there are quite a number of areas below the required tolerance. It is felt however that these levels are satisfactory and will have no effect structurally on the slab nor on the first stage concrete to be cast on top.
| 01CV - Civils | Cxxx-NCR-001555 | NCR | 3 months baseline not achievable for sockets & prisms between STG and WCH |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2014-07-30 | 2014-07-15 13:45 | -15 | 2013-11-14 10:57 | Surveying - Instrumentation and Monitoring | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | The 3 months baseline will not be achievable for the sockets & prisms between STG and WCH • The Contractor’s subcontractor did not issue the Method Statement on time to the Project Manager. • The Project Manager exceeded the agreed contract ‘comment & approval’ period for the MS and further delayed the works. The Contractor believes that with a minimum of 3 consecutive stable readings, a suitable baseline can be achieved and there will be no impact to the quality, reliability and accuracy of the monitoring data in this instance.
| 01CV - Civils | Cxxx-NCR-001556 | NCR | Precast Concrete Retaining unit failure |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2014-05-13 | 2014-04-28 13:42 | -15 | 2013-11-14 17:53 | Architectural - Walls | 1000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | On 7th November It was noticed and reported to the Tunnel Agent, that a section of the retaining wall (pre-cast concrete segment) had been pushed out of line at Pudding Mill Lane Muck pit. A similar event happened on 13th November.
| 01CV - Civils | Cxxx-NCR-001557 | NCR | Reinforcement drawing revisions westbound cavern invert slab bay 1 |  | Crossrail | XRL | TUY - Tunnel Drive Y (Central) |  | 2014-04-15 | 2014-02-18 09:16 | -56 | 2013-11-15 14:10 | Civil - Tunnelling | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Fixing of the reinforcement for the Drive Y westbound cavern invert slab bay 1 using the incorrect drawing revisions C05 instead of C06. Drawing reference as below: Eastbound Turnout Cavern Invert Reinforcement Details Sheet 1 of 2 Cxxx-MMD-C4-DDD-CR094_SH005-01101 Eastbound Turnout Cavern Invert Reinforcement Details Sheet 2 of 2 Cxxx-MMD-C4-DDD-CR094_SH005-01102 Note that PMI 507 issued the above referenced drawings to revision C06 on the 5th of November and our records show that steel fixing commenced on the 6th of Novemeber. This issue was identified during a surveillance carried out on the 13th of November.
| 01CV - Civils | Cxxx-NCR-001566 | NCR | DLR Limehouse Automated Monitoring |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2014-07-30 | 2014-07-15 14:15 | -15 | 2013-11-29 12:58 | Surveying - Instrumentation and Monitoring | 500 |  | Equipment Breakdown | Rework | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | From 21:00 28/11/2013 to 11:00 29/11/2013 a section of the automatic monitoring system at DLR Limehouse did not take hourly readings due to a technical problem with a computer/data logger. No adverse trends have been detected over this period.
| 01CV - Civils | Cxxx-NCR-001567 | NCR | Cross Passage 13 - Dewatering __ substation plinth |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2013-12-19 | 2013-12-17 10:33 | -2 | 2013-12-05 16:43 | Civil - Utilities Engineering | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Personnel Error - Verbal communication problem | Completed |  | As per the Temporary Works Design "Cross Passage 13 - Blackwall Way Substation Plinth" Cxxx-DSJ-N2-CER-CRG03-50089 and Method Statement "Cross Passage 13 - __ Substation plinth" Cxxx-DSJ-C-GMS-CRG03-50054, a concrete plinth is required for the installation of a __ substation at Blackwall Way dewatering main compound area. The plinth is required to be built above ground level (above the road) with a perimetral earthing mat buried approx 600mm. Ground has been broken and excavated 300mm within the whole plinth layout, no just for the earthing mat.
| 01CV - Civils | Cxxx-NCR-001569 | NCR | Canning Town Flyover - Temporary Bridge. |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2014-01-30 | 2014-01-14 12:13 | -16 | 2013-12-13 16:04 | Surveying - Surveying General | 10000 |  | Supervision/Management | Repair | 2 (6-60k) | Complete | Management Problem - Misunderstand the definition of the requirement | Completed |  | The Temporary bridge, required as part of the Canning Town Jacking Works, has been positioned incorrectly. Whilst the drawings used are correct, and the requirements interperpreted correctly in setting out, the centre lines for the bridge and the stairs have been incorrectly identified during installation, resulting in the bridge being positioned on the wrong grid point.
| 01CV - Civils | Cxxx-NCR-001570 | NCR | Temporary Works Eastern Connection Pit |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2014-03-31 | 2014-02-03 09:51 | -56 | 2013-12-18 12:18 | Utilities Engineering - Water | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Existing Issue/ Non-conformance: The Eastern Connection Pit has not been completed in accordance with the temporary works design. Omissions include: 1. The Excavation Support frame arrangements – top frame not installed at stage 3 2. The steel sheet pile should be installed and reach the formation level. 3. Some of the sheet piles are missing 4. Timber lagging not installed correctly causing some of the excavation to collapse. 5. There is lack of support to Third Party (__ & NGG) assets, also supporting beam not fixed as per design The construction on site does not reflect the subcontractor design that was issued for acceptance. Check the design used onsite to ensure its suitability and if applicable update the design to reflect the site changes.
| 01CV - Civils | Cxxx-NCR-001571 | NCR | Blinding at eastern connection pits |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2014-06-30 | 2014-06-02 09:30 | -28 | 2013-12-18 13:55 | Utilities Engineering - Water | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The Eastern Connection Pit has not been completed in accordance with the temporary works design: 1. Blinding was poured approximately 250mm too high which prevents the mechanical arrangement from being installed as per the drawings. 2. Blinding now needs to be broken out in order to complete installation of the concrete thrust block and associated mechanical arrangement.
| 01CV - Civils | Cxxx-NCR-001573 | NCR | Reduction in thrust block size |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2014-02-26 | 2014-02-03 10:21 | -23 | 2014-01-08 09:28 | Utilities Engineering - Water | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | The size of the thrust block on the northern connection pit was reduced by approximately 300mm due to unforeseen onstructions during excavtion.
| 01CV - Civils | Cxxx-NCR-001574 | NCR | Southern Connection and Gas Stopple Pit |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2014-02-19 | 2014-02-03 10:51 | -16 | 2014-01-08 09:39 | Utilities Engineering - Water | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The Southern Connection Pit has not been completed in accordance with the temporary works design. Omissions include: 1. The Excavation Support frame arrangements 2. The steel support frames around Stanchion #1 base 3. Connection between Southern connection pit and the southern gas stopple pit
| 01CV - Civils | Cxxx-NCR-001575 | NCR | Retaining Wall Propping Pile Support |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2014-02-19 | 2014-01-23 14:20 | -27 | 2014-01-08 09:52 | Utilities Engineering - Utilities General | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | The Compound Retaining Wall Propping additional Pile Support has not been implemented in accordance with the temporary works requirements on site. The additional pile support has not implemented as per Site Design Change Cxxx-DSJ-N2-NOX-CRG03-50143
| 01CV - Civils | Cxxx-NCR-001576 | NCR | Kwikastrip spacing |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2015-05-31 | 2014-02-18 09:08 | -467 | 2014-01-14 13:51 | Tunnelling - Linings - In-situ Concrete | 2000 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Due to the formwork that was being utilised for the invert slab, a gap between the kwikastrip sections was necessary due to the dowels running through the formwork Spacing between Kwikastrip sections in some locations was reported to be excessive. Any gap of 150mm or greater is deemed to be excessive (150mm is the spacing of the re-bars present in the Kwikastrip sections). Attached is a guide as to the locations of theses excessive gaps. Bay 3 Northside of Invert Slab – 6 Locations: Approximately at Chainages; 26m, 27.5m, 28.8m, 31.3m, 33.5m, 35m Southside of Invert Slab – 4 Locations: Approximately at Chainages; 27.7m, 28.9m, 30.1m, 32.3m Bay 4 The issue regarding the spacing of the Kwikastrip sections was raised before the steel fixing for bay 4 commenced. Therefore no issue is present in the spacing of bay4 Bay 5 No issue in this bay. Bay 5A No issue is present in this bay as only one section of Kwikastrip would fit in this small bay. However, it is noted that the gap between the adjacent sections of Kwikastrip between bays 5 and 5A was in excess of 150mm.
| 01CV - Civils | Cxxx-NCR-001579 | NCR | Cross Passage 14 - Faulty surface piezometer PV04080/81/82 |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2014-04-30 | 2014-03-27 16:04 | -34 | 2014-01-21 19:16 | Surveying - Instrumentation and Monitoring | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | PV04080/81/82 Surface piezometer was installed at Lower Lee Crossing footpath, by Lea Valley Park Cross Passage 14 compound area, on March/13, in order to track and record the water levels on the Lambeth Group Sand layers and Lower Aquifer at the cross passage vicinity. After the 100mm borehole was drilled, the installation was completed with 3 sensors placed at different depths, 31.20, 38.5 and 47.10 respectively. Incoherent water level readings collected from the different sensors, issues with water ingress into the datalogger and sensors stuck into the tubing are considered to be due a faulty installation, grouting and sealing of the piezometer.
| 01CV - Civils | Cxxx-NCR-001580 | NCR | Missing dowel |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2014-08-30 | 2014-02-18 10:10 | -193 | 2014-01-23 10:17 | Tunnelling - Tunnelling General | 0 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Contamination | Completed |  | On 20th January 2014 dayshift a standard segment type D was installed in Drive Z Eastbound (ring no. 1455) without 1 of the 3 dowels that connects one segment to the previous ring. (please refer to the ring built sheet, attached)
| 01CV - Civils | Cxxx-NCR-001581 | NCR | segments with small surface cracks |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2014-03-20 | 2014-03-20 16:39 | 0 | 2014-01-29 16:11 | Tunnelling - Linings - Precast | 1000 |  | Damaged | Reject | 4 (0.5-3k) | Complete | Discipline/Workmanship - Not Defined | Completed |  | The following list of segments have had small cracks appear on the intrados where the conial bolt is placed . They are traveling to the outer edge of the segment . Ring 4201 Carousel 1 all segments except the key . Ring 4200 Carousel 1 all segments except the key . Ring 4320 Carousel 2 all segment except the key . Ring 4275 Carousel 2 all segments except the key . Ring 4308 Carousel 2 CL5 , BL5 , AL5 . Ring 3677 Carousel 2 3677 DL4 , CL4 , BL4 , TRL4 , TLL4 and EL4 . Ring 3674 Carousel 2 CR4 , BR4 , AR4 . Ring 3957 Carousel 2 Whole ring . Ring 703 Carousel 2 Ar4 . Ring 4250 Carousel 1 DR2 , CR2 and BR2 . Ring 3273 Carousel 2 Whole ring Ring 3274 Carousel 2 Whole Ring .
| 01CV - Civils | Cxxx-NCR-001582 | NCR | Victoria Dock Road - Connection Pit Thrust Block Concrete |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2014-03-31 | 2014-03-27 19:01 | -4 | 2014-01-30 14:54 | Civil - Utilities Engineering | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The concrete for the thrust blocks in the east and west connection pits must be a structural grade C28/35 – DC2, supplied by an approved ready-mix concrete supplier in accordance with the approved Material Conformance Report for structural concrete and the ITP for the works (__). The concrete used to pour the thrust blocks in the east and west connection pits was not in accordance with the approved documentation listed below. In particular, the supplier ( {East} and Sivyer {west}) used was not approved by the Contractor. MCR Document Number: Cxxx-DSJ-U-LRC-CR144_PT003-50002 ITP Document Number: Cxxx-DSJ-U-ITP-CR144_PT003-50004 Western Connection Thrust Restraint Design Document Number: Cxxx-DSJ-N2-RGN-CR144_PT003-50022 Eastern Connection Thrust Restraint Design Document Number: Cxxx-DSJ-N2-RGN-CR144_PT003-50021
| 01CV - Civils | Cxxx-NCR-001583 | NCR | TTGB for South Piers, Canning Town Flyover |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2014-05-01 | 2014-03-07 15:03 | -55 | 2014-01-31 12:24 | Surveying - Instrumentation and Monitoring | 10000 |  | System Defect | Reject | 2 (6-60k) | Complete | Management Problem - Inadequate administrative control | Completed |  | Starting fabrication works for the TTGB assemblies without an accepted ITP and welding documentation.
| 01CV - Civils | Cxxx-NCR-001585 | NCR | Victoria Dock Road - Rider Main Connections - East and West |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2014-06-30 | 2014-06-07 10:32 | -23 | 2014-02-05 08:36 | Civil - Utilities Engineering | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | The rider main connection in the connection pits (east and west) has not been implemented in accordance with the accepted temporary works design and must conform to the materials, dimensions and levels detailed in the design completed by the Subcontractor.
| 01CV - Civils | Cxxx-NCR-001586 | NCR | Cracking within SP5 vertical jack grout bed |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2014-03-30 | 2014-04-07 13:24 | 8 | 2014-02-07 14:22 | Surveying - Instrumentation and Monitoring | 1000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | have been subcontracted by to carry out amongst other activities the grouting to both the base and the upper plate to the vertical jacks. Grouting took place on Tuesday 28/1/14 on the vertical jacks on piers SP1 to SP5. Upon inspection cracking was found on the vertical jacks on pier SP5.
| 01CV - Civils | Cxxx-NCR-001587 | NCR | Fabrication of SP3 TTGB |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2014-03-30 | 2014-03-20 16:42 | -10 | 2014-02-07 14:36 | Surveying - Instrumentation and Monitoring | 10000 |  | Documentation and Records | Reject | 2 (6-60k) | Complete | Management Problem - Other | Completed |  | s sub-contracted DAS Fabrications to fabricate Temporary Transverse Guided Bearing (TTGB) Assembly for pier SP3, Canning Town Flyover. The sub-contractor could not provide the requisite assurance documentation and certification for the works.
| 01CV - Civils | Cxxx-NCR-001588 | NCR | Wick Lane Compound Pit Excavation Works - Temporary Works |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2014-02-28 | 2014-03-03 19:18 | 3 | 2014-02-10 08:53 | Utilities Engineering - Water | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During hand excavation works on the Wick lane Compound Pit to facilitate installation of 355mm PE Gasmain and 400mm PE watermain, DSJV subcontractor has removed kingpost and crossboard retaining structure. This task is not covered in the temporary works sequence, and so has not been analysed or accomodated. The works were ceased to facilitate Temporary Works Designer appraisal. The temporary works in question are required to protect an existing retaining wall in Wick Lane - a third party asset.
| 01CV - Civils | Cxxx-NCR-001589 | NCR | Not protecting Waterproofing membrane |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2015-02-24 | 2014-10-22 08:36 | -125 | 2014-02-10 13:39 | Tunnelling - Tunnelling General | 500 |  | Supervision/Management | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | During Pour 1 EB Drive Z Transit Rails – 29/01/2014 – Stepney Green It was noted during pour 1 of the EB Drive Z transit rails that the water proof membrane layer adjacent to the pour was not adequately protected. No concrete appeared to make contact with the waterproof membrane. The membrane was protected with sand and covered with concrete after the pour. An inspection of the membrane will take place after the haunches are broken out to clarify whether or not the membrane incurred any damage.
| 01CV - Civils | Cxxx-NCR-001590 | NCR | Welding of TBM Lifting Eyes |  | Crossrail | XRL | TUY - Tunnel Drive Y (Central) |  | 2014-03-31 | 2014-03-20 16:45 | -11 | 2014-02-18 11:20 | Tunnelling - Tunnelling General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Welding of lifting eyes to TBM cutterhead were undertaken without a signed off Inspection and Test Plan in place.
| 01CV - Civils | Cxxx-NCR-001591 | NCR | Burdett Rd. 500mm Watermain Chambers |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2014-04-30 | 2014-04-02 10:36 | -28 | 2014-03-06 11:50 | Utilities Engineering - Water | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | 3 nr valve chambers on the 500mm Watermain works on Burdett Rd have become unstable, resulting in pavement failure at each location and dislodging of the chamber frames and lids.
| 01CV - Civils | Cxxx-NCR-001593 | NCR | RAMS not followed for installation of Ring 2 of Cross Passage 13 |  | Crossrail | XRL | TUY - Tunnel Drive Y (Central) |  | 2014-06-30 | 2014-04-03 11:26 | -88 | 2014-03-18 09:02 | Tunnelling - Linings - SGI Rings | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Procedure Problem - Defective or inadequate procedure | Completed |  | Section 20.1, item 8 of document Cxxx-DSJ-C-GMS-CRG03-50044 Cxxx Cross Passage 13 Construction, states that ring #2 would be fully grouted folloing its installation. During the nighshift of 12/03/2014, invert excavation and the installation of ring 1 commenced without ring 2 being fully grouted.
| 01CV - Civils | Cxxx-NCR-001594 | NCR | Out of Tolerance Rings EB Tunnel Drive Y |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2015-12-09 | 2014-10-22 15:48 | -413 | 2014-03-19 09:43 | Tunnelling - Alignment | 50000 |  | Incorrect Installation | Use As-Is | 2 (6-60k) | Complete | Discipline/Workmanship - Other | Completed |  | The ring building tolerance specified within KT 10 clause KT 10.4221 (Cxxx-OVE-Z4-RSP-CR001-00001) requires "For tunnels greater than 6.0m diameter the centreline of each ring shall not depart from the design position by more than ±50mm". Following the completion of the wriggle survey for the Drive Y Eastbound tunnel of section Limmo to Canary Wharf for ring numbers 1 - 1083it has identified a number of rings that exceed this tolerance. Attached is a detailed spread sheet indicating all out of tolerance rings. However for further information this should be made to the full wriggle survey(Cxxx-DSJ-C4-RGN-CR144_WS155-50025).
| 01CV - Civils | Cxxx-NCR-001595 | NCR | Drive Z Westbound lips on rings 114,116 and 117 |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2014-11-30 | 2014-08-29 17:16 | -93 | 2014-03-27 12:13 | Civil - Tunnelling | 50000 |  | Incorrect Installation | Use As-Is | 2 (6-60k) | Complete | Discipline/Workmanship - Other | Completed |  | While installing rings 113 to 116 in Drive Z Westbound the following steps exceeding KT10 requirements were identified: R113 to R114: circa 20mm step in crown; R114 to R115: 20 to 30mm step in crown; R115 to R116: 20 to 30mm step in crown. (Actual measurements to be confirmed when defects are accessible
| 01CV - Civils | Cxxx-NCR-001596 | NCR | Cross Passage 11 - Dewatering Discharge Route |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2014-04-17 | 2014-04-14 09:24 | -3 | 2014-04-03 16:51 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Supervision - Other | Completed |  | A road crossing is required at Kiln Court (CP11) for the installation of the surface dewaterin discharge route. As per the SNC Cxxx-DSJ-C-CCN-CRG03-50041 rev. 1.0, a trench will be excavated and a 12" and 6" corrugated ducts will be placed at the bottom over a minimum 150mm blinding. Ducts has been placed inside the trench with no blinding.
| 01CV - Civils | Cxxx-NCR-001597 | NCR | CP13 EB Collar - Position of reinjectable tubes |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2015-12-05 | 2015-06-09 14:56 | -179 | 2014-04-02 11:08 | Tunnelling - Linings - In-situ Concrete | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The position of the injection tubing termination points was not agreed prior to casting the concrete in the CP13 EB collar. 150x150x50mm galvanised termination boxes were installed in the Cross Passage face of the concrete collar. These termination boxes appear to be installed inside the exclusion zone sketch sent by Jon Quilliam.
| 01CV - Civils | Cxxx-NCR-001598 | NCR | CP13 EB Soffit Concrete Mix Design |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2014-06-30 | 2014-05-23 15:00 | -38 | 2014-04-02 11:42 | Tunnelling - Linings - In-situ Concrete | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The concrete used to cast the CP13 EB collar soffit was a derivative mix design, 13a, from the approved concrete mix 13. This derivative mix design was used to prolong the useable life of the concrete from 2 hours to 3 hours and also to increase the flowability from S3 to S4 to aid the flow of the mix around the rebar and SGI rings.
| 01CV - Civils | Cxxx-NCR-001600 | NCR | Movement of Westbound Drive Y Cradle Plinth |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2015-06-02 | 2014-11-25 09:53 | -189 | 2014-04-08 18:35 | Tunnelling - Linings - Sprayed Concrete | 2000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | When the Tunnel Boring Machine came through the Westbound Drive Y Eye at the Stepney Green Cavern a slight misalignment in height meant there was contact with the support plinth. This contact generated forward and upward movement of the plinth.
| 01CV - Civils | Cxxx-NCR-001602 | NCR | CP13 EB - Casting Collar Walls - Concrete cubes not taken |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2014-04-25 | 2014-04-14 16:48 | -11 | 2014-04-11 05:17 | Tunnelling - Linings - In-situ Concrete | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Misunderstand the definition of the requirement | Completed |  | No concrete cubes were taken when casting the walls of the CP13 EB Collar.
| 01CV - Civils | Cxxx-NCR-001603 | NCR | Victoria Dock Road - Manhole S3 Surround |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2014-05-30 | 2014-05-27 09:51 | -3 | 2014-04-30 17:09 | Civil - Utilities Engineering | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Concrete surround to the manholes should be 150mm in accordance with the approved detail CH7083/D05 rev B, RAMS ref. Cxxx-DSJ-C-GMS-CR144_PT003-50008 rev 4 and TWUL standard detail STDS-PL-02101 Rev G. Surround concrete does not equal 150mm all around - please see attached photos.
| 01CV - Civils | Cxxx-NCR-001604 | NCR | Stepney Green Eastbound Drive Z Final Ring Dropped Invert Segment |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2014-12-31 | 2014-06-18 13:15 | -196 | 2014-05-08 03:34 | Tunnelling - Excavation - TBM | 5000 |  | Damaged | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Not Defined | Completed |  | Following inspection of the final Drive Z Eastbound after the removal of the TBM transit temporary works, it has been found that the invert segment has dropped significantly at the leading edge (approx. 50mm). In addition to this the invert segment has clearly defined longitudinal crack running roughly along it's centreline.
| 01CV - Civils | Cxxx-NCR-001605 | NCR | Installation of Pour 8 Sheet Membrane |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2014-06-30 | 2014-06-03 10:20 | -27 | 2014-05-14 07:20 | Tunnelling - Linings - Sprayed Concrete | 1000 |  | Damaged | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | During the installation of the sheet membrane at the Eastbound Launch Adit. it was found by the Subcontractor Russetts Developments that not enough of the existing sheet membrane overlap left in place form Pour 5 at Ch26.3 was available to carry out dual track welding using the LTS mobile welding machine. Enough material was available to carry out hand welding using LTD method. This was not the method proposed for the main sheet proposed under RAMS Cxxx-DSJ-C-GMS-CR094_WS108-50044, however it is used for all awkward connections as per RAMS section page 13 section 'Phase 3a 2'. Full dual welding was used where space was available outside of the pinch point at the connection between Pour 5 and 8. As LTD method had to be employed at this connection, it was decided to install the sheet membrane longitudinally to reduce the overall number of welds required.
| 01CV - Civils | Cxxx-NCR-001606 | NCR | Damage to Sheet Membrane at Eastbound Launch Invert Slab |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2014-11-30 | 2014-09-29 11:51 | -62 | 2014-05-14 07:34 | Tunnelling - Linings - Sprayed Concrete | 1000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The previously installed sheet membrane along the Eastbound Launch Adit Invert had been previously rolled and protected using sand and a thin layer of concrete. However, when the sheet membrane was exposed for installation of the required connect detail it was found that a small area approx. 05m long (Ch11.8 to 12.25) RHS was damaged so that not enough of the membrane was visible past the Kwikastrip connection bars to weld additional sheeting to.
| 01CV - Civils | Cxxx-NCR-001607 | NCR | Materials Proposal Schedule not current and regularly submitted as required by WI vol 2B |  | Crossrail | XRL | TUY - Tunnel Drive Y (Central) |  | 2014-10-30 | 2014-08-13 08:23 | -78 | 2014-05-14 15:35 | Civil - Tunnelling | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | Materials Proposal Schedule (MPS) Rev 3, Cxxx-DSJ-C4-LRG-CRG03-50038, was reviewed during the CE/ MCR surveillance carried out on 16th April 2014. The MPS was recently updated to Rev 3 on 15th April 2014 which currently sits with Crossrail for review; however Rev 2 dated 17/06/13 is still currently at a Code 2 decal with the comments yet to be closed and accepted by Crossrail. Additionally there is a ten month time lapse between Rev 2 and Rev 3 submissions, with WI vol 2B Part 13 stating: “The Contractor shall regularly submit the Material Proposal Schedule and a matrix of approvers for all materials and products, commencing within 6 weeks of the starting date”. NCR raised to ensure the MPS undergoes update and regular submission for CRL review.
| 01CV - Civils | Cxxx-NCR-001608 | NCR | Materials Proposal Schedule not being used for forward planning of materials |  | Crossrail | XRL | TUY - Tunnel Drive Y (Central) |  | 2014-10-30 | 2014-08-04 09:59 | -87 | 2014-05-14 15:41 | Civil - Tunnelling | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | During the CE/ MCR surveillance carried out on 16th April 2014, it was stated that the responsibility of raising Materials Compliance Records’ (MCR) for Crossrail acceptance lies with both the Construction team and Materials Engineer. On review of the MPS it was identified that this document is not being used for the forward planning of materials for approval to allow for timely submission and review before the incorporation into the works date. The requirements of the Works Information vol 2B clause 20.7 states “The Contractor shall develop a Materials Proposal Schedule (MPS) listing all proposed permanent works materials and products and indicating any variances from the specified materials ... The MPS shall identify .,target dates (approval, delivery, over dues)”. It was further confirmed that there was no process in place for forward planning of required materials, such as a look a-head programme. It was highlighted that material requirements are typically discussed in weekly/ fortnightly and monthly meetings; however this does not allow for timely submission and review by CRL. This is further confirmed on review of the MPS, where on 51 occasions out of a total number of 449 submitted MCR’s, the MCR ‘submission date’ is detailed as being past the ‘planned date for incorporation in the works’ (note – 51 occasions relate to Rev 1 MCR’s only).
| 01CV - Civils | Cxxx-NCR-001609 | NCR | Material Proposal Schedule not current with respect to MCR code statuses (Code 2) |  | Crossrail | XRL | TUY - Tunnel Drive Y (Central) |  | 2014-08-09 | 2014-06-25 11:44 | -45 | 2014-05-14 15:47 | Civil - Tunnelling | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | During CE/ MCR surveillance dated 16th April 2014, the MPS was reviewed for its completeness with respect to MCR Code statuses. Review of the MPS showed that only 9 out of 449 MCR’s were identified as being at a Code 2 status for periods between 3-12 months and currently remain at a Code 2 status. Under Document management Procedure Rev 2, CRL1-XRL-Z3-GPD-CR001-50001, a Code 2 decal stands for “Not accepted, revise and resubmit work may proceed subject to incorporation of changes indicated”. The 9 MCR’s were therefore not current at the time of the surveillance as the required changes were not incorporated. Works Information vol 2B clause 13.2 details the provision of contemporaneous records. Cxxx-DSJ-C-LRC-CRG03-50030 Code 2 01/03/2013 Cxxx-DSJ-C-LRC-CRG03-50046 Code 2 27/06/2013 Cxxx-DSJ-C-LRC-CRG03-50040 Code 2 05/10/2012 Cxxx-DSJ-U-LRC-CRG03-50052 Code 2 07/10/2013 Cxxx-DSJ-C-LRC-CRG03-50043 Code 2 15/05/2013 Cxxx-DSJ-C4-LRG-CRG03-50031 Code 2 16/01/2013 Cxxx-DSJ-C-LRC-CRG03-50044 Code 2 27/06/2013 Cxxx-DSJ-C4-LRC-CRG03-50026 Code 2 16/01/2013 Cxxx-DSJ-C-LRC-CRG03-50045 Code 2 27/06/2013
| 01CV - Civils | Cxxx-NCR-001611 | NCR | MCR Cxxx-DSJ-C-LRC-CRG03-50029 ½ steel Sof-fix Anix 60 Dowel used in the works at Code 3 status |  | Crossrail | XRL | TUY - Tunnel Drive Y (Central) |  | 2014-07-09 | 2014-06-10 10:12 | -29 | 2014-05-14 16:07 | Civil - Tunnelling | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | During CE/ MCR surveillance dated 16th April 2014, it was identified that MCR Cxxx-DSJ-C-LRC-CRG03-50029 ½ steel Sof-fix Anix 60 Dowel was used in the perminant works at a Code 3 status. A Code 3 decal stands for “Not Accepted. Revise and resubmit. Work may not proceed”.
| 01CV - Civils | Cxxx-NCR-001612 | NCR | Requirements of Cxxx-PMI-00533 not fully undertaken with respect to CE marking |  | Crossrail | XRL | TUY - Tunnel Drive Y (Central) |  | 2014-07-30 | 2014-07-15 14:18 | -15 | 2014-05-14 16:14 | Civil - Tunnelling | 1000 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | The Construction Products Regulations 2011 came into force in the UK in July 2013 which requires Manufacturers to draw up a Declaration of Performance for all products that are covered by a harmonised European Standard or European Technical Assessment. This is a mandatory requirement and is law under the regulations. To ensure materials being used on CRL conform to these CE Marking requirements, a Project Managers Instruction was instructed to Cxxx under PMI number 00533. The PMI stated: 'It is the Contractors responsibility to ensure that all documentation is in place to support the new regulations. Ant MCR’s which have been submitted to date, including those submitted pre July 2013 still being sourced post July 2013 are not required to be re-submitted at this time, but supporting documentation must be obtained by the Contractor and kept on record and available upon CRL’s request or for auditing purposes’. It was identified that an audit had been carried on all MCR’s previously accepted before July 2013 detailing which ones are still in use post July 2013, however it was confirmed that all materials submitted between the period of July 2013 and Nov 2013 had not undergone internal update as required by PMI 00533. NCR raised to ensure the requirements of PMI 00533 are fully met.
| 01CV - Civils | Cxxx-NCR-001613 | NCR | Damage to Area of Launch Invert Slab |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2014-11-30 | 2014-09-29 11:54 | -62 | 2014-05-16 08:59 | Tunnelling - Linings - Sprayed Concrete | 1000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During the required removal of a Kwikastrip to expose sheet membrane at CH20 RHS, a site based misinterpretation of the instruction meant that some concrete was broken out from the slab which was not required. The concrete was removed as it was believed at the time that it was required to achieve a lap to the sheet membrane for weld repair. This activity was not what was instructed and also was not covered by a current approved RAMS.
| 01CV - Civils | Cxxx-NCR-001614 | NCR | Canning Town Flyover: NP9.2VA & NP9.2VB Vertical jack positions |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2014-07-03 | 2014-06-25 11:41 | -8 | 2014-05-20 13:57 | Surveying - Instrumentation and Monitoring | 5000 |  | Incorrect Installation | Rework | 3 (3-6k) | Complete | Design Problem - Other | Completed |  | The Contractor notes that there is an issue with the position of the vertical jacks at pier NP9, due to the repositioning and installation of the jacks from the locations shown in GA-22991-222 Rev H, to the locations shown in SK-22991-55 Rev B. The change has now caused an increase in the span between NP9.1 and NP9.2 by approximately 1m, changing the jack loads considerably, the operational control, and loads imparted to the bridge deck.
| 01CV - Civils | Cxxx-NCR-001616 | NCR | VDR - Incorrect concrete levels at East Connection Thrust Block |  | Crossrail | XRL | TUY - Tunnel Drive Y (Central) |  | 2014-09-30 | 2014-08-26 17:41 | -35 | 2014-06-10 19:19 | Utilities Engineering - Water | 15000 |  | Workmanship | Use As-Is | 2 (6-60k) | Complete | Previous Construction - Problems based on previous construction errors | Completed |  | It was highlighted in NCR 01571 that the Eastern Connection Thrust restraint was poured 49mm higher than the designed levels. This non conformance reduce the space requirements between the pipe & fittings and the concrete slab which will have future maintenance implications when working on the asset
| 01CV - Civils | Cxxx-NCR-001617 | NCR | VDR - Utilities - Manhole S8 access ladder procurement failure |  | Crossrail | XRL | TUY - Tunnel Drive Y (Central) |  | 2014-08-30 | 2014-07-24 11:04 | -37 | 2014-06-14 12:27 | Civil - Sewage/Water services | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | The access ladder mounting brackets for manhole S5 are the incorrect length
| 01CV - Civils | Cxxx-NCR-001618 | NCR | CP13 Void in Concrete Collar Between 4.5mID and 3.75mID Hanging Ring |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2014-10-30 | 2014-09-01 16:58 | -59 | 2014-06-18 19:31 | Tunnelling - Linings - In-situ Concrete | 500 |  | Equipment Breakdown | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During the pour of the Concrete Collars between the 4.5mID and 3.75mID Hanging Rings over the Sump Shaft a solenoid went on the concrete pump. The Pour was abandoned half way through. Due to the time lost and the loss of workability in the concrete a void was left under a PFC Channel used to support the 3.75mID Ring as it was built as an independent Ring.
| 01CV - Civils | Cxxx-NCR-001619 | NCR | Eastbound Drive Y Invert Segment |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2014-11-30 | 2014-10-07 12:55 | -54 | 2014-06-18 05:18 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | As the Drive Y Eastbound final ring was generally found to be in good condition, it was kept in place and remedial cleaning and invert support grouting works were carried out as per Preliminary Works RAMS Cxxx-DSJ-C-GMS-CR094_WS108-50064. A slight lip was found between the invert segment and adjacent segments to the extent of 8mm on RHS and 11mm on LHS. (Please see attached pictures)
| 01CV - Civils | Cxxx-NCR-001621 | NCR | VDR - Voids in excavations |  | Crossrail | XRL | TUY - Tunnel Drive Y (Central) |  | 2014-09-30 | 2014-07-23 10:58 | -69 | 2014-06-19 18:38 | Civil - Excavation | 10000 |  | Workmanship | Rework | 2 (6-60k) | Complete | Discipline/Workmanship - Other | Completed |  | Voids created in trench/ excavation sides due to insufficient and/or no trench support being installed to avoid ground collapsing. These voids have potential for future sinking of road and footpath surfaces as compaction in accordance with the HAUC could not be achieved
| 01CV - Civils | Cxxx-NCR-001623 | NCR | Vic Dock - Washout Cover at __ |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2014-10-02 | 2014-09-23 11:01 | -9 | 2014-06-26 13:17 | Civil - Utilities Engineering | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | One of the washout covers at the Eastern Connection Pit required raising by 40mm from the last chamber section installed. Due to time constraints, this had been temporarily lifted using timbers in order that the base course of tarmac could be laid. The Subcontractor had agreed with the manufacturer that a resin-mortar infill section with both tensile and compressive strength of >40N/mm could be used and had confirmed this with the Contractor and the Project Manager. This method conforms with the HAUC specification and the material was available on site. The Project Manager's Representative on site subsequently instructed the Subcontractor to build up the 40mm using cut bricks. This does not conform with the HAUC specification but due to time constraints, the instruction was acted upon.
| 01CV - Civils | Cxxx-NCR-001624 | NCR | CP12 WB Collar Invert – Additional construction joint |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2014-09-30 | 2014-08-15 13:04 | -46 | 2014-07-05 05:59 | Tunnelling - Linings - In-situ Concrete | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The casting of the CP12 WB collar invert was stopped part way through the pour when the time since batching past three hours. The invert was poured up to the level of the SGI opening sets sill and the invert of SGI ring 40, but the wall kickers were not cast to full height. This will lead to an additional construction joint in the concrete collar. Surface retarder was applied and subsequently removed to expose the aggregate in preparation of a construction joint.
| 01CV - Civils | Cxxx-NCR-001625 | NCR | Hollow Regulating Layer |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2014-09-30 | 2014-08-15 15:41 | -46 | 2014-07-08 07:41 | Tunnelling - Linings - Sprayed Concrete | 5000 |  | Workmanship | Rework | 3 (3-6k) | Complete | Discipline/Workmanship - Other | Completed |  | Regulating layer was sprayed in EBCA between chainage 28-25 on Friday 4th of July. When carrying out a hammer test inspection it was discovered that numerous areas along the bottom of the spray area ( 1900 on a clock face) had a hollow sound. This area is where the invert regulating layer finished and was sprayed standing in the invert meaning the nozzle was pointed higher than head level which may have resulted in the defect occurring.
| 01CV - Civils | Cxxx-NCR-001626 | NCR | Hollow Regulating Layer - EBCA RHS |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2014-09-30 | 2014-08-15 15:29 | -46 | 2014-07-11 06:20 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Whilst carrying out the hammer test inspection in EBCA RHS ( 1900 on clock face) it was discovered several areas were hollow This area is where the invert regulating layer finished and was applied with the nozzleman standing in the invert spraying higher than head level resulting in a less than favourable spraying application and finish.
| 01CV - Civils | Cxxx-NCR-001629 | NCR | Out of Tolerance Rings WB Tunnel Drive Y |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2014-11-30 | 2014-10-15 16:45 | -46 | 2014-07-22 12:46 | Civil - Tunnelling | 50000 |  | Incorrect Installation | Use As-Is | 2 (6-60k) | Complete | Discipline/Workmanship - Other | Completed |  | The ring building tolerance specified within KT 10 clause KT 10.4221 (Cxxx-OVE-Z4-RSP-CR001-00001) requires "For tunnels greater than 6.0m diameter the centreline of each ring shall not depart from the design position by more than ±50mm". Following the completion of the wriggle survey for the Drive Y Westbound tunnel of section Limmo to Canary Wharf for ring numbers 1 - 1083it has identified a number of rings that exceed this tolerance. Attached is a detailed spread sheet indicating all out of tolerance rings and the whole drive survey (From Limmo to Canary Wharf) . However for further information this should be made to the full wriggle survey .
| 01CV - Civils | Cxxx-NCR-001631 | NCR | Damaged Sheet Membrane and Water-Bar |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2014-09-15 | 2014-08-20 13:09 | -26 | 2014-07-29 17:31 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Damage to water-bar and sheet membrane at Ch11 EBLA right hand side.
| 01CV - Civils | Cxxx-NCR-001632 | NCR | Damaged Sheet Membrane at Headwall |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2014-11-30 | 2014-10-23 11:50 | -38 | 2014-07-29 18:16 | Tunnelling - Linings - In-situ Concrete | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | External Phenomenon - Not Defined | Completed |  | In order to release the water that building up underneath the sheet membrane between invert slab and headwall in EBCA, DSJV propose to make a hole and pump the water out. Additionally, two damage, close to the above has been detected.
| 01CV - Civils | Cxxx-NCR-001633 | NCR | SGI Opening Set Waterproofing Bolt Hole |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2014-10-30 | 2014-08-28 10:21 | -63 | 2014-07-31 18:28 | Tunnelling - Linings - SGI Rings | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | At CP11EB, where the upper heading crown beams back plate is fixed to the SGI opening sets using a bolted connection, the back plate was incorrectly installed which meant the SGI needed to be drilled twice leaving two holes in the SGI opening set without a bolt fixing.
| 01CV - Civils | Cxxx-NCR-001634 | NCR | Water Ingress as Sprayed Membrane Trial Area |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2014-11-30 | 2014-09-29 11:56 | -62 | 2014-07-30 11:15 | Tunnelling - Linings - Sprayed Concrete | 5000 |  | Incomplete Works | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Other | Completed |  | Following spraying of Masterseal 345 in the trial section of the EB Launch Adit, areas that had previously been identified as damp developed into areas of active water ingress due to the reduction in evaporation from the regulating layer following spraying. (See attached plan for location with coordinates)
| 01CV - Civils | Cxxx-NCR-001636 | NCR | Niche 3 Collar Invert Concrete Mix |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2014-09-24 | 2014-08-28 10:26 | -27 | 2014-08-07 14:16 | Tunnelling - Linings - In-situ Concrete | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | An unapproved concrete mix was used for the casting of the Niche 3 Collar Invert. This was due to the concrete supplier running out of PFA on the day of the pour. The supplier informed DSJV of this after the collar invert was excavated. The supplier provided an alternative mix which was also C32/40, with PPFib, S4 with a 3 hour life. Concrete cubes were taken for testing.
| 01CV - Civils | Cxxx-NCR-001637 | NCR | Missed Wet Film Thickness Testing |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2014-10-30 | 2014-10-14 10:06 | -16 | 2014-08-12 14:33 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | On the night shift 07/08/14 spraying of waterproofing membrane took place at Stepney Green Eastbound Cavern headwall area. Spraying took place at two areas 1) at the crown where head wall meets lining wall, and 2) at a low level around the Z Drive final ring. As the membrane had to be sprayed using a hand pump (Picolla) and access was required around the rings a MEWP had to be used instead of the usual Titan working platform. This meant that the Shift Engineer could not be in attendance during spraying to record the wet film tests. The MEWP operator carried out some wet film tests to aid the Nozzleman but these were not recorded on a check sheet as the intention was for the Shift Engineer to record these after the spraying had been completed. This did not happen for the crown area, only for the spray applied around the Z Dive ring.
| 01CV - Civils | Cxxx-NCR-001638 | NCR | Anti Flotation Slab |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2015-01-16 | 2014-12-19 15:08 | -28 | 2014-09-10 17:52 | Civil - Civil Engineering General | 0 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The chairs supporting the top layers of reinforcement were incorrectly calculated resulting in the separation between the top and bottom of the reinforcing cage being reduced by around 20mm.
| 01CV - Civils | Cxxx-NCR-001641 | NCR | Damage to sheet membrane at headwall |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2014-10-30 | 2014-09-08 15:20 | -52 | 2014-08-18 10:21 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | At the headwall, on the left hand side, damage to the sheet membrane was detected. The area is approximately 400x200mm. Location: E86177.4302/N36270.8790
| 01CV - Civils | Cxxx-NCR-001642 | NCR | Damage to sheet mebrane at Eastbound Launch tunnel |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2014-10-30 | 2014-09-08 15:19 | -52 | 2014-08-18 10:18 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | An area of damage to the sheet membrane was detected in the Eastbound Launch Tunnel, Ch 0, Left hand side (E86119.5843/N36289.5924)
| 01CV - Civils | Cxxx-NCR-001643 | NCR | Electrolevels damage in VDP |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2014-09-29 | 2014-08-29 11:51 | -31 | 2014-08-18 10:46 | Surveying - Instrumentation and Monitoring | 500 |  | Damaged | Use As-Is | 4 (0.5-3k) | Complete | External Phenomenon - Not Defined | Completed |  | The 13-14/08/14, one rod and 2 sensors were damage by the lorries for the 200t crane in VDP. The 15/08/14 the damage to the electrolevels were fixed.
| 01CV - Civils | Cxxx-NCR-001644 | NCR | Spraying of second coat of membrane after an hour at EB Launch |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2015-12-05 | 2015-11-04 12:10 | -31 | 2014-08-29 16:53 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | During Spraying works of waterproof membrane at Ch1.5 the time gap between the application of the two coats it is not according to supplier specification.
| 01CV - Civils | Cxxx-NCR-001645 | NCR | Damaging of regulating layer due injections for water ingress |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2014-11-23 | 2014-11-05 14:16 | -18 | 2014-08-29 16:56 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Damaging of regulating layer due injections for water ingress at Ch34 RHS (86688.8822/36312.5632)
| 01CV - Civils | Cxxx-NCR-001646 | NCR | Damage of sprayed membrane. Eastbound Launch Ch31 RHS |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2014-09-09 | 2014-09-04 11:49 | -5 | 2014-08-26 13:11 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Not Defined | Completed |  | Sprayed membrane was damaged by a plant (200x200x approx.). See picture attached. Location: Eastbound Launch, Ch32.0, Axis Level, Right Hand Side
| 01CV - Civils | Cxxx-NCR-001647 | NCR | Niche 3 Headwall Cold Joint |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2014-12-25 | 2014-09-09 11:28 | -107 | 2014-08-27 12:20 | Tunnelling - Linings - In-situ Concrete | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The casting of the final concrete pour of the headwall at Niche 3 was stopped due to the concrete becoming too stiff. Therefore a cold joint is formed approximately 500mm below the crown of the tunnel.
| 01CV - Civils | Cxxx-NCR-001648 | NCR | Niche 3 rebar installation |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2014-10-30 | 2014-09-17 13:07 | -43 | 2014-08-27 20:02 | Tunnelling - Linings - In-situ Concrete | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | At the Niche 3 Headwall, two reinforcement bars were cut. The bars which were cut were bar mark 06 NF. Also there were areas where the cover to the formwork was more than 50mm on the near face.
| 01CV - Civils | Cxxx-NCR-001649 | NCR | Rock Anchor Failure |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2014-10-30 | 2014-09-19 07:49 | -41 | 2014-08-29 09:00 | Civil - Civil Engineering General | 5000 |  | Equipment Breakdown | Rework | 3 (3-6k) | Complete | Supervision - Insufficient supervision | Completed |  | The Contractor was undertaking works to prepare for the removal of the WB TBM Victoria Dock Portal. The crawler crane that is to be used was spragging into position. The crane was to sit with one track supported on top of the piles of the head wall of Victoria dock portal. There was in place temporary slab sections above the pile capping beam which were fixed to the protection slab using rock anchors and DYWIDAG bars. As the crane spragged, it appears that a number of the rock anchors holding the temporary slabs in place failed, although the contractor is currently investigating the root cause. The Contractor has raised the corresponding EWN and will propose a design solution to rectify the problem while avoiding impact on the programme. The design will be covered in and FCD
| 01CV - Civils | Cxxx-NCR-001650 | NCR | Aggregates for Sprayed Concrete |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2014-12-16 | 2014-11-05 14:22 | -41 | 2014-09-02 10:43 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Contamination | Completed |  | Oversize material up to 30mm has been found in sprayed concrete delivered by / Silvertown to Stepney Green on 27th August, resulting in a blockage to the spraying nozzle
| 01CV - Civils | Cxxx-NCR-001651 | NCR | Sagging of secondary lining at Eastbound Launch Tunnel |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2014-12-12 | 2014-10-28 11:13 | -45 | 2014-09-03 17:22 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Not Defined | Completed |  | It was observed the presence of a area with sagging of S2 layer relative to S1
| 01CV - Civils | Cxxx-NCR-001652 | NCR | Crown void during final stages of pumping Pour 4 of EB Cavern headwall |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2014-11-10 | 2014-10-14 14:30 | -27 | 2014-09-08 09:32 | Tunnelling - Linings - In-situ Concrete | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Contamination | Completed |  | Formation of crown void during final stages of pumping Pour 4 of EB Cavern headwall on 06/09/14 (refer photo attached for dimensions and extent). Approximate volume of void = 4.6 x 0.2 x 1.5 = 1.38m3
| 01CV - Civils | Cxxx-NCR-001654 | NCR | CP11 Ring Wall Void |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2014-12-16 | 2014-09-26 09:35 | -81 | 2014-09-17 09:27 | Tunnelling - Linings - In-situ Concrete | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | A void was formed in the concrete during the casting of the concrete ring wall between the 3.75m ID and 4.5m ID SGI rings on the EB side of CP11.
| 01CV - Civils | Cxxx-NCR-001655 | NCR | GRP Dowels Protruding from S2 Lining |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2016-03-31 | 2016-04-07 08:46 | 7 | 2014-09-18 05:52 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | It was found that after the spraying of the S2 layer at the East Bound Launch Adit that two GRP dowels were proud of the lining at Ch11.466 (86111.208, 36301.743, 84.891) and Ch11.433 (86111.050, 36301.385, 86.267). The dowels are currently 98mm and 124mm proud of the S2 maximum profile respectively.
| 01CV - Civils | Cxxx-NCR-001658 | NCR | Bolts used to Fix Mesh Reinforcement at EBLA Ch5-10 |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2014-12-08 | 2014-10-22 14:42 | -47 | 2014-09-24 09:25 | Tunnelling - Linings - Sprayed Concrete | 0 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Dues to the presence of a void after the spraying of the S2 P425 with Polypropylene Fibres mix at the Eastbound Launch Crown Adit. Ch 5 - 10, the area was broken back to remove the unbounded concrete in order to re-apply the SCL lining. Once the un-bonded material had been removed it was found that the mesh was loose and further fixing to the existing dowels was impossible due to the level of encapsulation present. As it was vital to prevent movement of the mesh during spraying with regard to safety and prevention of further void forming, DSJV installed a series of galvanised mechanical anchor bolts of largest diameter 20mm and total largest bolt length of 170mm. The Shift Surveyor monitored drilling to ensure that maximum embedment was 40mm and that a minimum 100mm offset was maintained from the waterproofing system (sprayed Masterseal 345). The threaded shaft of the bolt in conjunction with nuts and tying wire was used to pull the mesh back into profile and restrain it securely. Cover was then checked on the bolts to ensure minimum 60mm encapsulation. An the area was prepared for re-spraying. There was not an existing MCR in place for the bolts with regard to this form of installation/application.
| 01CV - Civils | Cxxx-NCR-001659 | NCR | Possible location of under thickness linining at EBLA |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2014-12-05 | 2014-11-25 09:52 | -10 | 2014-09-24 10:22 | Tunnelling - Linings - Sprayed Concrete | 0 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The Amberg TMS Survey asbuilt for the Eastbound Launch Adit Ch32 appear to indicate a single point on the LHS shoulder (approx 1.5m from tunnel vertical axis) giving a combined Secondary Lining thickness of 242mm when compared with the asbuilt of the regulating layer in the area. As the design thickness at this location is 250mm, the lining thickness is approximately 13-15mm under-sprayed.
| 01CV - Civils | Cxxx-NCR-001660 | NCR | Ground treatment works at VDP |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2014-12-28 | 2014-11-21 12:07 | -37 | 2014-09-29 18:11 | Geotechnical Engineering - Geotechnical Engineering - General | 0 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Procedure Problem - Lack of approval Code 1 procedures excessive | Completed |  | On Thursday Sept 25th, the Contractor received unofficial comments on rev 2.0 of VDP Eastbound tunnel eye Ground Treatment (Cxxx-DSJ-N2-RGN-CR144_PT003-50043 and Cxxx-DSJ-N2-CER-CR144_PT003-50043- Temporary Works Design Report and Certificate Victoria Dock Portal Ground Eye Treatment of Drive G EB Eye). On Friday Sept 26th, the Contractor addressed those comments in rev 3.0 of the aforementioned documents however did not get approval from the Project Manager prior to starting those works on Saturday Sept 27th. For avoidance of doubt the works were undertaken according to the rev 3.0 (ie incorporating Cxxx and the Project Manager comments)
| 01CV - Civils | Cxxx-NCR-001661 | NCR | Cross Passage Grout Testing |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2015-01-27 | 2014-10-13 16:16 | -106 | 2014-09-29 19:55 | Tunnelling - Linings - SGI Rings | 500 |  | Testing and Commissioning | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | The contractor has not met the requirements of KT10.3107 of grout testing to be carried out every five rings at CP13, CP12, CP11 or the Niche. The number of grout samples tested from each of these Cross Passages is 1, 3, 3 and 0 respectively. From these grout samples the average compressive strength of the grout was 70N/mm2 at 28 days.
| 01CV - Civils | Cxxx-NCR-001662 | NCR | Cutting of Eastbound tunnels contraction joints for Secondary Lining |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2014-10-31 | 2014-10-22 14:45 | -9 | 2014-10-01 17:11 | Tunnelling - Linings - Sprayed Concrete | 0 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | One contraction of the contraction joints in the Eastbound Cavern S1 layer (Ch 10) and 2 in the Eastbound Launch S2 layer (Ch26.18 and 35.45) have not being cut within the required 24 hour period.
| 01CV - Civils | Cxxx-NCR-001663 | NCR | Implementation of change in EBLA secondary reinforcement before submission of RFI |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2014-11-12 | 2014-10-14 09:52 | -29 | 2014-10-03 08:18 | Tunnelling - Linings - Sprayed Concrete | 0 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Reinforcement Schedule Cxxx-MMD-C4-DDJ-CR094_SH005-01125 for the Eastbound Launch Adit lists the circumferential bar marks as 8mm diameter. An issue with the supply of 8mm bar meant that the supplier replaced with 10mm. This change was agreed verbally however it took effect before raising and RFI.
| 01CV - Civils | Cxxx-NCR-001664 | NCR | Incision in sprayed waterproof membrane EBCAV Ch 1 Left hand side |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2016-01-29 | 2016-01-26 08:59 | -3 | 2014-10-03 09:58 | Tunnelling - Linings - Sprayed Concrete | 500 |  | System Defect | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | In the Eastbound Cavern, Chainage 1, Left hand side (Coordinates X: Y: Z: ) an incision (0.75m2 approx. )has been made. The purpose is to create a path for the water drain so there is no build up of pressure.
| 01CV - Civils | Cxxx-NCR-001665 | NCR | Termination Strip of PVC sheet waterproof membrane |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2015-01-12 | 2015-01-12 09:39 | 0 | 2014-10-14 14:10 | Tunnelling - Linings - In-situ Concrete | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Installation of PVC sheet membrane in Cxxx commenced in July 2013. Since then, it has been used the same termination tape in all the Eastbound locations. The termination tape uses 0.7 mm sheet in HD EN 10343 DX 51 d + Z steel, in 2m length tapes, and double welted on its edge. It is the recommended product by the supplier for use in conjunction with its waterproof membrane. This material have been used without a MCR in place and does not comply with design specification as stainless steel is the required material.
| 01CV - Civils | Cxxx-NCR-001666 | NCR | Secondary Lining Sprayed Concrete Produced After 2 hours Period of Production |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2015-01-15 | 2015-01-05 15:44 | -10 | 2014-10-16 15:44 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | In three occasions the sprayed concrete for the secondary lining has been place more than 2 hour after its batching time. According to KT20.3220, sprayed concrete can only be used up to two hours after the addition of cement provided.
| 01CV - Civils | Cxxx-NCR-001667 | NCR | Walkway Whitechapel Drive Y Eastbound |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2015-03-14 | 2014-12-01 12:58 | -103 | 2014-10-15 17:57 | Tunnelling - Walkways | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The Drive Y Eastbound temporary walkway was not installed as per drawign attached; instead to the haunches it was fixed to the cavern walls.
| 01CV - Civils | Cxxx-NCR-001668 | NCR | Use of non authorized bonding agent during primary lining reparing works |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2014-11-29 | 2014-11-20 11:07 | -9 | 2014-10-24 15:31 | Tunnelling - Linings - Sprayed Concrete | 0 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Contamination | Completed |  | A bonding agent was used during the repairing works of primary lining at some locations in Stepney Green Westbound Cavern.
| 01CV - Civils | Cxxx-NCR-001670 | NCR | Cxxx Crosspassage 14 Tiltmeter loss of data |  | Crossrail | PDP | TUY - Tunnel Drive Y (Central) |  | 2014-12-12 | 2014-12-17 11:16 | 5 | 2014-11-17 16:29 | Geotechnical Engineering - Geotechnical Monitoring | 500 |  | Equipment Breakdown | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Cxxx-PMI-00635 was issued in April 2014, instructing installation of tiltmeters to monitor effects of ground movement on the DLR River Lea Bridge due to Crosspassage 14 depressurisation works. The scope requires a monitoring frequency of one reading every 30 minutes. Between 21st October and 4th November 2014, 14days, no data was available on the deck tiltmeter installed on Pier L5 (P0), as displayed on the Contractor's database, SAI. This issues was raised at the CTC on 6th November 2014. The monitoring of structure movement on the DLR viaduct to critical to maintaining third party assurance of the control of ground movement and loss of data due to equipment failure and/or maintenance is not acceptable.
| 01CV - Civils | Cxxx-NCR-001671 | NCR | Production testing of concrete |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2015-01-16 | 2014-11-25 09:55 | -52 | 2014-11-21 14:48 | Tunnelling - Linings - In-situ Concrete | 0 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Concrete mix ref 29 C32/40 PPFib & SF supplied by __ for headwall construction at Stepney Green did not fully comply with the Specification between the dates 6th September and 22nd September 2014. The 28-day group mean fell below the target 43N/mm2 as calculated in accordance with KF10.2213 (Cxxx-JUL-S-RSP-CR094_SH005_Z-50002). Additionally, one result did not comply with the requirement for an individual test
| 01CV - Civils | Cxxx-NCR-001672 | NCR | Wick Lane - Valve Covers |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2015-12-05 | 2015-06-10 07:55 | -178 | 2014-11-24 12:13 | Utilities Engineering - Water | 1500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Valve covers on the 12" and 24" mains installed at Wick Lane have started to corrode.
| 01CV - Civils | Cxxx-NCR-001673 | NCR | Wick Lane 36" - Connection Detail 2 - hydrant too high |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2015-12-05 | 2015-06-10 07:57 | -178 | 2014-11-24 12:24 | Utilities Engineering - Water | 2500 |  | Incorrect Installation | Reject | 4 (0.5-3k) | Complete | Discipline/Workmanship - Not Defined | Completed |  | One of the hydrants on Connection Detail 2 (36") is too high.
| 01CV - Civils | Cxxx-NCR-001675 | NCR | Production testing of sprayed concrete - compressive strength |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2015-02-28 | 2015-01-31 10:17 | -28 | 2014-12-02 15:51 | Tunnelling - Linings - Sprayed Concrete | 0 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Sprayed concrete mix AAA SC50 supplied by Reader, which was used as a regulating layer at Stepney Green East Bound Launch Adit & Cavern did not fully comply with the Specification between the dates 22nd July and 18th October 2014. The 28-day compressive strength results for cores taken from the sprayed mix do not comply with Table 13 of BS EN 14487-1 - group conformity criterion 1 as illustrated by the attached summary, i.e. the 28-day group mean fell below the target 38N/mm2. Additionally, two results are marginally below the requirement for an individual test
| 01CV - Civils | Cxxx-NCR-001676 | NCR | Expansive foam installed in between tunnel rings |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2015-12-05 | 2016-01-07 13:34 | 33 | 2014-12-04 18:12 | Tunnelling - Tunnelling General | 1000 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Due to unknown steel fiber reinforced SCL thickness at Whitechapel Westbound launch chamber, and as a precautionary measure, the launch of S720 TBM included short shoves (around 300 mm.) and the cutterhead inspection and proof drilling of the ground face after each of them. This discontinuity in the tunnelling process caused the last rings installed (2980-2981-2982) to slighty separate allowing the recently injected grout to ingress into the TBM. Expansive foam was placed in the joints to avoid further entrance of grout.
| 01CV - Civils | Cxxx-NCR-001677 | NCR | Grout tube not included along the construction joint at bay 1, pour 1 - WBLA |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2015-02-15 | 2015-01-19 13:39 | -27 | 2014-12-09 18:37 | Tunnelling - Linings - In-situ Concrete | 0 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Westbound Launch adit lower pour at bay 1, Ch9 to 14, was poured last week. The grout tube joint due at the interface with invert was not installed
| 01CV - Civils | Cxxx-NCR-001678 | NCR | Sprayed Concrete Performance Requirements - Drying Shrinkage |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2015-01-22 | 2015-01-05 09:30 | -17 | 2014-12-11 12:41 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Test prisms cast from P425 PPFib secondary lining S2 mix on 03-09-14 have marginally failed to comply with the drying shrinkage requirement, maximum 0.037%. The reported length change at 28 days was 0.038% (mean of 3 prism specimens)
| 01CV - Civils | Cxxx-NCR-001679 | NCR | Performance requirements of cast in situ cocncrete - drying shrinkage |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2015-02-20 | 2015-02-03 09:52 | -17 | 2014-12-11 14:26 | Tunnelling - Linings - In-situ Concrete | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | In Table KF10-01: Performance requirements of cast concrete, a maximum 28 day drying shrinkage of 0.03% is given. Two recent tests carried on Mix 28 C32/40 SCC PPFib have failed to comply with the criteria above. The reported length change at 28 days in each case was 0.044%, and 0.038% (both based on a mean of 3 prism specimens). Following a research on the subject, DSJV have established that with small unrestrained prisms, "low shrinkage" is generallly deemed to be length change up to 0.05%, and our results are below this. Furthermore, insitu concrete shrinks less than laboratory specimens due to the restraining effect. Typically, a length change of 0.05% to 0.08% as found in laboratory specimens would equate to 0.01% to 0.03% insitu, therefore the laboratory specimens tend to yield pesimistic results, and might explain why DSJV have had difficulty achieving Crossrail's Specification
| 01CV - Civils | Cxxx-NCR-001680 | NCR | Excess of cover in Pour 1 Bay 1 North Side Westbound Launch |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2015-03-31 | 2015-02-19 16:46 | -40 | 2014-12-16 15:22 | Tunnelling - Linings - In-situ Concrete | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | In some areas it was detected an excess cover in Bay 1 and Pour 1 (up to 120mm)
| 01CV - Civils | Cxxx-NCR-001681 | NCR | Westbound Launch Pour 2 Far face mesh |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2016-01-31 | 2016-01-11 10:45 | -20 | 2014-12-16 15:28 | Tunnelling - Linings - In-situ Concrete | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | It has been detected that in some areas of the top of Bay1 Pour2 at Westbound Launch, the far face mesh has not the correcpt lap length (100mm in the worse location)
| 01CV - Civils | Cxxx-NCR-001682 | NCR | Presence of timber in the Secondary Lining Westbound LA Pour2 Bay1 |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2015-05-04 | 2016-01-11 11:04 | 252 | 2015-01-08 10:19 | Tunnelling - Linings - In-situ Concrete | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Contamination | Completed |  | A piece of timber was detected in the concrete poured at Pour2 Bay1 Westbound LA
| 01CV - Civils | Cxxx-NCR-001683 | NCR | Cold Joint in Westbound LA, Secondary Lining, Bay 1 Pour2 |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2016-01-29 | 2015-12-18 15:19 | -42 | 2015-01-08 10:23 | Tunnelling - Linings - In-situ Concrete | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | A cold joint was detected in the upper part of Bay 1 Pour 2 in the Westbound LA
| 01CV - Civils | Cxxx-NCR-001685 | NCR | Using of unapproved repair methodology and materials at Bay 2 Pour 1 WB Launch Adit |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2015-03-07 | 2015-02-11 14:34 | -24 | 2015-01-08 11:05 | Tunnelling - Linings - In-situ Concrete | 500 |  | Planning | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | Operatives were detected using unapproved materials to repair areas of Bay2 Pour 1 WB Launch Adit
| 01CV - Civils | Cxxx-NCR-001686 | NCR | Damage to sheet membrane in WB Launch Adit, North Side |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2015-02-22 | 2015-01-22 15:54 | -31 | 2015-01-08 15:43 | Tunnelling - Linings - In-situ Concrete | 500 |  | Damaged | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | At Bay 1, WB Launch Adit an area of damaged sheet membrane was detected (86081.906/36270.950;86082.192/36270.786;86082.109/36207.676;86081.867/36270.633).
| 01CV - Civils | Cxxx-NCR-001687 | NCR | Canning Town Flyover - SA0 final vertical position. |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2015-04-30 | 2015-03-24 07:45 | -37 | 2015-01-09 09:59 | Structural Engineering - Structural Engineering - General | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Not Defined | Completed |  | The permanent bearings at SA0 have been installed at a premanent level beyond the allowable limit under the CRL assessment (doc no Cxxx-OVE-R4-RGN-CR144-50001), which stated that the movement of the deck relative to the transition slab would be no more than 1.5mm vertically during Engineering Hours, and 1.0mm vertically during Traffic Hours. The permanent bearings have been installed and have a current vertical position of -1.0mm for SA0.1, and -1.5mm for SA0.4. The breach is therefore 0.5mm on SA0.4. SA0.1 is within the acceptable tolerable limit. The reasoning for this was due to the compressability in the elastomer being larger than expected, and the pre-load being removed after grouting causing a minor extension in the bearing componentry. This is only an issue at SA0 where the tolerances are tighter than all other bearings. The compression in the bearings is as the manufacture expected for a new bearing.
| 01CV - Civils | Cxxx-NCR-001688 | NCR | CP12 Drainage Pipework |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2015-12-05 | 2015-10-01 09:01 | -65 | 2015-01-10 09:15 | Tunnelling - Linings - In-situ Concrete | 500 |  | Material | Repair | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | Non conforming material used in permanent works. For the Drainage Ducting in CP12 Cast In-Situ Invert Concrete Slab (see attached Drawing No. Cxxx-OVE-C4-DDD-CR001_Z-23417) a Non-Conforming Material was used. See attached MCR for the Material that was used for the Drainage Ducting.
| 01CV - Civils | Cxxx-NCR-001689 | NCR | Cross Passage 14 - Ground Treatment works - SGI fissures |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2015-12-05 | 2016-01-04 12:28 | 30 | 2015-01-13 17:56 | Civil - Civil Engineering General | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During the CP14 surface ground treatment drilling operations of Saturday 10th January 2015, specifically during the drilling of the WB collar TAM number 65, a hard layer/material was found at approximately 33m depth and identified as the tunnel lining due deviation of the borehole. The drilling operation was immediately stopped and the borehole relocated within 500mm radius of the current location as per TW Design Report Cxxx-DSJ-N2-RGN-CRG03-50206 procedure (see attached sketch for new location). Inspection of the tunnel lining in the WB tunnel DSJV identified two locations where the drill had penetrated the SGI units (approximately 20cm long x 2 cm wide) at the SGI plate on ring number 233 as per the attached sketch and pictures. Both penetrations and water ingress have already been sealed from the tunnel by the installation of temporary wedges and a back grouted steel plate (see attached pictures).
| 01CV - Civils | Cxxx-NCR-001691 | NCR | Damage of BA anchors in Bay 3 Westbound Launch Adit |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2015-03-01 | 2015-02-20 10:08 | -9 | 2015-01-15 16:03 | Tunnelling - Tunnelling General | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During the installation of the sheet membrane in the north side of the Westbound Launch Adit the skirts of two BA Anchors were damage (86101.662/36258.162 and 86102.770/36257.186).
| 01CV - Civils | Cxxx-NCR-001692 | NCR | Westbound Cavern Bay 4 Pour 1 honeycomb |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2016-12-05 | 2016-01-11 10:44 | -329 | 2015-01-15 16:40 | Tunnelling - Linings - In-situ Concrete | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | In the bottom of the Westbound Cavern Bay 4, Pour 1 a honeycomb has been encountered due to loss of grout
| 01CV - Civils | Cxxx-NCR-001693 | NCR | CP 11 Sump Secondary Lining Concrete Finish |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2015-01-29 | 2015-01-23 16:18 | -6 | 2015-01-15 17:33 | Tunnelling - Linings - In-situ Concrete | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Upon striking the CP11 sump secondary lining formwork, a poor visual finish as shown in the attached photos was observed. As a result cores were taken from the lining to investigate the structural qaulity of the concrete and have proved sufficient. 4 cores from the CP 11 Sump Secondary Lining have been tested and the __ report is attached (Pictures also attached). The reported values for compressive strength are at least 75% of the Characteristic Cube Strength (40N/mm2) therefore the concrete is compliant in accordance with KF10.2207 f) iii). Furthermore, the average core density is 2374 Kg/m3 which is as one would expect, and in excess of the performance requirement of 2300 kg/m3 and this, combined with the satisfactory visual appearance of the cores suggests there is no issue with durability. Note: a similar finish, albeit not as bad, was present in at CP13 Sump Lining and CP10 Collar Side Walls.
| 01CV - Civils | Cxxx-NCR-001695 | NCR | CP Dry Shrinkage Testing Frequency |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2015-02-20 | 2015-02-03 09:57 | -17 | 2015-01-20 14:34 | Tunnelling - Linings - In-situ Concrete | 500 |  | Testing and Commissioning | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The contractor has not tested the dry shrinkage of the cross passage cast in situ concrete once per month as detailed in the ITP Cxxx-DSJ-C-ITP-CRG03-50022 Rev 05.
| 01CV - Civils | Cxxx-NCR-001696 | NCR | STG Lift Shaft Starter bars |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2015-03-31 | 2015-02-12 09:50 | -47 | 2015-01-20 18:03 | Civil - Civil Engineering General | 5000 |  | Supervision/Management | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | In line with the responses to RFI’s 001051 and 001074, the starter bars for the lift shaft walls 7, 8, 9 and 10 to be cast into B5 level were replaced by an equivalent “Kwikastrip”. The Kwikastrip has been found to be out of position by 35mm. While looking into it the Project Manager requested further investigative work to expose any existing rebar and confirm the connection into the structural beam at the pit bottom. As a result of these investigative works no rebar has been found which means that there is not sufficient structural integrity with the beam.
| 01CV - Civils | Cxxx-NCR-001697 | NCR | STG Internal works - B5 level Wall 6 honeycomb |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2015-05-30 | 2015-05-26 09:00 | -4 | 2015-01-20 18:17 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | After pouring and striking of wall 6 at level B5 honeycombing is visible on the face above the kicker (see attached pictures). Grout loss at the joint between the kicker and the formwork caused the honeycombing. Excessive compaction using external vibrators would have aided for the grout loss.
| 01CV - Civils | Cxxx-NCR-001698 | NCR | STG Internal works - B3 Level Wall 10 __ out of position |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2015-02-19 | 2015-02-16 11:06 | -3 | 2015-01-20 18:31 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | At level B3, wall 10, __ channel for the connection into the existing props was to be installed as per drawing Cxxx-JUL-S-DDD-CR094_SH005-00427 in accordance with KF10.3208 and KF10.3104. The __ channel is out of position by approximately 126mm as per the attached sketch.
| 01CV - Civils | Cxxx-NCR-001699 | NCR | STG - Internal Works - Lift Shaft Level B5 to B4 pour |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2015-12-05 | 2015-06-08 13:35 | -180 | 2015-01-20 18:46 | Civil - Civil Engineering General | 0 |  | Equipment Breakdown | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | For the pouring of the lift shaft walls (GL7-8) from level B5 to B4, the concrete deliveries were scheduled to arrive at 1 o'clock and 2 o'clock. This would have allowed for the concrete to be placed in the wall, allow for the waiting time due to the controlled pour and place the next layer within the hour as per specification Cxxx-JUL-S-RSP-CR0994_SH005_Z-50002, KF10.3210. The 1 o'clock delivery was refused entrance to site as the vehicle had a fault which rendered in non-complaint with the vehicles requirements. The 2 o'clock delivery arrived at 2.05 and discharge ended at 2.50. Due to a fault at the plant the next load did not come until 4.45 which exceeded the 1hr time stated in the spec.
| 01CV - Civils | Cxxx-NCR-001700 | NCR | STG - Internal works - Lift Shaft pour Level B5-B4 |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2015-02-19 | 2015-02-19 16:39 | 0 | 2015-01-20 19:10 | Civil - Civil Engineering General | 0 |  | Supervision/Management | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During the pouring of the lift shaft walls from level B5 to B4 a skip was used with the concrete falling in excess of the 2m failing to comply wit the requirement as specified in KF10.3210. The trunk of the skip could not be fed down lower into the wall because of its flexible nature and the narrow nature of the wall. A tremmie pipe was scheduled by the subcontractor for delivery but did not arrive on time. Its absence was not noted by the subcontractor team until after the concrete had been batched. A tremmie pipe should have been made available for the pour and the concrete should not have been confirmed until all items were in position to successfully carry out the placement of the concrete.
| 01CV - Civils | Cxxx-NCR-001703 | NCR | Joint of pour1/pour2 Bay 8 North side Westbound Cavern |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2015-02-27 | 2015-02-09 15:54 | -18 | 2015-01-28 11:20 | Tunnelling - Linings - In-situ Concrete | 0 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Contamination | Completed |  | The profile of radial Joint of pour1/pour2 Bay 8 North side Westbound Cavern was very irregular (see pictures attached)
| 01CV - Civils | Cxxx-NCR-001704 | NCR | Westbound Secondary Lining Curing Agent for striking shutters |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2015-03-19 | 2015-03-06 14:16 | -13 | 2015-02-02 10:39 | Tunnelling - Linings - In-situ Concrete | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Curing agent has not been used after the striking of shutters in some of the pours of the in situ cast secondary lining. WB Launch: Bays 1, 2 and 3 WB Cavern: Bay 1 Pour 1 and 2;Bay 2 Pour 1 and 2; Bay 3 Pour 1 and Bay 4 Pour 1 and 2
| 01CV - Civils | Cxxx-NCR-001705 | NCR | Incorrect extension of Sheet Membrane at Westbound Cavern |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2016-03-31 | 2016-02-15 11:49 | -45 | 2015-02-02 10:49 | Tunnelling - Tunnelling General | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The required overlap between the sheet membrane and sprayed membrane is a minimum of 300mm. A section of approximately 5m, at the interface of Bay10 and Bay 9, will only achieve 200mm approximately.
| 01CV - Civils | Cxxx-NCR-001706 | NCR | Non Stainless Steel bars to secure base of Pour 2 Westbound Cavern |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2016-01-29 | 2015-12-16 14:00 | -44 | 2015-02-02 11:05 | Tunnelling - Linings - In-situ Concrete | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Non Stainless Steel Bars were employed to secure the base of Pour 2 Westbound Cavern
| 01CV - Civils | Cxxx-NCR-001707 | NCR | Concrete over starting bars at VDP |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2015-03-04 | 2015-02-27 15:25 | -5 | 2015-02-02 12:52 | Civil - Civil Engineering General | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | during the pouring of the invert section of the Drive G Eastbound arrival craddle at Victoria Dock Portal (please see Cxxx-DSJ-N2-NOX-CRG03-50298 for further details) some concrete covered Cxxx starting bars on the side of the walls.
| 01CV - Civils | Cxxx-NCR-001708 | NCR | WB Cavern Secondary Lining - DSJV Quality Inspections |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2015-03-26 | 2015-02-11 14:27 | -43 | 2015-02-09 09:07 | Tunnelling - Linings - SGI Rings | 0 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The ITP checksheet for reinforcement and sheet membrane for Bay 1, Pour 1 - pre pour inspection covered various elements of the works and a signature box is provided against each activity. At the completion of the dayshift the DSJV Inspector checked the works and was satisfied with the progress. At this point the checksheet was signed off by the Inspector showing that the works were complete however some activities continued into the following nightshift. Works Information- Part 20: Quality Management (CRL1-PDP-W-XWI-CRG03-00020) The Contractor shall be responsible for demonstrating that the works have been completed in accordance with the requirements of the Works Information and shall produce records that provide clear evidence of conformance
| 01CV - Civils | Cxxx-NCR-001709 | NCR | STG Internal Works - B1 and B2 levels Wall 6 __ out of position |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2015-12-05 | 2015-06-08 13:38 | -180 | 2015-02-06 09:59 | Shafts - Shafts General | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | At levels B1, B2 and B3, the __ for the connection into the existing props was to be installed as per drawing Cxxx-JUL-S-DDD-CR094_SH005-00427 in accordance with KF10.3208 and KF10.3104. The __ channels are out of position by approximately 101, 119 and 74mm for B1, B2 and B3 respectively. See attached sketches.
| 01CV - Civils | Cxxx-NCR-001710 | NCR | CP10 Concrete Floor Level |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2015-06-24 | 2015-04-16 14:08 | -69 | 2015-03-25 18:48 | Tunnelling - Linings - In-situ Concrete | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | At CP10, there are sections of the concrete invert which were cast out of tolerance. It was agreed that the floor was to be cast between 75-150mm below FFL (Cxxx-RFI-002121) and the concrete tolerances are +-20mm for the floor within the cross passage (Cxxx-RFI-002253). The attached as built survey shows the sections of the cross passage which are out of tolerance >170mm below FFL, these are highlighted in red. Note the sections of the floor which are <55mm below FFL will be scabbled back on site.
| 01CV - Civils | Cxxx-NCR-001711 | NCR | Lift Shaft internal and External wall concrete |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2015-12-05 | 2015-06-10 15:13 | -178 | 2015-02-16 15:38 | Shafts - Excavation | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Honeycombing has been found on wall 10 (see attached picture)
| 01CV - Civils | Cxxx-NCR-001713 | NCR | Out of Tolerance Rings EB & WB Tunnel Drive G |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2015-04-28 | 2015-04-21 15:39 | -7 | 2015-04-14 08:01 | Tunnelling - Alignment | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The ring building tolerance specified within KT 10 clause KT 10.4221 (Cxxx-OVE-Z4-RSP-CR001-00001) requires "For tunnels greater than 6.0m diameter the centreline of each ring shall not depart from the design position by more than ±50mm". Following the completion of the wriggle survey for the Drive G Eastbound (Rings 1-518) and Westbound (rings 1-523) it thas identified a number of rings that exceed this tolerance. Attached are the detailed spread sheets indicating all out of tolerance rings. However for further information this should be made to the full wriggle surveys (Cxxx-DSJ-C4-RGN-CR144_WS155-50028 and Cxxx-DSJ-C4-RGN-CR144_WS155-50029).
| 01CV - Civils | Cxxx-NCR-001715 | NCR | Out of Tolerance Rings EB & WB Tunnel Drive Z |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2015-12-05 | 2015-06-25 16:31 | -163 | 2015-04-13 12:24 | Tunnelling - Alignment | 5000 |  | Incorrect Installation | Rework | 3 (3-6k) | Complete | Discipline/Workmanship - Other | Completed |  | The ring building tolerance specified within KT 10 clause KT 10.4221 (Cxxx-OVE-Z4-RSP-CR001-00001) requires "For tunnels greater than 6.0m diameter the centreline of each ring shall not depart from the design position by more than ±50mm". Following the completion of the wriggle surveys for the Drive Z Eastbound (rings 1-1699) and Westbound (rings 1-1751) tunnels from Stepney Green to Pudding Mill Lane it has been identified a number of rings that exceed this tolerance. Attached are the detailed spread sheets indicating all out of tolerance rings. However for further information this should be made to the full wriggle survey(Cxxx-DSJ-C4-RGN-CR094_PT002-50009 and Cxxx-DSJ-C4-RGN-CR094_PT002-50013).
| 01CV - Civils | Cxxx-NCR-001717 | NCR | Out of Tolerance Rings EB & WB Tunnel Drive Y Canary Wharf to Stepney Green |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2015-12-05 | 2015-10-05 13:18 | -61 | 2015-04-13 12:25 | Tunnelling - Alignment | 10000 |  | Incorrect Installation | Rework | 2 (6-60k) | Complete | Discipline/Workmanship - Other | Completed |  | The ring building tolerance specified within KT 10 clause KT 10.4221 (Cxxx-OVE-Z4-RSP-CR001-00001) requires "For tunnels greater than 6.0m diameter the centreline of each ring shall not depart from the design position by more than ±50mm". Following the completion of the wriggle surveys for the Drive Y Eastbound and Westbound tunnels Canary Wharf to Stepney Green it has been identified a number of rings that exceed this tolerance. Attached are the detailed spread sheets indicating all out of tolerance rings. However for further information please refer to the full wriggle surveys (Cxxx-DSJ-C4-RGN-CR094_WS108-50011 & Cxxx-DSJ-C4-RGN-CR094_WS108-50012)
| 01CV - Civils | Cxxx-NCR-001718 | NCR | CP14 surface piezometers |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2015-05-31 | 2015-05-13 11:47 | -18 | 2015-02-24 13:47 | Civil - Geotechnical Engineering | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | At the moment, the surface grouting works are on going at the CP14 location. The Contractor and the Project Manager are aware from the design development period and the beginning of the works of the high possibility for the piezometers or well points being blocked by the grout due to their close proximity with the grouting works area. After inspection and manual dips of the piezometers the situation is as follows: PV04080 – Response Zone Partially blocked - Manual dip from GL 27.90m – Original depth from GL 32.00m PV04081 – Response Zone Partially blocked- Manual dip from GL 38.60m – Original depth from GL 39.00m PV04082 – Response Zone Partially blocked - Manual dip from GL 47.30m – Original depth from GL 48.00m PV04083 – Response Zone Fully blocked - Manual dip from GL 6.20m – Original depth from GL 31.50m PV04084 – Response Zone Fully blocked - Manual dip from GL 11.20m – Original depth from GL 35.00m PV04085 – Response Zone Partially blocked - Manual dip from GL 41.50m – Original depth from GL 45.00m PV04086 – Response Zone Fully blocked - Manual dip from GL 22.60m – Original depth from GL 32.00m PV04087 – Response Zone Fully blocked - Manual dip from GL 20.40m – Original depth from GL 32.00m PV14G – Response Zone Fully blocked - Manual dip from GL 12.50m – Original depth from GL 40.00m In tunnel piezometers and surface ejectors well points will be checked on due course and a separate NCR will be raised if required.
| 01CV - Civils | Cxxx-NCR-001719 | NCR | Rebate in B1 and B2 Walers |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2015-05-15 | 2015-03-16 14:59 | -60 | 2015-02-27 13:46 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Part of the rebate in the prop along gridline 7 at the B1 and B2 level has been cast 100mm low. Attached sketch refers.
| 01CV - Civils | Cxxx-NCR-001720 | NCR | Waler cast above design level |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2015-05-15 | 2015-03-16 15:02 | -60 | 2015-03-02 09:20 | Civil - Civil Engineering General | 500 |  | Planning | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The top of the reinforcement previously cast within the walers at the B2 level has been found to encroach into the cover of the slab to be cast above.
| 01CV - Civils | Cxxx-NCR-001721 | NCR | Setting out of box GL 9-10 |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2015-05-23 | 2015-04-20 09:10 | -33 | 2015-03-09 16:27 | Shafts - Shafts General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Personnel Error - Inattention to detail | Completed |  | For the setting of box GL 9-10 the measurements have been taken from the edge of the beam. However, in drawing Cxxx-JUL-S-DDA-CR094_SH005-00223, the setting out measurement are taken from the gridline. As a consequence the box out is 41mm out of position. (See attached sketch)
| 01CV - Civils | Cxxx-NCR-001722 | NCR | SCL Performance Testing During Construction – Limmo Backshunt Tunnels Primary Lining |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2015-12-05 | 2015-12-18 17:10 | 13 | 2015-03-26 15:22 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Compressive Strength Testing Between ch.27-51m(measured from Aux. shaft) of the WB Backshunt tunnel no test results exist for the compressive strength testing. DSJV to take 2 sets of 3 cores from the lining for testing. With one set of cores taken from the invert. Estimated fibre & aggregate rebound This test was not carried out during construction at Limmo. DSJV to include results of fibre content tests in the handover packages to demonstrate compliance with the performance requirement. Water permeability This test was not carried out during construction at Limmo. DSJV to take 2 sets of 3 cores per tunnel for water permeability testing to BS EN 12390-8. Concrete drying shrinkage Due to delays outside of DSJV’s control, the moulds required for drying shrinkage were late in delivery and as a consequence only two tests were taken per mix (these are appended to the MCRs). DSJV to include results from SCL works at Stepney Green which used identical mixes. Modulus of elasticity No result were submitted relating to testing during construction: DSJV to submit 5no results on cores taken from the tunnel. Flexural Strength is covered in NCR 001723
| 01CV - Civils | Cxxx-NCR-001723 | NCR | SCL Performance Testing During Construction – Limmo Backshunt Tunnels Primary Lining |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2015-06-30 | 2015-05-06 12:46 | -55 | 2015-03-26 15:18 | Tunnelling - Linings - Sprayed Concrete | 0 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Flexural strength Insufficient tests carried out during the construction at Limmo (Compressive strength testing, estimated fibre & aggregate rebound, water permeability, concrete drying shrinkage, modulus of elasticity is covered in NCR 001722
| 01CV - Civils | Cxxx-NCR-001724 | NCR | Cold Joint in Bay 5 |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2015-12-05 | 2015-06-08 13:41 | -180 | 2015-03-30 12:53 | Shafts - Shafts General | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | 2.4m x 3.6m of Bay 5 lacking sufficient concrete to form correct level. Concrete is 100mm in the area shown on the attached drawing.
| 01CV - Civils | Cxxx-NCR-001725 | NCR | CP14 - P3 Surface Piezometer installation |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2015-04-13 | 2015-04-01 10:36 | -12 | 2015-03-30 17:25 | Civil - Geotechnical Engineering | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | In relation to the additional surface piezometers required to be installed at CP14 as per PMI-00888, the Contractor informs that at P3 (see attached sketch for location references – P3 is a double installation piezometer - Intermediate and Lower Aquifer), during the removal of the borehole casing and grouting up of the standpipe required for the Lower Aquifer readings, the PVC pipe was damaged and broken at a depth were recovery or reinstallation is not feasible.
| 01CV - Civils | Cxxx-NCR-001726 | NCR | CP12 Floor Levels |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2015-04-14 | 2015-04-29 12:33 | 15 | 2015-03-31 12:20 | Tunnelling - Linings - In-situ Concrete | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Some parts of the CP12 floor levels are <50mm below the FFL, therefore out of tolerance.
| 01CV - Civils | Cxxx-NCR-001727 | NCR | B4 D-Wall Coupler's |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2015-12-05 | 2015-06-08 14:35 | -180 | 2015-04-22 16:51 | Shafts - Shafts General | 0 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | A total of 38no bottom couplers were casted with in the diaphragm wall below the designed level, thus interfering with the bottom layer of steel within the waler beam. A total of 2no top couplers have been damaged during construction works.
| 01CV - Civils | Cxxx-NCR-001728 | NCR | B4 Waler Starter bar to be re-drilled |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2015-12-05 | 2015-06-26 09:19 | -162 | 2015-04-27 16:13 | Shafts - Shafts General | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The starter bar being cast too low has resulted in a clash with the false work that is being installed for the B4 waler works.
| 01CV - Civils | Cxxx-NCR-001729 | NCR | BR Starter Bar Location |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2015-12-05 | 2015-06-10 12:25 | -178 | 2015-04-27 16:22 | Shafts - Shafts General | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Starter bars were to be cast in to the prop of the basement roof for the next contractor installing the ground level walls, as per setting out on Cxxx-JUL-S-DDA-CR094_SH005-00226_Rev C02 The starter bars were cast in the wrong location, as shown on attached sketch.
| 01CV - Civils | Cxxx-NCR-001730 | NCR | B4 waler couplers outside of beam |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2016-01-29 | 2016-01-26 13:58 | -3 | 2015-04-28 12:02 | Shafts - Shafts General | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The screw bars that are to be cast in the B4 waler at GL4/E cannot be connected to the previously cast couplers due to the position these couplers were cast in, in the previous beam. BM 310ae shown on drawing Cxxx-JUL-SDDL- CR094_SH005-02649 is cast too close to the d-wall to allow the screw bar to be connected to it. There is also an issue with BM27ae Cxxx-JUL-S-DDL-CR094_SH005-02648. One of the couplers is cast in a position that results the connecting screw bar being outside the edge of the beam and 1 no screw bar being situated in the cover zone on the edge of the beam.
| 01CV - Civils | Cxxx-NCR-001731 | NCR | B4 waler beam connection with d-wall |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2015-12-05 | 2015-06-26 09:06 | -162 | 2015-04-28 12:08 | Shafts - Shafts General | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The attached picture shows the lcation where the existing B4 waler beam connects to the section being currently constructed at GL4-5/B. BM 309 is coupled at the construction joint. The screw bar connecting to one of the BM309 couplers is clashing with a d-wall coupler and cannot be installed.
| 01CV - Civils | Cxxx-NCR-001732 | NCR | Calibration certificates for the pressure gauges being used to undertake double seam weld testing were out of date. |  | Crossrail | XRL | TUY - Tunnel Drive Y (Central) |  | 2015-12-05 | 2015-07-06 10:13 | -152 | 2015-04-29 13:43 | Tunnelling - Tunnelling General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | During a planned Crossrail surveillance which looked at sheet waterproof membrane installation on 08th April 2015, a request was made for the calibration certificates for pressure gauges being used to undertake double seam weld testing; whithese were provided post surveillance. On review of the calibration certificate which was provided in __, it was highlighted that the pressure gauge was calibrated on 08th January 2014 by Bautech Labor GmbH, a UKAS equivalent calibration laboratory. UKAS Publication LAB 21 ‘Calibration and Measurement Traceability for Construction Materials Test Equipment’ details under Appendix A that ‘pressure / vacuum gauges’ shall be calibrated at ‘yearly’ intervals by a ‘UKAS laboratory’ in accordance with BS EN 837-1:1998 ‘Pressure Gauges. Bourdon Tube Pressure Gauges. Dimensions, Metrology, Requirements and Testing’. The pressure gauge being used on site had been calibrated by a UKAS equivalent __ laboratory against an equivalent standard to BS EN 837-1 where the yearly calibration frequency requirement applies; as such the calibration of the pressure gauge being used on site to undertake weld seam testing expired 08th January 2015, as such this NCR was raised to ensure the gauges are appropriately calibrated and added to the calibration schedule. Regular calibration of pressure gauges is important to ensure the safety and accuracy of the gauge, as general use of equipment can potentially cause the instrumentation to drift.
| 01CV - Civils | Cxxx-NCR-001733 | NCR | Drive Y EB 4273 Ring step |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2015-12-05 | 2015-12-18 17:11 | 13 | 2015-05-05 09:49 | Tunnelling - Linings - Precast | 10000 |  | Incorrect Installation | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | While shoving ring no. 4275 in Drive Y EB it was spotted that ring no. 4273 dropped slightly when leaving the tailskin. This resulted in the following approximate steps : Crown: 5cm Shoulder right: 4cm Shoulder left: 2,5cm Knee left: 7cm Knee right: 2,5cm These steps exceed KT10.4219 building tolerances of bored tunnels.
| 01CV - Civils | Cxxx-NCR-001734 | NCR | Insufficient cover in near face steel |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2016-03-31 | 2016-03-22 16:31 | -9 | 2015-05-07 16:03 | Tunnelling - Linings - In-situ Concrete | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During the in situ cast secondary lining works an area in the Westbound Launch, South wall, Bay 2, Pour 2, has been identified with insufficient cover of the near face steel.
| 01CV - Civils | Cxxx-NCR-001737 | NCR | Box-Out in Wall, B1-Roof |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2015-12-05 | 2015-06-23 15:52 | -165 | 2015-05-18 13:34 | Shafts - Excavation | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The Box-Out in wall 6 has been casted 100mm higher than the design position
| 01CV - Civils | Cxxx-NCR-001738 | NCR | Starter Bars missing from Slab for Wall 15, Level B4 to Suffit Level B3 Soffit |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2015-12-05 | 2015-06-10 15:18 | -178 | 2015-05-18 14:28 | Shafts - Shafts General | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Starter Bars missing from Slab for Wall 15 Level B4 to Suffit Level B3 Soffit
| 01CV - Civils | Cxxx-NCR-001739 | NCR | Drive G Westbound FSC surface finish |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2015-12-05 | 2015-11-09 16:38 | -26 | 2015-05-20 14:40 | Tunnelling - Linings - In-situ Concrete | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Not Defined | Completed |  | The Contractor notes that the central finish of the section cast during 19th dayshift and nightshift in Drive G Westbound covering rings 481-501 does not meet the standards specified in M&W Specification KF10 Cxxx-OVE-Z4-RSP-CR001-00002.
| 01CV - Civils | Cxxx-NCR-001740 | NCR | EB Bay 4 Cast In situ repairs |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2016-12-27 | 2016-01-11 10:42 | -351 | 2015-06-10 16:22 | Tunnelling - Linings - In-situ Concrete | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The concrete in the lower pour in Bay 4 contains a void at the top right hand corner and another in the centre at the joint to the invert slab. The joint between the invert slab and the wall panel and the top of the pour also show signs of poor compaction. The attached marked up photograph refers.
| 01CV - Civils | Cxxx-NCR-001742 | NCR | Production testing of sprayed concrete - compressive strength |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2015-07-03 | 2015-06-01 11:06 | -32 | 2015-05-22 13:28 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | KT20.2202 d) The strength of sprayed concrete measured by cores taken from the works shall be acceptable if the compressive strength results comply with Table 13 of BS EN 14487-1 90-day compressive strength test results for cores taken from mix P425 Plain (S1) on 8th September 2014 do not comply with Table 13 - group conformity criterion 1 as illustrated by the attached summary
| 01CV - Civils | Cxxx-NCR-001743 | NCR | Out of Tolerance Rings EB Drive Y Stepney Green to Whitechapel |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2016-01-31 | 2016-01-06 10:53 | -25 | 2015-05-28 08:44 | Tunnelling - Tunnelling General | 5000 |  | Incorrect Installation | Rework | 3 (3-6k) | Complete | Discipline/Workmanship - Other | Completed |  | The ring building tolerance specified within KT 10 clause KT 10.4221 (Cxxx-OVE-Z4-RSP-CR001-00001) requires "For tunnels greater than 6.0m diameter the centreline of each ring shall not depart from the design position by more than ±50mm". Following the completion of the wriggle surveys for the Drive Y Eastbound (rings 2456-2988) and Westbound (rings 2444-2971 ) tunnels from Stepney Green to Whitechapel it has been identified a number of rings that exceed this tolerance. Attached are the detailed spread sheets indicating all out of tolerance rings. However for further information this should be made to the full wriggle surveys.
| 01CV - Civils | Cxxx-NCR-001744 | NCR | WB Cavern Southern Wall Bay 10 Pour 1 LHS corner damage |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2015-12-05 | 2015-07-01 11:04 | -157 | 2015-06-01 14:14 | Tunnelling - Tunnelling General | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | After installing the shutter on Bay 10 pour 1, expanding foam was used to seal the stop end. . As a result when the stop end and foam were removed a void had formed along the water bar.
| 01CV - Civils | Cxxx-NCR-001747 | NCR | Void formed in top corner of Wall 15 next to beam on GL10 |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2015-12-18 | 2015-10-08 12:52 | -71 | 2015-06-15 12:49 | Shafts - Shafts General | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Void formed in top corner of Wall 15 next to beam on GL10
| 01CV - Civils | Cxxx-NCR-001748 | NCR | Cover to BM329 |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2015-12-18 | 2015-08-10 08:58 | -130 | 2015-06-15 13:20 | Shafts - Shafts General | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | BM 306ae is protruding at such an angle from the existing beam on B4 that when BM 329 is in place there is 10mm cover. Area in question shown in attached photographs and drawing.
| 01CV - Civils | Cxxx-NCR-001749 | NCR | Out of Tolerance Rings EB & WB Tunnel Drive Y (Whitechapel to Liverpool Street section) |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2015-12-18 | 2015-12-18 17:01 | 0 | 2015-06-15 13:55 | Tunnelling - Alignment | 10000 |  | Workmanship | Rework | 2 (6-60k) | Complete | Discipline/Workmanship - Other | Completed |  | The ring building tolerance specified within KT 10 clause KT 10.4221 (Cxxx-OVE-Z4-RSP-CR001-00001) requires "For tunnels greater than 6.0m diameter the centreline of each ring shall not depart from the design position by more than ±50mm". Following the completion of the wriggle surveys for the Drive Y Eastbound (rings 2989-3909) and Westbound (rings 2972-4010) tunnels from Whitechapel station to Liverpool St. Station it has been identified a number of rings that exceed this tolerance. Attached are the detailed spread sheets indicating all out of tolerance rings. However for further information this should be made to the full wriggle survey.
| 01CV - Civils | Cxxx-NCR-001750 | NCR | Ducting not installed in prop/waler for drainage B1-B4 |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2016-03-31 | 2016-04-07 09:16 | 7 | 2015-07-01 16:16 | Shafts - Shafts General | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The Stepney Green drainage plan drawing’s Cxxx-JUL-P-DDA-CR094_SH005-00532/533/534/535/536 show a down pipe and floor gully to be installed adjacent to the lift shaft on levels B1-B4, ducting would be cast in to the beam (as per DRY-CRL RFI-Cxxx-00546.) to facilitate the installation of 100mm diameter down pipe at a later date. When casting the waler’s and prop’s from level B1-B4 the contractor has not installed the two ducts to enable the installation of a down pipe and floor gully, only one duct has been installed on each level in this location.
| 01CV - Civils | Cxxx-NCR-001751 | NCR | Grout tube missing in the EBCV south wall |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2015-09-16 | 2015-06-29 11:20 | -79 | 2015-06-18 10:17 | Tunnelling - Tunnelling General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | In the joint along the In situ cast and sprayed secondary lining a grout tubes is required (drawings Cxxx-MMD-C4-DDD-CR094_SH005_Z-00050 and 51) In bays 2, 4 and 6 of south wall in the Eastbound Cavern these grout tube was not installed.
| 01CV - Civils | Cxxx-NCR-001752 | NCR | CP14 EB SGI Opening Set 16mm Holes |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2015-08-12 | 2015-07-27 11:55 | -16 | 2015-06-23 19:14 | Tunnelling - Linings - SGI Rings | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | At CP14 EB, 2no holes were drilled through the SGI opening sets S1 and S2a above the sill at the locations marked in the attached sketch.
| 01CV - Civils | Cxxx-NCR-001753 | NCR | CP14 EB Collar Invert Pour >3hrs |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2015-12-18 | 2015-08-19 14:12 | -121 | 2015-06-26 12:08 | Tunnelling - Linings - In-situ Concrete | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | For the construction of the cross passage collar, the invert is cast along with the sidewall kickers. To allow for this, the concrete needs to be sufficiently stiff enough to stand within the sidewall kicker formwork without slumping and heaving up through the sill of the collar opening. For this reason Concrete Mix 13a is used instead of Concrete Mix 28, as Mix 13a has less retarder then Mix 28. According to the MCR mix 13a is noted as a “3 Hour Mix” and is expected to be stiff after 3 hours. For the casting of CP14 EB collar invert, after 3 hours from batching the concrete was still too fluid to allow for the sidewalls to be cast without the concrete slumping and causing the sill of the opening to heave. The concrete was kept in the remixer on rotation to allow more time to pass so that the concrete started to stiffen to a consistency to allow the sidewalls to be poured. At 3hours 40mins from batching, the concrete was suitable for pouring the sidewalls and the pour was completed. The face of the concrete was still workable and the concrete was very fluid at this time, as recorded by videos which will be shown to the CRL field engineers. A sample of the concrete was taken after the pour was completed and supplementary cubes were made to be tested.
| 01CV - Civils | Cxxx-NCR-001754 | NCR | CP06 invert cast with prior to SGI touch up paint fully dried |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2015-12-18 | 2015-08-11 09:54 | -129 | 2015-06-26 16:10 | Tunnelling - Linings - SGI Rings | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | For the casting of the invert bay 1 at CP06, defects on the SGI which are below the concrete invert were touched up by paint, but the paint was not fully dry before the concrete was poured. There was also some dirt stuck to parts of the wet paint.
| 01CV - Civils | Cxxx-NCR-001755 | NCR | Incorrect application of sprayed membrane at EB Cavern Bay 1 North wall |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2016-01-31 | 2016-01-07 16:01 | -24 | 2015-07-01 16:43 | Tunnelling - Tunnelling General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Worker not correctly instructed | Completed |  | Operatives applied the sprayed applied membrane, EB Cavern Bay 1 North wall, using a gloved hand and not as per the Specification KW20.
| 01CV - Civils | Cxxx-NCR-001756 | NCR | Cast in-situ concrete repairs in the wb cavern and launch adit |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2016-03-31 | 2016-04-07 15:07 | 7 | 2015-07-02 13:51 | Tunnelling - Tunnelling General | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The Westbound South wall Cavern and Launch Adit cast insitu bays have been completed. Defects in the concrete have been found in a few bays. The defects found are in accordance with the specification [BS EN 13670:2009] and KF 10.3221. The majority of bays require general repairs to the concrete surface due to bolts and bolt holes used for the installation of the concrete shuttering. However there are areas within the cavern; bay 4 and bays 8-11 as well as all of the Launch Adit which will require further attention. This NCR discusses the specific remediation’s intended for the launch adit and bays 4, 8-11 in the cavern.
| 01CV - Civils | Cxxx-NCR-001757 | NCR | CP14 EB Collar Walls - King Cross Batching Plant Concrete |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2015-08-31 | 2015-08-05 13:01 | -26 | 2015-07-06 14:47 | Tunnelling - Linings - In-situ Concrete | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The concrete used for the CP14 EB Collar Walls was Mix 13a batched at the Kings Cross __ batching plant as opposed to the Stepney Green Plant or Canning Town Plant.
| 01CV - Civils | Cxxx-NCR-001759 | NCR | Over-pour of concrete in HAM Access Shaft |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2015-10-30 | 2015-08-06 12:44 | -85 | 2015-07-20 12:13 | Civil - Utilities Engineering | 5000 |  | Workmanship | Rework | 3 (3-6k) | Complete | Discipline/Workmanship - Other | Completed |  | The final section on the HAM Access shaft was found not to fit due to the existing concrete surround having been poured approximately 40mm too tight to fit the closure piece in.
| 01CV - Civils | Cxxx-NCR-001760 | NCR | Lower Compound Kerb Levels - Wick Lane |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2016-02-28 | 2016-01-05 08:05 | -54 | 2015-07-20 12:25 | Civil - Utilities Engineering | 1000 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Reinstated kerbs and footpath in the lower compound at Wick Lane (post-replacement of 12"and 24" water and gas) have subsequently been found to be at the incorrect level for the surface (tarmac) reinstatement.
| 01CV - Civils | Cxxx-NCR-001761 | NCR | Drive G eastbound and westbound tunnels, paved section, final surface level and catchpit locations |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2015-12-18 | 2015-12-17 12:06 | -1 | 2015-07-23 14:48 | Civil - Civil Engineering General | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The Contractor refers to the final tolerances achieved of the first stage concrete works achieved in Drive G tunnels (including catchpits; please refer to the attached documents) for the paved sections . Some sections higher than the design level have been scarified as agreed on site with the Project Manager representatives. The contractor seeks clarification from the Project Manager of any additional repair works to be done. The Contractor also informs the Project Manager that another document will be submitted for the hand-lay sections of Drive G tunnels.
| 01CV - Civils | Cxxx-NCR-001762 | NCR | HAM and Wick - Access Shaft Temp Works |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2015-12-11 | 2015-08-25 13:05 | -108 | 2015-08-05 17:43 | Civil - Utilities Engineering | 5000 |  | Workmanship | Rework | 3 (3-6k) | Complete | Discipline/Workmanship - Worker not correctly instructed | Completed |  | Several sheet piles in the HAM and Wick Access Shaft have been mistakenly cut - 8no. total: 5no in the NE corner, 3no. in the SW corner - after frame 2 was removed. This does not conform with the backfilling sequence of the Access Shaft and will ultimately result in 8no. shortened piles being extracted. Due to the number and location of the cuts, the Contractor does not deem this to have an implication to the structural stability of the shaft.
| 01CV - Civils | Cxxx-NCR-001763 | NCR | Drive G UTX checks |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2015-12-11 | 2015-09-29 11:35 | -73 | 2015-08-06 13:10 | Civil - Civil Engineering General | 10000 |  | Testing and Commissioning | Use As-Is | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The Contractor refers to the attached summary of the UTX checks carried out in Drive G and Z and seeks confirmation of acceptance from the Project Manager. The tests include both mandrel and camera tests (in those where 70 mm clearance with the mandrel test was not achieved). In most cases the camera test proved 80 mm. clearance in the UTXs as per the attached lists. Videos and Pictures of the tests are available. For the avoidance of doubt, the Contractor suggests no further actions are required.
| 01CV - Civils | Cxxx-NCR-001764 | NCR | Concrete Cube Failure in HAM Pump Shaft Weir |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2015-12-11 | 2015-10-26 08:16 | -46 | 2015-08-06 11:15 | Civil - Utilities Engineering | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Not Defined | Completed |  | The 28 day cube results for concrete poured on the 08-07-15 for the Weir in the HAM Pump Shaft have failed to reach the required strength of 40N/mm^2. The cubes crushed at 34.4N/mm and 32.7N/mm respectively.
| 01CV - Civils | Cxxx-NCR-001765 | NCR | Westbound Cavern Headwall- Void in crown |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2015-08-25 | 2015-09-14 09:55 | 20 | 2015-08-11 10:07 | Tunnelling - Linings - In-situ Concrete | 500 |  | Incomplete Works | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During the final stages of the final pour (4) in the headwall the concrete pressure built up at the concrete port which required the pour to be terminated before the crown had been filled. A void remains at the top of pour 4 with a depth of 150-250mm either side of the crown of the cavern.
| 01CV - Civils | Cxxx-NCR-001766 | NCR | Damage of sheet membrane and water bar at EB Cavern Southwall Bay 4 Pour 1 |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2016-01-21 | 2016-01-11 11:03 | -10 | 2016-01-07 07:17 | Tunnelling - Tunnelling General | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During the break out of Bay 4 pour 1, the invert sheet membrane and water bar were damaged in a couple of areas.
| 01CV - Civils | Cxxx-NCR-001767 | NCR | CP13 WB Catch Pit Leak 2015.08.16 |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2015-09-03 | 2015-09-22 08:54 | 19 | 2015-08-20 16:20 | Tunnelling - Linings - In-situ Concrete | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | On Sunday 16th August 2015 there was a leak formed at the CP13WB catch pit. The leak was at the joint between the top of the box out, which was installed to allow the auger boring pipes to be installed, and the concrete sidewall. There was water ingress, with a very small amount of fines. See the attached photo. On Monday 17th august 2015 a specialist sub-contractor was on site, and the leak was sealed by injecting a polyurethane resin using injection packers in two locations.
| 01CV - Civils | Cxxx-NCR-001768 | NCR | Westbound Backshunt Missing Injectable Grout Tubes |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2016-01-31 | 2016-01-07 11:18 | -24 | 2015-10-20 10:27 | Civil - Civil Engineering General | 500 |  | Material | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | The Contractor informs the Project Manager that during Pour 1 of Westbound Backshunt, two injectable grout tubes were not installed as per drawing Cxxx-MMD-C4-DDD-CR144_SH011-05050. See attached for details of the two tubes and the Product Datasheet of the material to be used to backfill (Cemrok Easi Flow). The Contractor informs that such material is a non shrink, high strength cementitious grout.
| 01CV - Civils | Cxxx-NCR-001769 | NCR | Limmo Upper Ring Beam - Inspection Level Slab Starter Bars |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2016-03-31 | 2016-03-23 11:07 | -8 | 2015-09-08 18:12 | Civil - Civil Engineering General | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | As per drawing Cxxx-JUL-S-DDL-CR144_SH011-01654 Storage Area Roof Slab (North), Starter Bars for the storage area slab are to be cast within the Upper Ring Beam. Due to the walkway created along the ring beam, for safety issues the 80 units Starter Bars closer to the D-Wall face (see attached sketch for location) have been cut.
| 01CV - Civils | Cxxx-NCR-001770 | NCR | D-Y WB & EB Collars - Spraying Out of Specification Time |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2015-09-28 | 2015-09-24 12:44 | -4 | 2015-09-14 16:02 | Civil - Civil Engineering General | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | While carrying the works for the Short Notice Change SCL Void Infill in Backshunts and Collars (Cxxx-DSJ-C4-CCN-CRG03-50038) in Drive Y Eastbound and Westbound collars on the 27th of August, the concrete was sprayed 3 hours after the batching time, exceeding 1 hour the allowed time in KT20 Specifications. As stated in KT20.3220: “Mixed base concrete may be used up to two hours after the additional of cement provided that the sprayed concrete can be applied satisfactory”. The concrete was tested and was within the slump range. In addition two panels were sprayed, to allow for early strength tests to be taken and compressive strength cores.
| 01CV - Civils | Cxxx-NCR-001771 | NCR | Drive Y Westbound Ring 4009 Backgrouting |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2015-12-01 | 2015-11-09 16:42 | -22 | 2015-09-20 11:10 | Tunnelling - Grouting | 10000 |  | Incomplete Works | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Other | Completed |  | As per the last ring before entering Liverpool Station of Drive Y Westbound (ring 4009), it is potentially not grouted. The annulus, in particular the invert, was not completely fluffed up / sealed.
| 01CV - Civils | Cxxx-NCR-001772 | NCR | Canary Wharf – High Point in First Stage Concrete |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2015-12-01 | 2015-12-18 17:07 | 17 | 2015-09-22 16:27 | Civil - Civil Engineering General | 1000 |  | Material | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Due to a poor workmanship while pouring First Stage Concrete at Canary Wharf Eastbound (see attachment for survey) the finished level concrete was higher than Design specifications.
| 01CV - Civils | Cxxx-NCR-001773 | NCR | CP10 Drainage Pipe Blockage |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2016-01-31 | 2016-01-29 09:07 | -2 | 2015-09-30 19:13 | Tunnelling - Linings - In-situ Concrete | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During the installation of the ACO drain at CP 10, the seal around the ACO drain to the discharge pipe was not sealed correctly and HP 45 leaked into the discharge pipe. This has solidified and is blocking the discharge pipe. Due to the 90⁰ bend at the bottom of the discharge pipe, it is not possible to break out the mortar without causing substantial damage to the pipe and the concrete in the invert.
| 01CV - Civils | Cxxx-NCR-001774 | NCR | Incorrect Lap lenght |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2016-01-03 | 2015-10-13 14:00 | -82 | 2015-10-05 11:29 | Tunnelling - Tunnelling General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During the preparation of the Cast in situ to Sprayed secondary lining joint, the reinforcement was not cut to the Eurocode 2.
| 01CV - Civils | Cxxx-NCR-001775 | NCR | Environmental-S61 |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2015-11-18 | 2015-10-07 13:52 | -42 | 2015-10-07 11:16 | Consents - Environment | 500 |  | System Defect | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Misunderstand the definition of the requirement | Completed |  | DSJV obtained a derogation to the existing S61, the City of London for TBM removal works at Moorgate without prior agreement from Crossrail.
| 01CV - Civils | Cxxx-NCR-001776 | NCR | Damage to EB invert slab |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2016-01-16 | 2015-12-18 15:23 | -29 | 2015-10-08 10:03 | Tunnelling - Tunnelling General | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Supervision - Other | Completed |  | When removing the temporary works for the TBM transit and the access ramps to drive Y and drive Z, the invert slab was damages (small grooves) and some steel fixings remain in the invert slab.
| 01CV - Civils | Cxxx-NCR-001777 | NCR | Stepney Green Drainage Ductile iron pipe B5 level |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2016-04-11 | 2016-02-15 11:45 | -56 | 2016-01-12 16:11 | Civil - Drainage | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Drawing Cxxx-JUL-P-DDA-CR094_SH005-01565 Rev C01 (mark up attached) specifies a 225mm diameter ductile iron drainage pipe to be installed beween the westbound pit bottom and the sump at B5 level. The outlet of the pipe into the sump to be +77.200m. An incorrect pipe of 270mm ductile iron was installed and cast in place in November 2012 without fall and IL of +77.15m.
| 01CV - Civils | Cxxx-NCR-001778 | NCR | Stepney Green Diaphragm Wall GL-6 to GL-10 |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2016-01-10 | 2016-01-13 12:21 | 3 | 2015-10-12 15:27 | Shafts - Shafts General | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Reinforcement Cover at certain panels of the D-Wall is not as per requirement.
| 01CV - Civils | Cxxx-NCR-001779 | NCR | Overlap on MS345 application in the EB cavern inverts |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2016-01-13 | 2016-01-08 09:57 | -5 | 2015-10-15 15:56 | Tunnelling - Tunnelling General | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Contamination | Completed |  | Weakened bond between the sprayed and sheet membrane.
| 01CV - Civils | Cxxx-NCR-001780 | NCR | Level B1 Corbels Misalignment |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2016-03-31 | 2016-02-15 11:28 | -45 | 2015-10-26 09:23 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Previous Construction - Improper As Built | Completed |  | As per Cxxx-RFI-002456, The Contractor informs the Project Manager of the misalignment on the position of the Level B1 Corbels’ couplers.
| 01CV - Civils | Cxxx-NCR-001781 | NCR | Pour Quality Joint Westbound Auxiliary Shaft (Pour A1) |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2016-03-31 | 2016-01-08 15:12 | -83 | 2015-10-26 10:25 | Civil - Civil Engineering General | 500 |  | Material | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The Contractor informs the Project Manager of the poor quality joint between the top and bottom invert pours of A1 in the westbound of the Auxiliary shaft.
| 01CV - Civils | Cxxx-NCR-001782 | NCR | Westbound Launch Tunnel Hollow area |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2016-01-24 | 2016-01-11 09:51 | -13 | 2015-10-26 16:48 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Not Defined | Completed |  | Post application of the S1 secondary lining, in Bay 1 Westbound Launch, a hammer test was carried out in the crown and identified two voids along the leading edge.
| 01CV - Civils | Cxxx-NCR-001783 | NCR | Concrete supplied from Victoria Deep plant |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2016-03-31 | 2016-03-10 12:28 | -21 | 2015-10-26 16:52 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Lack of procedure | Completed |  | Shotcrete was ordered from Victoria Deep Batching plant on the 23/10/2105, for the S1 Secondary Lining and Stepney Green. The batching plant has been used as a backup plant for both the primary lining work and the 1st stage of secondary lining works. MCR for the Secondary Lining mixes does not include a certificate for the Victoria Deep Batching plant.
| 01CV - Civils | Cxxx-NCR-001784 | NCR | WBLA bay 1 - Concrete used in Permanent Works that was batched with re-cycled water |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2016-02-07 | 2016-01-07 15:55 | -31 | 2015-11-09 15:36 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Incomplete Works | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Contamination | Completed |  | Concrete used in Permanent Works was batched with recycled water, that could have been of a higher pH resulting in poorer quality of concrete.
| 01CV - Civils | Cxxx-NCR-001785 | NCR | WBLA bay 2 - Hollow areas and subsequent damage to the Masterseal. |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2016-02-07 | 2015-12-18 15:25 | -51 | 2015-11-09 15:41 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During inspection of the substrate post spraying of the S1 layer and pre installation of steel in bay 2; 3 hollow patches where discovered.
| 01CV - Civils | Cxxx-NCR-001786 | NCR | WBLA bay 3 and D wall - concrete sprayed not achieving the required EAS gain (J2) |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2016-02-07 | 2016-01-07 15:54 | -31 | 2015-11-09 15:50 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The S1 layer that was sprayed on 5/11/15 on bay 3 and the D wall did not achieve adequate early strength. The exclusion zone was not lifted until the strength had reached 1N/mm^2
| 01CV - Civils | Cxxx-NCR-001787 | NCR | WBLA bay 3 - Hollow areas and subsequent damage to the Masterseal |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2016-02-09 | 2015-12-18 15:26 | -53 | 2015-11-11 14:28 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Not Defined | Completed |  | During inspection of the substrate post spraying of the S1 layer and pre installation of steel in bay 3; a hollow patch was discovered. The area where broken out for remediation; during this process the Masterseal 345 layer was damaged, slight water ingress was observed through one of the damaged points
| 01CV - Civils | Cxxx-NCR-001788 | NCR | WB Backshunt Collar - Incomplete Concrete Filling at crown |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2016-03-31 | 2016-03-08 08:49 | -23 | 2015-11-13 11:42 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | During the pouring of the Limmo Main Shaft - WB Backshunt Collar - and by the time when the last load were poured, the subcontractor noticed the lack of concrete to complete the crown section. The batching plant was inmediately informed however, and due to the timing runing late in the evening, the additional load required was not posible to be sent. Consequently the concrete filling at head of tunnel in westbound backshunt collar was incompleted and an approximately 30mm high by 300/400mm wide void was left visible from the main shaft.
| 01CV - Civils | Cxxx-NCR-001789 | NCR | WBLA Bay 3 and D wall – Poor early strength |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2016-02-27 | 2016-01-07 15:40 | -51 | 2015-11-19 10:48 | Tunnelling - Tunnelling General | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Not Defined | Completed |  | Concrete used in the S2 layer, and remediation of the S1 hollow patch in bay 3, possessed early strength characteristics below the J2 curve
| 01CV - Civils | Cxxx-NCR-001790 | NCR | WBLA bay 3 Coverage of the steel of the cast in situ was found to be lower than tolerance |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2016-03-31 | 2016-03-22 16:43 | -9 | 2015-11-19 10:51 | Tunnelling - Linings - In-situ Concrete | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Coverage of the steel of the cast in situ was found to be lower than tolerance (40mm)
| 01CV - Civils | Cxxx-NCR-001791 | NCR | WBLA bay 1-2 contraction joint |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2016-02-27 | 2015-11-30 16:21 | -89 | 2015-11-19 10:57 | Tunnelling - Tunnelling General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | The contraction joint between bays 1-2 was not cut within 24 hours as designed.
| 01CV - Civils | Cxxx-NCR-001792 | NCR | Conveyor Bracket left in Cast in situ concrete Eastbound Cavern Bay 4 |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2016-02-28 | 2016-01-08 09:56 | -51 | 2015-11-30 10:38 | Tunnelling - Tunnelling General | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During the construction of the cast in situ concrete, a conveyor bracket was not removed
| 01CV - Civils | Cxxx-NCR-001793 | NCR | Secondary Lining missing 8mm starter bars , Bay 2 North Wall. |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2016-02-28 | 2015-12-04 15:30 | -86 | 2015-11-30 10:59 | Tunnelling - Tunnelling General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | There a 4 no. 8mm starter bars missing from the Cast in situ concrete, Bay 2 North Wall. Eastbound Cavern
| 01CV - Civils | Cxxx-NCR-001796 | NCR | SCL out of spec (530 flow) EB Cavern Bay 4 |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2016-01-19 | 2016-01-14 16:54 | -5 | 2016-01-05 12:24 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Insufficient quantity of material to do the job | Completed |  | During the spraying of the S2 layer in the EBCavern Bay 4, an additional 1 – 2m3 of concrete was required to complete the advance. On arrival at site the flow test was carried out and recorded at 530mm.
| 01CV - Civils | Cxxx-NCR-001797 | NCR | Nails on termination strip have rusted |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2016-03-18 | 2016-03-02 13:15 | -16 | 2016-01-05 12:43 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Contamination | Completed |  | A number of the nails securing the stainless steel termination strip on the Westbound Cavern South Wall have become rusty over time.
| 01CV - Civils | Cxxx-NCR-001800 | NCR | Limmo Main Shaft Missing Couplers in the Patch |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2016-03-18 | 2016-02-22 13:25 | -25 | 2016-01-07 12:14 | Civil - Civil Engineering General | 500 |  | Incomplete Works | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Not Defined | Completed |  | The Contractor informs the Project Manager of the missing couplers in the patch. (Bar mark 53E / Drawing No. Cxxx-JUL-S-DDL-CR144_SH011-01675 section D-D).
| 01CV - Civils | Cxxx-NCR-001801 | NCR | WBLA S2 Hollow Areas |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2016-05-31 | 2016-04-26 15:02 | -35 | 2016-01-11 10:56 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Material | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | On completion of the S2 lining a hammer test was completed and identified approximately 11 voids. Further investigation required by contractor.
| 01CV - Civils | Cxxx-NCR-001802 | NCR | Blocked UTX pipes in Haunch WB Pit bottom |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2016-03-31 | 2016-02-15 11:42 | -45 | 2016-01-14 16:43 | Civil - Civil Engineering General | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | 4nr UTX pipes cast into the haunch of the Westbound pit bottom as marked up in attached Cxxx-JUL-S-DDA-CR094_SH005-00211 Rev C03 and Cxxx-JUL-S-DDL-CR094_SH005-02683_Rev_C01 are filled with concrete. The pipes are 110mm OD and 100mm ID. The length of each pipe is about 3000mm at a slight angle. Pictures attached.
| 01CV - Civils | Cxxx-NCR-001803 | NCR | Void Present in EBCav Bay 8 and Damage to MS345 |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2016-03-19 | 2016-02-15 11:12 | -33 | 2016-01-19 13:12 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | On completion of the S1 Layer in the EB Cavern Bay 8, a hammer test was carried out to determine if the lining had fully bonded. At approximately Chainage 9 on the LHS a void was present. The area was broken back to the extent of the void and until sound concrete was found. During the break out an area of the MS345 was damaged.
| 01CV - Civils | Cxxx-NCR-001804 | NCR | Damage to sheet membrane EB Launch |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2016-03-19 | 2016-01-26 09:01 | -53 | 2016-01-19 13:24 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Insufficient information made available to the worker. | Completed |  | On completion of the S1 sprayed secondary lining in the EB Launch Adit, a hammer test was carried out to identify if there were any voids present. It was noted that there was a potential void on the south wall knee at chainage 0 (D'Wall). It was agreed that the area should be broken back. During the breaking out of the void, the break damaged the sheet membrane.
| 01CV - Civils | Cxxx-NCR-001805 | NCR | Stepney Green, BFK21 lower early strengths (EB Cavern) |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2016-04-24 | 2016-04-22 09:53 | -2 | 2016-01-25 11:45 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | During the construction of the EB Cavern the contractor has used the 21 mix for the Secondary Lining S2 Layer. Two 28d compressive strength test results for cores are below the performance requirement of the specification (KT.20) and British Standard. The two failed test results are applicable to the S2 layer sprayed in the EBCV Bays 1&2 (cores taken 15/12/15) and EBCV Bays 3&4 (cores taken 18/12/15).
| 01CV - Civils | Cxxx-NCR-001806 | NCR | Pressure relief drainage Eastbound Cavern Stepney Green |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2016-04-25 | 2016-04-01 15:06 | -24 | 2016-01-26 13:11 | Civil - Civil Engineering General | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The pressure relief drainage within the EBCV has been cut level with the first stage concrete slab.
| 01CV - Civils | Cxxx-NCR-001807 | NCR | Wrong Inclination Main Shaft Eastbound First Stage Concrete Drainage Pipe |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2016-03-28 | 2016-02-24 10:54 | -33 | 2016-01-27 15:54 | Civil - Civil Engineering General | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Conflicting information on drawings | Completed |  | The Contractor informs the Project Manager of a discrepancy with the design drawings (Cxxx-SKC-P-DDA-CR144_SH011-00533 Rev. C01 and Cxxx-OVE-D-DDD-CR001_Z-53231 Rev. C02). The drainage pipe for the First Stage Concrete in Eastbound Main Shaft has been installed with the gradient on as per drawing Cxxx-SKC-P-DDA-CR144_SH011-00533 Rev. C01.
| 01CV - Civils | Cxxx-NCR-001808 | NCR | EB Drainage pipe (ductile iron) |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2016-03-31 | 2016-03-10 10:48 | -21 | 2016-01-29 17:02 | Civil - Civil Engineering General | 5000 |  | Incorrect Installation | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Drawing Cxxx-JUL-P-DDA-CR094_SH005-01556 (mark up attached) specifies a 225mm diameter ductile iron drainage pipe to be installed between the EB pit bottom and the sump at B5 level. The incorrect pipe of 275mm ductile iron was installed and cast in place in November 2012 with ILs of 81.730m and 81.715m
| 01CV - Civils | Cxxx-NCR-001809 | NCR | Missing Grout Pipes Westbound Cavern North Wall |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2016-05-03 | 2016-04-06 10:02 | -27 | 2016-02-03 10:50 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During the construction of the Westbound Cavern North wall cast in situ the contractor did not install adequate number of feeder/breather pipes, to allow for the re-injectable tubes in the sprayed secondary to be terminated in the termination boxes.
| 01CV - Civils | Cxxx-NCR-001810 | NCR | S2 Voids EB Cavern & EB Launch Adit |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2016-05-09 | 2016-03-02 13:10 | -68 | 2016-02-09 10:48 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Material | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Post application of the S2 sprayed concrete a hammer test was completed in both the Eastbound Cavern and Launch Adit. It has been noted that on completion of the hammer test, voids have been identified in both the Eastbound Cavern (Bays 2, 4 & 8) and in the Eastbound Launch Adit (Dwall).
| 01CV - Civils | Cxxx-NCR-001812 | NCR | CP14 Blocked Ducting |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2016-03-11 | 2016-03-01 08:51 | -10 | 2016-02-10 13:27 | Civil - Tunnelling | 5000 |  | Damaged | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During the leak sealing works inside the cross passage, TamPur 150 was introduced into one of the cable ducts. This has solidified and is blocking the duct. Due to the 90 bend at the bottom of the duct, it is not possible to break out the TamPur 150 without causing substantial damage to the ducting and the concrete in the cross passage invert.
| 01CV - Civils | Cxxx-NCR-001813 | NCR | MS345 Damage Bay 3 Crown Westbound Cavern |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2016-05-14 | 2016-03-01 16:42 | -74 | 2016-02-14 18:13 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During the clean up of the trailing edge in Bay 3, the MS345 was damage by a jigger point.
| 01CV - Civils | Cxxx-NCR-001814 | NCR | BFK18 - Running mean of 28 day strengths |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2016-05-17 | 2016-04-26 14:58 | -21 | 2016-02-17 16:21 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Not Defined | Completed |  | The 28 day running mean results have not all reached the 28 day/34 N requirement for 18 mix. The average for the EB Cavern is 35.3N however the averages for bay 1= 32.3 N & 35 N, bay 2 = 39.33 N, bay 3 = 36.16 N, bay 4 = 30.13 N & 33 N, bay 5 = 35.1 N, bay 6 = 41.36 N.
| 01CV - Civils | Cxxx-NCR-001815 | NCR | Longitudinal cracks in the crown of the WB Cavern |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2016-05-17 | 2016-04-25 11:07 | -22 | 2016-02-17 16:19 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Material | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During hammer testing of the WB Cavern several cracks have been found within the crown of bays in the WB Cavern. The size of the cracks exceeded the definition of a hairline crack according to KT20.2201 (0.3mm) and therefore require repair.
| 01CV - Civils | Cxxx-NCR-001816 | NCR | Missing Drainage Openings in Core Walls |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2016-04-17 | 2016-03-21 11:09 | -27 | 2016-02-16 14:25 | Civil - Civil Engineering General | 500 |  | Incomplete Works | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The Contractor informs the Project Manager that one drainage opening in each of the core walls have been left out. See attached drawing for openings location.
| 01CV - Civils | Cxxx-NCR-001817 | NCR | Westbound collar concrete pour 2 |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2016-05-19 | 2016-04-12 15:39 | -37 | 2016-02-19 08:40 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The bottom area of the pour is filled with grout instead of concrete. See attached photo.
| 01CV - Civils | Cxxx-NCR-001818 | NCR | Stepney Green B5 Wall Starter Bars/Kwikastrip |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2016-05-22 | 2016-03-10 11:57 | -73 | 2016-02-22 15:25 | Civil - Civil Engineering General | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Please see attached mark up of drawing Cxxx-JUL-S-DDA-CR094_SH005-00211 rev C03. The pull out bars/kwikastrip have been exposed and a survey has found that; The Pull Out Bars/kwikastrip that have been installed are H10 @ 200 c/c with 400mm protruding. The Cxxx reinforcement drawing shows H12 starter bars @ 200 c/c. Can Cxxx please advise. In addition some of the H10 bars have been damaged and cannot be used.
| 01CV - Civils | Cxxx-NCR-001819 | NCR | Spraying out of spec concrete with a slump of 530mm in the S1 layer of Bay 7 |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2016-05-28 | 2016-03-21 09:18 | -68 | 2016-02-28 07:38 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Not Defined | Completed |  | During the spraying of the S1 layer in bay 7, 3m3 of concrete which was tested and confirmed to be out of specification by the accredited tester (__) was used to spray with. The specification for concrete used in SCL works is that the slump should be between 540mm and 670mm, with a temperature between 15 and 35 degrees Celsius. In this case the second batch from the wagon was measured at 530mm and 19 degrees; therefore the slump was short by 10mm.
| 01CV - Civils | Cxxx-NCR-001821 | NCR | Stepney Green D-Wall Repairs B4 and B5 levels on Cxxx Scope |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2016-05-31 | 2016-05-16 08:58 | -15 | 2016-03-02 17:47 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Reinforcement Cover at certain panels of the D-Wall is not as per requirement.
| 01CV - Civils | Cxxx-NCR-001824 | NCR | fsc, catchpit 3c |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2016-05-31 | 2016-04-15 19:35 | -46 | 2016-03-07 09:52 | Civil - Civil Engineering General | 1000 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Design Problem - Conflicting information on drawings | Completed |  | The catchpit Type 3C in the WB tunnel at CH 7421.750 / CH 8064.050 and in the EB tunnel at CH 8045.750 were installed in dim 1200x400, different than the drw.Cxxx-OVE-D-DDD-CR001_2-53211 states 1400x400. Therefore the Type 3C catchpits are too short by 200mm.
| 01CV - Civils | Cxxx-NCR-001826 | NCR | Misalignment of Level B1 Corbel Dowel Bars |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2016-05-07 | 2016-05-06 07:49 | -1 | 2016-03-07 12:55 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The Contractor informs the Project Manager that there is an incorrect alignment of well void tubes in four B1 corbels. See ‘Attachment 1’ and ‘Attachment 2’ for further details.
| 01CV - Civils | Cxxx-NCR-001827 | NCR | Repair to MS345 in Bay 8 WB Cavern |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2016-06-05 | 2016-04-27 12:00 | -39 | 2016-03-07 16:30 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During the preparation of Bay 8 WB Cavern, it was noted that the MS345 had been damaged/debonded from the sheet membrane at the trailing edge of Bay 9.
| 01CV - Civils | Cxxx-NCR-001828 | NCR | Void around grout tube EB Cavern Crown |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2016-06-05 | 2016-05-06 12:26 | -30 | 2016-03-07 16:43 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Contact grout tube were installed onto the MS345 in the event of possible voiding. The feeder/breather tubes were positioned at the end of the 12m bay. During the application of the S2 the grout tubes have moved crating a small void.
| 01CV - Civils | Cxxx-NCR-001829 | NCR | EB Cavern S1 Layer Bay 4 Compressive Strengths |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2016-06-08 | 2016-05-05 15:22 | -34 | 2016-03-10 13:38 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The Compressive strength results for the Eastbound Cavern S1 Layer Bay 4 have failed with a result of 35.6MPa
| 01CV - Civils | Cxxx-NCR-001830 | NCR | WB Cavern S1 Layer Bay 2 Compressive strengths |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2016-06-08 | 2016-05-20 13:57 | -19 | 2016-03-10 13:42 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | The 28day Compressive strength results for the Westbound Cavern S1 Layer Bay 2 have failed with a result of 28.7MPa Update : 90day compressive strength results for Westbound cavern s1 layer bay 2 are compliant at 42.1MPa - Use as is
| 01CV - Civils | Cxxx-NCR-001831 | NCR | Eastbound Launch Headwall leak |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2016-06-08 | 2016-05-06 12:24 | -33 | 2016-03-10 13:55 | Tunnelling - Linings - In-situ Concrete | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Not Defined | Completed |  | During a joint inspection of the Eastbound Launch adit, it was noted that there is a potential water leak between the two head wall pours. (Axis level)
| 01CV - Civils | Cxxx-NCR-001834 | NCR | EB Cavern S2 layer Bays 1&2 - Compressive Strengths |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2016-06-05 | 2016-04-18 09:19 | -48 | 2016-04-06 14:01 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The 90day Compressive strength results for the Eastbound Cavern S2 Layer Bays 1&2 have failed with a results of 28.17Mpa (sprayed on 15/12/2015) and 36.20Mpa (sprayed on 17/12/2015)
| 01CV - Civils | Cxxx-NCR-001835 | NCR | EB Cavern S2 layer Bays 3&4 - Compressive Strengths |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2016-06-05 | 2016-04-18 09:21 | -48 | 2016-04-06 14:03 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The 90 day compressive strength results for the Eastbound Cavern S2 Layer in Bays 3&4 have failed with a result of 31.87Mpa (sprayed on 15/12/2015)
| 01CV - Civils | Cxxx-NCR-001836 | NCR | WB Cavern S2 Layer Bays 1&2 Compressive strengths |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2016-07-12 | 2016-06-15 15:03 | -27 | 2016-04-13 13:08 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The 28day Compressive strength results for the Westbound Cavern S2 layer in Bays 1&2 have failed with a result of 24.13MPa (sprayed on 23/02/2016)
| 01CV - Civils | Cxxx-NCR-001837 | NCR | Missing B5 Beam Connections |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2016-06-06 | 2016-05-25 11:40 | -12 | 2016-04-06 11:46 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Not Defined | Completed |  | The Contractor informs the Project Manager that there are missing beam connections between beams B4 and B10 as highlighted in mark 1 in ‘Attachment 1’.
| 01CV - Civils | Cxxx-NCR-001838 | NCR | Missing B5 Slab Connections |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2016-06-06 | 2016-05-25 11:39 | -12 | 2016-04-06 12:06 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The Contractor informs the Project Manager that there are missing slab connections at level B5 as shown in ‘Attachment 1’.
| 01CV - Civils | Cxxx-NCR-001839 | NCR | EBLA GRP Dowels Protruding from S2 (Ref NCR1655) |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2016-05-07 | 2016-04-14 12:21 | -23 | 2016-04-07 13:38 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | This NCR is in reference to NCR1655. Repair methodology had not been up updated on the close out of NCR 1655, see proposed answer below.
| 01CV - Civils | Cxxx-NCR-001840 | NCR | Eastbound Cavern S2 Hollow Areas |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2016-05-02 | 2016-04-18 10:32 | -14 | 2016-04-12 12:23 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Hollow areas in S2 lining as per NCR 1810.
| 01CV - Civils | Cxxx-NCR-001841 | NCR | North Core Wall – Incorrect Box Positions |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2016-07-04 | 2016-06-27 13:53 | -7 | 2016-04-18 16:24 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The Contractor informs the Project Manager that 2no. boxes have been positioned incorrectly in the North Core Wall as shown on ‘Attachment 1’.
| 01CV - Civils | Cxxx-NCR-001842 | NCR | Ground Floor Missing / Incorrect Placed Couplers |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2016-06-18 | 2016-05-13 14:57 | -36 | 2016-04-18 16:47 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The Contractor informs the Project Manager of missing / incorrect placed couplers in the core walls for ground floor internal core slab between gridline 7 and 9 on south and west walls as shown in ‘Attachment 1’.
| 01CV - Civils | Cxxx-NCR-001843 | NCR | Incorrect Mesh used in EBCav Bay 2 S2 crown repair |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2016-05-26 | 2016-05-12 08:30 | -14 | 2016-04-26 17:06 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Repair required to defects related to NCR-1828. Stainless steel mesh was instructed to be used, but the contractor installed the incorrect gauge stainless steel mesh.
| 01CV - Civils | Cxxx-NCR-001845 | NCR | Westbound Launch Adit - Low S2 steel coverage in crown |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2016-07-02 | 2016-05-06 12:22 | -57 | 2016-05-03 14:49 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Areas of low coverage of the S2 steel reinforcement to the internal profile of the tunnel where identified when the S2 mesh profiles where compared to the S2 final profiles. These areas of concern were then surveyed using a cover meter and 2 areas of low coverage where found: Chainage (-1) - minimum 34mm very localised point at the left hand shoulder Chainage (27) - minimum 36mm top of cast in situ on the right hand side As per Cxxx-RFI-002552 (Relaxation of tolerance for S2 Reinforcement) the minimum coverage of the steel should be 40mm
| 01CV - Civils | Cxxx-NCR-001846 | NCR | Couplers, Moorgate pit bottom |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2016-06-30 | 2016-06-13 09:40 | -17 | 2016-05-05 15:45 | Civil - Civil Engineering General | 3000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Design Problem - Conflicting information on drawings | Completed |  | Further to Cxxx_EWN_01541 the Contractor notes that Moorgate shaft pit bottom surface was not fit for the TBM transit works as several couplers were protruding on the pit bottom surface. As agreed with the Project Manager representatives some of these couplers were trimmed off to allow for the timber blocks to be installed.
| 01CV - Civils | Cxxx-NCR-001847 | NCR | BFK18 28 day dry shirnkage results |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2016-07-05 | 2016-05-17 06:44 | -49 | 2016-05-06 12:08 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | Dry shrinkage results for 18 have 28days have failed at 0.049%
| 01CV - Civils | Cxxx-NCR-001848 | NCR | Eastbound Cavern Cast in situ out of tolerance |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2016-07-05 | 2016-05-18 10:22 | -48 | 2016-05-06 12:26 | Tunnelling - Linings - In-situ Concrete | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | It has been noted from the asbuilt surveys that areas of the cast in situ are out of tolerance.
| 01CV - Civils | Cxxx-NCR-001849 | NCR | Limmo Main Shaft Missing Openings |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2016-07-09 | 2016-06-16 09:51 | -23 | 2016-05-09 10:19 | Civil - Civil Engineering General | 500 |  | Incomplete Works | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The Contractor informs the Project Manager that the two openings highlighted in ‘Attachment 1’ and ‘Attachment 2’ have been missed during construction.
| 01CV - Civils | Cxxx-NCR-001850 | NCR | Insufficent compressive strength core samples taken for 90 day tests - STG EB cavern Bays 1 and 2 - BFK 18 |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2016-07-10 | 2016-05-16 09:15 | -55 | 2016-05-11 11:50 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Not Defined | Completed |  | Not enough compressive strength core samples where taken for 90 day crush tests to be completed. Compressive strengths of the Cores where not sufficient at 28 days to make the 90 day test non applicable, these insufficient strengths are outlined in Cxxx-NCR-001814
| 01CV - Civils | Cxxx-NCR-001851 | NCR | BFK21 - Low compressive strengths 28 day results - WBCAV bays 2,3,4,7,8,9 + Running mean |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2016-07-10 | 2016-06-15 14:58 | -25 | 2016-05-11 14:36 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | WB cavern S2 layer has low compressive strength @ 28 days in some areas: Bays 2,3,4 : average = 23.4MPa Bays 7,8,9 : average = 28.70MPa Final running mean of 28 day test results is 31.10MPa
| 01CV - Civils | Cxxx-NCR-001852 | NCR | P445 + PPFib - Low compressive strengths - WBLA S2 |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2016-07-10 | 2016-05-17 06:53 | -54 | 2016-05-11 15:03 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | P445 + PPFib had low compressive strength when crushed at 28 and 90 days after spraying, Westbound Launch Adit 28d = 27.5MPa average 90d = 32.4MPa average
| 01CV - Civils | Cxxx-NCR-001853 | NCR | Limmo Main Shaft Out of Tolerance Opening |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2016-07-12 | 2016-06-16 09:46 | -26 | 2016-05-12 09:43 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The Contractor informs the Project Manager that an opening in a ground level internal core wall (see ‘Attachment 1’) has been cast out of tolerance.
| 01CV - Civils | Cxxx-NCR-001854 | NCR | Limmo Main Shaft Incorrect Diameter Used |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2016-07-12 | 2016-06-27 13:59 | -15 | 2016-05-12 10:36 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The Contractor informs the Project Manager that bar mark 101 diameter should have been H16 as shown on Cxxx-JUL-XSK-CR144_SH011-50040 Rev. 1.0, but instead H12 has been installed.
| 01CV - Civils | Cxxx-NCR-001855 | NCR | BFK 21 - Drying Shrinkage out of spec |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2016-07-15 | 2016-05-20 06:52 | -56 | 2016-05-16 15:20 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | 21 drying shrinkage 28 day test results are out of specification at -0.044%
| 01CV - Civils | Cxxx-NCR-001856 | NCR | Limmo Main Shaft Incorrect Box Positions B6 |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2016-11-30 | 2016-11-22 09:22 | -8 | 2016-05-23 12:00 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The Contractor informs the Project Manager that 2 no. boxes at B6 level have been positioned incorrectly as shown in ‘Attachment 1’.
| 01CV - Civils | Cxxx-NCR-001857 | NCR | Limmo Main Shaft – Core Walls Finish |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2016-07-31 | 2016-07-27 10:15 | -4 | 2016-05-26 15:08 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The Contractor informs the Project Manager that due to the Core Walls at Limmo Main Shaft being constructed with a slipform, the concrete finish does not meet the F2 finish described in Cxxx-RFI-002675, KF10 (Cxxx-JUL-S-RSP-CRG03-00005).
| 01CV - Civils | Cxxx-NCR-001858 | NCR | Limmo Main Shaft – Room 1 Level B6 Out of Tolerance Slab |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2016-08-31 | 2016-08-25 10:48 | -6 | 2016-06-08 14:17 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The Contractor informs the Project Manager that Room 1 slab in level B6 has been cast with significant variations in level (see ‘Attachment 1’).
| 01CV - Civils | Cxxx-NCR-001860 | NCR | SCL BFK 21 - Drying Shrinkage out of spec |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2016-06-27 | 2016-06-14 11:51 | -13 | 2016-06-13 14:55 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | 21 drying shrinkage 28 day test results are out of specification at -0.050%
| 01CV - Civils | Cxxx-NCR-001861 | NCR | Limmo Main Shaft – Missing Chamfers |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2016-08-31 | 2016-08-24 12:07 | -7 | 2016-06-29 09:18 | Civil - Civil Engineering General | 500 |  | Incomplete Works | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The Contractor informs the Project Manager that chamfers have not been formed to the external corners as described in the general notes document Cxxx-JUL-S-DDJ-CR144_SH011-00010 (‘Attachment 1’ & ‘Attachment 2’).
| 01CV - Civils | Cxxx-NCR-001862 | NCR | Limmo Main Shaft – Missing Couplers at Ground Floor |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2016-10-21 | 2016-10-04 15:17 | -17 | 2016-06-30 16:04 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The Contractor informs the Project Manager that a number of couplers have been missed for the connection between wall 1 and wall 10 & 12 at Ground Floor. The missing couplers cover a 1 metre high strip in each case. See ‘Attachment 1’ for photographic evidence.
| 01CV - Civils | Cxxx-NCR-001863 | NCR | Limmo Main Shaft – Level B1 South Damaged Earthing Cable |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2016-10-21 | 2016-10-18 07:03 | -3 | 2016-07-19 16:15 | Civil - Civil Engineering General | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | The Contractor informs the Project Manager that one of the earthing cables in the South side of Level B1 (shown in ‘Attachment 1’) was damaged while pouring the slab.
| 01CV - Civils | Cxxx-NCR-001864 | NCR | Stepney Green – Brackets Slotted Holes |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2016-10-28 | 2016-10-24 12:01 | -4 | 2016-07-25 11:36 | Civil - Civil Engineering General | 6000 |  | Incorrect Installation | Repair | 3 (3-6k) | Complete | Design Problem - Use of unapproved drawings | Completed |  | The Contractor informs the Project Manager that the slotted holes for the Stepney Green’s brackets have been fabricated and installed 90 degrees from the correct orientation.
| 01CV - Civils | Cxxx-NCR-001865 | NCR | Stepney Green – Joint between Walls & Slabs 15mm Bigger |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2016-09-23 | 2016-09-22 11:52 | -1 | 2016-07-25 15:26 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The Contractor informs the Project Manager that 2no. walls (GL 5 to 6/C and GL 4 to 6/C to D) were poured 15mm lower than the required 50mm gap between the top of the wall and the soffit of the slab as shown in ‘Attachment 1’.
| 01CV - Civils | Cxxx-NCR-001866 | NCR | Drive Y WB Farringdon end – Reinstatement of boreholes |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2016-10-10 | 2016-09-27 10:30 | -13 | 2016-08-05 14:39 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Other | Completed |  | Reinstatement of the vertical borehole in Drive Y WB at Farringdon end was carried out on 26/04/2016 following the TW design. Pour inspection and approval sheets and permit to load were completed correctly. Due to the small amount [c. ½m3] of concrete involved, concrete cubes were not taken for strength testing, as required in ITP Cxxx-DSJ-C4-ITP-CRG03-50023 section 4.4. Mix 6 - S3 H/LAY C32/40 from PJD batching plant was used, the same mix and batching plant used for all the First Stage Concrete. No failures in compressive strength in that concrete were recorded throughout its use up to completion 4 days earlier on 22/04/16.
| 01CV - Civils | Cxxx-NCR-001867 | NCR | Limmo Main Shaft – Ground Floor Level – Cover to Couplers |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2016-10-21 | 2016-10-04 15:56 | -17 | 2016-08-09 14:48 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | A number of coupler positions in wall GL 3-9 / E-F at the interface with future walls W11, W12 and W13 have inadequate cover.
| 01CV - Civils | Cxxx-NCR-001868 | NCR | Limmo Main Shaft – Slipform Core – Rebar Lap Length |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2016-10-21 | 2016-10-04 15:57 | -17 | 2016-08-09 15:02 | Civil - Civil Engineering General | 500 |  | Incomplete Works | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | Wall GL 4-5 / D-E: Vertical bars cut down to top of pour to accommodate walkway access. No protruding bars to provide lap length.
| 01CV - Civils | Cxxx-NCR-001869 | NCR | Drive Y - LIV - FAR EB & WB FTS surface finish |  | Crossrail | XRL | TUY - Tunnel Drive Y (Central) |  | 2016-09-16 | 2016-09-13 13:00 | -3 | 2016-08-10 17:23 | Civil - Tunnelling | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Background: Areas of the infill section of Floating Track Slab (FTS) were scabbled in order to bring the infill finish level into tolerance as it was cast too high. Following the scabbling the surface was not worked such that it met the surface finish requirements as specified on the relevant drawings. Locations of the defect: EB and WB FTS sections LIV-FAR and recorded as out of tolerance in Cxxx-RFI-2636&Cxxx-RFI-2671. Further Details: Cxxx have carried out an assessment (report is attached)
| 01CV - Civils | Cxxx-NCR-001870 | NCR | STG - Diaphragm Wall Repairs GL1-6 & GL10-14 |  | Crossrail | XRL | TUY - Tunnel Drive Y (Central) |  | 2016-08-31 | 2016-08-12 12:04 | -19 | 2016-08-11 16:12 | Structural Engineering - Diaphragm Walls | 0 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Reinforcement Cover at certain panels of the D-Wall is not as per requirement.
| 01CV - Civils | Cxxx-NCR-001871 | NCR | Steney Green shaft- works to fitting brackets commenced without an accepted ITP in place. |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2016-09-18 | 2016-09-15 15:46 | -3 | 2016-08-18 12:00 | Civil - Civil Engineering General | 500 |  | Planning | Rework | 4 (0.5-3k) | Complete | Procedure Problem - Other | Completed |  | The works to fit the head restraint brackets commenced without an accepted ITP (Cxxx-DSJ-C-ITP-CR094_WS108-50037 Revision 5.0) at code 1 in place. Also within the ITP the MCR for the brackets was not included.
| 01CV - Civils | Cxxx-NCR-001872 | NCR | Limmo Main Shaft – Level B4 Slab – Seepage Holes |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2016-11-30 | 2016-11-30 15:29 | 0 | 2016-08-31 15:43 | Civil - Civil Engineering General | 500 |  | Incomplete Works | Repair | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Seepage holes in the Level B4 slab not installed in accordance with drawing Cxxx-SKC-P-DDA-CR144_SH011-10532 Rev. P01. See ‘Evidence 1’ showing centre and south openings in room 5 partially clear, north opening blocked. Room 1 condition unknown, no access available in the escape stair shaft.
| 01CV - Civils | Cxxx-NCR-001873 | NCR | Limmo Main Shaft – Core Wall – Cast-in Pipe Detail |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2017-01-06 | 2016-12-09 12:20 | -28 | 2016-09-01 09:11 | Civil - Civil Engineering General | 500 |  | Incomplete Works | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Omission of puddle flanges on GL 7 shown in Cxxx-JUL-S-DDB-CR144_SH011-00404 rev P14.
| 01CV - Civils | Cxxx-NCR-001874 | NCR | Limmo Main Shaft – Missing __ Concrete Pour Reports: Determination of Slump & QA37 Sheets |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2016-10-28 | 2016-10-26 09:38 | -2 | 2016-09-15 13:55 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Verification Problems - Other | Completed |  | A number of ‘__ Concrete Pour Reports: Determination of Slump’ and . QA37 Sheets have not been located. These reports cover the batch / delivery information, workability and temperature of delivered concrete as required by the ITP. These reports are missing from the following records: - Cxxx-DSJ-C4-LRC-CRG03-50336 - Cxxx-DSJ-C4-LRC-CRG03-50337 - Cxxx-DSJ-C4-LRC-CRG03-50338 - Cxxx-DSJ-C4-LRC-CRG03-50321 - Cxxx-DSJ-C4-LRC-CRG03-50320 - Cxxx-DSJ-C4-LRC-CRG03-50319 - Cxxx-DSJ-C4-LRC-CRG03-50324 - Cxxx-DSJ-C4-LRC-CRG03-50325 - Cxxx-DSJ-C4-LRC-CRG03-50326 - Cxxx-DSJ-C4-LRC-CRG03-50341 - Cxxx-DSJ-C-LRC-CR144_SH011-50059 In all cases where these records are missing the concrete strength test results have been satisfactory. Post pour checks have not identified any issues.
| 01CV - Civils | Cxxx-NCR-001875 | NCR | Limmo Main Shaft – Structural Core |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2017-02-03 | 2017-01-26 16:02 | -8 | 2016-09-29 11:27 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The slipformed central core of Limmo Shaft exhibits a number of deviations in the geometrical tolerances for holes and openings in the structure when compared with the Cxxx drawings. Where conventional reinforced concrete techniques were used in other elements of the shaft there are also minor displacements in plan position of pits and sumps and deviations in SSL at level B1. Attached are red line drawings with the more significant displacements highlighted.
| 01CV - Civils | Cxxx-NCR-001876 | NCR | STG WB Shaft – __ Coating |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2016-11-30 | 2016-11-08 16:36 | -22 | 2016-10-04 08:48 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Areas of steel mesh are exposed in the __ applied to the beam soffit in the vicinity of grid location E5 and B5 at level B5 of STG westbound shaft. See attachment 1 and 2 for photo evidence. 2no. brackets were incorrectly installed in grid location B5 at level B5 and fixed to the beam soffit where __ had been applied. See ‘Attachment 2’ for photo evidence. 7no. holes were drilled for which 6 bolts have been left in place and an extra hole where rebar was hit. See attachment 3 for photo evidence.
| 01CV - Civils | Cxxx-NCR-001877 | NCR | Limmo Main Shaft – Level B6 Cable Pit |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2016-10-21 | 2016-10-21 10:39 | 0 | 2016-10-04 08:56 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | In the Limmo shaft cable pit at level B6 [grid line E-5/6] there is evidence of water weeping from the southern wall of the pit.
| 01CV - Civils | Cxxx-NCR-001878 | NCR | Regulating Layer Records |  | Crossrail | XRL | TUY - Tunnel Drive Y (Central) |  | 2016-10-20 | 2016-10-10 14:43 | -10 | 2016-10-06 14:17 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | Following the review of the sub-construction certificates for Limmo Backshunts EB & WB and a Surveillance by the CRL verification team. Inconsistencies and missing records as per the agreed ITP and Specification Requirements have been delivered. The missing deliverables were identified in the following records: Cxxx-DSJ-C-LRC-CR144_WS155-50061 - EB Collars & Backshunts Regulating Layer Checksheets Cxxx-DSJ-C-LRC-CR144_WS155-50061 - WB Collars & Backshunts Regulating Layer Checksheets As per ITP Cxxx-DSJ-C4-ITP-CR144_WS155-50012: Activities 2.1.3, 2.1.5, 2.1.6, 2.1.7, 2.1.8 2.1.10& 2.1.11 have not been recorded for instances of the application and the wrong checksheet at times has been used. Further to this in the following records: Cxxx-DSJ-C4-LRC-CR094_WS108-50015 - STG Invert slab eastbound launch adit - regulating layer. Sheet membrane/ Waterproofing layer - Checksheets As per ITP Cxxx-DSJ-C-ITP-CR094_WS108-50038: Activities 2.1.6, 2.1.7, 2.1.8 & 2.1.9 have not been recorded. While the above is not ideal, the PM notes that prior to the waterproofing being applied the waterproofing checksheets have recorded that there is satisfactory application/coverage of the regulating layer in place. The regulating layer applied in both the Limmo backshunts and the adit was a readymix product. Cxxx-DSJ-C-LRC-CR094_WS108-50034 - Reader Spraycrete 40 AAA .
| 01CV - Civils | Cxxx-NCR-001879 | NCR | Limmo Main Shaft – Ground Level South Slab |  | Contr | DSJ | TUY - Tunnel Drive Y (Central) |  | 2016-11-30 | 2016-11-02 09:26 | -28 | 2016-10-11 10:08 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | In a number of locations (see attachments 1 to 3) of the south slab in ground level the correct rebar (127) has not been installed as per ‘Section D-D’ in drawing Cxxx-JUL-S-DDL-CR144_SH011-01623 Rev. C02 (‘Attachment 4’). 1. Attachment 2 – Correct upper links (127) installed but additional starter bars installed not as per design. 2. Attachment 3 – Incorrect starter bars installed instead of correct upper links (127). 3. Numerous 16mm starter bars where installed instead of 12mm starter bars as per design – Correct cover achieved.
| 01CV - Civils | Cxxx-NCR-001880 | NCR | STG - Firestopping B4/B5 |  | Crossrail | XRL | TUY - Tunnel Drive Y (Central) |  | 2017-01-16 | 2017-01-12 14:17 | -4 | 2016-11-02 16:59 | Fire - Compartmentation | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Fire-stopping has been installed on level B4 & B5 at Stepney Green Shaft in the movement gaps of the bracket restrained walls (See attachment 1 for marked up locations). The installation of the fire-stopping was carried out by . who are not 3rd party accredited by FIRAS, LPCB or similar. The installed fire-stopping was inspected by __ (CEG) on the 22/09/16 who advised that the sealant had not been applied properly and that there was evidence of the passage of air through the fire-stopping where access for a high level inspection was available in one area.
| 01CV - Civils | Cxxx-NCR-001881 | NCR | STG - B3 Earthing Bond |  | Crossrail | XRL | TUY - Tunnel Drive Y (Central) |  | 2017-01-16 | 2017-01-12 14:18 | -4 | 2016-11-22 15:13 | Systems - Earthing and Bonding | 500 |  | Incomplete Works | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Earthing Bond has not been installed in 1 location on level B3 G/L 11-12. The location of the bonds were indicated on Cxxx-JUL-E-DDL-CR094_SH005-00801 and clarified following Cxxx-RFI-002170. Please see the attached B3 Plan - Missing Earth Bond.pdf for the location of where the earth bond should have been installed. Note this drawing is not controlled and forms part of the testing schedule.
| 01CV - Civils | Cxxx-NCR-001882 | NCR | CP13 - Grout Tubes Install Location |  | Crossrail | XRL | TUY - Tunnel Drive Y (Central) |  | 2017-02-28 | 2017-10-13 16:35 | 227 | 2016-11-30 18:39 | Civil - Tunnelling | 0 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Grout tubes installed as part of the construction of CP13 EB collar have been located such that their protrusion from the RC collar clashes with the install location of the fire door. The grout tubes that clash with the install of the fire door are circled in red in attachment IMG_303.jpg. Detailed photos are also attached IMG_307 to IMG_310. Cxxx-RFI-001964 clarified the allowable install location of grout tubes, several have been installed in the area defined as the exclusion zone. See attachment "Cxxx-RFI-001964-attachment.pdf" which clarifies the allowable install location zone. The tubes are required as part of the permanent works as detailed on Cxxx-OVE-C4-DDD-CR001_Z-23162 and Cxxx-FCD-001519 and as such should be accessible to inject in the future as required.
| 01CV - Civils | Cxxx-NCR-001883 | NCR | CP11 - Grout Tubes Install Location |  | Crossrail | XRL | TUY - Tunnel Drive Y (Central) |  | 2017-02-28 | 2017-10-13 16:30 | 227 | 2016-12-01 14:16 | Civil - Tunnelling | 0 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Grout tubes installed as part of the construction of CP11 WB & EB collar have been located such that their protrusion from the RC collar clashes with the install location of the fire door. The grout tubes that clash with the install of the fire door are shown in the attached pictures. "EB-CP11.jpg" & "WB-CP11.jpg". Cxxx-RFI-001964 clarified the allowable install location of grout tubes, several have been installed in the area defined as the exclusion zone. See attachment "Cxxx-RFI-001964-attachment.pdf" which clarifies the allowable install location zone. The tubes are required as part of the permanent works as detailed on Cxxx-OVE-C4-DDD-CR001_Z-23162 and Cxxx-FCD-001519 and as such should be accessible to inject as required.
| 01CV - Civils | Cxxx-NCR-001884 | NCR | CP09 - Grout Tubes Install Location |  | Crossrail | XRL | TUY - Tunnel Drive Y (Central) |  | 2017-02-24 | 2017-10-13 16:36 | 231 | 2016-12-09 12:25 | Civil - Tunnelling | 0 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Grout tubes installed as part of the construction of CP09 WB collar have been located such that their protrusion from the RC collar clashes with the install location of the fire door. The grout tubes that clash with the install of the fire door are shown in the following attached pictures: IMG_371, IMG_372, IMG_373. Cxxx-RFI-001964 clarified the allowable install location of grout tubes, several have been installed in the area defined as the exclusion zone. See attachment "Cxxx-RFI-001964-attachment.pdf" which clarifies the allowable install location zone. The tubes are required as part of the permanent works as detailed on Cxxx-OVE-C4-DDD-CR001_Z-23162 and Cxxx-FCD-001519 and as such should be accessible to inject in the future as required.
| 01CV - Civils | Cxxx-NCR-001885 | NCR | CP14 - Leaks in CP |  | Crossrail | XRL | TUY - Tunnel Drive Y (Central) |  | 2017-02-28 | 2020-10-08 14:20 | 1318 | 2016-11-30 18:35 | Tunnelling - Linings - SGI Rings | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Previous Construction - Problems based on previous construction errors | Completed |  | 24/11/2017 CP14 was inspected on the 07 Oct 2017 and it was observed to no longer be leaking with leaks previously observed and as noted in the original text of this NCR (below) no longer present. However, there is now notable damage to the SGI paint which will require to be addressed as per specification requirements KN20. Also noted during the visit was a pool of stagnant water on the floor of the CP. Water was stained and portable loo's sited in the CP. ---------- Original NCR text: 30/11/2016 Multiple Leaks are present in the CP14 both at the interface of the CP SGI rings with the RC collars and within the SGI section. Photos of the leaks are attached IMG_314,316,317,319,320. The leaks have caused excessive staining to the SGI and formations of stalactites, they are also inducive to a wet environment within the CP. Leaks at the RC collar pose a durability issue for the fire door install. The CPs are designed to be a dry environment as detailed in KT10 and as such leaks are not permissible. Specification relevance to KT10.1301 iii) has been confirmed as part of Cxxx-FCD-1519.
| 01CV - Civils | Cxxx-NCR-001886 | NCR | Niche 3 - Grout Tubes Install Location |  | Crossrail | XRL | TUY - Tunnel Drive Y (Central) |  | 2017-02-28 | 2017-10-13 16:29 | 227 | 2016-12-01 14:14 | Tunnelling - Linings - SGI Rings | 0 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Grout tubes installed as part of the construction of niche 03 collar have been located such that their protrusion from the RC collar clashes with the install location of the fire door. The grout tubes that clash with the install of the fire door are shown in the attached picture "Niche03.jpg" Cxxx-RFI-001964 clarified the allowable install location of grout tubes, several have been installed in the area defined as the exclusion zone. See attachment "Cxxx-RFI-001964-attachment.pdf" which clarifies the allowable install location zone. The tubes are required as part of the permanent works as detailed on Cxxx-OVE-C4-DDD-CR001_Z-23162 and Cxxx-FCD-001519 and as such should be accessible to inject as required.
| 01CV - Civils | Cxxx-NCR-001887 | NCR | CP06 - Grout Tubes Install Location |  | Crossrail | XRL | TUY - Tunnel Drive Y (Central) |  | 2017-02-24 | 2018-10-05 12:43 | 588 | 2016-12-09 12:27 | Civil - Tunnelling | 0 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Grout tubes installed as part of the construction of CP06 EB collar have been located such that their protrusion from the RC collar clashes with the install location of the fire door. The grout tubes that clash with the install of the fire door are shown in the following attached pictures CP06 (2) and CP06 (3). Cxxx-RFI-001964 clarified the allowable install location of grout tubes, several have been installed in the area defined as the exclusion zone. See attachment "Cxxx-RFI-001964-attachment.pdf" which clarifies the allowable install location zone.
| 01CV - Civils | Cxxx-NCR-001888 | NCR | CP11 - Leaks in CP |  | Crossrail | XRL | TUY - Tunnel Drive Y (Central) |  | 2017-02-24 | 2020-10-08 14:17 | 1322 | 2016-12-09 12:28 | Tunnelling - Linings - SGI Rings | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Previous Construction - Problems based on previous construction errors | Completed |  | CP11 was inspected on the 07 Oct 2017 and it was observed to be leaking in only 1 location from a bolt. Leaks previously observed and document in the original text of this NCR (below) were no longer present. See photo: CP 11 07OCT17 1.jpg Photos CP 11 07OCT17 2,3 .jpg have been added further showing the paint damage that still needs to be addressed. ---- Original text: 09/12/16 Multiple Leaks are present in CP11 mostly in the region of the enlarged diameter interface of the SGI. Photos of the leaks are attached IMG_343,344,345,349,350,353. The leaks have caused excessive staining to the SGI and have started to cause spalling of the protective SGI paint system and visible signs of localised rust is present. The leaks are also inducive to a wet environment within the CP. The CPs are designed to be a dry environment as detailed in KT10 and as such leaks are not permissible. The paint system requirements are detailed in KN20. Specification relevance to KT10.1301 iii) has been confirmed as part of Cxxx-FCD-1519.
| 01CV - Civils | Cxxx-NCR-001889 | NCR | CP10 - Leaks in CP |  | Crossrail | XRL | TUY - Tunnel Drive Y (Central) |  | 2017-02-24 | 2020-10-08 14:18 | 1322 | 2016-12-09 12:29 | Tunnelling - Linings - SGI Rings | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Previous Construction - Problems based on previous construction errors | Completed |  | 24/11/17 CP10 was inspected on the 07 Oct 2017 and it was observed to be leaking in only 1 location from a bolt. Leaks previously observed and document in the original text of this NCR (below) were no longer present. See photo: CP 10 07OCT17 1.jpg However, there is now notable damage to the SGI paint which will require to be addressed as per specification requirements KN20. Photos CP 10 07OCT17 2.jpg shows a section of the paint damage that needs to be addressed. ---- Original NCR text 09/12/16 Multiple Leaks are present in CP11 at the WB column and within the SGI lined section. Photos of the leaks are attached IMG_357,358,360,361,363. The leaks have caused staining to the SGI and they are inducive to a wet environment within the CP. The CPs are designed to be a dry environment as detailed in KT10 and as such leaks are not permissible. Specification relevance to KT10.1301 iii) has been confirmed as part of Cxxx-FCD-1519.
| 01CV - Civils | Cxxx-NCR-001890 | NCR | CP09 - Leaks in CP |  | Crossrail | XRL | TUY - Tunnel Drive Y (Central) |  | 2017-02-24 | 2020-10-08 14:19 | 1322 | 2016-12-09 12:31 | Tunnelling - Linings - SGI Rings | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Previous Construction - Problems based on previous construction errors | Completed |  | 24/11/17 Following inspection of the CP9 on 14/09/17 leaks were still present at multiple joints within the CP and SGI paint coating system is still damaged. New photos attached: CP09 14SEP17 1.JPG CP09 14SEP17 2.JPG --- Original NCR Text: 09/12/16 Several leaks are present in CP09 . Photos of the leaks are attached IMG_374,376,377,378,379. The leaks have caused some staining to the SGI and have started to cause spalling of the protective SGI paint system and visible signs of localised rust is present. The leaks are also inducive to a wet environment within the CP. The CPs are designed to be a dry environment as detailed in KT10 and as such leaks are not permissible. The paint system requirements are detailed in KN20. Specification relevance to KT10.1301 iii) has been confirmed as part of Cxxx-FCD-1519. The CPs are designed to be a dry environment as detailed in KT10 and as such leaks are not permissible. The paint system requirements are detailed in KN20. Specification relevance to KT10.1301 iii) has been confirmed as part of Cxxx-FCD-1519.
| 01CV - Civils | Cxxx-NCR-001891 | NCR | Limmo - Lift Shaft As-built Data |  | Crossrail | XRL | TUY - Tunnel Drive Y (Central) |  | 2017-02-24 | 2017-02-22 16:22 | -2 | 2016-12-14 10:37 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Verification Problems - Other | Completed |  | As-built information for the interior walls of the lift shaft at Limmo has not been provided as part of the redline drawings submission.
| 01CV - Civils | Cxxx-NCR-001892 | NCR | CP05a - Grout Tubes Install Location |  | Crossrail | XRL | TUY - Tunnel Drive Y (Central) |  | 2017-03-31 | 2017-10-13 16:27 | 196 | 2017-01-10 09:51 | Civil - Tunnelling | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Grout tubes installed as part of the construction of CP05a EB collar have been located such that their protrusion from the RC collar clashes with the install location of the fire door. The grout tubes that clash with the install of the fire door are shown in the following attached picture: CP5A.jpg Cxxx-RFI-001964 clarified the allowable install location of grout tubes, several have been installed in the area defined as the exclusion zone. See attachment "Cxxx-RFI-001964-attachment.pdf" which clarifies the allowable install location zone. The tubes are required as part of the permanent works as detailed on Cxxx-OVE-C4-DDD-CR001_Z-23162 and Cxxx-FCD-001519 and as such should be accessible to inject in the future as required.
| 01CV - Civils | Cxxx-NCR-001893 | NCR | Wrexham Road Car Park |  | Crossrail | PDP | TUY - Tunnel Drive Y (Central) |  | 2017-10-10 | 2018-10-05 10:34 | 360 | 2017-03-24 18:02 | Civil - Landscaping | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | Ten of the fifteen trees at the Wrexham Road Car Park are dead
| 01CV - Civils | Cxxx-NCR-001894 | NCR | Limmo - Limmo D-Wall / Core Wall Firestop Materials |  | Crossrail | XRL | TUY - Tunnel Drive Y (Central) |  | 2018-10-31 | 2018-10-25 08:37 | -6 | 2017-06-30 15:06 | Fire - Compartmentation | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | Further to Cxxx-RFI-002501, the firestop materials installed within Limmo Main Shaft (between the D-Wall/Core Wall as shown in detail 2 Cxxx-JUL-S-DDD-CR144_SH011-00426 Rev. C03) have been done so without submitting MCRs for acceptance by CRL. There is to the best of CRL knowledge no other evidence or records available on eB that provide evidence that the installed materials, suspected to be Nullfire 703 & Flexcell , are as Cxxx designer proposed as an acceptable change.
| 01CV - Civils | Cxxx-NCR-001895 | NCR | CP13 - Leaks in CP & Paint Damage |  | Crossrail | XRL | TUY - Tunnel Drive Y (Central) |  | 2021-01-16 11:50 | 2020-10-08 14:22 | -100 | 2017-11-24 12:23 | Tunnelling - Linings - SGI Rings | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Improper preservation of material after installation | Completed |  | CP13 was inspected on the 07 Oct 2017: Multiple leaks were identified at the interface between the large and small SGI sets. Photos of leaks attached: CP13 07OCT17 1,2,3. The CPs are designed to be a dry environment as detailed in KT10 and as such leaks are not permissible. Specification relevance to KT10.1301 iii) has been confirmed as part of Cxxx-FCD-1519. Also identified is damage to the SGI coating system. This will require to be addressed as per the specification requirements KN20.
| 01CV - Civils | Cxxx-NCR-001896 | NCR | CP06 - SGI Coating Damage |  | Crossrail | XRL | TUY - Tunnel Drive Y (Central) |  | 2021-01-16 09:28 | 2020-10-08 10:06 | -100 | 2017-11-24 12:24 | Tunnelling - Linings - SGI Rings | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Previous Construction - Problems based on previous construction errors | Completed |  | CP06 was inspected on the 14 Sep 17. The CP was observed not to be exhibiting any signs of leaking. However it was noted that there was damage to the coating system applied to the SGI at the transition areas of the SGI small and large sets. This will require to be addressed as per the specification requirements KN20.
| 01CV - Civils | Cxxx-NCR-001897 | NCR | CP05A - Leaks in CP & Paint damage |  | Crossrail | XRL | TUY - Tunnel Drive Y (Central) |  | 2021-01-16 09:16 | 2020-10-08 14:26 | -100 | 2017-11-24 12:25 | Tunnelling - Linings - SGI Rings | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | CP05A was inspected on 22/09/17. Several minor leaks were identified at the interface between the large and small SGI sets. The CPs are designed to be a dry environment as detailed in KT10 and as such leaks are not permissible. Specification relevance to KT10.1301 iii) has been confirmed as part of Cxxx-FCD-1519. Also identified is damage to the SGI coating system. This will require to be addressed as per the specification requirements KN20. Photos of these are attached to the NCR.
| 01CV - Civils | Cxxx-NCR-001898 | NCR | Niche 3 - Leaks in Niche & SGI coating system |  | Crossrail | XRL | TUY - Tunnel Drive Y (Central) |  | 2021-01-16 09:07 | 2020-10-08 14:27 | -100 | 2017-11-24 12:26 | Tunnelling - Linings - SGI Rings | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Niche 3 was inspected on 14/09/17. Several leaks were identified at the interface between the large and small SGI sets. The CPs are designed to be a dry environment as detailed in KT10 and as such leaks are not permissible. Specification relevance to KT10.1301 iii) has been confirmed as part of Cxxx-FCD-1519. Also identified is damage to the SGI coating system. This will require to be addressed as per the specification requirements KN20. Photos of these are attached to the NCR.
| 01CV - Civils | Cxxx-NCR-001899 | NCR | Limmo - Leaks within shaft and bankshunt |  | Crossrail | XRL | TUY - Tunnel Drive Y (Central) |  | 2021-03-10 15:26 | 2020-12-21 15:33 | -79 | 2017-12-20 16:12 | Tunnelling - Tunnelling General | 500 |  | Design | Repair | 4 (0.5-3k) | Complete | Previous Construction - Problems based on previous construction errors | Completed |  | Since handover of the tunnel envelope in the vicinity of Limmo from Cxxx to Cxxx numerous leaks have been observed within the tunnel envelope in the area of Limmo main shaft and the backshunt area of the tunnels. Some facts: Significant amount of leak injections were carried out in this area in the period of August-October 2016: Cxxx-DSJ-C4-LRC-CRG03-50354 Shaft is in close proximity to the River Thames/Lee and the ground is saturated. Dewatering was used during construction. The main shaft was designed by Cxxx interfacing with Cxxx tunnels and Cxxx designed primary lined SCL backshunts. Observed Leaks: 1. At all four of the interfaces between the main shaft and the tunnel eyes to the running tunnels and backshunts tunnels cracks through the kerbs and trackbed are present. Water has been observed and is suspected to be emanating from these cracks. 2. A leak is present between the tunnel eye (east) and soffit of the B4 level slab on the eastbound side of the mainshaft. This leak has been present since first observed in q4 2016. No visible signs of a water source on the b4 inspection level. 3. Leaks within the backshunt - several leaks have been observed in both the westbound and eastbound backshunt tunnels. These leaks are located within several of the construction joints of the cast in-situ sections. Several of the leaks are causing significant pooling of the water on the kerb and drainage channels. 4. Leaks observed within the storage rooms at track level.
| 01CV - Civils | Cxxx-NCR-000050 | NCR | Document Control |  | Contr |  | TUH - Thames Tunnel (East) |  | 2011-09-16 | 2011-10-06 15:32 | 20 | 2011-08-26 | Human Factors - Human Factors General | 500 |  | System Defect | Rework |  | Complete |  | Completed |  | During a surveillance carried out on the ITP process relating to the installation of the Asset Protection Barrier, there was no evidence available to demonstrate that adequate control was being exercised over the review, issue and receipt of the drawings in use.
| 01CV - Civils | Cxxx-NCR-000071 | NCR | Finding on Specification of HSFG Bolts |  | Contr |  | TUH - Thames Tunnel (East) |  | 2011-09-22 | 2011-11-07 15:35 | 46 | 2011-09-08 | Structural Engineering - Bolted Connections | 500 |  | Material | Rework |  | Complete |  | Completed |  | Two types of coating supplied & specifications quoted on ITP were not in accordance with __ Drawing, but were specified to the Crossrail Specifications. Bolts were not supplied to zinc coating specified on ITP which was compliant with NR specified SHW table 19/2B. The original bolts supplied by CWW compliant to BS 4395 were uncoated specified as self coloured. Bolts and washers supplied through __ specified as sheradised.
| 01CV - Civils | Cxxx-NCR-000072 | NCR | Finding on Material Compliance Certificate for HSFG Bolts & Washers |  | Contr |  | TUH - Thames Tunnel (East) |  | 2011-09-22 | 2011-11-07 15:33 | 46 | 2011-09-08 | Structural Engineering - Bolted Connections | 500 |  | Material | Rework |  | Complete |  | Completed |  | The Method Statement & ITP did not identify additional materials used, identify on the material certificate and seen in the assembley of the bolted connection on site. The Material Certificate from __ Ltd. could not be traced to the material order for the APB Barrier and the quoted specifications for material compliance on the ITP & Material conformance certificate were not in accordance with NR specification on Drawings. HSFG Bolts were supplied to BS EN 14399 coating specified as Sheradised, additional washers were supplied to German Standard DIN 6916 and were not identified as being zinc coated. __ had used a sub-supplier __. The order number on the materials certificate was not the __ (__) order no. and no __ delivery tickets were available on site to validate the __ order no. with __ material certificate to a site delivery address. There was no site delivery address on the material certificate. Nuts & washers are not supplied with the bolts as a unit but are specified separately to meet the order specifications and contractors preferred method of construction. See finding (c) The Order did not contain sufficient specification detail or customer (Crossrail) requirements for traceability.
| 01CV - Civils | Cxxx-NCR-000073 | NCR | Finding on Welders Qualification & Weld Procedure |  | Contr |  | TUH - Thames Tunnel (East) |  | 2011-09-22 | 2011-10-06 16:01 | 14 | 2011-09-08 | Structural Engineering - Welding | 500 |  | System Defect | Rework |  | Complete |  | Completed |  | The was no evidence of Weld qualification or weld procedure in place for welding specified on NR drawing to BS EN ISO 3834 – 3:2005. A Field Change Document DRH-CRL FCD-Cxxx-00047 was raised to request testing to BS4515 on 22 July no reply has been given. The Procedure and competence tests are currently on hold until FCD 47 has been responded..
| 01CV - Civils | Cxxx-NCR-000074 | NCR | The requirements for Inspection & Test had not been adequately communicated. |  | Contr |  | TUH - Thames Tunnel (East) |  | 2011-09-22 | 2011-11-07 15:21 | 46 | 2011-09-08 | Human Factors - Human Factors General | 500 |  | Planning | Rework |  | Complete |  | Completed |  | Review of the inspection & test check sheets during Crossrail Surveillance audit show a lack of understanding of the ITP process. The ITP procedure had not been released but two revisions of the ITP & several iterations of the ITP check sheets had been communicated agreed and released prior to fabrication and installation. However the part 1 and Part 2 for Installation and part 3 of the Fabrication showed omission and amendments indicating misunderstanding of the process. Part 1 of installation identified checks from revision 1 of the ITP deleting the agreed Rev 2.0 checks. The checks inserted on Part 1 pre installation checks were part 3 post installation checks from the superseded Rev 1.0 ITP.
| 01CV - Civils | Cxxx-NCR-000087 | NCR | Installation of NR Asset Protection Barrier Panels |  | Contr |  | TUH - Thames Tunnel (East) |  | 2011-10-20 | 2011-10-06 16:07 | -14 | 2011-09-20 10:22 | Civil - Structural Engineering | 500 |  | Workmanship | Rework |  | Complete |  | Completed |  | up to 70mm of shims have been used between panel and posts 153 & 154
| 01CV - Civils | Cxxx-NCR-000089 | NCR | Construction of Piling Mat |  | Contr |  | TUH - Thames Tunnel (East) |  | 2011-10-06 | 2011-10-06 16:11 | 0 | 2011-09-22 11:48 | Civil - Civil Engineering General | 500 |  | System Defect | Rework |  | Complete |  | Completed |  | Construction of the piling mat commenced prior to the relevant ITP being accepted.
| 01CV - Civils | Cxxx-NCR-000091 | NCR | Waste segregation on site inadequate |  | Contr |  | TUH - Thames Tunnel (East) |  | 2011-09-26 | 2011-10-25 16:15 | 29 | 2011-09-23 08:39 | Environmental - Waste & Material Management | 500 |  | Supervision/Management | Rework |  | Complete |  | Completed |  | Mixed waste found in timber skip, timber found in mixed waste skip.
| 01CV - Civils | Cxxx-NCR-000111 | NCR | Acceptance of Contractor ITP |  | Contr |  | TUH - Thames Tunnel (East) |  | 2011-10-17 | 2011-11-07 15:20 | 21 | 2011-10-31 | Civil - Fill | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | Revision 1 of the ITP, Cxxx-HTM-Z-ITP-CR148_PT005-50001 for the Piling Platform, was issued, with comments, at code 2, permitting the contractor to proceed with the works, but prior to obtaining the no objection status required from __.
| 01CV - Civils | Cxxx-NCR-000112 | NCR | Document Control - Records & Archiving - Work Package Records Cxxx-HTM-O4-CER-CR148_PT005-50002 - Plumstead Portal - Embedded Wall & Piling - Working Platform |  | Contr |  | TUH - Thames Tunnel (East) |  | 2011-11-30 | 2011-11-07 15:19 | -23 | 2011-10-31 | Civil - Fill | 500 |  | Supervision/Management | Rework |  | Complete |  | Completed |  | Records filed against Crossrail Filing System in Work Package files were not readily retrievable and once found were incomplete or lacing traceability to the location in the works. Identified in planned Surveillance Period 8 October 2011.
| 01CV - Civils | Cxxx-NCR-000138 | NCR | Plumstead Portal - Embedded Wall & Piling(__) - North Wall - Type C - Secant CFA Male (Reinforced) Pile No. 1056 |  | Contr |  | TUH - Thames Tunnel (East) |  | 2012-01-31 | 2012-01-18 08:48 | -13 | 2011-12-06 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | Proposed Accepted method of construction adopted but 3rd pile out or 4 male piles (Ref. No. 1056 Type C on North Wall) constructed on 6th December had reinforcement cage reach refusal at 12.6m depth. The Cage reinforcement was cut of at pile cap level. Resulting in bottom 5.4m of male pile no. 1056 being unreinforced. Conditions were identical in all 4 cases.
| 01CV - Civils | Cxxx-NCR-000140 | NCR | Plumstead Portal - Embedded Wall & Piling (__) - North Wall - Secant CFA Male (Reinforced) Pile No. 1042 |  | Contr |  | TUH - Thames Tunnel (East) |  | 2012-01-31 | 2012-01-31 16:26 | 0 | 2011-12-09 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | Male Scant Pile (Ref. No. 1042on North Wall) constructed on 7th December had reinforcement cage reach refusal at 17.4m depth. The Cage reinforcement was cut of at pile cap level. Resulting in bottom 0.6 m of male pile no. 1042 being unreinforced. One failure out of Six piles driven on 7th December.
| 01CV - Civils | Cxxx-NCR-000148 | NCR | Plumstead Portal - Embedded Wall & Piling - Secant CFA Piles North Wall cast 01/12 - 16/16/11 - Cube Samples |  | Contr |  | TUH - Thames Tunnel (East) |  | 2011-12-23 | 2012-02-08 14:25 | 47 | 2011-12-16 | Civil - Civil Engineering General | 500 |  | System Defect | Repair |  | Complete |  | Completed |  | Cubes samples made for __ (__) by their subcontractor __(UKAS concrete testing) were not protected ( driven off site) in the 1st 16 hrs. A steel box was eventually provided to store but was not temperature controlled. Cubes made were either non compliant with protection or storage conditions. This affected samples taken between 1/12 & 16 /12 /11 for Secant CFA piles betwwem 1003 & 1101 on the north wall phase 1.
| 01CV - Civils | Cxxx-NCR-000159 | NCR | Plumstead Portal - Embedded Wall & Piling - Secant & CFA Piling - Concrete Sampling |  | Contr |  | TUH - Thames Tunnel (East) |  | 2012-01-09 | 2012-03-06 08:44 | 57 | 2011-12-21 | Civil - Civil Engineering General | 500 |  | System Defect | Use As-Is |  | Complete |  | Completed |  | Spot sample was being taken by Concrete Tecnician who stated he had been instructed to do so.
| 01CV - Civils | Cxxx-NCR-000167 | NCR | Plumstead Portal - Embedded Wall & Piling - Records of Calibration |  | Contr |  | TUH - Thames Tunnel (East) |  | 2012-01-17 | 2012-01-17 10:58 | 0 | 2012-01-10 | Civil - Civil Engineering General | 500 |  | System Defect | Repair |  | Complete |  | Completed |  | Records were not available on site or could be retrived for the purpose of the Crossrail Surveillance on the Secant cased CFA piling operations week commencing 19th December 2011.
| 01CV - Civils | Cxxx-NCR-000179 | NCR | Plumstead Portal - Embedded Wall & Piling - Secant CFA Pile - Supply of Concrete - Material Records Conformity Requirements |  | Contr |  | TUH - Thames Tunnel (East) |  | 2012-02-23 | 2012-02-08 14:21 | -15 | 2012-01-23 | Civil - Civil Engineering General | 500 |  | System Defect | Use As-Is |  | Complete |  | Completed |  | It was identified during routine daily inspection of Subcontractor __ works that the Concrete delivery for the Female pile softmix had water added on site. Further investigation revealead that the delivery ticket had no consistence information or W/C ratio information in order to material determine compliance. Under EN ISO 206 water addition is allowable if the target Considtance value is below thew limit and water is not added to increase the slump over the Target. Water was added on the instruction of the Batcher on assumption that the target was S4. It was further identified that all Softpile mix delivery tickets has the same information missing. It was also identified that the addition of water had been signed for as instructed water (not permitted) and not water added to bring into tolerance for target slump(permitted).
| 01CV - Civils | Cxxx-NCR-000199 | NCR | On site addition of water to concrete. |  | Contr |  | TUH - Thames Tunnel (East) |  | 2012-02-17 | 2012-03-12 15:57 | 24 | 2012-02-02 07:37 | Civil - Civil Engineering General | 500 |  | Planning | Repair |  | Complete |  | Completed |  | Contractor ITP Cxxx-HTM-Z-ITP-CR148_PT005-50004 rev 2.0 Does not reference the above requirements for on site addition of water to concrete.
| 01CV - Civils | Cxxx-NCR-000207 | NCR | Plumstead Portal - Embedded Wall & Piling - Rotary & Secant Piles - Concrete Placed with concrete temp less than 5°C |  | Contr |  | TUH - Thames Tunnel (East) |  | 2012-03-09 | 2012-03-27 15:34 | 18 | 2012-02-09 | Civil - Civil Engineering General | 500 |  | Planning | Repair |  | Complete |  | Completed |  | On 2 Feb 2012 - Concrete poured for P181 (Rotary), P1415 and P1409 (Secant Females) was poured with recorded temprature of concrete below 5 degrees C. As per clause KF10. 3205 of Cxxx-CSY-S-RSP-CR146_PT004-0003 Rev6 KF10, no concrete shall be poured if the temprature of concrete is below 5 degrees C. (See attached concrete delivery tickets with pile numbers marked at the top).
| 01CV - Civils | Cxxx-NCR-000213 | NCR | Plumstead Portal - Embedded Wall Piling - CFA piles - Placement of concrete more than 2 hrs after batching |  | Contr |  | TUH - Thames Tunnel (East) |  | 2012-03-17 | 2012-03-20 17:18 | 3 | 2012-02-17 09:14 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | Concrete delivered on 8th Feb 2012for CFA Pile 221was recorded at time of discharge as being 2.5 hrs old.
| 01CV - Civils | Cxxx-NCR-000214 | NCR | Plumstead Portal - Embedded Wall & Piling - D Wall reinforcement cage - use of non conforming material |  | Contr |  | TUH - Thames Tunnel (East) |  | 2012-03-17 | 2012-04-27 11:52 | 41 | 2012-02-17 09:59 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | Coupled L bar was identified as being incorrect in fabricated cage for Panel N39. N39 cage was placed in the permanent works prior to clear authorisation for use of a non conforming material. The Contractors (__) designer for rthe cage einforcement was asked for opinion but no acceptance by Crossrail of the decision was formally recorded prior to placing the non conforming material. It is understood a verbal communication with Crossrail was made between __ and Crossrail and not Wriiten communication between __ and Crossrail. Incorrect materials had been supplied by The Reinforcement supplier and modifications to the reinbforcement had been made by the cage fabricator on site. see notes
| 01CV - Civils | Cxxx-NCR-000215 | NCR | Plumstead Portal - Embedded Wall & Piling - Acceptance of - Polymer & Bentonite Site Testing |  | Contr |  | TUH - Thames Tunnel (East) |  | 2012-03-17 | 2012-03-20 17:36 | 3 | 2012-02-17 10:23 | Civil - Civil Engineering General | 500 |  | System Defect | Repair |  | Complete |  | Completed |  | •The support fluid laboratory did not meet the Contract requirements for accreditations or Project Managers acceptance. Evidence for Crossrail acceptance of non UKAS lab was not sunbmitted. •There was no evidence to demonstrate that the Laboratory personnel were suitably skilled for the sampling and testing of support fluids. •Calibration records were not available for support fluid test and measurement equipment. Evidence requested were not available at the time of surveillance.
| 01CV - Civils | Cxxx-NCR-000221 | NCR | Plumstead Portal - Embedded Wall & Piling - Rotary Bore - Concrete Sampling & Acceptance |  | Contr |  | TUH - Thames Tunnel (East) |  | 2012-03-12 | 2012-03-20 17:06 | 8 | 2012-02-22 08:41 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | Sampling of fresh concrete for consistence prior to acceptance. Delivery ticket & __ pour record sheet attached indicates that the load was not sampled during pour for the Rotary Bore Pile No. 175 cast 07/02/12. There have been a number of similar instances of incorrect sampling due to supervision and managemernt of the works. Ref. NCR 159, 199, 207 & 213. not ensuring adequate cover is maintained during mandatory rest periods throughout the day.
| 01CV - Civils | Cxxx-NCR-000223 | NCR | Plumstead Portal - Embedded Wall & Piling - CFA Piles - Reinforcement not to full depth |  | Contr |  | TUH - Thames Tunnel (East) |  | 2012-03-23 | 2012-03-27 14:48 | 4 | 2012-02-24 10:13 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | CFA pile 279 toe of steel is 949mm above design level, CFA pile 281 toe of steel is 516mm above design level.
| 01CV - Civils | Cxxx-NCR-000224 | NCR | Plumstead Portal - Embedded Wall & Piling - |  | Contr |  | TUH - Thames Tunnel (East) |  | 2012-03-24 | 2012-03-30 17:42 | 6 | 2012-02-24 11:09 | Civil - Civil Engineering General | 500 |  | System Defect | Repair |  | Complete |  | Completed |  | With Ref. to NCR' on CFA Piles 279 & 281 constructed 21/02/12 & 16/02/12 correct information on non-conformance was not notified or confirmed until 23/02/12. In these instances It would be obvious at the time of installation that the non conformance existed and could not be corrected within the shift. __ notified __ on 20th of one instance without detail, __ requested clarification to raise on PTR. __ raised Internal NCR on 23rd and forward to __ by email on 23rd.
| 01CV - Civils | Cxxx-NCR-000225 | NCR | Plumstead Portal - Embedded Wall & Piling - Secant Wall - Instrument void former |  | Contr |  | TUH - Thames Tunnel (East) |  | 2012-03-23 | 2012-03-12 15:35 | -11 | 2012-02-24 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | Void Formers were missed from secant Pile 1250 as indicated in schedule / drawing ref. to Appendix 6/12
| 01CV - Civils | Cxxx-NCR-000233 | NCR | Plumstead Portal - Embedded Wall & Piling - Identity Sampling of Concrete Strength - 56 & 90 day samples |  | Contr |  | TUH - Thames Tunnel (East) |  | 2012-04-05 | 2012-04-27 11:58 | 22 | 2012-03-05 | Civil - Civil Engineering General | 500 |  | System Defect | Repair |  | Complete |  | Completed |  | Due to insufficient instructions to the cube testing labaratory and sampling technicians, this has not been followed from the begining of the job up until 30/01/12.
| 01CV - Civils | Cxxx-NCR-000236 | NCR | Diaphragm Wall IFC accepted after installation |  | Contr |  | TUH - Thames Tunnel (East) |  | 2012-03-23 | 2012-04-27 12:10 | 35 | 2012-03-09 | Civil - Civil Engineering General | 500 |  | System Defect | Repair |  | Complete |  | Completed |  | Panels N14 and N5 constructed on 06/03/12 and 07/03/12 respectively prior to the issue and acceptance of IFC drawing certificate. The IFC drawing certificate for thesespanels was received on 08/03/12.
| 01CV - Civils | Cxxx-NCR-000237 | NCR | Sheet Piling commenced without accepted documentation in place |  | Contr |  | TUH - Thames Tunnel (East) |  | 2012-03-23 | 2012-04-27 12:31 | 35 | 2012-03-09 | Civil - Civil Engineering General | 500 |  | System Defect | Repair |  | Complete |  | Completed |  | Sheet piling adjacent to the North __ Line in section 1A was commenced on 1 March without the agreed document approved by CRL and NR. Notably the Technical Statement that was highlighted as being required to address previous comments from NR was not delivered to CRL until 29 Feb.
| 01CV - Civils | Cxxx-NCR-000254 | NCR | Plumstead Portal- Embedded Wall & Piling- Rotary Bore - Pile 102 - Lost end of Tremmie in concrete pour. |  | Contr |  | TUH - Thames Tunnel (East) |  | 2012-04-23 | 2012-03-27 15:38 | -27 | 2012-03-23 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | Rotary Bored Pile 102 was completed on 21/03/2012 with 1no 3m section of steel tremmie pipe section cast insitu. The tremmie was not attached to the string when it was finally removed following completion of the pile. A delay was encountered waiting on the final part load of concrete for Pile 102
| 01CV - Civils | Cxxx-NCR-000255 | NCR | Tunnel Drive H - Precast Lining - Smallscale Fire Testing - Displacement of cast in Thermocouples |  | Contr |  | TUH - Thames Tunnel (East) |  | 2012-07-23 | 2012-03-27 15:01 | -118 | 2012-03-23 | Tunnelling - Linings - Precast | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | During casting of the Small Scale Fire Test pieces It was noted that a number of thermocouples were displaced during the casting process reducing the 25mm specified depth increment.
| 01CV - Civils | Cxxx-NCR-000261 | NCR | Plumstead Portal - Embedded Wall & Piling - Bentonite for Diaphragm Wall Contaminated |  | Contr |  | TUH - Thames Tunnel (East) |  | 2012-04-10 | 2012-03-29 08:43 | -12 | 2012-03-27 | Civil - Civil Engineering General | 500 |  | Material | Repair |  | Complete |  | Completed |  | High pH measured in Mixed Bentonite. Silo of Powder from same delivery checked also had high pH
| 01CV - Civils | Cxxx-NCR-000289 | NCR | Plumstead Portal - Embedded Wall & Piling - Secant Wall Pile Marmadon Sewer Section - Incorrect Reinforcement Cage Installed |  | Contr |  | TUH - Thames Tunnel (East) |  | 2012-05-11 | 2012-04-27 12:03 | -14 | 2012-04-11 | Civil - Civil Engineering General | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | 18m Long 9B40 cage was installed in pile 1186, which is in excess of design requirement, Pile had been cast before mistake ahad been realised. 05/04/2012
| 01CV - Civils | Cxxx-NCR-000290 | NCR | Plumstead Portal - Embedded Wall & Piling - D Wall Reinforcement Panel S1 |  | Contr |  | TUH - Thames Tunnel (East) |  | 2012-05-17 | 2012-05-01 13:29 | -16 | 2012-04-17 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | Welded Bars Spacing incorrect Bars touching adjacent bars, Incorrect Spacing of couplers insufficient gap between bars to allow flow of aggregate during placement of concrete.
| 01CV - Civils | Cxxx-NCR-000291 | NCR | Plumstead Portal - Reinfoced Concrete Form Work - Phase 1A Capping Beam dimensional Tolerance (flatness) of exposed to view concrete |  | Contr |  | TUH - Thames Tunnel (East) |  | 2012-08-31 | 2012-08-29 15:02 | -2 | 2012-04-17 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | Shuttering to external face uneven undulating along line of shutter which will result in unacceptrable surface finish exposed to public view. KF10.3223 in the opinion of the Project manager surface fails to meet dimensional tolerance Clause KF10.3226 straightness and KF10.3224 abrubt irregularity.
| 01CV - Civils | Cxxx-NCR-000302 | NCR | Volume C2 specifications |  | Contr |  | TUH - Thames Tunnel (East) |  | 2012-05-25 | 2012-06-01 10:25 | 7 | 2012-04-26 09:27 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Repair |  | Complete |  | Completed |  | Contractor was not fully informed of content of above specification resulting in note to NCR number DRH-CRL NCR-Cxxx-00291 on the subject that F4 finish has not been defined.
| 01CV - Civils | Cxxx-NCR-000303 | NCR | Calculations for all Temporary Works in Method Statements |  | Contr |  | TUH - Thames Tunnel (East) |  | 2012-08-03 | 2012-08-07 16:50 | 4 | 2012-04-26 09:48 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | Drawings & Calculations were not included in the Method Statement ref. Cxxx-HTM-Z-GMS-CR148-50053 for the fresh concrete loads against the single sheet plywood formwork that was supported by TW sheet piling.
| 01CV - Civils | Cxxx-NCR-000304 | NCR | Inspection verification records |  | Contr |  | TUH - Thames Tunnel (East) |  | 2012-05-25 | 2012-07-04 11:57 | 40 | 2012-04-26 10:05 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Repair |  | Complete |  | Completed |  | Planned arrangements or inspection verification records were not made available to demonstrate that appropriate controls were in place firstly to ensure that the sheet piling was installed in accordance with the Contractor’s TW design Cxxx-HTM-Z-RGN-CR148-50356 rev 3.0, and reinforcement steel traceability could not be demonstrated maintained as required by BS 4449:2005 referenced in specifications included in volume 2c
| 01CV - Civils | Cxxx-NCR-000322 | NCR | Plumstead Portal Flood Wall - Incorrect Flood Wall Dimensions and Geometry |  | Contr |  | TUH - Thames Tunnel (East) |  | 2012-08-31 | 2012-08-29 14:51 | -2 | 2012-05-15 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | South capping beam 33 flood wall was not constructed as per approved general arrangement drawings Cxxx-CSY-S-DDD-CR148_PT005-00131. The angle of the flood wall formed is greater than the angle specified, therefore creating a visible difference between SCB 34 flood wall to SCB 33 flood wall and also SCB 32 flood wall to SCB 33 flood wall.
| 01CV - Civils | Cxxx-NCR-000323 | NCR | Barth Mews sewer lining started work without fully signed ITP |  | Contr |  | TUH - Thames Tunnel (East) |  | 2012-05-29 | 2012-06-01 10:44 | 3 | 2012-05-15 | Civil - Sewage/Water services | 500 |  | System Defect | Repair |  | Complete |  | Completed |  | Works to reline Barth Mews sewer were started without the relevant ITP being signed off. Rev 2 incorporating TW comments was received by CRL on 3th May. Works to the sewer commenced on 9th May without the ITP being signed by CRL or third party, __.
| 01CV - Civils | Cxxx-NCR-000325 | NCR | Plumstead Portal South Capping Beam Bilnding Set out 500mm Short |  | Contr |  | TUH - Thames Tunnel (East) |  | 2012-06-15 | 2012-05-18 12:07 | -28 | 2012-05-15 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | 500mm of blinding was not poured to the western part of south capping beam 31. The precise location of the missing blinding was where the CFA piles terminate and the secant piles commence. Timber was used beneath the formwork in the location of the missing blinding to prevent the loss of any concrete during the pouring of SCB 31.
| 01CV - Civils | Cxxx-NCR-000331 | NCR | Plumstead Portal Flood Wall Profile & Finish not to Specification |  | Contr |  | TUH - Thames Tunnel (East) |  | 2012-08-31 | 2012-08-29 14:54 | -2 | 2012-05-18 10:40 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | South capping beam 33 - 35 flood wall was not constructed as per approved general arrangement drawings Cxxx-CSY-S-DDD-CR148_PT005-00131 to the satisfaction of the Supervisor ref Cls
| 01CV - Civils | Cxxx-NCR-000345 | NCR | NCB35-NCB31_closely installed top reinforcement bars |  | Contr |  | TUH - Thames Tunnel (East) |  | 2012-06-12 | 2012-07-25 12:54 | 43 | 2012-05-29 11:30 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | NCB32 Top reinforcement bars (Bar mark 12) were moved for concrete tremie pipe and vibrators to have sufficient space to enter cage and when concreting was completed they were not moved over as per drawing Cxxx-HTM-C-DWG-CR148-PT005-50301 and as discussed on site during pouring of concrete. This resulted in the overlap sections four reinforcement bars to be very close as well as all along the top of the capping beam the space betweeen two rebars to be 220mm deviating from 150mm design.
| 01CV - Civils | Cxxx-NCR-000346 | NCR | Repair works in North Flood Wall 32 |  | Contr |  | TUH - Thames Tunnel (East) |  | 2012-08-31 | 2012-08-29 15:07 | -2 | 2012-05-30 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Repair |  | Complete |  | Completed |  | Honeycombing of concrete and presence of large trapped air bubbles was noticed in the formed side and top faces of the top detail of the flood wall and remedial works were in the process of being carried out at the time of observation. The contractor had not informed the PM of a request for inspection of the finish of this concrete prior to remedial works starting and the PM had not accepted any remedial proposals or materials for the repairs. Currently there is no approved method statement for the required concrete remedial works. The PM reminds the contractor of clause KH 10.3224 a) “Workmanship in formwork and concreting shall be such that concrete shall normally not require any making good”
| 01CV - Civils | Cxxx-NCR-000347 | NCR | Non-Treatment of Concrete Joints between North Capping Beam kickers NCB 32, 33 & 35 & Floodwalls |  | Contr |  | TUH - Thames Tunnel (East) |  | 2012-06-13 | 2012-07-04 09:52 | 21 | 2012-05-30 | Civil - Structural Engineering | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | Construction Joints between North Capping Beam NCB 32, 33 & 35 and floodwalls NFW 32, 33 & 35 have not been treated to free joints from laitance.
| 01CV - Civils | Cxxx-NCR-000348 | NCR | D-Wall panel records for S9,S20,N2,S15,S8,N12 and S16 not complying |  | Contr |  | TUH - Thames Tunnel (East) |  | 2012-06-13 | 2012-07-03 11:38 | 20 | 2012-05-30 | Civil - Civil Engineering General | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | The following have been not complying on the D-Wall records for S9,S20,N2,S15,S8,N12 and S16: - Bentonite Fluid Loss tests for S9,S20,N2,S15 - No results for Viscocity and Gel strength test because the Rheometer was broken for panels S9,S20,S15,S8,N12 and S16. The records were submitted for review on 30/05/12 and the panels were constructed on 20/03/12 to 27/03/12. The PM was not made aware of this issues prior to the review.
| 01CV - Civils | Cxxx-NCR-000349 | NCR | New brick discharge manhole |  | Contr |  | TUH - Thames Tunnel (East) |  | 2012-06-13 | 2012-07-25 13:39 | 42 | 2012-05-30 | Civil - Drainage | 500 |  |  | Repair |  | Complete |  | Completed |  | ITP was submitted to CRL for review 3 days before start of work. Work commenced without signed ITP. ITP was subsequently rejected.
| 01CV - Civils | Cxxx-NCR-000354 | NCR | Plumstead - __ / __ Identity Testing 28 Day Concrete Strength |  | Contr |  | TUH - Thames Tunnel (East) |  | 2012-07-07 | 2012-07-16 12:37 | 9 | 2012-06-07 | Civil - Civil Engineering General | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | See attached Summary Spread sheet identifying failures in providing pairs from a sample, and failures against Criteria 1 & 2 for C32/40 and C40/ 50 families of non overlapping results for up to six results.__ have provided there own sampling results (not the same samples but samples taken on site) see attachments but have not yet tested at 28 days. They state the Mix design will continue to gain strength between 28 & 56 days. __ state poor cube making by our UKAS accredited professional service __. Attached evidence suggests samples have been missed or incorrectly allocated (no pair available for 28 day result. change in numbering system. Review of sampling (part 2 checksheet shows consistance has been below specified and water addition made. currently not proven as related to above samples.
| 01CV - Civils | Cxxx-NCR-000377 | NCR | Plumstead Portal Phase 1B - Base Slab B25 – B30, incorrect fixing detail used for reinforcement bars to be post drilled into Male secant piles. |  | Contr |  | TUH - Thames Tunnel (East) |  | 2012-07-22 | 2012-07-04 09:40 | -18 | 2012-06-25 11:34 | Civil - Civil Engineering General | 500 |  | System Defect | Use As-Is |  | Complete |  | Completed |  | 25mm Bars were drilled and proposed fixing was with __ RE 500. Design Change had not been communicated effectively. FCD had not been submitted for change to use of Epoxy Grout. Ref. Civil Engineering Design Standard 3.8.10.2 Piled Walls - "Links with couplers cast into the pile are preferred to avoid drilling and grouting, provided that the main bars are so detailed as to indicate un-ambiguously the location of the couplers, for example by the addition of an additional main bar. Drilled & grouted dowels may be used with a high strength, non-shrink, cementitious grout. Epoxy grouted dowels should not be used as they are prone to creep deflection."
| 01CV - Civils | Cxxx-NCR-000378 | NCR | Plumstead Portal Bulk Excavation Phase 1B – Construction sequence was changed without acceptance of Designer |  | Contr |  | TUH - Thames Tunnel (East) |  | 2012-07-25 | 2012-08-06 17:26 | 12 | 2012-06-25 | Civil - Civil Engineering General | 500 |  | System Defect | Use As-Is |  | Complete |  | Completed |  | Construction sequence was changed without acceptance of Designer. Poor change control management using acceptance of Method Statement to short cut procedure for acceptance of design change.Crossrail issued construction sequence drawings for the Plumstead Portal. Although not changing the Permanent Works, __ have changed the sequence of construction in Phase 1B of the Permanent Works, which is reflected in __’s submitted Method Statement (Cxxx-HTM-Z-GMS-CR148_PT005-50010, Rev. 3.0) to Crossrail, May 1st 2012.
| 01CV - Civils | Cxxx-NCR-000379 | NCR | Plumstead Portal Phase 1B Base SlabSplicing to Rollmat & Base Slab Reinforcement not in accordance with IFC Drawings , change to location of construction joints. |  | Contr |  | TUH - Thames Tunnel (East) |  | 2012-07-25 | 2012-07-04 09:34 | -21 | 2012-06-25 | Civil - Civil Engineering General | 500 |  | System Defect | Use As-Is |  | Complete |  | Completed |  | Splicing to Rollmat & Base Slab Reinforcement not in accordance with IFC Drawings , change to location of construction joints.Poor change control management FCD have not been raised prior to on site alteration during construction.
| 01CV - Civils | Cxxx-NCR-000385 | NCR | Phase 1B: Incorrect Base Slab Blinding Levels B28 and B29 |  | Contr |  | TUH - Thames Tunnel (East) |  | 2012-06-29 | 2012-08-07 16:34 | 39 | 2012-06-29 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | Blinding concrete to base slab B28 and B29 are higher than the design level i.e. 800mm below SSL level (See attached survey). The level is 32mm above design level in the worst case situation
| 01CV - Civils | Cxxx-NCR-000388 | NCR | Plumstead Portal D Wall Ground Anchor No. 6 As built position incorrect to design |  | Contr |  | TUH - Thames Tunnel (East) |  | 2012-08-03 | 2012-07-13 17:08 | -21 | 2012-07-03 | Civil - Civil Engineering General | 500 |  | Design | Use As-Is |  | Complete |  | Completed |  | For Anchor No. 6, due to a snapped casing, the original anchor position had to be abandoned. 4.0m length of casing was unrecoverable. Possible cause of casing snapping was an obstruction within the ground.
| 01CV - Civils | Cxxx-NCR-000389 | NCR | Plumstead Portal Base Slab B30 Incorrect installation of __ M__ Type ET Full strength Couplers |  | Contr |  | TUH - Thames Tunnel (East) |  | 2012-08-03 | 2012-07-13 17:06 | -21 | 2012-07-03 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | See attached Photo Typical on Pile caps in section B30 Pile cap reinforcement bar cropped too short to allow coupler to meet with each bar central to coupler (+/- 6mm gap between bars) Lock shear bolts not sheared identify width of gap. Bottom reinforcement mat prevents coupler being lowered prior to fixing. some lockshear bolts have been sheared prior to checking.
| 01CV - Civils | Cxxx-NCR-000390 | NCR | Plumstead Portal Phase 1B Construction Joints. Incorrect installation of Waterstop |  | Contr |  | TUH - Thames Tunnel (East) |  | 2012-08-03 | 2012-07-25 15:00 | -9 | 2012-07-03 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | Construction Joint fabricated from Hyrib is on outside edge of waterstop and not centred over it
| 01CV - Civils | Cxxx-NCR-000409 | NCR | Plumstead Portal - Floodwall Kicker - Formed Finish exposed to view is not F4 |  | Contr |  | TUH - Thames Tunnel (East) |  | 2012-08-17 | 2012-08-02 10:43 | -15 | 2012-07-20 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | The kicker formed from the capping beam pour for the Floodwall pour has been formed with timber and the finish to an exposed to view face at the base of the floodwall is not as specified in KF10 Structural Concrete Cxxx-CSY-S-RSP-CR146_PT004-00003 Rev 6.0 Ref. KF10.3222 Ref . Drawing Cxxx-CSY-S-DDL-CR148_PT005-00001 General Notes Structural Concrete Note 2 Formed Finishes. Class F4 - Faces of elements exposed to view in completed works. Formwork Class F4: The requirements for Class F4 are as for Class F3 except that internal ties and embedded metal parts may be permitted. The ties shall be positioned only in rebates or in other positions as shown on the Drawings.The surface finish of Class F3 formwork shall be that obtained by lining the formwork with smooth unblemished lining material such as large panels of filmfaced plywood arranged in a systematic and uniform pattern and fixed to back formwork by oval nails. The nailholes and joints shall be properly filled or taped. Alternatively steel sheet panels may be used. Unfaced wrought boarding or standard steel panels or internal ties and embedded metal parts shall not be used for Class F3 finish. The surface shall be entirely free from board and panel marks, surface pitting, fins, staining or blemishes of any kind.
| 01CV - Civils | Cxxx-NCR-000410 | NCR | Plumstead Portal - Base Slab Phase 1A &1B Bases B26 - B35 - Preparation of Rebar Drawings |  | Contr |  | TUH - Thames Tunnel (East) |  | 2012-08-20 | 2012-08-06 17:57 | -14 | 2012-07-20 | Civil - Civil Engineering General | 500 |  | System Defect | Use As-Is |  | Complete |  | Completed |  | Contractor Delarations of reinforcement were not raised prior to construction with changes for use of Rollmat, with changed splice and construction joint locations. Ref. DRH-CRL-FCD-Cxxx-00406 , 00400 ,00394, 00373 & 00372, and change to IFC Drawings Cxxx-CSY-S-DDL-CR148_PT005-02122 to 02125 Reference Contractors Drawings Ref. CCS_Cxxx_B35,to B26_ST??? issued under FCD's
| 01CV - Civils | Cxxx-NCR-000412 | NCR | Plumstead Portal - Base Slab Construction Joints - Encroachment of Hy-Rib into minimum cover zone |  | Contr |  | TUH - Thames Tunnel (East) |  | 2012-08-31 | 2012-08-29 14:32 | -2 | 2012-07-20 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | Proposal in FCD 384 not accepted non compliance to CEDS Cls 3.4.2.7 Construction Joints ref. Cxxx-CSY-S-DDD-CR148_PT005-00421 rev C01 joints between bases B26/B27 , B27/B28 & B28/B29 have been constructed with Hi-Rib stop end sitting on Serviseal 195 waterstop.
| 01CV - Civils | Cxxx-NCR-000418 | NCR | Preparation of Temporary Works ITPs |  | Contr |  | TUH - Thames Tunnel (East) |  | 2012-08-10 | 2012-08-02 10:38 | -8 | 2012-07-25 | Civil - Excavation | 500 |  | System Defect | Rework |  | Complete |  | Completed |  | The Temporary Works Coordinator whilst being involved in the preparation of the TW ITP was not entered on the front cover as either Prepared by or Reviewed by.
| 01CV - Civils | Cxxx-NCR-000444 | NCR | Plumstead Portal - South Capping beams S21 Kicker formwork to Floodwall |  | Contr |  | TUH - Thames Tunnel (East) |  | 2012-09-30 | 2012-08-29 15:22 | -32 | 2012-08-14 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | Flood wall kicker on capping beam S21 formed using planed timber only. This defect had previously been identified on capping beams S26-30 and rectified using a formwork grade plywood kicker.
| 01CV - Civils | Cxxx-NCR-000446 | NCR | Plumstead Portal - South Capping Beam 21 - Poor Concrete Compaction |  | Contr |  | TUH - Thames Tunnel (East) |  | 2012-09-30 | 2012-08-29 15:15 | -32 | 2012-08-14 11:14 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | Poor Compaction Honeycombing identified in Finished Concrete.
| 01CV - Civils | Cxxx-NCR-000447 | NCR | Plumstead Portal - South Capping Beam - Construction Joint Hyrib encroaching cover zone |  | Contr |  | TUH - Thames Tunnel (East) |  | 2012-09-30 | 2012-08-29 15:15 | -32 | 2012-08-14 11:23 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | Hyrib encroaching cover zone
| 01CV - Civils | Cxxx-NCR-000453 | NCR | Plumstead Portal - Concrete Placement of Concrete Prior to acceptance the by Project manager |  | Contr |  | TUH - Thames Tunnel (East) |  | 2012-08-30 | 2012-08-29 14:30 | -1 | 2012-08-16 | Civil - Civil Engineering General | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | Material Proposals Schedule Accepted, Submitted for acceptance Material Compliance Record ref. Cxxx-HTM-C-CER-CR148-50041 Rev 1.0 had not been returned as accepted prior to placing concrete mix ref Mix 3 DC3 / S4
| 01CV - Civils | Cxxx-NCR-000454 | NCR | Plumstead Portal - Placement of Non Conforming Concrete |  | Contr |  | TUH - Thames Tunnel (East) |  | 2012-08-30 | 2012-08-29 14:18 | -1 | 2012-08-16 | Civil - Civil Engineering General | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | Mix 3 Fibre DC3 placed in South Capping Beam 21, North Capping Beam 21 & Mix 3 DC3 placed in South Capping Beam 28 Material Compliance Records Pending Acceptance Mix 3 DC3 ref. Cxxx-HTM-C-CER-CR148-50041 Mix 3 Fibre DC3 ref. Cxxx-HTM-C-CER-CR148-50 Rev 1.0042 Rev 1.0
| 01CV - Civils | Cxxx-NCR-000460 | NCR | North Woolwich - Working Platform - No accepted ITP prior to Starting Work |  | Contr |  | TUH - Thames Tunnel (East) |  | 2012-09-21 | 2012-08-29 15:20 | -23 | 2012-08-21 08:17 | Civil - Civil Engineering General | 500 |  | System Defect | Repair |  | Complete |  | Completed |  | Inspection & Test Plan (ITP) - Piling Platform Phase 1 CH 88430-88820 - North Woolwich Work started 23/07/2012 Cxxx-HTM-Z-ITP-CR146_PT004-50001 Rev 1.0 issued late 03/08/12 Cxxx-HTM-C-RGN-CR146-50003 Rev 1.0 Code 3 ref. Cxxx-XRL-C-XCS-CR146-50014
| 01CV - Civils | Cxxx-NCR-000461 | NCR | North Woolwich - Construction of Guide Walls for Diaphragm Wall and Secant Piled Walls - ITP not accepted prior to Construction |  | Contr |  | TUH - Thames Tunnel (East) |  | 2012-09-21 | 2012-08-29 15:27 | -23 | 2012-08-21 08:30 | Civil - Civil Engineering General | 500 |  | System Defect | Repair |  | Complete |  | Completed |  | Inspection & Test Plan (ITP) - Construction of Guide Walls for Diaphragm Wall and Secant Piled Wall - North Woolwich (__) Work started 13/08/2012 Cxxx-HTM-Z-ITP-CR146_PT004-50002 Rev 2.0 re submitted 09/08/12 Cxxx-HTM-Z-ITP-CR146_PT004-50002 Rev 1.0 submitted 13/06/12 not accepted no code returned
| 01CV - Civils | Cxxx-NCR-000462 | NCR | Plumstead Portal Temporary D-Wall Extensions - Construction Started without accepted ITP in Place |  | Contr |  | TUH - Thames Tunnel (East) |  | 2012-09-21 | 2012-08-29 14:31 | -23 | 2012-08-21 08:53 | Civil - Civil Engineering General | 500 |  | System Defect | Repair |  | Complete |  | Completed |  | Inspection & Test Plan (ITP) - Construction of Plumstead Portal Temporary D-Wall Extensions - Work Started 13/08/12 Cxxx-HTM-Z-ITP-CR148_PT005-50016 Rev 1.0 submitted 09/08/12
| 01CV - Civils | Cxxx-NCR-000463 | NCR | Tunnel Drive H - Relining of __ 381mm & 457mm Sewers - Work started without accepted ITP in place. |  | Contr |  | TUH - Thames Tunnel (East) |  | 2012-09-21 | 2012-08-29 14:16 | -23 | 2012-08-21 09:06 | Civil - Civil Engineering General | 500 |  | System Defect | Repair |  | Complete |  | Completed |  | Inspection & Test Plan (ITP) - Lining of the 381mm +457mm Sewers work Started on relining the 457mm sewer in White Hart Road 13/08/12 Cxxx-HTM-Z-ITP-CR148-50003 Rev 2.0 resubmitted 26/07/12 Cxxx-HTM-Z-ITP-CR148-50003 Rev 1.0 submitted 11/07/12 not accepted no code returned
| 01CV - Civils | Cxxx-NCR-000464 | NCR | Plumstead Portal - Bulk Excavation and Installation of temporary Propping - Phase 4 -6 |  | Contr |  | TUH - Thames Tunnel (East) |  | 2012-09-21 | 2012-08-29 15:26 | -23 | 2012-08-21 09:25 | Civil - Civil Engineering General | 500 |  | System Defect | Repair |  | Complete |  | Completed |  | Inspection & Test Plan (ITP) - Plumstead Portal - Bulk Excavation and Installation of temporary Propping & Waling Supports ITP revised from rev 3 to rev 4 with change in scope of works from Phase 1A to Phase 4-6 Propping, Rev 4 & 5 have not been accepted prior to Construction. Excavation Work Started 26/06/12 Propping Work started 06/07/12 Cxxx-HTM-Z-ITP-CR148_PT005-50006 Rev 5.0 submitted 01/08/12 not accepted no code returned Cxxx-HTM-Z-ITP-CR148_PT005-50006 Rev 4.0 submitted 17/07/12 not accepted no code returned Cxxx-HTM-Z-ITP-CR148_PT005-50006 Rev 3.0 submitted 3/04/12 accepted code 1 18/04/12
| 01CV - Civils | Cxxx-NCR-000496 | NCR | Plumstead Portal - RC Prop L33 Concrete Cover |  | Contr |  | TUH - Thames Tunnel (East) |  | 2012-10-15 | 2012-10-17 17:34 | 2 | 2012-09-13 08:18 | Civil - Civil Engineering General | 500 |  | Design | Use As-Is |  | Complete |  | Completed |  | L33 RC prop that was poured 11/9/2012. There was localised minimum cover observed of 25mm (see attached photographs for detail). The RC prop U-bar that connects to the capping beam is 32mm diameter. The Capping beam T1 reinforcement is 25mm.I.e. 7mm difference between T1 reinforcement at the capping beam to RC prop connection.
| 01CV - Civils | Cxxx-NCR-000503 | NCR | Cxxx - Plumstead Portal - Incorrect Base Slab 35 to Transition Slab Coupler Position |  | Contr |  | TUH - Thames Tunnel (East) |  | 2012-10-01 | 2012-10-03 17:02 | 2 | 2012-09-18 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | Part 1: -As shown in drawing Cxxx-CSY-S-DDL-CR148_PT005-02126 and CSS_Cxxx_B35_RC_ST_010 the 5 couplers at the end of Base Slab 35 on the south capping beam should have been 45mm cover. However this coupler was positioned outside of the pour. -No bar could be inserted into the top coupler (BM 07) at the end of BS 35 on the north capping beam as there was a clash with the U-Bar (BM 11) running in the opposite direction. Part 2: -Furthermore remedial works were undertaken without approval.
| 01CV - Civils | Cxxx-NCR-000507 | NCR | Cxxx - Plumstead Portal - South Capping Beam 17 Concrete |  | Contr |  | TUH - Thames Tunnel (East) |  | 2012-10-04 | 2012-10-03 17:52 | -1 | 2012-09-20 11:25 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | At box out for reinforced concrete prop 29 (as shown on Cxxx-HTM-C-DWG-CR148_PT005-50307) in south capping beam 17 and at interface with south capping beam 16 concrete has not been place or compacted sufficiently leaving a void and poorly compacted concrete below horizontal layer of Hy-rib.
| 01CV - Civils | Cxxx-NCR-000508 | NCR | Re-lining of the 381 sewer |  | Contr |  | TUH - Thames Tunnel (East) |  | 2012-10-04 | 2012-10-02 09:02 | -2 | 2012-09-20 | Civil - Utilities Engineering | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | CRL and TW did not witness the pre-lining CCTV survey and jet washing of the cleaner. CRL and TW were informed that will happen between 9:00-9:30. The jetter was not on site and would be later in. __ failed to inform CRL and TW when they arrived. When TW querried wen they arrive __ informed them the lining of the sewer was in progress.
| 01CV - Civils | Cxxx-NCR-000510 | NCR | Plumstead Portal - RC Prop 32 - 18mm iregularity in formed concrete |  | Contr |  | TUH - Thames Tunnel (East) |  | 2012-10-25 | 2012-10-24 16:32 | -1 | 2012-09-25 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | A section of ply at the shutter support location on RC Prop 32 was poorly installed and has created an uneven line in the bottom face of the prop. See photo below. The defect is an 18mm abrupt irregularity, in the worst case across a large area. (KF10 – Structural Concrete is the relevant specification).
| 01CV - Civils | Cxxx-NCR-000511 | NCR | Plumstead Portal - Base Slab Coupler Detail Change |  | Contr |  | TUH - Thames Tunnel (East) |  | 2012-10-25 | 2012-10-24 16:31 | -1 | 2012-09-25 | Civil - Civil Engineering General | 500 |  | System Defect | Use As-Is |  | Complete |  | Completed |  | __ installed B32 at both insert locations, on both the north and south wall. The bar schedule and corresponding reinforcement drawings for this section do not reflect this change.
| 01CV - Civils | Cxxx-NCR-000512 | NCR | Plumstead Portal - D Wall Alignment - Headwall |  | Contr |  | TUH - Thames Tunnel (East) |  | 2012-10-25 | 2012-10-24 16:05 | -1 | 2012-09-25 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | The alignment of D-Wall Headwall Panel H3 is out of tolerance (Specification KP10.3212 - Vertical Alignment 1:150). This misalignment in the headwall has affected the details for the RC lining wall at this location, as well as the starter bars in the RC slab in Base Slab B1, which will no longer fit as detailed.At the bottom of the base slab the wall is out of position (encroaching into the wall position) by a maximum of 443mm.
| 01CV - Civils | Cxxx-NCR-000518 | NCR | Plumstead Portal - South Capping Beam 16 - Honeyconmbing & Grout loss |  | Contr |  | TUH - Thames Tunnel (East) |  | 2012-10-26 | 2012-10-24 16:50 | -2 | 2012-09-26 08:57 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | The inside face of SCB16, adjacent to SCB17, has suffered from a section of honeycombing/grout loss at the bottom edge of the shutter (photo held under Contractors Records). This was identified following the striking of the shutter on 25/09/12 and recorded on the Post Pour Inspection Record. The defect was classified as a Type 3 Defect (as defined in Cxxx-HTM-Z-GMS-CR148_PT005-50016) and an NCR has been raised in accordance with the outlined procedure.
| 01CV - Civils | Cxxx-NCR-000520 | NCR | Bored Pile Cut-Off Levels |  | Contr |  | TUH - Thames Tunnel (East) |  | 2012-10-05 | 2012-10-03 17:58 | -2 | 2012-09-28 | Civil - Civil Engineering General | 500 |  | Design | Use As-Is |  | Complete |  | Completed |  | Bored pile cut off-level in Phase 4 base slab B1 and B2 was set out as per drawing Bored Piling Schedule: Cxxx-CSY-S-DDJ-CR148_PT005-00300. Asbuilt – Pile Cut-Off Level As-Built shows the survey record of setting out. Concrete blinding is placed at grade and the pile cut off is shown level. Therefore the distance from the blinding to the pile cut-off level increases from the eastern side of the pile to the western side of the pile. This has caused the reinforcement to be set high as the chairs are at a fixed height. This has the resulting effect of the base slab cast 40-50mm above design SSL. Note: Mass concrete is to be constructed above the SSL as per drawing Cxxx-CSY-S-DDL-CR148_PT005-00401
| 01CV - Civils | Cxxx-NCR-000521 | NCR | Base Slab B1 Reinforcement |  | Contr |  | TUH - Thames Tunnel (East) |  | 2012-10-01 | 2012-10-03 17:48 | 2 | 2012-09-28 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | Part 1: RFI 00458 states that 1 No. bar can be cut in each direction in the top and bottom layers to accommodate the puddle flange and allow for the installation of the blanking plate. At 1 No. well location the top layer reinforcement, 3 No. bars where cut in one direction and 4 No. cut in the other direction Part 2: The minimum lap of 1100mm was not achieved for BM 04 and BM29 splicing with BM 01 ABR B2. The distance between north and south D-wall in this area is on average 18.8m. The overall length of BM 01 + BM 04 + BM 29 – lap length = 18.450. Difference of 0.350m. I.e. The design does not allow for the lap lengths to be achieved.
| 01CV - Civils | Cxxx-NCR-000531 | NCR | Plumstead Portal - Low 28 Day Characteristic Strength Results - Supplier __ |  | Contr |  | TUH - Thames Tunnel (East) |  | 2012-10-08 | 2012-10-10 11:38 | 2 | 2012-10-01 | Civil - Civil Engineering General | 500 |  | Material | Rework |  | Complete |  | Completed |  | Following on from the change in Mix design from DC4 to DC3 some improvement was shown in Consistance and strength gain for Mix 3 DC3 however on starting with Mix 3 Fibre (addition of 2kg of Poly fibre for fire resistance) Compressive strength results produced a number of failures. Most noticable were results for concrete placed on 9th August. 56 Day results taken for High GGBS were also showing low or failed results. Summary of Cube test results attached.
| 01CV - Civils | Cxxx-NCR-000533 | NCR | Plumstead Portal - __ Mix 3 DC4 - Low 28 day Concrete Cube Strengths |  | Contr |  | TUH - Thames Tunnel (East) |  | 2012-11-02 | 2012-11-02 17:08 | 0 | 2012-10-02 | Civil - Civil Engineering General | 500 |  | Material | Rework |  | Complete |  | Completed |  | 28 Day Cube Strengths fail as individual cube result , & as Average test result Criterial 1 non overlapping results for 1 - 6 results & Criteria 2 average result. Areas where individual result (Criteria 2) failed to meet Design Strength are Capping Beam <50N/mm2 (SCB 31)(NCB 31)(SCB27) & Flood Wall <40N/mm2 ( NFW32)( NFW34)( NFW31)(NFW33) see attached Charts & concrete conformity analysis
| 01CV - Civils | Cxxx-NCR-000534 | NCR | Plumstead Portal - Wrong Concrete Mix called off & placed South Capping Beam 22 |  | Contr |  | TUH - Thames Tunnel (East) |  | 2012-11-02 | 2012-10-29 09:52 | -4 | 2012-10-03 | Civil - Civil Engineering General | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | Shedukled call off identified correctly that capping beam 22 was outside of the covered section and mix 3 DC3 S4 was provisionally ordered with the batcher. The Pre pour inspection record also identifies Mix 3. On the day of the Pour the supervisor called off Mix 3 Fibre. Post inspection it was noted that the surface finish was different and investigation identified the wrong material had been placed.
| 01CV - Civils | Cxxx-NCR-000539 | NCR | Plumstead Portal - Base Slab B2 |  | Contr |  | TUH - Thames Tunnel (East) |  | 2012-11-05 | 2012-11-06 09:37 | 1 | 2012-10-05 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | A number of bar mark 09 and 10 bars were omitted from the pour. These bars comprise the threaded dowel bars that are attached to the insert couplers of the diaphragm wall. The threads of the couplers have been damaged and would not accept threaded dowels. This damage is likely to have occurred during the diaphragm wall construction. Each panel of the diaphragm wall should have two inserts of 14 bars - a total of 28 per panel. The sketch attached details the number of bars achieved:
| 01CV - Civils | Cxxx-NCR-000546 | NCR | Plumstead Portal - Method Statement not accepted prior to stating work |  | Contr |  | TUH - Thames Tunnel (East) |  | 2012-11-09 | 2012-11-09 16:38 | 0 | 2012-10-09 | Civil - Civil Engineering General | 500 |  | System Defect | Repair |  | Complete |  | Completed |  | Method Statement for Base slab Cxxx-HTM-Z-GMS-CR148_PT005-50015 Rev 1.0 had not been accepted on eB prior to starting construction of Base slab B1 & B2 (Phase 4 works) Submitted 13th September. Works commenced on B1 25.09/12 Document on eB had not been accepted by 05/10/12 when revision 2 superseded revision 1. neither rev 1 or rev 2 have been accepted by croissrail as of todays date 9th October 2012.
| 01CV - Civils | Cxxx-NCR-000547 | NCR | Plumstead Portal - Checking Competency Persons Performing Quality Assurance |  | Contr |  | TUH - Thames Tunnel (East) |  | 2012-11-09 | 2012-11-06 10:06 | -3 | 2012-10-09 | Civil - Civil Engineering General | 500 |  | System Defect | Repair |  | Complete |  | Completed |  | o__ & __ were not on Subcontract Supplier QA Schedule no assessment of organisation structure or competences. oCV & organisation held in subcontract files identified competence in years experience and certification for Lightning Conductor engineer. Certificates had not been included. o__ __ Records of organisation Design Plan & Competence were not found at the time surveillance and have ben requested The Schedule of Subcontractors Cxxx-HTM-O4-TSC-CR148-50004 Rev 2.0 Code 2 effective date 17/04/12 Ref. QA requirements & competence not up to date.
| 01CV - Civils | Cxxx-NCR-000548 | NCR | Plumstead Portal - No material Compliannce acceptance for built in items changed from WI - base B1. |  | Contr |  | TUH - Thames Tunnel (East) |  | 2012-11-09 | 2012-11-06 10:10 | -3 | 2012-10-09 | Civil - Civil Engineering General | 500 |  | Material | Repair |  | Complete |  | Completed |  | oMateriald discussed in RFI not on Material proposal schedule No MCR for Dewatering Puddle Flanges built into pour, Flanges fitted by __. Bespoke fabrication of Flange & Blanking Plate by __ ref RFI 00458 oNo MCR for RASCO tight Hydrophilic Channel Ref. Observation Report 04-1213P07W3 - For the Base Slab B2 installation (and onwards) the RASCOtight QVE Hydrophilic Strip has been substituted by a RASCO tight Hydrophilic Channel to remove the issues with installation and fixing.
| 01CV - Civils | Cxxx-NCR-000549 | NCR | Cxxx Plumstead – North Capping Beam 16 Missing Couplers |  | Contr |  | TUH - Thames Tunnel (East) |  | 2013-02-11 | 2013-02-07 15:19 | -4 | 2012-10-10 08:56 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | Griptech couplers are installed in the phase 3 north capping beam to facilitate the construction of the NKL run-on slab at a later date. During the construction of north capping beam 16 the run-on slab couplers where not installed.
| 01CV - Civils | Cxxx-NCR-000553 | NCR | North Woolwich Portal - Embedded Wall & Piling - Rotary Bore Pile No.2 |  | Contr |  | TUH - Thames Tunnel (East) |  | 2012-11-11 | 2012-11-01 15:24 | -10 | 2012-10-11 | Civil - Civil Engineering General | 500 |  | Workmanship | Rework |  | Complete |  | Completed |  | __ concreting operatives allowed the bentonite level (within the casing) to get lower than permitted resulting in reduction of head of pressure. __ Engineer reported the incident when producting the on site tremmie graph and __ supervisor then recorded bentonite levels to be 3-4m below ground level at the time of the incident. There have been no issues reported during the excavations of this pile or others even when left over night levels of bentonite and settlement were as expected. __ also report that this pile should not be used in the permanent design and request CRL Designers look at the permanent works design and advise an alternative.
| 01CV - Civils | Cxxx-NCR-000560 | NCR | Tunnel Drive H - Ground Treatment (__) Pali Radice - Grout cube storage on site |  | Contr |  | TUH - Thames Tunnel (East) |  | 2012-11-19 | 2012-11-12 14:29 | -7 | 2012-10-19 09:03 | Civil - Civil Engineering General | 500 |  | Material | Repair |  | Complete |  | Completed |  | Cube Storage for Grout Cubes Sampled by __s & Collected by __ for Testing werre observed to be stored in an unheated water tank. The Tank was located outside a container without power to provide heating & thermostatic Control.
| 01CV - Civils | Cxxx-NCR-000561 | NCR | Tunnel Drive H - Ground Treatment (__) - Control of Calibrated Equipment |  | Contr |  | TUH - Thames Tunnel (East) |  | 2012-11-19 | 2012-11-12 14:53 | -7 | 2012-10-19 09:18 | Civil - Civil Engineering General | 500 |  | System Defect | Repair |  | Complete |  | Completed |  | Mud Density test recorded with Mud Balance (Fann Model 140) which had no calibration or serial no.
| 01CV - Civils | Cxxx-NCR-000562 | NCR | Tunnel Drive H - Ground Treatment (__) - Document Control Document Numbering |  | Contr |  | TUH - Thames Tunnel (East) |  | 2012-11-19 | 2012-11-14 15:32 | -5 | 2012-10-19 09:32 | Civil - Civil Engineering General | 500 |  | System Defect | Rework |  | Complete |  | Completed |  | Ref Method Statement section 2 & Appendix & Drawing No. References contained in Method Statement & ITP - Doc control of Drawing Numbers - There were Mixed __ & eB numbers referenced in Documents Cxxx-HTM-Z-GMS-CR146_ST004-50006 , Cxxx-HTM-X-STP-CR148-50035 Cxxx-KGE-C-DWG-0001 (Cxxx-HTM-C-DWG-CR146-PT004-81001) Cxxx-HTM-C-ITP-CR146_ST004-50003
| 01CV - Civils | Cxxx-NCR-000564 | NCR | Damaged Couplers in D-Wall at B5 and B6 Slabs |  | Contr |  | TUH - Thames Tunnel (East) |  | 2012-11-16 | 2012-10-29 09:52 | -18 | 2012-10-19 | Civil - Civil Engineering General | 500 |  | Damaged | Use As-Is |  | Complete |  | Completed |  | In Base Slab B5 there are two damaged couplers in the north D-Wall panel N18. In Base Slab B6 there is one damaged coupler in the south D-Wall panel S22. The couplers have been crushed during the works and we will be unable to tap the threads as has previously been possible for damaged couplers.
| 01CV - Civils | Cxxx-NCR-000568 | NCR | Test cubes –storage |  | Contr |  | TUH - Thames Tunnel (East) |  | 2012-11-07 | 2012-11-06 09:40 | -1 | 2012-10-24 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Repair |  | Complete |  | Completed |  | Cubes seen during surveillance of 23rd October were stored at temperature of 29°C in plastic bags which were ineffective at preventing dehydration.
| 01CV - Civils | Cxxx-NCR-000569 | NCR | Reinforcement steel cover |  | Contr |  | TUH - Thames Tunnel (East) |  | 2012-11-21 | 2012-10-25 10:33 | -27 | 2012-10-24 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Rework |  | Complete |  | Completed |  | Not all tie wire seen during the surveillance of 23rd October was turned into the main body of the concrete reducing cover by up to 50mm
| 01CV - Civils | Cxxx-NCR-000570 | NCR | Base Slab B7 |  | Contr |  | TUH - Thames Tunnel (East) |  | 2012-11-15 | 2012-11-01 15:12 | -14 | 2012-10-25 08:54 | Civil - Civil Engineering General | 500 |  | Damaged | Use As-Is |  | Complete |  | Completed |  | 2 no. wall couplers in the D-Wall Panel are damaged beyond repair. This has meant that 1 no. 25mm threaded wall bar has not been installed in each of panels N25 and S26.
| 01CV - Civils | Cxxx-NCR-000571 | NCR | Damage to surface of B7 B8 Base Slab |  | Contr |  | TUH - Thames Tunnel (East) |  | 2012-11-15 | 2012-11-12 14:11 | -3 | 2012-10-25 | Civil - Civil Engineering General | 500 |  | Damaged | Use As-Is |  | Complete |  | Completed |  | Due to an issue with the dewatering system on the evening of the 23/10/12, water leaked across the surface of the frsh concrete of the base slab poured on the same day. The surface has been lightly scarred and some of the concrete around the pockets for the wells has spalled.
| 01CV - Civils | Cxxx-NCR-000574 | NCR | Cxxx - Plumstead Portal - RC Prop L29 / NCB 16 Box Out Location |  | Contr |  | TUH - Thames Tunnel (East) |  | 2012-11-07 | 2012-11-09 16:45 | 2 | 2012-10-27 | Civil - Civil Engineering General | 500 |  | Workmanship | Rework |  | Complete |  | Completed |  | RC Prop L29 north capping beam box out has been constructed 282mm west of the correct alignment. L29 prop has not yet been constructed; however the box out to NCB 16 (which has been constructed) dictates the position of L29 RC prop. The alignment error occurred due to incorrect co-ordinates on Cxxx-HTM-C-DWG-CR148-PT005-51034 Rev 3.0 which were used for setting out.
| 01CV - Civils | Cxxx-NCR-000575 | NCR | Steel Reinforcement for Head Wall Lining Wall - Inserts in adjacent D-Wall Panels (1st Lift) |  | Contr |  | TUH - Thames Tunnel (East) |  | 2012-10-29 | 2012-11-01 16:21 | 3 | 2012-10-29 08:34 | Civil - Civil Engineering General | 500 |  | Damaged | Rework |  | Complete |  | Completed |  | A number of the couplers have been damaged and will not receive the threaded dowel bar. There are a total of 14 missing on the south wall and 5 missing on the north wall. The missing bars are split between both the NF and FF. *Note: 3 no. couplers were repaired on the north wall bringing the total missing to 2.
| 01CV - Civils | Cxxx-NCR-000576 | NCR | Steel Reinforcement for Head Wall Lining Wall - Inserts in adjacent D-Wall Panels (2nd Lift) |  | Contr |  | TUH - Thames Tunnel (East) |  | 2012-11-02 | 2012-11-01 17:08 | -1 | 2012-10-29 | Civil - Civil Engineering General | 500 |  | Damaged | Rework |  | Complete |  | Completed |  | A number of the couplers have been damaged and will not receive the threaded dowel bar. There are a total of 13 missing on the south wall and 12 missing on the north wall. The missing bars are split between both the NF and FF. See attached sketch for positions.
| 01CV - Civils | Cxxx-NCR-000582 | NCR | Phase 3: Concrete Compressive Strengths for Capping Beams |  | Contr |  | TUH - Thames Tunnel (East) |  | 2012-11-15 | 2012-11-14 15:27 | -1 | 2012-11-01 | Civil - Civil Engineering General | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | The C40/50 DC3 Fibre S4 concrete used to form the capping beams in Phase 3 do not meet the requirements of BS EN 206-1. Refer to attached document: 12.10.30 Graph DC3 Fibre.pdf; for a summary of the cube results. In trying to understand the reasons for this failure to attain the required compressive strength, __ undertook a coring survey of the capping beams in Phase 3 to determine in-situ compressive strengths. Refer to attached document: Phase 3 Coring Overview.pdf; for details of coring positions and results. __ have undertaken an assessment of these result, following the guidance of BS EN 13971 and BS 6089. The final determination of whether each of the capping beams is deemed to contain concrete with adequate strength is based on Clause 9 of BS EN 13791. Refer to attached document: Clause 9 Analysis - Phase 3 Beam.xlsx; for an assessment of core results for each capping beam. The assessment identifies capping beams that are not deemed to contain concrete with adequate strength.
| 01CV - Civils | Cxxx-NCR-000583 | NCR | Phase 2: Concrete Compressive Strengths for Capping Beam SCB22 |  | Contr |  | TUH - Thames Tunnel (East) |  | 2012-11-22 | 2012-11-19 16:41 | -3 | 2012-11-01 | Civil - Civil Engineering General | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | The C40/50 DC3 Fibre S4 concrete used to form the capping beam SCB22 in Phase 2 does not meet the requirements of BS EN 206-1. Refer to attached document: 12.10.30 Graph DC3 Fibre.pdf; for a summary of the cube results. In trying to understand the reasons for this failure to attain the required compressive strength, __ undertook a coring survey of the capping beam SCB22 in Phase 2 to determine in-situ compressive strengths. Refer to attached document: Phase 3 Coring Overview.pdf; for details of coring positions and results. __ have undertaken an assessment of these result, following the guidance of BS EN 13971 and BS 6089. The final determination of whether each of the capping beams is deemed to contain concrete with adequate strength is based on Clause 9 of BS EN 13791. Refer to attached document: Clause 9 Analysis - Phase 2 Beam.xlsx; for an assessment of core results for each capping beam.
| 01CV - Civils | Cxxx-NCR-000586 | NCR | North Woolwich Portal - D Wall - Top S18 Cage installed low |  | Contr |  | TUH - Thames Tunnel (East) |  | 2012-12-02 | 2012-11-29 11:21 | -3 | 2012-11-02 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | Bar BM06 installed 750mm above cut off level / Reinforcement not checked prior to release.
| 01CV - Civils | Cxxx-NCR-000587 | NCR | Tunnel Drive H - Ground Treatment - Palli Radice Pile Obstruction missed out pile |  | Contr |  | TUH - Thames Tunnel (East) |  | 2012-11-05 | 2012-11-06 15:58 | 1 | 2012-11-02 | Civil - Civil Engineering General | 500 |  | Design | Use As-Is |  | Complete |  | Completed |  | Obstruction encountered Pile WAP08 missed out
| 01CV - Civils | Cxxx-NCR-000588 | NCR | Reinforcemtn for Base Slabs B9 & B10 |  | Contr |  | TUH - Thames Tunnel (East) |  | 2012-12-03 | 2012-11-14 15:33 | -19 | 2012-11-05 | Civil - Civil Engineering General | 500 |  | Damaged | Use As-Is |  | Complete |  | Completed |  | A number of couplers, cast into the D Wall panels, have been damaged during the portal works. This has resulted in a number of threaded dowel bars being omitted from the reinforcement installation for base slabs 9 and 10. The locations of the missing threaded dowel bars: 1 no. at Panel N35 1 no. at Panel N36 1 no. at Panel N38 1 no. at Panel S35 1 no. at Panel S38 2 no. at Panel N31 1 no. at Panel S31
| 01CV - Civils | Cxxx-NCR-000597 | NCR | Position of Headwall Lining Wall |  | Contr |  | TUH - Thames Tunnel (East) |  | 2012-12-07 | 2012-12-05 11:03 | -2 | 2012-11-09 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | A positional survey has been carried out on the headwall lining wall as part of the post pour inspection. Please see attached sketch. There is lipping at the south end of the wall between the 1st and 2nd lifts. At its most pronounced the lip is 27mm. It is assumed that this has occured as the 2nd shutter face caught on the back face of the 1st lift shutter face (dims are approx thickness of ply sheet).
| 01CV - Civils | Cxxx-NCR-000601 | NCR | Surface Finish of Concrete at Headwall Lining Wall |  | Contr |  | TUH - Thames Tunnel (East) |  | 2012-12-12 | 2012-12-11 11:16 | -1 | 2012-11-14 10:11 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | The concrete surface does not meet the requirements of the specification. There has been grout loss at both the vertical and horizontal joints of the shutters. at the central location of the lining wall i.e. between the tunnel eye positions where the two part shutters connected together.
| 01CV - Civils | Cxxx-NCR-000604 | NCR | Base Slab 35 - Concrete finishing |  | Contr |  | TUH - Thames Tunnel (East) |  | 2012-11-29 | 2012-11-29 09:24 | 0 | 2012-11-15 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | During finishing of concrete at base slab 35 additional water was added to concrete by the concreting gang. This is not in accordance with the method statement (Cxxx-HTM-Z-GMS-CR148_PT005-50009) for these works.
| 01CV - Civils | Cxxx-NCR-000612 | NCR | Concrete Finish for NCB17 and RC Prop 28 |  | Contr |  | TUH - Thames Tunnel (East) |  | 2012-12-17 | 2012-11-26 13:20 | -21 | 2012-11-19 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | The concrete surface does not meet the requirements of the specification. There has been grout loss at the bottom edge of the shutters and a cold joint in NCB17. The RC Prop 28 has grout loss at the interface with the south capping beam and the bottom edges are poorly finished.
| 01CV - Civils | Cxxx-NCR-000614 | NCR | Base Slab 11 Couplers |  | Contr |  | TUH - Thames Tunnel (East) |  | 2012-12-19 | 2012-12-05 11:47 | -14 | 2012-11-21 | Civil - Civil Engineering General | 500 |  | Damaged | Use As-Is |  | Complete |  | Completed |  | Base Slab 11 and Base Slab 12 are to be poured together. During a pre pour inspection it was noted that a number of D-wall couplers had been damaged and were unable to accept the threaded dowel bar as per the design. The panel locations were: 1 no. in N39 1 no. in N41 2 no. in S40 2 no. in S42
| 01CV - Civils | Cxxx-NCR-000632 | NCR | Concrete Finish to RC Prop L29 |  | Contr |  | NOW - North Woolwich Portal (East) |  | 2012-12-21 | 2012-11-29 | -22 | 2012-11-27 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | The concrete surface does not meet the requirements of the specification. Mastic used to seal the shutter at the interface with the capping beam had built up and formed an obstruction within the shutter. This has created a large void in the concrete finish (see photographs)
| 01CV - Civils | Cxxx-NCR-000635 | NCR | North Woolwich Portal - Embedded Wall & Piling - Rotary Bore Pile No.70 |  | Contr |  | TUH - Thames Tunnel (East) |  | 2012-12-13 | 2012-12-07 16:04 | -6 | 2012-11-29 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | The top of steel for Pile 70 has been cast 289mm higher than designed (95.563 m OD) level at 95.852 m AOD. This makes the cage 139mm over the allowed tolerance of 150mm. The cage is usually set 100mm above the designed level to accommodate any sinking in the chalk (standard practice).
| 01CV - Civils | Cxxx-NCR-000639 | NCR | Base Slab 13 and 14 Couplers |  | Contr |  | TUH - Thames Tunnel (East) |  | 2013-01-10 | 2012-12-11 11:23 | -30 | 2012-11-30 | Civil - Civil Engineering General | 500 |  | Damaged | Use As-Is |  | Complete |  | Completed |  | Base Slab 13 and Base Slab 14 are to be poured together. During a pre pour inspection it was noted that a number of D-wall couplers had been damaged and were unable to accept the threaded dowel bar as per the design. The panel locations were: Base Slab 13: 1 no. in S48 Base Slab 14: 1 no. in S51 1 no. in S52 2 no. in S54
| 01CV - Civils | Cxxx-NCR-000646 | NCR | Phase 2: Concrete Compressive Strengths for Capping Beam SCB22 UPDATE |  | Contr |  | TUH - Thames Tunnel (East) |  | 2013-01-11 | 2012-12-17 14:42 | -25 | 2012-12-07 | Civil - Civil Engineering General | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | The 28 day compressive cube strengths and the 28 day in situ compressive core strengths did not meet the requirements of the design specification. This has been documented in DRH-CRL NCR-Cxxx-00583. Following the criteria outlined in BS6089 and BS EB 13791 a C40/50 design mix would have an equivalent in-situ compressive strength requirement of 39.1 N/mm2 at 28 days. We have carried out additional testing and have attached test certificates which show that cores taken from the SCB22 have achieved an equivalent in-situ cube strength of 55 N/mm2 and 53.8 N/mm2 at 56 days. Please see attached certificates.
| 01CV - Civils | Cxxx-NCR-000647 | NCR | Phase 3/Phase 6: Leak at joint between D-Wall and Secant Pile Wall |  | Contr |  | TUH - Thames Tunnel (East) |  | 2013-01-14 | 2012-12-11 11:42 | -34 | 2012-12-10 | Civil - Civil Engineering General | 500 |  | Design | Repair |  | Complete |  | Completed |  | Following excavation a considerable leak was discovered at the join in the south wall between the secant piled section and the diaphragm wall. At Plumstead Portal the secant piled section was constructed prior to the diaphragm wall. As such, the secant piles could not be ‘cut’ into the diaphragm wall. Instead the line of the secant pile section, at the joint location, was modified to miss the diaphragm wall with a gap to allow for installation tolerances. Refer to attached drawing Cxxx-HTM-C-DWG-CR148-PT005-52021 for details of how the design accounted for the closing of this gap using a permeation grout plug. For the permanent works and final situation a lining wall will be installed and concreted in front of the secant wall. The permeation grouting which was to create a grout plug from ground level to the base of the terrace gravel was installed for the temporary phase of the works to allow for the bulk excavation. A summary of the grouting records is attached – refer to TAM Grouting Plumstead. The relevant records on this spreadsheet are those of COW3. TAMs 16, 17 &18 are on the north wall. TAMs 19, 20 &21 are on the south wall.
| 01CV - Civils | Cxxx-NCR-000649 | NCR | NWP - High steel in rotary bored tension pile no 77 |  | Contr |  | TUH - Thames Tunnel (East) |  | 2012-12-25 | 2012-12-19 09:49 | -6 | 2012-12-11 | Civil - Civil Engineering General | 500 |  |  | Use As-Is |  | Complete |  | Completed |  | The top of steel for Pile 77 has been cast 500mm higher than designed due to a communication error for the datum - Top of Casing. In this case, the site team mis-communicated the TOC as 102.203 not is actual position as 102.703 thus making the Top of Steel 500mm higher than required. The pile had been cast before the mis communication was realised. The bottom of the cage is located at (-77.303m TBC) with the top of the cage at (-96.733m). The Cage had 3No legs attached of 32mm bar that extend 0.39m to the bottom of the pile.
| 01CV - Civils | Cxxx-NCR-000650 | NCR | NWP - N18 COUPLERS INSTALLED IN INCORRECT POSITION |  | Contr |  | TUH - Thames Tunnel (East) |  | 2012-12-25 | 2012-12-17 14:42 | -8 | 2012-12-11 | Civil - Civil Engineering General | 500 |  |  | Use As-Is |  | Complete |  | Completed |  | 24 no. B25 couplers in the top row of roof boxout R1 and R2 of Panel N18 (see dwg Cxxx-HTM-C-DWG-CR146-PT004-62218) were not installed as per Detail '1'. The vertical legs of the couplers were installed running 'upward' as opposed to running 'downwards'. This resulted in the legs of the couplers finishing above the Final Cut-Off Level of +100.900m, hence, when the wall is broken down, a portion of the coupler leg will be cut off, reducing the overall anchorage length. The as-built levels of the top row of couplers are: N18 West Cage = +100.452m N18 East Cage = +100.347m This detail is different to the detailing on every other panel cage fabricated so far (over 200 cages produced on project to date) and was not picked up in the cage check until the cage was ready to go into the panel and could not be altered. __ designer contacted immediately to determine if the remaining anchorage length provided would still be adequate. Confirmation given that these reduced leg lengths would still be adequate was received via email. A review of all upcoming cage fabrication drawings has been undertaken to determine the cages where this detailing is neseccary. Steel fixers informed of error and made aware of which cages will have this change in detailing.
| 01CV - Civils | Cxxx-NCR-000661 | NCR | Ring delivered to site unchecked by supplier |  | Contr |  | TUH - Thames Tunnel (East) |  | 2013-02-08 | 2013-01-16 15:33 | -23 | 2013-01-08 | Tunnelling - Linings - Precast | 500 |  | System Defect | Use As-Is |  | Complete |  | Completed |  | A set of segments (1 no. complete ring) was sent to site by __ and subsequently accpeted on to site without a single green dot marking on the leading or trailing edge. This marking identifies that the segment has been passed by __ Precast Quality Control for release and delivery. QTB03 (Cxxx-HTM-O4-GUI-CR148-50003) identifies the need for this marking, as does item B.2 of the Works Procedure (Cxxx-HTM-X-GPD-CR146-ST004-50008).
| 01CV - Civils | Cxxx-NCR-000668 | NCR | PP - Base Slab B15-B16 Reinforcement |  | Contr |  | TUH - Thames Tunnel (East) |  | 2013-02-18 | 2013-02-19 08:59 | 1 | 2013-01-21 07:56 | Civil - Civil Engineering General | 500 |  | Damaged | Use As-Is |  | Complete |  | Completed |  | A single dowel bar (BM 08) was unable to be installed in base slab B15 due to the coupler cast into the diaphragm wall being damaged beyond repair. This coupler was located in the bottom row of Panel N56. At base slab B16, 4no. inserts (BM 06 and BM 10) were to be installed in each male secant pile. These were not installed in the last male secant pile adjacent to the diaphragm wall on both the north and south sides of the portal. There had previously been heavy leakage at the joints between the diaphragm wall and the secant pile wall and, in conjunction with grouting works, a concrete 'plug' was poured at this position, covering the final male secant pile at base slab level.
| 01CV - Civils | Cxxx-NCR-000669 | NCR | PP - Base Slab B16 Levels |  | Contr |  | TUH - Thames Tunnel (East) |  | 2013-02-22 | 2013-02-22 13:56 | 0 | 2013-01-25 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | The top mat of the reinforcing steel was installed high. To maintain the required cover the finished surface of the slab has been installed 22mm higher than the design level.
| 01CV - Civils | Cxxx-NCR-000676 | NCR | NWP Piles 006, 014, 030 and 032 |  | Contr |  | TUH - Thames Tunnel (East) |  | 2013-02-26 | 2013-02-11 15:38 | -15 | 2013-01-29 10:35 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | In the area between Piles 001 - 073 there has been difficutly in inserting cages without mechanical assistance. In most cases a vibrator has been adequate to push the cage to the required level. Whilst inserting the cages for piles 006, 014, 030 and 032 it became increasingly difficult to insert and a failed attempt was made at vibrating the cages. The top of steel for these cages were 103.564 (Pile 006), 103.544 (Pile 014), 103.300 (Pile 030) and 103.498 (Pile 032). The design top of steel was 102.300. A potential cause of this non conformance is a dry layer of chalk, which may have driued the concrete faster than anticipated and caused it to become stiff.
| 01CV - Civils | Cxxx-NCR-000681 | NCR | Precast Tunnel Lining - Flexural Beam Test Failures - CO |  | Contr |  | TUH - Thames Tunnel (East) |  | 2013-04-12 | 2013-04-12 13:09 | 0 | 2013-01-30 | Tunnelling - Linings - Precast | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | Individual beam specimen failures noted in test report with occassional average result of three test specimens sampled from same batch failing. Particular problem was noted for samples made in November.
| 01CV - Civils | Cxxx-NCR-000685 | NCR | Acceptance of Precast Segments without knowledge of production compliance. |  | Contr |  | TUH - Thames Tunnel (East) |  | 2013-03-04 | 2013-02-27 11:24 | -5 | 2013-02-04 | Tunnelling - Linings - Precast | 500 |  | System Defect | Use As-Is |  | Complete |  | Completed |  | Westbound Tunnel Drive - Special Cross Passage Opening Rings for XP19 were delivered and accepted on site without reciept & check of paperwork prior to release from factory. Rings had been checked as compliant by SMPL but paperwork had not been issued to __ for acceptance prior to release.
| 01CV - Civils | Cxxx-NCR-000695 | NCR | NWP - Drop in concrete level in Panel N22 |  | Contr |  | TUH - Thames Tunnel (East) |  | 2013-03-12 | 2013-03-01 17:38 | -11 | 2013-02-12 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | Panel N22 was concreted to a final level of +101.9m on 15/01/13 at 18:00. Concrete was well flushed over the top of the panel and left high. At 08:00 on 16/01/13, it was noticed that the concrete level in parts on N22 had dropped up to 0.5m (approx. +101.4m) and was "green" to depths of 1.0m (approx. +100.9m). The temporary cut-off level of the panel is +101.9m The final cut-off level of the panel is +100.9m A potential cause of this non conformance is a dry layer of chalk, which may have dried the concrete faster than anticipated and caused it to become too stiff or a void in the profile of the panel.
| 01CV - Civils | Cxxx-NCR-000697 | NCR | Phase 4 - Concrete Cube Compressive Strength Results - 28 Day Failures |  | Contr |  | TUH - Thames Tunnel (East) |  | 2013-03-14 | 2013-03-13 15:43 | -1 | 2013-02-14 | Civil - Civil Engineering General | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | The C40/50 DC3 S4 concrete used to form the base slabs in Phase 4 do not meet the requirements of BS EN 206-1. Refer to attached document: Concrete Cube Test Register B1-B5. 28 day (average of pair) failures occur in: B1, B2, B3 and B4 Using BS 206-1 Annex B Idenitity Criteria for Compressive Strength failures occur in B1, B2 and B3.
| 01CV - Civils | Cxxx-NCR-000698 | NCR | Phase 1A - Concrete Cube Compressive Strength Results - 28 Day Failures |  | Contr |  | TUH - Thames Tunnel (East) |  | 2013-03-14 | 2013-03-13 16:32 | -1 | 2013-02-14 | Civil - Civil Engineering General | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | The C40/50 DC3 S4 concrete used to form the base slabs in Phase 1A do not meet the requirements of BS EN 206-1. Refer to attached document: Concrete Cube Test Register B31-B35. 28 day (average of pair) failures occur in: B33 and B34 Using BS 206-1 Annex B Idenitity Criteria for Compressive Strength failures occur in B33 and B34
| 01CV - Civils | Cxxx-NCR-000699 | NCR | Phase 1B: Concrete Finish to SFW27 |  | Contr |  | TUH - Thames Tunnel (East) |  | 2013-03-14 | 2013-02-27 16:04 | -15 | 2013-02-14 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | The concrete surface does not meet the requirements of the specification. There has been grout loss at the bottom edge of the shutters of SFW27.
| 01CV - Civils | Cxxx-NCR-000700 | NCR | Plumstead Portal - __ Mix 3 DC4 - Low 28 day Concrete Cube Strengths |  | Contr |  | TUH - Thames Tunnel (East) |  | 2013-03-14 | 2013-03-18 17:02 | 4 | 2013-02-14 | Civil - Civil Engineering General | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | The C40/50 DC3 S3 concrete used to form the Capping beam & flood wall in Phase 1A do not meet the requirements of BS EN 206-1. Refer to attached document: Concrete Cube Test Register Phase 1A 28 day (average of pair) failures occur in: SCB34, 32, NCB35, SFW 31 to 35 Using BS 206-1 Annex B Idenitity Criteria for Compressive Strength failures occur in SCB34, 32, NCB35, SFW 31 to 35
| 01CV - Civils | Cxxx-NCR-000718 | NCR | Tunnel Drive H - Precast Concrete - Production Sampling & Testing for Water Absorption - Not in accordance with Specified Requirements |  | Contr |  | TUH - Thames Tunnel (East) |  | 2013-03-20 | 2013-03-22 13:15 | 2 | 2013-02-20 | Tunnelling - Linings - Precast | 500 |  | Material | Rework |  | Complete |  | Completed |  | Sampling frequencies & Testing Methods was not in accordance with Vol. 2C KH11 -Specification for Precast Segments Cls. KH11.2203 f & g or the Contractors Acceped Code 1 ITP Cxxx-HTM-X-~ITP-CR146_ST004-50001 Rev 3.0. Sampling & Testing was being carried out in accordance with SMPL preferred method using Cubes instead of Cores from the segments cast and the frequency of taking specimens had not been met. Two FCD have been raised requesting this change but not accepted. Ref. DRH-CRL-FCD-Cxxx-00478 & DRH-CRL-FCD-Cxxx-00691
| 01CV - Civils | Cxxx-NCR-000731 | NCR | MCR for Segments Adjacent to Cross Passage |  | Contr |  | TUH - Thames Tunnel (East) |  | 2013-04-03 | 2013-03-06 11:10 | -28 | 2013-03-06 | Tunnelling - Linings - Precast | 500 |  | System Defect | Use As-Is |  | Complete |  | Completed |  | The precast concrete mix design was altered for the tunnel segments adjacent to the cross passages. Previously the Precast Concrete Mix Design (Precast Tunnel Segments) Cxxx-HTM-C-CER-CR146_ST004-50006 Rev 2.0 had been approved Code 1. SMPL erroneously supposed that, as the change to the mix design amounted to little more than a change of additive quantities, a revised mix design would not be required. __ raised the need for a revised mix design as an observation during a planned surveillance. It was then raised as a CAR during the last __ audit when it was discovered that this observation had not been acted upon. An MCR, Precast Reinforced Concrete Segment (Adjacent to Cross Passage and Nadir Sump) Mix Design C55/67 Ref: Cxxx-HTM-C-CER-CR146_ST004-50034 Rev1.0, was submitted on 25/02/13. The first segment using this revised mix had already been delivered to site at this time.
| 01CV - Civils | Cxxx-NCR-000736 | NCR | Plumstead Portal - __ Mix 3 DC3 - Low 28 day Concrete Cube Strengths |  | Contr |  | TUH - Thames Tunnel (East) |  | 2013-04-08 | 2013-03-06 09:52 | -33 | 2013-03-04 | Civil - Civil Engineering General | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | The C40/50 DC3 S3 concrete used to form the Capping beamin Phase 2 do not meet the requirements of BS EN 206-1. Refer to attached document: Concrete Cube Test Register Phase 2 28 day (average of pair) failures occur in: NCB22 Using BS 206-1 Annex B Idenitity Criteria for Compressive Strength failures occur in NCB22
| 01CV - Civils | Cxxx-NCR-000753 | NCR | NWP - Projection on tension piles |  | Contr |  | TUH - Thames Tunnel (East) |  | 2013-03-29 | 2013-04-05 10:44 | 7 | 2013-03-15 | Civil - Civil Engineering General | 500 |  | Workmanship | Rework |  | Complete |  | Completed |  | Please see attached as-built schedule for tention piles where the projection in the reinforcement steel above COL could not be provided as per the design requirements. This was due to the piling platform not built high enough to provide the required projection. If the required projection was provided then the top of steel would have been sticking above ground level making access to other pile positions impossible. __ kindly request for Confirmation of acceptance for reduced projection.
| 01CV - Civils | Cxxx-NCR-000755 | NCR | North Woolwich Portal - Embedded Wall & Piling- North D Wall - Incorrect Installation & Protection of Instrument Void Forming Tubes |  | Contr | HTM | TUH - Thames Tunnel (East) |  | 2013-04-17 | 2013-04-12 13:28 | -5 | 2013-03-20 12:46 | Civil - Civil Engineering General | 1000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | • The inclinometer tube installed in the D wall panel number N11has been slightly bent at top and needs a cap on the tube and protect the void formed for installation of instrument by third party. • Inclinometer void forming tube on the eastern side of diaphragm wall panel number N24 has been cut off at top of cage level and left exposed, it needs to be capped off. The inclinometer void forming tube on the western side of D Wall panel N 24 needs to be capped off properly, it was taped up and covered in mud. In all cases void forming tube need extend above the ground level and capped off to protect from further damaged
| 01CV - Civils | Cxxx-NCR-000757 | NCR | Tunnel Drive H- Delivery of Precast Segments under Quarantine Pending outcome of NCR00681 |  | Contr | HTM |  |  | 2013-04-19 | 2013-04-08 17:19 | -11 | 2013-04-05 12:23 | Tunnelling - Linings - Precast | 500 |  | System Defect | Rework |  | Complete |  | Completed |  | Segment Supplier Shay Murttagh Precast has been Transporting Quarantined Segments to Site, Site have accepted thes Quarantined Segments for use in the Westbound Tunnel Plumstead to Woolwich - Ref DRH-CRL NCR-Cxxx-00681. NCR closure extended to complete Modelling on NCR before submitting __ case for use as is.
| 01CV - Civils | Cxxx-NCR-000758 | NCR | Tunnel Drive H- Westbound - Plumstead - Woolwich Station Box at Cross passage 18 Ring 476 - Incorrect Key Position |  | Contr | HTM |  |  | 2013-04-22 | 2013-04-24 14:51 | 2 | 2013-04-08 15:24 | Civil - Tunnelling | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Worker not correctly instructed | Completed |  | Tunnel Drive H- Westbound - Plumstead - Woolwich Station Box at Cross passage 18 Ring 476 - Incorrect Key Position Key was built in wrong position according to planned arrangements - Drawing Detail for Crosspassage Opening Set.
| 01CV - Civils | Cxxx-NCR-000759 | NCR | Tunnel Drive H - Westbound - Plumstead to Woolwich Station Box - Rings Delivered with cast dates November were built in tunnel in contravention of Quarantine requested in NCR 757 |  | Contr | HTM | TUH - Thames Tunnel (East) |  | 2013-04-22 | 2013-04-23 10:31 | 1 | 2013-04-08 15:59 | Tunnelling - Linings - Precast | 500 |  | System Defect | Rework |  | Complete |  | Completed |  | Tunnel Linings Cast in November were under investigation By Crossrail Ref. NCR 681, Subsequently it was discovered that rings were being delivered to site NCR 757 requested that Segments with cast dates 6th & 26th November 2012 be quarantined on site and prevented from use. Prduction continued and these segments were not prevented from being installed in the permanent works.
| 01CV - Civils | Cxxx-NCR-000760 | NCR | Tunnel Drive H - WestBound - Pumstead Portal - Woolwich Box - System failure - Acceptance and checking of special reiforced segments - resulting in major delay to Ring Build |  | Contr | HTM |  |  | 2013-04-26 | 2013-04-23 11:59 | -3 | 2013-04-12 12:06 | Tunnelling - Linings - Precast | 2500 |  | System Defect | Rework |  | Complete |  | Completed |  | Segment Delivery of Special Reinforced Precast Linings from __ specifically for Nadir Catchpitatadjacent to Crosspassage 18. The first Nadir Catch it Ring a Type VI with Type 1 cage A,B & C segments at. Ring No. 482 Wetbound Tunnel PP-WSB Segments have WP bar code ( Westbound catchPit) currently TPC cannot accept this code therefore it is not logged in the TPC with the barcode scanner. The Visual inspection of the segments at delivery failed to pick up that the segments were stacked in the wrong order. The visual inspection at reception on the TBM failed to identify the segments were in the wrong order. The Barcode scanner cannot identify that the Segments are in the wrong order this is only achieved by human inspection. It is not allways practical or possible to check the segments in order of position on the segment handler delivering to the buiild area. The first three plates (A,B,C) were built prior to recognising the A & B plates were in the wrong order (B,A,C). The plates were removed resulting in damage to those segments (Breaking out around the dowel) and several hours delay to tunnelling. The whole ring was removed from the Tunnel and put to Quarantine. A similar Ring was found from stock which was allocated for Cross passage 17, a type VI with cage type 1 A, B & C segments. This ring was built in the Tunnel ar Ring 482.
| 01CV - Civils | Cxxx-NCR-000761 | NCR | NWP - Reinforcement at Pile 178 |  | Contr | HTM | TUH - Thames Tunnel (East) |  | 2013-05-01 | 2013-04-24 15:00 | -7 | 2013-04-17 08:33 | Civil - Civil Engineering General | 500 |  | Damaged | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Not Defined | Completed |  | After exposing Pile 175, following excavation and pile cut off, it was discovered that one piece of the reinforcing steel had been damaged/cut above pile cut off level. Pile 175 will be cast in to Base Slab B35 in Phase 5. There are no pile head connections to be made in this area. The cut piece of reinforcing steel has been cut off 30mm above pile cut off.
| 01CV - Civils | Cxxx-NCR-000762 | NCR | Concrete Pour Base Slab 34/35 |  | Contr | HTM | NOW - North Woolwich Portal (East) |  | 2013-05-14 | 2013-05-03 12:54 | -11 | 2013-04-30 14:34 | Civil - Civil Engineering General | 500 |  | System Defect | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Use of unapproved materials | Completed |  | It is a requirement of Works Information Volume 2B - Part 20 Quality Management (CRL1-PDP-W-XWI-CRG02-00020 Rev 5.0 ) that all on-site testing be carried out be laboritories accredited by UKAS or similar, acceptable national body or by persons accredited to a similar standard. The ITP for Construction of North Woolwich Portal Base Slab (Cxxx-HTM-C-ITP-CR146_PT004-50006 Rev 2.0) states that every load of concrete be subjected to a slump test. Note: This is above and beyond the general requirements of the Crossrail specification KF10 and the __ concreting procedure. The first load of concrete delivered from __ on 29/04/13 for the base slab pour at base slab location B34/B35 was not subject to a slump test. This was due to the __ technician (UKAS accredited) mistakenly attending Plumstead Portal instead of North Woolwich __ concrete wagons arrived on site from 08:00 and with wagons backing up the decision was taken to pump the concrete without a slump test being taken by a UKAS accredited technician. The technician arrived on site at 09:00 and the second and subsequent loads were all slump tested.
| 01CV - Civils | Cxxx-NCR-000763 | NCR | West bound TBM launch chamber- Mass concrete to base slab cube complressive strength result - 28 days failure |  | Contr | HTM | NOW - North Woolwich Portal (East) |  | 2013-05-14 | 2013-05-14 16:08 | 0 | 2013-04-30 14:15 | Civil - Civil Engineering General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Not Defined | Completed |  | West bound TBM launch chamber- Mass concrete to base slab cube complressive strength result - 28 days failure
| 01CV - Civils | Cxxx-NCR-000764 | NCR | NWP = Concrete Finish to Base Slab B34 and B35 |  | Contr | HTM | NOW - North Woolwich Portal (East) |  | 2013-05-17 | 2013-05-17 10:16 | 0 | 2013-05-03 10:22 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The concrete surface finish does not meet the requirements of the specification. There are a number of minor defects includign honeycombing, poor compaction at shutter edges and blow holes. Further details are include in observation report Cxxx-
| 01CV - Civils | Cxxx-NCR-000765 | NCR | NWP - __ - Pile 1004 Incorrect Pile Cage |  | Contr | HTM | NOW - North Woolwich Portal (East) |  | 2013-05-23 | 2013-05-21 17:28 | -2 | 2013-05-09 17:19 | Civil - Civil Engineering General | 1000 |  | Supervision/Management | Repair | 4 (0.5-3k) | Complete | Supervision - Insufficient supervision | Completed |  | The incorrect pile cage has been installed for Pile No. 1004. The actual cage installed is that of either Pile No. 1010 or Pile No. 1016. All cages are unique for their intended pile. See attached sketch which shows the the coupler levels for each possible scenario of installed cage.
| 01CV - Civils | Cxxx-NCR-000766 | NCR | NWP - __ - Pile 1034 Incorrect cage |  | Contr | HTM | NOW - North Woolwich Portal (East) |  | 2013-05-23 | 2013-05-21 17:33 | -2 | 2013-05-09 17:19 | Civil - Civil Engineering General | 1000 |  | Supervision/Management | Repair | 4 (0.5-3k) | Complete | Supervision - Insufficient supervision | Completed |  | The incorrect pile cage has been installed for Pile No. 1034. The actual cage installed is that of either Pile No. 1010 or Pile No. 1016. All cages are unique for their intended pile. See attached sketch which shows the the coupler levels for each possible scenario of installed cage.
| 01CV - Civils | Cxxx-NCR-000767 | NCR | NWP - __ - Pile 1024 Toe Level |  | Contr | HTM | NOW - North Woolwich Portal (East) |  | 2013-05-23 | 2013-05-17 15:41 | -6 | 2013-05-09 17:28 | Civil - Civil Engineering General | 5000 |  | Equipment Breakdown | Use As-Is | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | HArd/Hard Wall Pile No. 1024 did not reach the correct toe level of -83.4m AOD. The pile was cast at -86.9m AOD as the pile could be progressed no further. Sequence of events: Tuesday 23/04/2013 Pile started only lead casing installed Wednesday 24/04/2013 Drilling continued on the pile, with a casing depth of 14.0m (-88.9mAOD) the casing became tight. While digging it was noticed that there was alot of flint coming out with the pile arisings, the site crew observed that progress was slow and digging was tight. Digging continued all day reaching a depth of 14.5m (-87.4m AOD) with 16.0m of casing installed and approx 1.5m of casing projecting out of the ground. Thursday 25/04/2013 Digging resumed, a further 500mm was dug with the digging bucket and while attempting to push the casing further into the ground the casing suddenly went down approx 0.8mm - 1m, at this point the digging bucket was lowered into the pile and could not get to the pile toe indicating that there was a problem with the casing at the toe level. At this time there was 16m of casing attached and the pile depth was 15.2 (-86.7mAOD). As we could not progress the excavation further the decision was made to soft mix the pile and extract the casing, on extracting the final casing it was observed that the cutter ( Cutter length approx 500mm) was missing from the lead casing and had been sheared off and was therefore still in the pile. Friday 26/04/2013 Drilling resumed on the pile and 16m of casing was installed, (top of casing = 102.9) the pile dug to a depth of 16.0 (15.0m from ground level) at this depth the bucket struck the cutting shoe that was still in the pile, as the casing could not be progressed it was decided that to continue digging would only damage more equipment so the pile was then concreted, the pile toe was- 86.9mAOD. The cage was also cut from 17.1m in length to 13.4m (3.7m cut off) to ensure that the couplers are still set at the correct level. The cage toe level is at -86.9m AoD.
| 01CV - Civils | Cxxx-NCR-000768 | NCR | Tunnel Drive H - West Bound Ring 799 - Cracked B Segment |  | Contr | HTM |  |  | 2013-07-31 | 2013-08-02 08:31 | 2 | 2013-05-13 17:59 | Tunnelling - Linings - Precast | 2000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Ringnumber: 799 K- Stone position: 8 Broken Segment: B from mould 3 dated 19/11/12 Crack 12cm over thrust ram 16 At the end of advance 800 ( Thrust rams by 2050mm) the shift engineer checked the tail skin and saw the broken segment. He informed Stefan Flachhuber at 23:30.
| 01CV - Civils | Cxxx-NCR-000770 | NCR | CFA Pile 187 Unable to Locat the rig computer printout |  | Contr | HTM | NOW - North Woolwich Portal (East) |  | 2013-05-28 | 2013-05-23 12:24 | -5 | 2013-05-14 11:20 | Civil - Civil Engineering General | 500 |  | System Defect | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | CFA Pile number 187 was installed on 18/03/2013 have been unable to locate the rig computer printout (pile log)
| 01CV - Civils | Cxxx-NCR-000772 | NCR | Records |  | Crossrail | XRL |  |  | 2013-05-29 | 2013-05-31 11:24 | 2 | 2013-05-15 09:54 | Tunnelling - Grouting | 500 |  | System Defect | Rework |  | Complete |  | Completed |  | Works Information Volume 2B – Part 13 Assurance, Records and Certification clause 13.3.91 Deliverable Records. Ring grouting records for tunnel construction Clause has not been implemented
| 01CV - Civils | Cxxx-NCR-000773 | NCR | NWP - Procedures - Works commencing without an approved GMS/ITP |  | Contr | HTM | NOW - North Woolwich Portal (East) |  | 2013-05-31 | 2013-05-23 13:46 | -8 | 2013-05-17 15:50 | Civil - Civil Engineering General | 500 |  | System Defect | Rework |  | Complete |  | Completed |  | Works have proceeded without an approved method statement and/or an approved inspection and test plan for activities at North Woolwich Portal. The documentation includes: Cxxx-HTM-C-ITP-CR146_PT004-50009 – Bulk Excavation and Installation of temp. Propping (submitted in first revision on the 10th of May, activity start date 9th of May), Cxxx-HTM-C-GMS-CR146_PT004-50004 – Bulk Excavation Phase 1 & 2 (submitted in first revision on the 13th of May, activity start date 9th of May), Cxxx-HTM-U-ITP-CR146_PT004-50001 – Lining of 300mm Sewer (submitted in first revision on 9th of May, activity completion date 10th of May), Cxxx-HTM-C-GMS-CR146_PT004-50010 – Temporary Propping Installation was submitted 16th of May with the Gallow bracket installation having commenced 17th May) This is contrary to the requirements of: CRL1-PDP-W-XWI-CRG003-020 Works Information Volume 2B Part 20 – Quality Management 20.8 “The Contractor shall submit the ITP to the Supervisor for acceptance 4 weeks prior to the start of the relevant works...the Contractor shall not start the relevant works until the Supervisor has accepted the ITP.” CRL1-PDP-W-XWI-CRG003-019 Works Information Volume 2B Part 19 – Health and Safety Management 19.5.2 “The Contractor shall allow a minimum of 4 weeks, prior to work commencing for the method statements review and acceptance by the Project Manager....The Contractor shall not start the relevant works activities until the Project Manager has accepted the method
| 01CV - Civils | Cxxx-NCR-000774 | NCR | NWP - Concret Finish to South Capping Beam SCB 29 |  | Contr | HTM | NOW - North Woolwich Portal (East) |  | 2013-05-31 | 2013-05-30 11:55 | -1 | 2013-05-17 15:21 | Civil - Civil Engineering General | 1000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The concrete surface finish does not meet the requirements of the specification. There are a number of minor defects includign honeycombing, poor compaction at shutter edges and blow holes. Photographs are included within the obseravtion report from Period 2 Week 3.
| 01CV - Civils | Cxxx-NCR-000775 | NCR | NWP - Concrete Finish to South Capping Beam 27 |  | Contr | HTM | NOW - North Woolwich Portal (East) |  | 2013-06-04 | 2013-05-30 11:57 | -5 | 2013-05-21 17:11 | Civil - Civil Engineering General | 1000 |  | Material | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The concrete surface finish does not meet the requirements of the specification. There are a number of minor defects including what appear to be blow holes. Discussions with __ at a recent Supplier Quality Review identified aggregate bridging as a possible cause for the defect.
| 01CV - Civils | Cxxx-NCR-000777 | NCR | Tunnel Drive H - Westbound Ring 438 to 439 Leaking Joint above axis |  | Contr | HTM |  |  | 2013-06-13 | 2013-06-14 15:36 | 1 | 2013-05-30 09:08 | Tunnelling - Linings - Precast | 2000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Heavy leak between circle joint of Rings 438 to 439 above LHS Axis approximate position 19 /20 (10 - 11 o'clock) looking inbye.
| 01CV - Civils | Cxxx-NCR-000779 | NCR | Loose Bolts within Tunnel Segment Lining |  | Crossrail | XRL |  |  | 2013-07-12 | 2013-07-12 13:07 | 0 | 2013-06-11 14:45 | Civil - Tunnelling | 5000 |  | Material | Rework | 3 (3-6k) | Complete |  | Completed |  | Instances of bolts working loose on segmental lining within tunnels constructed to date
| 01CV - Civils | Cxxx-NCR-000780 | NCR | Tunnel Drive H - Precast Segment Manufacture - Post Pour Inspection - Blocked Grout Hole |  | Contr | HTM |  |  | 2013-06-25 | 2013-06-14 12:08 | -11 | 2013-06-11 18:37 | Tunnelling - Linings - Precast | 500 |  | Damaged | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The following Key segment was discovered to be missing its grouting socket during post pour inspection; K2 – 22-04-13
| 01CV - Civils | Cxxx-NCR-000781 | NCR | Tunnel Drive H - Precast Segments - Production Tests - Flexural Beam Test Failures - April 13 |  | Contr | HTM |  |  | 2013-06-25 | 2013-06-19 15:42 | -6 | 2013-06-11 18:50 | Tunnelling - Linings - Precast | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Not Defined | Completed |  | Flexural beam samples T-2528 to T-2530 manufactured 11-04-13 have returned results with the fR.1 average less than 4.8N/mm2.
| 01CV - Civils | Cxxx-NCR-000782 | NCR | NWP - Concrete Finish to South Capping Beams 25 and 26 |  | Contr | HTM | NOW - North Woolwich Portal (East) |  | 2013-07-24 | 2013-07-03 12:30 | -21 | 2013-06-26 07:53 | Civil - Civil Engineering General | 1000 |  | Material | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The concrete surface finish does not meet the requirements of the specification. There are a number of minor defects caused by aggregate bridging and some minor workmanship issues
| 01CV - Civils | Cxxx-NCR-000783 | NCR | NWP - Phase 4 Base Slab 30 Reinforcement |  | Contr | HTM | NOW - North Woolwich Portal (East) |  | 2013-07-15 | 2013-07-02 14:12 | -13 | 2013-07-01 17:13 | Civil - Civil Engineering General | 2000 |  | Material | Rework | 4 (0.5-3k) | Complete |  | Completed |  | Several bar marks to base slab 30 reinforcement have been bent poorly by the manufacturer – bar marks 8a-8h, schedule Cxxx-CSY-S-DDJ-CR146_PT004-02156. The link leg is longer on one side than the other, causing an unacceptable reduction in concrete cover – see attached photo. This error was noted during fixing and the affected bars removed.
| 01CV - Civils | Cxxx-NCR-000784 | NCR | NWP - North Capping Beam 23 |  | Contr | HTM | NOW - North Woolwich Portal (East) |  | 2013-07-19 | 2013-07-19 12:54 | 0 | 2013-07-05 12:57 | Civil - Civil Engineering General | 2500 |  | Material | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Not Defined | Completed |  | The concrete surface finish does not meet the requirements of the specification. There are a number of minor defects caused by aggregate bridging.
| 01CV - Civils | Cxxx-NCR-000785 | NCR | Tunnel Drive H - EB - PP-WSB - Stepping in Crown Rings 485 - 488 |  | Contr | HTM |  |  | 2013-08-14 | 2013-08-01 15:54 | -13 | 2013-07-17 14:34 | Tunnelling - Linings - Precast | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | Stepping has been observed up to 15mm between rings in the tunnel crown.
| 01CV - Civils | Cxxx-NCR-000786 | NCR | Confirmation of compliance by the generation of contemporaneous records |  | Crossrail | PDP |  |  | 2013-08-07 | 2013-07-31 10:54 | -7 | 2013-07-24 07:38 | Tunnelling - Grouting | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete |  | Completed |  | The M & W specification clause KT10.3106 requires the method statement on grouting to contain details of mix design and constituent materials and initial testing for Project Manager’s (PM) acceptance. The grout mix design, constituent materials and initial testing were submitted on materials compliance record Cxxx-HTM-C-CER-CR146_ST004-50026 rev 1 dated 16/11/2012. The document received a code 2 decal on 19/12/2012 .The Contractor has therefore failed to provide continual confirmation of compliance by the generation of contemporaneous records as required by Works Information volume 2B Clause 13.2.
| 01CV - Civils | Cxxx-NCR-000787 | NCR | Calibration records |  | Crossrail | PDP |  |  | 2013-08-07 | 2013-08-05 13:43 | -2 | 2013-07-24 07:47 | Tunnelling - Grouting | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete |  | Completed |  | Calibration records for the Marsh cone, 1000ml cylinder, density balance (mud balance) and 100mm compressive sample cube moulds were not made avaialble for surveillance QS310-11
| 01CV - Civils | Cxxx-NCR-000788 | NCR | The requirement for UKAS accreditation |  | Crossrail | PDP |  |  | 2013-08-07 | 2013-07-30 13:34 | -8 | 2013-07-24 07:57 | Tunnelling - Grouting | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete |  | Completed |  | No records were made available for Surveillance QS310-11 to demonstrate PM acceptance with respect to the grout testing, which was confirmed as undertaken by the site laboratory for which UKAS accreditation had not been gained
| 01CV - Civils | Cxxx-NCR-000789 | NCR | NWP - Base Slab 28 - Pile A35 |  | Contr | HTM | NOW - North Woolwich Portal (East) |  | 2013-08-07 | 2013-07-30 13:51 | -8 | 2013-07-24 16:48 | Civil - Civil Engineering General | 1500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During the excavation and subsequent break down of piles for base slabs 28 and 29, pile no A35 was fractured at one edge, below the cut off level.
| 01CV - Civils | Cxxx-NCR-000790 | NCR | Tunnel Drive H - Precast Segments post Pour Inspection / Pre Delivery Inspection - Missing or damaged grout socket |  | Contr | HTM |  |  | 2013-09-17 | 2013-08-23 10:10 | -25 | 2013-07-29 17:02 | Tunnelling - Linings - Precast | 500 |  | Damaged | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The following segment was discovered to be missing its grouting socket during post pour inspection; • K-4 – 21-05-13 • K-8 – 24-05-13 • B-3 – 28-06-13 • B-3 – 03-07-13 • C-3 – 16-07-13 • C-3 – 19-07-13
| 01CV - Civils | Cxxx-NCR-000791 | NCR | Tunnel Drive H - Precast Segments - Production Testing - Beam Test Failure - FR1 Results - June 2013 |  | Contr | HTM |  |  | 2013-09-09 | 2013-09-09 15:53 | 0 | 2013-07-29 17:21 | Tunnelling - Linings - Precast | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | • Flexural beam samples T-3587 to T-3589 manufactured 11-06-13 have returned results with the fR.1 average less than 4.8N/mm2.
| 01CV - Civils | Cxxx-NCR-000792 | NCR | Tunnel Drive H - Precast Segments - Segment Damage Category A0 - Caused by lifting device in Stock Yard |  | Contr | HTM |  |  | 2013-08-13 | 2013-08-14 15:21 | 1 | 2013-07-30 12:56 | Tunnelling - Linings - Precast | 2000 |  | Material | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Tunnel Rings accepted and unloaded in the Yard were noted as showing signs of minor damage to the Iner edge and very occassionally the outer edge of rings in contact with the segment lifting devices feet. It was observed that the damage was consistent with unloading and stacking in the Plumstead stock yard not damage caused pre-delivery or in transit.
| 01CV - Civils | Cxxx-NCR-000793 | NCR | Plumsted Portal - Marmadon Sewer Diversion - MH03 - 6.0m id Caisson shaft - __ Shaft Segment bolt socket failure. |  | Contr | HTM |  |  | 2013-08-30 | 2013-08-30 12:46 | 0 | 2013-08-02 11:11 | Shafts - Linings | 500 |  | Damaged | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | The plastic inserts for the spear bolts that tie plates together have pulled out resulting in the choker ring losing shape. The Tolerance exceeds that set by JTS ITP 15mm Ovality.
| 01CV - Civils | Cxxx-NCR-000794 | NCR | NWP - South Capping Beam 24 - Incorrect Mix |  | Contr | HTM | NOW - North Woolwich Portal (East) |  | 2013-08-19 | 2013-08-08 16:21 | -11 | 2013-08-05 08:15 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | South Capping Beam 24 was poured on Friday 02/08/13. __, the concrete supplier, mistakenly delivered Mix 11 concrete instead of the ordered Mix 3. The beam was cast using the Mix 11 concrete. Mix 11 is not a Crossrail approved concrete mix. The mix design for Mix 11 is attached to this NCR for information.
| 01CV - Civils | Cxxx-NCR-000795 | NCR | Damage to tunnel lining segments - W/B drive PLU to WOO - rings 816 to 819 |  | Crossrail | PDP |  |  | 2013-08-23 | 2013-08-30 18:38 | 7 | 2013-08-09 15:23 | Civil - Tunnelling | 1000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | During removal of TBM1 from the W/B tunnel at Woolwich station box, some part of the TBM has ground into the tunnel lining and caused major spalling damage over a length of 4 rings
| 01CV - Civils | Cxxx-NCR-000796 | NCR | Damage to tunnel lining segments - W/B drive PLU to WOO - rings 760 to 763 |  | Crossrail | PDP |  |  | 2013-09-30 | 2013-09-10 15:25 | -20 | 2013-08-09 15:52 | Civil - Tunnelling | 2500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | During removal of TBM1 from the W/B tunnel at Woolwich station box, some part of the TBM has ground into the tunnel lining and caused major spalling damage over a length of 4 rings
| 01CV - Civils | Cxxx-NCR-000797 | NCR | North Woolwich Portal - __ Concrete - C40/50/DC3/S4 - Low Compressive Strength - 28 day cube Results |  | Contr | HTM | NOW - North Woolwich Portal (East) |  | 2013-09-27 | 2013-09-25 15:45 | -2 | 2013-08-20 17:27 | Civil - Civil Engineering General | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Not Defined | Completed |  | Pours involving __ Mix C40/50 DC3 S4 showing low 28 day compressive strength results 09/05/13 NWP SCB 30 &3 1 09/07/13 BASE Slab 30 10/07/13 NCB 21 12/07 SCB 20 17/017/13 NWP FW 33 19/07/13 NWP Wall Slab 31
| 01CV - Civils | Cxxx-NCR-000798 | NCR | Tunnel Drive H - Precast Segment Manufacture - Post Pour Inspection - Blocked Grout Hole |  | Contr | HTM |  |  | 2013-09-10 | 2013-09-09 15:57 | -1 | 2013-08-20 17:47 | Tunnelling - Linings - Precast | 500 |  | Damaged | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The following segment was discovered to be missing its grouting socket during post pour inspection; • K-8 – 10-08-13 Sample photos attached from previous segments as representative.
| 01CV - Civils | Cxxx-NCR-000799 | NCR | NCR-NWP- Concrete finish to North Flood Wall 27( NFW27) |  | Contr | HTM | NOW - North Woolwich Portal (East) |  | 2013-09-30 | 2013-09-03 15:00 | -27 | 2013-08-27 15:09 | Civil - Civil Engineering General | 2500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The concrete surface finish does not meet the requirements of the specification. There are a number of minor voids by poor compaction
| 01CV - Civils | Cxxx-NCR-000800 | NCR | Tunnel Drive H - Westbound - PPL - WSB (rings 176, 190, 370, 664, 728, 816 & 820) As-built measured outside of specified build tolerance |  | Contr | HTM |  |  | 2014-01-31 | 2014-01-16 11:00 | -15 | 2013-09-05 12:05 | Tunnelling - Alignment | 2500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Ring 176 - exceed Combined Tolerances KT10.4222(a) +/- 100 mm Ring 176 - exceed Building Tolerances KT10.4220 a) diameter +/- 50mm Ring 190 - exceed Alignment Tolerances KT10.4221. Tolerance +/- 50 mm Ring 370 - exceed Combined Tolerances KT10.4222(a) +/- 100 mm Ring 370 - exceed Building Tolerances KT10.4220 a) diameter +/- 50mm Ring 816 - exceed Alignment Tolerances KT10.4221. Tolerance +/- 50 mm Ring 820 - exceed Alignment Tolerances KT10.4221. Tolerance +/- 50 mm Ring 664 - exceed Alignment Tolerances KT10.4221. Tolerance +/- 50 mm Ring 728 - exceed Alignment Tolerances KT10.4221. Tolerance +/- 50 mm See attached reports
| 01CV - Civils | Cxxx-NCR-000801 | NCR | NWP - Damaged D Wall Couplers in Portal Box Outs |  | Contr | HTM | NOW - North Woolwich Portal (East) |  | 2013-09-24 | 2013-09-20 11:47 | -4 | 2013-09-10 12:46 | Civil - Civil Engineering General | 1500 |  | Damaged | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Following the excavation of the portal in Phases 1 & 2 and the subsequent revealing of the coupler box outs within the diaphragm wall panels, a number of couplers have been identified as damaged. See attached reports for the locations of the damaged couplers.
| 01CV - Civils | Cxxx-NCR-000803 | NCR | NWP - Phase 2 D-Wall Couplers into Base Slab 03 |  | Contr | HTM | NOW - North Woolwich Portal (East) |  | 2013-10-02 | 2013-09-25 16:12 | -7 | 2013-09-18 14:54 | Civil - Civil Engineering General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | An inpsection of the reinforcing steel for BS03 identified 4 no. missing couplers in D-Wall panel S55. These couplers clashed with the shutter for the 'step' at Base Slab 03 and the reinforcing steel at this location. Refer to attached sketch.
| 01CV - Civils | Cxxx-NCR-000804 | NCR | Marmadon Sewer Diversion - Shaft Base Pour - MH04 - Placing of Concrete outside specified requirements for Slump. |  | Contr | HTM |  |  | 2013-11-15 | 2013-11-13 15:43 | -2 | 2013-09-19 13:55 | Shafts - Shafts General | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | 1.5 m3 of the mix 4 (C35/45) out of a 9.5m3 pour was discharged in to the manhole from the first load while slump test was being taken. Upon failure of the slump test for an S3, the concrete discharge was immediately stopped and concrete truck was sent away .Batching plant was contacted to inform the non conformity of the mix.The placed concrete has been left insitu and covered with fresh concrete from 2nd and 3rd loads which were measured as compliant
| 01CV - Civils | Cxxx-NCR-000805 | NCR | Pile bearing surface |  | Crossrail | PDP |  |  | 2013-10-18 | 2013-10-14 12:23 | -4 | 2013-09-20 09:49 | Civil - Civil Engineering General | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Execution of pile cutting to level for South Capping Beam20 & 21 resulted in damaging the pile head and reducing the load bearing area.
| 01CV - Civils | Cxxx-NCR-000806 | NCR | Tunnel Drive H - Middlegate House Compensation Grouting Shaft - Backfilling Prior to Project Managers Acceptance of ITP & Material |  | Contr | HTM |  |  | 2013-10-18 | 2013-10-18 13:46 | 0 | 2013-09-20 10:10 | Shafts - Shafts General | 500 |  | System Defect | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Jet Grout waste arisings from Subcontractor __ at Marmadon Sewer MH03 Works were used to start backfilling the Middlegate House Compensation Grouting Shaft. The method of using jet Grout arisings instead of Specified material was accepted in principle in FCD as a change specified material to works information. Ref. Cxxx-FCD-00793 & Cxxx-RFI-00886. Information requested in the FCD was not submitted prior to works commencing and there was no acceptance of material or inspection & test plan.
| 01CV - Civils | Cxxx-NCR-000807 | NCR | Tunnel Drive H - Eastbound - PP-WSB - Ring 816 damaged during removal of TBM at WSB. |  | Contr | HTM |  |  | 2013-11-01 | 2013-11-07 11:48 | 6 | 2013-09-20 10:29 | Tunnelling - Linings - Precast | 2000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Ring 816 damaged during removal of TBM at WSB.
| 01CV - Civils | Cxxx-NCR-000808 | NCR | NWP - Pile Head Detail for Pile No.41 |  | Contr | HTM | NOW - North Woolwich Portal (East) |  | 2013-10-07 | 2013-09-30 14:46 | -7 | 2013-09-23 16:43 | Civil - Civil Engineering General | 1000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The reinforcing steel from Pile No.41, into base slab 5, was damaged by the the 'tracking over' of vehicles used during the excavation works. A number of the bars had snapped at the pile cut off level - see atached sketch.
| 01CV - Civils | Cxxx-NCR-000809 | NCR | NWP - 28 Day Compressive Cube Strength Failures (July-August 2013) |  | Contr | HTM | NOW - North Woolwich Portal (East) |  | 2013-10-25 | 2013-10-29 11:54 | 4 | 2013-09-24 15:38 | Civil - Civil Engineering General | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The C40/50 Design Mix 3 concrete used to form the capping beams, flood walls and base slabs do not meet the requirements of BS EN 206-1. Refer to attached document for a summary of the cube results and the relevant locations within the works.
| 01CV - Civils | Cxxx-NCR-000810 | NCR | NWP - Base Slab 5 / S46 D Wall Panel Damaged Coupler |  | Contr | HTM | NOW - North Woolwich Portal (East) |  | 2013-10-09 | 2013-10-04 10:48 | -5 | 2013-09-25 15:57 | Civil - Civil Engineering General | 500 |  | Damaged | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The coupler box out, within the diaphragm wall panel S46, has 1 no. coupler damaged beyond repair (top row). __ will be unable to install an insert in to the base slab at this location.
| 01CV - Civils | Cxxx-NCR-000811 | NCR | NWP - Base Slab 6 Tension Pile No.44 Damaged |  | Contr | HTM | NOW - North Woolwich Portal (East) |  | 2013-10-10 | 2013-10-07 16:28 | -3 | 2013-09-26 17:23 | Civil - Civil Engineering General | 500 |  | Damaged | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The reinforcing steel from Pile No.44, into base slab 6, has been damaged. 1 no. bar has been damaged at pile cut off level (11 no. bars remain, installed as per design drawing). A repair has been attempted as per the original proposal detailed in Cxxx-NCR-808. This proposal has subsequentally been rejected by Cxxx.
| 01CV - Civils | Cxxx-NCR-000812 | NCR | NWP - Corbel 68 Holding Down Bolts |  | Contr | HTM | NOW - North Woolwich Portal (East) |  | 2013-10-10 | 2013-10-09 14:14 | -1 | 2013-09-26 17:19 | Civil - Civil Engineering General | 1500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | During the pouring of the flood wall, the void formers around the holding down bolts for Corbel 61 were filled with grout.
| 01CV - Civils | Cxxx-NCR-000813 | NCR | Tunnel Drive H - Crosspassage Opening Set - XP18 - Ring 478 Eastbound PP-WSB is outside tolerance for centre of crosspassage opening |  | Contr | HTM |  |  | 2013-11-15 | 2013-11-15 15:36 | 0 | 2013-10-01 11:38 | Tunnelling - Alignment | 25000 |  | Supervision/Management | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Other | Completed |  | The maximum displacement of 800mm between centreline of Westbound & Eastbound tunnel opening sets has been exceeded.
| 01CV - Civils | Cxxx-NCR-000814 | NCR | Tunnel Drive H - Crosspassage Opening Set - XP19 - Ring 178 Eastbound PP-WSB is outside tolerance for centre of crosspassage opening |  | Contr | HTM |  |  | 2013-11-15 | 2013-11-15 15:34 | 0 | 2013-10-01 11:59 | Tunnelling - Alignment | 2000 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Ref NCR 813 XP18 - A similar situation has occured - Maximum displacement between East & Westbound openings has exceeded Design tolerance of 800mm. As Built displacemrent is 1.216m.
| 01CV - Civils | Cxxx-NCR-000815 | NCR | NWP -Missing Bar in D Wall Panel N11 into Capping Beam |  | Contr | HTM | NOW - North Woolwich Portal (East) |  | 2013-10-16 | 2013-10-09 17:22 | -7 | 2013-10-02 15:27 | Civil - Civil Engineering General | 1000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | 1 no. 32mm bar within D-Wall panel N11 has been damaged during the breaking down of the D-Wall to cut off level. This bar is meant to protrude into the capping beam that sits on top of the D-Wall at this location.
| 01CV - Civils | Cxxx-NCR-000816 | NCR | NWP - D Wall Cut Off Levels ay NCB 14 |  | Contr | HTM | NOW - North Woolwich Portal (East) |  | 2013-10-18 | 2013-10-22 08:59 | 4 | 2013-10-04 11:23 | Civil - Civil Engineering General | 1500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The diaphragm wall at NCB14 location has been broken down below the required cut off level of 100.500 (up to 30mm in some locations at the edge of the d-wall). A portion of the blinding concrete, at the east end of the capping beam, was poured after the d-wall break down rather than prior to the break down which is normally the case. The blinding has been poured slightly high (approx 20-30mm). This combination has resulted in the blinding concrete, at a few locations, overlapping onto the structural concrete. (Note: Blinding concrete was Mix 3 which is a C40/50 approved concrete; the same as is used in the capping beams)
| 01CV - Civils | Cxxx-NCR-000817 | NCR | NWP - NCB 15/16 Soffit Finish |  | Contr | HTM | NOW - North Woolwich Portal (East) |  | 2013-10-18 | 2013-10-09 17:25 | -9 | 2013-10-04 11:46 | Civil - Civil Engineering General | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Following the issues raised in NCR816 it was decded by CRL and __ that the formation of the soffit for the capping beam, that overhangs the portal d-wall could not be guaranteed to be formed as per the design. No shutter, grout check or fillet had been installed and CRL expressed concerns regarding the levels of d-wall cut off and blinding concrete (as per NCR 816). NCB 15 and 16 had already been poured at the time of this inspection.
| 01CV - Civils | Cxxx-NCR-000818 | NCR | Tunnel Drive H - Precast Segment Lining Production Tests - Casting dates August 21st - Beam Test FR1 fauilures |  | Contr | HTM |  |  | 2013-11-15 | 2013-11-12 13:48 | -3 | 2013-10-04 15:34 | Tunnelling - Linings - Precast | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | See attachedSMPL NCR 0139 and associated documentation for flexural beam samples produced on 21st Aug 2013. The average result returned for fR,1 was lower than the required 4.8N/mm2. Results for the testing of the fresh concrete and the cube and cylinder results for hardened concrete are typical of normal production.
| 01CV - Civils | Cxxx-NCR-000819 | NCR | Tunnel Drive H - Third Party __ Assets - White Hart Road 381mm Sewer Relining - Deformation of UV liner identified in Post Tunnelling CCTV Survey. |  | Contr | HTM |  |  | 2014-01-31 | 2014-01-17 17:04 | -14 | 2013-10-18 11:19 | Utilities Engineering - Utilities General | 2500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | Post Tunneling CCTV Survey identifies Deformation in White Hart Road 381mm Sewer at a chainage 104.79 on the post CCTV survey. As built drawings Ref Cxxx-RFI-000937 and CCTV Survey Contractors Communication Cxxx-CCM-00081 Thames water confirm in responce to RFI 937 s ignificant deformation of the structural liner in the 381mm sewer was identified at 104.79m along the post TBM CCTV survey. and that this willl have an operational impact on the sewer and is expected to further deteriorate over time. MH 3803 to MH 3902
| 01CV - Civils | Cxxx-NCR-000820 | NCR | NWP - Missing Couplers in SCB22 |  | Contr | HTM | NOW - North Woolwich Portal (East) |  | 2013-11-04 | 2013-10-25 12:42 | -10 | 2013-10-21 17:27 | Civil - Civil Engineering General | 1500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The couplers (originally kwikastrip on drawing Cxxx-CSY-S-DDL-CR146_PT004-02114) at the west end of south capping beam 22 were not installed prior to the pour. At south capping beam 24, the couplers were installed but 3 no. have been damaged.
| 01CV - Civils | Cxxx-NCR-000821 | NCR | NWP - Cut flood wall starter bars in SFW28 |  | Contr | HTM | NOW - North Woolwich Portal (East) |  | 2013-11-04 | 2013-10-28 14:48 | -7 | 2013-10-21 17:38 | Civil - Civil Engineering General | 2000 |  | Supervision/Management | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | A number of flood wall starter bars have been cut at kicker level at south flood wall 28. In total 5 no. BF bars (32mm) and 3 no. FF (16mm) have been cut.
| 01CV - Civils | Cxxx-NCR-000822 | NCR | Tunnel Drive H - Precast Segment Lining - WB- WSB - NW - Rings 959 & 961 made up with segments from different mould sets |  | Contr | HTM |  |  | 2013-11-14 | 2013-11-12 13:38 | -2 | 2013-10-31 15:39 | Tunnelling - Linings - Precast | 500 |  | System Defect | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Westbound Tunnel Woolwich Station Box to North Woolwich . Rings were made up and sent down tunnel from mixed moud sets. Rings Built on Night shift Report date Sun 20th Oct. Ring 959 and 961 built between 00:00hrs & 04:30 hrs 21st Oct. Traceability System Failure. Ring 959: Segment A,B,C,D from mould 8-cast date 14.08.13 Segment E, KL, KR, K from mould 6 cast date 15.08.13 Ring 961 Segment A,B,C,D mould 6 cast date15.08.13 Segment E, KL, KR, K from mould 8 cast date 14.08.13
| 01CV - Civils | Cxxx-NCR-000823 | NCR | Plumstead Portal - __ Utilities - Marmadon Sewer Diversion - PipeJack - MH03 - MH04 - Incorrect Gradient - MTBM exited MH04 above Design Level |  | Contr | HTM |  |  | 2013-11-29 | 2013-11-26 15:24 | -3 | 2013-11-01 11:52 | Utilities Engineering - Utilities General | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | MTBM 1200id Pipejack MH03 - MH04 Marmadon Road Sewer Diversion exeded at MH04 above design Level. Tunnel was driven on Positive gradient instead of a Negative Gradient. Level or Gradient of Laser was not checked. Pipe levels recorded daily from laser were assumed to bee correct within specified tolerances.
| 01CV - Civils | Cxxx-NCR-000824 | NCR | Tunnel Drive H - Precast Segments - Production Tests - Flexural Beam Test Failures - Sept 13 |  | Contr | HTM |  |  | 2013-12-20 | 2013-12-10 17:06 | -10 | 2013-11-07 10:31 | Tunnelling - Linings - Precast | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | See attached NCR 0142 and associated documentation for flexural beam samples produced on 13th Sep 2013 and 26th Sep 2013 The average results returned for fR,1 in both cases was lower than the required 4.8N/mm2.
| 01CV - Civils | Cxxx-NCR-000825 | NCR | Plumstead Portal - Marmadon Sewer Diversion - Utilities Material Compliance - Acceptance - Jacking Pipes |  | Contr | HTM |  |  | 2013-11-22 | 2013-11-20 14:18 | -2 | 2013-11-08 08:51 | Utilities Engineering - Utilities General | 500 |  | System Defect | Rework | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | Quality Surveillance on Marmadon Sewer Diversion Pipejack MH03 - MH04 identified that the Material compliance records for Jacking Pipes had not been submitted for CRL acceptance. It was identified that the Procedure for gaining __ acceptance through RFI had been followed and CRL had recieved __ Acceptance. However the systems require that All Materials are proposed on the Material Proposal Schedule and Material compliance records submitted for Crosrail Acceptance under Works information Vol 2B Part 14 Cls 13.3 .7 & 13.3.8
| 01CV - Civils | Cxxx-NCR-000826 | NCR | NWP - Store Road Culvert Repair |  | Contr | HTM | NOW - North Woolwich Portal (East) |  | 2013-12-10 | 2013-12-09 14:44 | -1 | 2013-11-26 10:30 | Civil - Sewage/Water services | 1000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | The Store Road culvert had an ingress of water at two locations: the joint between pipe sections 3 and 4 the joint between the roof slab sections and the wall joint at both MH1 and MH1906
| 01CV - Civils | Cxxx-NCR-000827 | NCR | NWP - Phase 3 D-Wall to Capping Beam Reinforcing Steel |  | Contr | HTM | NOW - North Woolwich Portal (East) |  | 2013-12-10 | 2013-12-09 17:25 | -1 | 2013-11-26 11:27 | Civil - Civil Engineering General | 2500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | At 6 locations in Phase 3, the D-Wall reinforcing steel that projects into the capping beam has been either a) cut at the incorrect level during the d-wall breaking operation or b) damaged beyond repair, such that it has had to be cut out.
| 01CV - Civils | Cxxx-NCR-000828 | NCR | Tunnel Drive H - Precast Segments - Production Tests - Flexural Beam Test Failures - Oct 13 |  | Contr | HTM |  |  | 2014-01-31 | 2013-12-11 17:40 | -51 | 2013-12-05 17:04 | Tunnelling - Linings - Precast | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | Flexural beam samples produced on 08.10.2013 have returned results with a CMOD 0.5mm fR,1 average of 4.4N/mm2 versus a specification of 4.8N/mm2 Ref, SMPL NCR 148, Beam Summary October, NCR Summary & Test Reports attached
| 01CV - Civils | Cxxx-NCR-000829 | NCR | Tunnel Drive H - Westbound Drive Woolwich Box - North Woolwich - Ring 1440 built with incorrect order of segments resulting in Plane Step not noticed until Ring had been shoved. |  | Contr | HTM |  |  | 2014-02-14 | 2014-02-18 12:12 | 4 | 2013-12-13 13:24 | Tunnelling - Linings - Precast | 10000 |  | Workmanship | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Other | Completed |  | Ring Delivered to TBM was built in the wrong order (B & C plates being reversed order) resulting in a large plane step on leading Edge. The Ring was fully shoved & Grouted before the Mistake was realised. Work was stopped to resolve as it would not be possible to remove and rebuild the ring exposing the ground. Packing required to pack out the step would exceed the allowable tolerance and affect the gasket sealing.
| 01CV - Civils | Cxxx-NCR-000830 | NCR | Tunnel Drive H - Eastbound - PPL - WSB (Rings As-built measured outside of specified build tolerance |  | Contr | HTM |  |  | 2014-02-15 | 2014-02-03 17:24 | -12 | 2013-12-20 10:02 | Tunnelling - Alignment | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Listed Rings (see Attached EB_Wriggle NCR) exceed Alignment Tolerances KT10.4221. Tolerance +/- 50 mm
| 01CV - Civils | Cxxx-NCR-000831 | NCR | Tunnel Drive H - Precast Segment Manufacture - Post Pour Inspection - Blocked Grout Hole |  | Contr | HTM |  |  | 2014-01-20 | 2014-01-17 17:07 | -3 | 2014-01-06 10:16 | Tunnelling - Linings - Precast | 1500 |  | Damaged | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | The following segment was discovered to be missing its grouting socket during post pour inspection; The grout sockets became loose during the vibration cycle resulting in the socket lifting off the holder and therefore grout ingress. Attached please find SMPL NCR 0150 which relates to grout socket issues on segments B-3 – 15-11-13, grout socket not in place KR-9 – 27-11-13 grout socket threads blocked with grout.and E-1 – 05-12-13 grout socket threads blocked with grout..
| 01CV - Civils | Cxxx-NCR-000833 | NCR | Tunnel Drive H - Crosspassage 19 - Insitu Concrete Lining & Waterproofing - Method Statement Code 3 |  | Contr | HTM |  |  | 2014-02-12 | 2014-02-07 10:01 | -5 | 2014-01-29 13:04 | Tunnelling - Linings - In-situ Concrete | 500 |  | System Defect | Rework | 4 (0.5-3k) | Complete | Procedure Problem - Other | Completed |  | Method Statement Cxxx-HTM-C4-GMS-CR146_ST004-50035 Code 3 - Comments relatibg to Waterproofing Design Detail not being Clarified. Waterproofing had been installed and insitu concrete lining of invert started. Surveillance Report identified System non-conformance
| 01CV - Civils | Cxxx-NCR-000834 | NCR | Tunnel Drive H - Cross Passages - Waterproofing Layer - Materials Compliance - Unapproved Material used in XP19 |  | Contr | HTM |  |  | 2014-02-21 | 2014-02-10 18:00 | -11 | 2014-02-07 09:07 | Tunnelling - Linings - In-situ Concrete | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | The junction boxes for the waterproofing/ grouting are be different to those submitted via MCR prior to construction. Material used in permanent works has not accepted or change in material notified by revision of MCR prior to installation.
| 01CV - Civils | Cxxx-NCR-000835 | NCR | Tunnel Drive H - EB WSB - NWP - Ring 846 cracked on segment C |  | Contr | HTM |  |  | 2014-03-13 | 2014-03-05 17:55 | -8 | 2014-02-13 17:42 | Tunnelling - Linings - Precast | 2000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Tunnel Drive H - EB WSB - NWP - Ring 846 cracked on segment C see attached pictures Possible cause is a faulty push ram that might be out of sequence
| 01CV - Civils | Cxxx-NCR-000836 | NCR | NWP - Base Slab 8 - Pile No 52 Connecting Bar |  | Contr | HTM | NOW - North Woolwich Portal (East) |  | 2014-03-12 | 2014-03-07 10:55 | -5 | 2014-02-19 15:50 | Civil - Concrete Pavement | 1000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Pile number 52 in base slab 8 was, sadly, damaged during the bulk excavation stage causing 1 no. of the 12 no. 32mm starter bars to shear off at the pile cut off level. This starter bar should have been cut at approximately 260mm above the cut off level so as to couple a connection bar to anchor into the base slab.
| 01CV - Civils | Cxxx-NCR-000837 | NCR | NWP - Phase 2 D-Wall to Capping Beam Interface |  | Contr | HTM | NOW - North Woolwich Portal (East) |  | 2014-05-14 | 2014-03-07 11:59 | -68 | 2014-02-19 16:50 | Civil - Civil Engineering General | 2500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Following excavation of the portal in Phase 2, beneath the RC Prop #2 location, a section of the D-Wall concrete has become dislodged and the reinforcing steel is exposed. This section of concrete would have been beneath the blinding level of the capping beam formation and any potential problem with the concrete was not observed during the breaking down of the diaphragm wall.
| 01CV - Civils | Cxxx-NCR-000838 | NCR | WSB - Incorrect Installation of Tunnel Collar Waterproofing |  | Contr | HTM |  |  | 2014-03-19 | 2014-03-14 10:29 | -5 | 2014-03-05 17:21 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | The inner most set of waterproofing (the re-injectable channel and hydrophilic strip at the inside face of the segmental lining) has not been installed in accordance with drawing Cxxx-OVE-T-DDL-CR001_Z-73461. The position of the hydrophilic strip should be on the inside of the re-injectable channel but has been installed on the outside of the channel due to construction constraints - photos attached. The channel must be positioned 50mm from the hydrophilic strip in order to be fully surrounded in concrete and it was not therefore possible to install both of these between the dowel postion and the grout to the segmental lining due to this spacing requirement. The dowels run along the axis of the segments – these are 30mm thick, but only 235mm between segments because of the 65mm drip detail. We could not have positioned the RASCOtec inside the dowels because it would be too close to the outside edge of the concrete (potential bursting) and the installation guidance warns against this. Hence the hydrophilic was installed in the only place it would fit – on the outside of the channel.
| 01CV - Civils | Cxxx-NCR-000839 | NCR | Tunnel Drive H Westbound Cross passage 19 - Insitu Concrete Lining - Unapproved Welding of Reinforcement bars in Crown |  | Contr | HTM |  |  | 2014-03-21 | 2014-03-12 13:24 | -9 | 2014-03-07 11:53 | Tunnelling - Linings - In-situ Concrete | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | During erection of Steel Reinforcement in the Crown of Crosspassage 19 adjacent to Tunnel Collar,reinforcement bar was tack welded instead of being tied. An approved welding system procedure or aproved certified welder accepted by Crossrail Project manager was not in place.The Method of construction had been changed without seeking acceptance. Potentially hot works has altered the property of the reinforcement steel however this is considered unlikley as the 8 no. welds are surface tacks. The hot works took place adjacent to a waterproof membrane, The integrity of the membrane may have been affected.
| 01CV - Civils | Cxxx-NCR-000840 | NCR | WSB - Concrete Finish to Platform Wall PWP-E-AE 03/03/14 |  | Contr | HTM |  |  | 2014-03-21 | 2014-03-21 11:43 | 0 | 2014-03-07 11:56 | Civil - Civil Engineering General | 1000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The concrete surface finish does not meet the requirements of the specification Cxxx-OVE-S-RSP-CR147-50001 There are a number of minor defects e.g. blow holes and larger 'bridged' holes
| 01CV - Civils | Cxxx-NCR-000841 | NCR | Tunnel Drive H - Precast Tunnel Segment Damaged Stock - Cambridge University Rings - Rivo Incident 2995944 "dropped Segment" |  | Contr | HTM |  |  | 2014-04-04 | 2014-03-27 13:00 | -8 | 2014-03-07 15:22 | Tunnelling - Linings - Precast | 1000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | On 20.02.14 during restacking of Fibre Optic Monitoring Ring for Cambridge University. the Key segment was reported as slipping in the nylon web sling and falling onto the Segment Stack Below. Incident was reported on RIVO without comunication to Quality Department the Report identifies minor damage but no reference to ring stack. Investigation by Quality department identified Ring to be Key & E plate for XP17 opening set ID CAMB 1 K9 20-11-13 and corresponding E plate from Ring Package. The adjacent ring stack also Cambridge rings show damage on the edge indicating key had possibly scraped along the edge of this segment. See attached reports. Joint inspection with __/CRL/Cxxx of the damaged plates on 5th March requide that further investigation of KR plate on bottom of stack would be needed to fully resolve, with the assistance of Cambridge students to check the strain gauges cast within the rings for Damage.
| 01CV - Civils | Cxxx-NCR-000842 | NCR | Plumstead Portal - Third Party Assets - __ - Marmadon Sewer Diversion - Non Specified Material used in Backfill for abandonment of old Sewer Pipe. |  | Contr | HTM |  |  | 2014-03-31 | 2014-03-27 09:35 | -4 | 2014-03-17 09:59 | Utilities Engineering - Utilities General | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | Foam Concrete was used to backfil and abandon the old sewerpipe pipe following diversion. The Method Statement stated the use of Foamed concrete. However the Specified material should have been G4 Grout. There was no prior acceptance of the Foamed Concrete through FCD or MCR prior to placing the non conforming material. Inclusion in the method statement does not constitute material acceptance.
| 01CV - Civils | Cxxx-NCR-000843 | NCR | NWP - Phase 3 - Pile 78 Base Slab 13 |  | Contr | HTM | NOW - North Woolwich Portal (East) |  | 2014-04-01 | 2014-03-21 12:00 | -11 | 2014-03-18 09:14 | Civil - Civil Engineering General | 1000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | During break down one of the bars in Pile 78 has been damaged - see attached photo. 1 No 32mm starter bar (out of a total 12 within the pile) from shearing off at the cut off point. This starter bar should have been cut at approximately 260mm above the cut off point so as to couple a connection Bar to anchor into the Base Slab.
| 01CV - Civils | Cxxx-NCR-000844 | NCR | Tunnel Drive H - Eastbound - Woolwich Box to North Woolwich - Ring Segment KL damaged Installed in Ring 1106 |  | Contr | HTM |  |  | 2014-04-15 | 2014-03-27 13:14 | -19 | 2014-03-18 14:07 | Tunnelling - Linings - Precast | 1500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | On the Dayshift (Shift II) on the 17th of February at 14:00 there was an incident on the TBM with the while unloading a segment with the segment crane, where a segment collides with another and damaged the surface. During the advance for ring 1106 The sixth segment (S-E2-140813-2) struck segment (S-KL2-140813-2) during unloading. The segment at the crane (S-E2-140813-2) shows no damage the segment (S-KL2-140813-2) shows damage on the intrados edge. See photo. The damage was discussed with the CRL Field Engineer and Construction Manager and assessed prior to installing the damaged segment into ring 1106
| 01CV - Civils | Cxxx-NCR-000845 | NCR | Tunnel Drive H - Eastbound - Woolwich Box - North Woolwich - Ring 1190 - Damaged Gasket key segment during ring build. |  | Contr | HTM |  |  | 2014-04-23 | 2014-04-17 15:37 | -6 | 2014-03-26 14:46 | Tunnelling - Linings - Precast | 1500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | When building R1191 After erecting the first 2 segments, the rams were removed from the keystone of 1190 and a slow leak of slurry came on the trailing edge of that keystone (S06 R1190). Visualy the Gasket wwas seen as displaced. Datwyler seal has also peeled away from the keystone due to the onrushing slurry, and is out of the recess but now maintaining water-tightness.To mitigate the keystone slipping forward and allow the completion of the build we used through-bolts and fishplates to fix the key of 1190 to ring 1189. While they were effective to a point, this measure did not stop the leakage while installing the ‘C’ segment of ring 1191. The bolts will be removed after advance 1192 to prevent any clash with trailing lines from the gantries. It was noted that crack appeared in next Ring Build R1191. at 4 oclock position.
| 01CV - Civils | Cxxx-NCR-000846 | NCR | NWP - Bay 16 Concrete Finishing (Top of Wall) |  | Contr | HTM | NOW - North Woolwich Portal (East) |  | 2014-04-14 | 2014-04-01 14:27 | -13 | 2014-03-31 16:33 | Civil - Civil Engineering General | 1000 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The top surface finish of the flood walls in bay 16 appears uneven. The wall is level but concrete 'fins' have formed where the top surface of the concrete has been pushed up against the inside face of the shutter. These fins are a few mm thick. Minor defects such as these would normally be raised as a snagging issue and __ would carry out the remedial works as detailed in the approved method statement Cxxx-HTM-C-GMS-CR146_PT004-50007. At the time of the handover with Cxxx and Crossrail's architects, this remedial work had not been carried out and an NCR had therefore been raised.
| 01CV - Civils | Cxxx-NCR-000847 | NCR | NWP - Bay 16 Concrete Finishing (Wall to Base Slab Construction Joint) |  | Contr | HTM | NOW - North Woolwich Portal (East) |  | 2014-05-12 | 2014-04-22 09:50 | -20 | 2014-03-31 17:02 | Civil - Civil Engineering General | 2000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The external face of the south flood wall, along Factory Road, at Bay 16 was specified as an F3 finish in Cxxx-OVE-Z4-RSP-CR001-00023 Rev 5.0. During an inspection with Crossrail Field Engineers and the Crossrail architects, it was felt that the requirements of F3 were not met as some making good had been carried out at the construction joint between the base slab and the flood wall. This was due to variation in the position/level of the base slab joint which led to overpour during the pouring of the flood walls. Crossrail take the view that no remedial works are permitted on an F3 finish. __ argue that Cxxx-OVE-Z4-RSP-CR001-00023 permits remedial works; specifically in KF10.3231. The remedial repairs carried out are not well colour matched and are untidy.
| 01CV - Civils | Cxxx-NCR-000848 | NCR | Plumstead Portal - Embedded Wall & Piling(__) - Male Secant Pile Ref. MS001 (Marmadon Section) - Concrete Consistence - Flow exceeded Specified F5 limit |  | Contr | HTM |  |  | 2014-04-17 | 2014-04-11 12:07 | -6 | 2014-04-03 09:06 | Civil - Civil Engineering General | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The second concrete load in the pile when tested for consistence was recorded over the limit of F5 as per the mix. The flow was recorded as 700mm+ whereas the F5 upper limit is 640mm. The concrete was used as this was the second load in the pile and any further delay could have caused issues with the integrity of the pile by having a cold joint.
| 01CV - Civils | Cxxx-NCR-000849 | NCR | Tunnel Drive H - Cross Passage 19 - Insitu Concrete - Installed Cast in items - Incorrect Material Specification - Cable Ducts |  | Contr | HTM |  |  | 2014-04-24 | 2014-04-24 15:13 | 0 | 2014-04-10 18:36 | Tunnelling - Linings - In-situ Concrete | 1500 |  | Material | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | Incorrect materials Procured ( 64mm Polypipe rigiduct & bends) were not compliant to specified requirements on Drawing (note 3) for low flamability & smoke emmissions. Cable Ducts were installed as Cast in items - Insitu concrete lining of Cross passage 19.
| 01CV - Civils | Cxxx-NCR-000850 | NCR | Control of documents |  | Crossrail | XRL |  |  | 2014-04-28 | 2014-04-28 14:56 | 0 | 2014-04-14 11:03 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | During a post review of the reinforcement drawings shown on the ITP that It could not be verified on eb that the Contractor is using the correct revision of drawings numbered; Cxxx-HTM-C-DWG-CR147-52030 rev 1, Cxxx-HTM-C-DWG-CR147-52031 rev 2, Cxxx-HTM-C-DWG-CR147-52032 rev 2, Cxxx-HTM-C-DWG-CR147-52033 revs 1, Cxxx-HTM-C-DWG-CR147-52034 rev 2 Cxxx-HTM-C-DWG-CR147-52035 revs 2, Cxxx-HTM-C-DWG-CR147-52036 rev 1, Cxxx-HTM-C-DWG-CR147-52037 rev 1 Cxxx-HTM-C-DWG-CR147-52038 rev 2, Cxxx-HTM-C-DWG-CR147-52039 rev 2 were found not approved on eb at the time of the surveillance. The above drawings are all now rev 1 code 4 decal received for information only, signed off on the 31/03/2014. The status of the drawings is unknown i.e. drawings do not state whether they are fit for construction, eb shows rev 1 as current drawing and rev 3 in draft.
| 01CV - Civils | Cxxx-NCR-000851 | NCR | Tunnel Drive H - Eastbound - Woolwich Station Box - North Woolwich - TBM Alignment outside Tollerance - Ring 1415 |  | Contr | HTM |  |  | 2014-05-01 | 2014-04-28 16:55 | -3 | 2014-04-17 13:20 | Tunnelling - Linings - Precast | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | TBM Alignment for Ring build Position 1414 show pridicted TBM line moving outside of allowed tollerance of 100mm on alignment. From Ring 1414 the theoretical ring build position is outside of the 100mm tolerance. the Maximum predicted alignment is 135 -140mm outside the 50mm Radis curve at Ring 1419 at which point the TBM alignment has been corrected Parallel to Design Tunnel alignment. There are no level errors.
| 01CV - Civils | Cxxx-NCR-000852 | NCR | NWP - Kwikastrip not extending the full length of wing walls for walkway slab |  | Contr | HTM | NOW - North Woolwich Portal (East) |  | 2014-05-20 | 2014-05-19 09:15 | -1 | 2014-05-06 07:43 | Civil - Civil Engineering General | 5000 |  | Workmanship | Repair | 3 (3-6k) | Complete | Personnel Error - Inattention to detail | Completed |  | The setting out position for the edge of the walkway slab in NWP was incorrectly taken as 500mm offset from the design position. As a result the kwikastrip that was cast in the base slab is offset away from the track alignment and is now too short (see attached pdf).
| 01CV - Civils | Cxxx-NCR-000853 | NCR | Tunnel Drive H - Cross Passage 18 - Insitu Concrete Lining - Concrete discharged 2hrs 35 minutes after batching |  | Contr | HTM |  |  | 2014-06-13 | 2014-06-12 10:14 | -1 | 2014-05-16 10:21 | Tunnelling - Linings - In-situ Concrete | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | Load 2 of 2 Delivery Ticket R8769874 dated 02/05/14 Side & Crown 1st pour for internal section of Cross Passage. Mix 25 C32/40 with PP fibres identified that load was batched at 08:24:51 Hrs and start of discharge was 11:00 hrs
| 01CV - Civils | Cxxx-NCR-000854 | NCR | Tunnel Drive H - Cross Passage 17 - Chalk fissure Grouting - Drilling from West bound Tunnel penetrated lining of eastbound tunnel. |  | Contr | HTM |  |  | 2014-06-16 | 2014-06-11 13:13 | -5 | 2014-05-19 10:57 | Tunnelling - Tunnelling General | 2000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Drilling from West bound to east bound during the Chalk fissure grouting of Cross passage 17 the drill prenetrated the lining of the East bound tunnel at ring 1207. see attachements.
| 01CV - Civils | Cxxx-NCR-000855 | NCR | Plumstead Portal - Marmadon Sewer & Pumping Station for __ - PS Shaft - Caisson Method - Rings unable to reach design formation level |  | Contr | HTM |  |  | 2014-07-14 | 2014-07-09 13:05 | -5 | 2014-05-19 15:12 | Shafts - Excavation | 5000 |  | Design | Use As-Is | 3 (3-6k) | Complete | Discipline/Workmanship - Other | Completed |  | 9.0m dia wet Caisson for Pumping Station Shaft became stuck at ring 17 approximately 4 rings short of completion at 87.77m . Contractor excavated below cutting edge to reach design formation approx 20.8m below top of ring at 83.97m. (Design formation 84.49m) Mass concrete (underwater mix P450) was poured to reach approx base of reinforcement
| 01CV - Civils | Cxxx-NCR-000856 | NCR | Plumstead Portal - South Capping Beam 23/24 - Honeyconmbing & Grout loss |  | Contr | HTM |  |  | 2014-06-16 | 2014-06-11 13:14 | -5 | 2014-05-19 16:49 | Civil - Civil Engineering General | 1000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The concrete surface finish does not meet the requirements of the specification. There are minor defects includign honeycombing, poor compaction at kicker to capping beam joint
| 01CV - Civils | Cxxx-NCR-000857 | NCR | NWP - Spine wall steel fixing - reduced lap length with kwikastrip at kicker not recorded |  | Contr | HTM | NOW - North Woolwich Portal (East) |  | 2014-06-03 | 2014-06-02 14:14 | -1 | 2014-05-20 17:14 | Civil - Civil Engineering General | 500 |  | System Defect | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | The required lap length between the kwikastrip starters, cast into the base slab, and the vertical NF2/FF2 bars of the spine wall (Drawing Cxxx-CSY-S-DDL-CR146_PT004-02181 BM03, BM12 and BM22) has not been acheived. This is due to the casting of a kicker at this location, without first fixing the vertical bars of the spine wall. All laps are 100mm short. This was discussed and agreed with the designer, ahead of pouring the kicker and steel fixing for the spine wall, as it was seen as a better production solution. This was not recorded as an FCD. There has been a failure to use the PTR process correctly.
| 01CV - Civils | Cxxx-NCR-000858 | NCR | WSB - Reduced cover for above platform wall starter bars |  | Contr | HTM |  |  | 2014-06-03 | 2014-06-02 17:25 | -1 | 2014-05-20 17:36 | Civil - Civil Engineering General | 1500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | ost pour inspection of platform slab between gridlines Z4 – Z2 has shown that the reinforcement for above platform walls had been installed in the incorrect position. A number of B25 cranked bar mark: 07,01 are protruding into cover for the above platform wall kicker(see attached photos). DWG No. : Cxxx-HTM-C-DWG-CR147-52044, Cxxx-HTM-C-DWG-CR147-52002
| 01CV - Civils | Cxxx-NCR-000859 | NCR | WSB - Reduced cover for above platform wall starter bars (north wall) |  | Contr | HTM |  |  | 2014-06-05 | 2014-06-02 17:28 | -3 | 2014-05-22 10:01 | Civil - Civil Engineering General | 1500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Post pour inspection of platform slab between gridlines Z2 – Z4 has shown that the reinforcement for above platform walls had been installed in the incorrect position. A number of B25 cranked bar mark: 05 are protruding into cover for the above platform wall kicker. DWG No. : Cxxx-HTM-C-DWG-CR147-52044 and Cxxx-HTM-C-DWG-CR147-52006
| 01CV - Civils | Cxxx-NCR-000860 | NCR | WSB: Stater bars at above platform door openings. |  | Contr | HTM |  |  | 2014-06-05 | 2014-06-02 17:29 | -3 | 2014-05-22 10:59 | Civil - Civil Engineering General | 1500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | At a number of door openings (see attached 'Drawing of Missing Rebar.pdf) the wall starter bars have been installed in incorrect positions. The bars now clash with the openings. The attached photograpsh show each of the locations. The yellow spray lines mark the positions where the walls end, as per design.
| 01CV - Civils | Cxxx-NCR-000861 | NCR | Plumstead Portal - South Capping Beam 24/25 andNorth capping beam 23/24- Honeyconmbing & Grout loss |  | Contr | HTM |  |  | 2014-06-25 | 2014-06-13 15:17 | -12 | 2014-05-28 17:45 | Civil - Civil Engineering General | 2000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The concrete surface finish does not meet the requirements of the specification. There are minor defects includign honeycombing, poor compaction at kicker to capping beam joint
| 01CV - Civils | Cxxx-NCR-000862 | NCR | WSB - Kicker for Above Platform Stairwell Walls BWP-E-EI & EJ |  | Contr | HTM |  |  | 2014-06-12 | 2014-06-11 13:10 | -1 | 2014-05-29 14:29 | Civil - Civil Engineering General | 1000 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Drawing Cxxx-OVE-S-DDB-CR147_Z-32651 shows a step from 300mm under platform walls to continue above platform as a 200mm thick wall. Kicker for above platform walls has been poured at 300mm rather than 200mm.
| 01CV - Civils | Cxxx-NCR-000863 | NCR | Plumstead portal - Phase 2 North capping beam 23/24 - Concrete finishes - surface cracking |  | Contr | HTM |  |  | 2014-06-26 | 2014-06-13 15:18 | -13 | 2014-05-29 10:29 | Civil - Civil Engineering General | 1000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The concrete surface finish does not meet the requirements of the specification. There are minor surcace cracking on top of NCB 23/24 may be cause due to excessive water on surface during initial curing phase
| 01CV - Civils | Cxxx-NCR-000864 | NCR | Plumstead Portal - North Capping Beam NCB23/24 - Construction Joint Hyrib |  | Contr | HTM |  |  | 2014-06-12 | 2014-06-09 15:13 | -3 | 2014-05-29 17:24 | Civil - Civil Engineering General | 1000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Hyrib stop ends allowable in no water retaining structures was not installed as per manufactur's installation guide
| 01CV - Civils | Cxxx-NCR-000865 | NCR | Tunnel Drive H - Cross Passage Insitu Concrete Lining & Waterproofing - Excessive Leakage through lining at XP19 |  | Contr | HTM |  |  | 2014-07-04 | 2014-07-01 15:14 | -3 | 2014-06-06 15:00 | Tunnelling - Linings - In-situ Concrete | 2000 |  | Design | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Not Defined | Completed |  | Recorded at XP19 inspection 06/06/13. Following sealing of the water pressure relief holes used during Installation of waterproofing & insitu concrete lining a build up of water pressure behind the lining has resulted in leakage of water through finished cast insitru lining and the joint between cast insitu and Tunnel Precast lining. see attached pdf of photo record.Most water is eminating from the reinjectable grout tubes at the junction boxes cast into the lining. Some small cracks with in the lining have also started leaking.
| 01CV - Civils | Cxxx-NCR-000866 | NCR | __ Pumping Station - Valve Chamber RC Base - Management System Failure - MCR not submitted |  | Contr | HTM |  |  | 2014-07-16 | 2014-06-23 16:08 | -23 | 2014-06-18 15:45 | Civil - Civil Engineering General | 500 |  | System Defect | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | Observation Cxxx-HTM-O4-RGN-CR148_PT005-50119 on the construction of __ Pumping Station Valve Chamber identified that although the correct concrete was being used there was no MCR submitted for Acceptance of the Concrete. Drawing A041-A1-21775 issued under TW Vol. 2 Information Site Specific - SE14-PCN144 - 492-TW-WI-99-08 specifies RC Walls & Base as C28/35 concrete.
| 01CV - Civils | Cxxx-NCR-000867 | NCR | __ - Pumping Station - Valve Chamber - RC Base - Non UKAS Sampling of Concrete |  | Contr | HTM |  |  | 2014-07-02 | 2014-07-01 14:17 | -1 | 2014-06-18 16:09 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Subcontractor Problems - Other | Completed |  | During Observation Cxxx-HTM-O4-RGN-CR148_PT005-50119 it was identified that concrete was sampled by a JTS Engineer. No dispensation was agreed with the CRL project Manager to use non UKAS sampling on Permanent Works Concrete.
| 01CV - Civils | Cxxx-NCR-000868 | NCR | WSB - Wall 71 (Top Lift) Concrete Finish |  | Contr | HTM |  |  | 2014-07-11 | 2014-07-09 12:33 | -2 | 2014-06-27 15:44 | Civil - Civil Engineering General | 1500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The concrete finish,htowards the top, of the 2nd lift of wall 71 (Northern Staircase wall in Eastbox) on the inside (Southern face) does not meet the requirements of the specification Cxxx-OVE-S-RSP-CR147-50001.
| 01CV - Civils | Cxxx-NCR-000869 | NCR | WSB - Eastern Box (South) Mass Infill Concrete Delivery Delays |  | Contr | HTM |  |  | 2014-07-11 | 2014-07-10 14:49 | -1 | 2014-06-27 15:54 | Civil - Civil Engineering General | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | External Phenomenon - Other | Completed |  | Due to delays in the concrete for the mass infill pour for the East Box (south track), from concrete supplier __, there is potential for a cold joint to have formed in the pour. Concrete delivery tickets record delivery times as: 07.30, 08:05, 08.25, 09.00, 09.35, 10.35, 11.35, 11.45, 12.05, 12.25, 12.20, 13.25, 13.40, 14.15, 15.30, 15.55, 16.20, 16.45. This puts the longest delay in supply at 1hr 15mins with further gaps of 1hr 5mins and 2 no. at 1 hr.
| 01CV - Civils | Cxxx-NCR-000870 | NCR | NWP - Roof Slab 11 - Missing Coupler |  | Contr | HTM | NOW - North Woolwich Portal (East) |  | 2014-07-16 | 2014-07-02 12:23 | -14 | 2014-07-02 09:23 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Not Defined | Completed |  | Due to a clash with the bars that cap the central spine wall, 1 no. coupled bar could not be installed in RC Prop #3 for the Roof Slab 11 pour. This bar is in the bottom mat - Bar Mark 09 (B3). The top threaded bar at this location, which also clashed, was installed by shifting the U bars over slightly. It is not possible to move the U bars for the bottom mat as it is too close to the concrete surface.
| 01CV - Civils | Cxxx-NCR-000872 | NCR | Tunnel Drive H - Westboud -WSB - NWP (Rings As-built measured outside of specified build tolerance |  | Contr | HTM |  |  | 2014-08-01 | 2014-07-11 17:13 | -21 | 2014-07-04 15:48 | Tunnelling - Alignment | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Listed Rings (see Attached WSB_NWP Wriggle Survey spread sheet) exceed Alignment Tolerances KT10.4221. Tolerance +/- 50 mm
| 01CV - Civils | Cxxx-NCR-000873 | NCR | WSB - Mass Fill Concrete Section 2 Pour 1 |  | Contr | HTM |  |  | 2014-07-22 | 2014-07-16 13:04 | -6 | 2014-07-08 09:47 | Civil - Civil Engineering General | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | External Phenomenon - Other | Completed |  | Due to delays in the concrete for the mass infill pour for Section 2 Pour 1 (on 03/07/14) from concrete supplier __, there is potential for a cold joint to have formed in the pour. The pour was abandoned after approx 66m3 and the surface sprayed with retarder. The final 35m3 was poured the next day after the concrete surface was prepared. Concrete delivery tickets record delivery times as: 9.10, 10.00, 10.05, 10.40, 11.30, 11.50, 12.05, 12.45, 14.20, 14.25 This puts the longest delay in supply at 1hr 35 mins.
| 01CV - Civils | Cxxx-NCR-000874 | NCR | WSB - Damage to formed voids during duct installation in Eastern Box |  | Contr | HTM |  |  | 2014-07-22 | 2014-07-22 14:14 | 0 | 2014-07-08 09:58 | Civil - Civil Engineering General | 1000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The ducts, cast into the Eastern Box mass fill, were originally specified as a flexible poly pipe. Due to issues with LU compliance on ducts of this diameter, cast iron pipes were used instead. The openings in the south platform wall are cast perpendicular with the wall face with no provision for a rigid, cast iron pipe passing through at such an angle, without the flexibility of a poly pipe. The most easterly duct has damaged the surrounding concrete during it's installation (see photo)
| 01CV - Civils | Cxxx-NCR-000875 | NCR | WSB - Lift Shaft Walls - Surface Finish |  | Contr | HTM | NOW - North Woolwich Portal (East) |  | 2014-08-06 | 2014-08-05 15:49 | -1 | 2014-07-08 10:32 | Civil - Civil Engineering General | 1500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Concrete surface finish does not meet the requirements of the specification. Defects include blow holes larger than 10mm diametre.
| 01CV - Civils | Cxxx-NCR-000876 | NCR | WSB - Damaged M20 Tension Anchors for Woolwich East Box Tunnel collar |  | Crossrail | PDP |  |  | 2014-08-06 | 2014-08-05 16:14 | -1 | 2014-07-11 09:33 | Civil - Civil Engineering General | 1500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Worker not correctly instructed | Completed |  | See attached drawing Cxxx-OVE-T-DDL-CR001_Z-73461 which details __ M20 Tension Anchors to be installed in the Dwall for the Tunnel Collar construction. During the removal of the Pressure Release Chamber 3 No of these Anchors have become damaged. Further process NCR arising from __ having already installed replacement anchors without agreement through the NCR process and use of resin anchors when not an approved material. Brief operatives on need for care to be taken around permanent works and brief engineers on the contract requirement to raise NCRs correctly and in accordance with __ quality plan.
| 01CV - Civils | Cxxx-NCR-000878 | NCR | WSB - Leak in D-Wall adjacent to WB Tunnel Collar in Eastern Box |  | Contr | HTM |  |  | 2014-08-18 | 2014-08-06 12:11 | -12 | 2014-07-11 15:56 | Civil - Tunnelling | 1000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | There is a leak around the tunnel collar of the WB tunnel in the Eastern Box. The tunnel collar has been injected on a number of occasions and __ now consider all leaks in the collar itself to have been stopped.The leak appears to be coming from the D-wall panel itself. Photo IMG7057 shows the leak highlighted in this NCR. Photo IMG7055 shows a leak at the construction joint which appears to have dried up since re-injection. Phot IMG7056 shows leaks from beneath the tunnel collar; again these appaear to have dried up since reinjection.
| 01CV - Civils | Cxxx-NCR-000880 | NCR | Tunnel Drive H - PP - WSB East bound (Tunnel 2) - Segmental lining / Headwall Collar Interface - Sand lenses within Grouted Anulus. |  | Contr | HTM |  |  | 2014-08-14 | 2014-08-12 12:24 | -2 | 2014-07-11 16:43 | Tunnelling - Grouting | 2000 |  | Incomplete Works | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The Last Ring built in Tunnel where the anuluar grouting is exposed in the headwall exhibits areas of soft sand like material within the grouted anulus.
| 01CV - Civils | Cxxx-NCR-000881 | NCR | Platform Wall Missing Kwikstrip - Reinforcement Bars Drilled & Fixed |  | Contr | HTM |  |  | 2014-08-06 | 2014-08-05 15:55 | -1 | 2014-07-15 10:16 | Civil - Civil Engineering General | 1000 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Kwikistrip reinforcement had not been installed for North platform wall mark CZ-BP-WG2, Gridline C20, Bars had then been drilled and fixed to connect reinforcment.
| 01CV - Civils | Cxxx-NCR-000882 | NCR | WSB - Couplers in roof slab for steel smoke duct hanges(PC) |  | Contr | HTM |  |  | 2014-08-01 | 2014-07-24 09:14 | -8 | 2014-07-18 12:41 | Civil - Civil Engineering General | 0 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Previous Construction - Problems based on previous construction errors | Completed |  | A number of couplers in the roof slab of the central box section, which are to be used for the connecting positions for the steel smoke duct hangers, are blocked with grout. As result the bolts cannot be screwed in to the required depth. These couplers were installed by a previous Crossrail contractor.
| 01CV - Civils | Cxxx-NCR-000883 | NCR | Plumstead Portal - Central Spine WallPhase 5 - Starter bars cast into kicker had been bent to form an access |  | Contr | HTM |  |  | 2014-08-14 | 2014-08-12 12:18 | -2 | 2014-07-21 18:29 | Structural Engineering - Reinforcement | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Unauthorised Pedestrian Access was created through Steel Reinforcement cast into Concrete kicker by bending back bars. Noted in conjunction with poor housekeeping trip hazards adjacent to this access through the spine wall construction.
| 01CV - Civils | Cxxx-NCR-000884 | NCR | Plumstead Portal - Concrete Sampling & Testing - Storage and Protection of Concrete Test Cubes |  | Contr | HTM |  |  | 2014-08-14 | 2014-08-12 12:21 | -2 | 2014-07-21 18:48 | Structural Engineering - Testing | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Cube Storage container adjacent gate 3 at Plumstead for storage of Portal Concrete samples was found to be 30 degrees, last max min temperature recorded on digital thermometer 30 /11 degrees. There were no cubes stored for stripping. Cubes are collected within 16 - 72 hrs by __ UKAS Lab. there was no record of daily temperatures being recorded.
| 01CV - Civils | Cxxx-NCR-000885 | NCR | NWP - Mortar selection for Factory Road coping stones |  | Contr | HTM | NOW - North Woolwich Portal (East) |  | 2014-08-27 | 2014-08-06 12:48 | -21 | 2014-07-30 09:23 | Civil - Civil Engineering General | 1500 |  | Material | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The installation of the coping stones along Factory Road proceeded without an approved MCR in place. This was due to the specification no clearly defining colour and a trial section required. __ had confirmed the colour and mortar via emails with the project architect. At the inspection the colour was not accepted and the installation rejected.
| 01CV - Civils | Cxxx-NCR-000886 | NCR | Plumstead portal - phase 5 spine wall pour 2 concrete surface finishing and cold joint |  | Contr | HTM |  |  | 2014-08-20 | 2014-08-19 15:04 | -1 | 2014-07-23 16:04 | Civil - Civil Engineering General | 1000 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The concrete surface finish does not meet the requirements of the specification. There are minor defects includign Cold joint and surface blow holes
| 01CV - Civils | Cxxx-NCR-000887 | NCR | WSB - Wall Pours - East Box - Mix 36 Cast Instead of Mix 26 for Basement Wall EB-PB-W76 |  | Contr | HTM |  |  | 2014-08-06 | 2014-08-06 12:14 | 0 | 2014-07-23 14:24 | Civil - Civil Engineering General | 2000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Wall Mk. EP-PB-W76, cast on 19/07/14 was poured using concrete mix 36 rather than the specified mix 26. Removal of shuttering revealed poor surface finish and some grout loss and slight discolouration.
| 01CV - Civils | Cxxx-NCR-000888 | NCR | NWP - 28 Day Cube Failure at SFW18 |  | Contr | HTM | NOW - North Woolwich Portal (East) |  | 2014-08-13 | 2014-08-07 12:00 | -6 | 2014-07-30 12:08 | Civil - Civil Engineering General | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Not Defined | Completed |  | The pair of 28 day cubes averaged at 46.85 N/mm2 for the pour for SFW18 and Corbel 74. The design strength should be 50 N/mm2
| 01CV - Civils | Cxxx-NCR-000889 | NCR | NWP - Excess cover to top face of roof slab RS6 |  | Contr | HTM | NOW - North Woolwich Portal (East) |  | 2014-08-15 | 2014-08-06 12:40 | -9 | 2014-08-01 11:06 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | At a number of locations, the top mat of the reinforcement for roof slab RS6 had cover in excess of the nominal 50mm cover. BS EN 13670 allows for a Class 1 Tolerance of 70mm. At a number of locations the actual cover was 80mm.
| 01CV - Civils | Cxxx-NCR-000890 | NCR | Tunnel Drive H - Eastbound -WSB - NWP (Rings As-built measured outside of specified build tolerance |  | Contr | HTM |  |  | 2014-08-29 | 2014-08-06 11:31 | -23 | 2014-08-01 14:53 | Tunnelling - Alignment | 2500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The tunnel Ring EB- WSB to NWP 918, 936, 938, 1384, 1416, 1418, 1420, 1422, 1424, 1426, 1428, 1430, 1432, 1434, 1436, 1438, 1508, 1510, 1512, 1572, 1574, 1576, 1640, 1642, 1644. exceed Alignment Tolerances KT10.4221 Tolerance +/- 50 mm (see Attached WSB_NWP Wriggle Survey spread sheet)
| 01CV - Civils | Cxxx-NCR-000891 | NCR | North Platform Walls - C1-C2: Surface Finish |  | Contr | HTM |  |  | 2014-08-18 | 2014-08-15 12:01 | -3 | 2014-08-04 17:34 | Civil - Civil Engineering General | 1000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | North Platform Walls - C1-C2 poured on 04/08/2014 showed obvious signs of grout loss, honeycombing and blow holes throughout the surface finish of the wall.
| 01CV - Civils | Cxxx-NCR-000892 | NCR | WSB - Coupler positions for smoke ducts in Central Box |  | Contr | HTM |  |  | 2014-09-03 | 2014-08-22 17:41 | -12 | 2014-08-06 15:00 | Civil - Civil Engineering General | 0 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Previous Construction - Other | Completed |  | The couplers, cast into the roof slab by a previous contractor, are not accurately positioned enough to comply with the specified tolerances of the __ contract. __ are not aware of the tolerances and co-ordinates that the previous contractor was working to. Please find attached results for steel hanger installation. 7 points have been recorded on each hanger. __ could control height but chainage and offset are governed by __`s home coupler installation. We only had 10mm play on the base plate to overcome any coupler positional error. 2 points have been checked on flange for offset (plumb) and 4 points have been checked 103mm from the web for rotation. Elevation has been checked on the bottom of each hanger. Design spacing between each set should be 1.600. In the attached spreadsheet __ has highlighted those which are over 10mm in position (the specified __ tolerance)
| 01CV - Civils | Cxxx-NCR-000893 | NCR | Plumstead Portal - __ Pumping Station - Dwarf Compound Wall - Failed to comply with ITP & Hold Point conditions |  | Contr | HTM |  |  | 2014-09-09 | 2014-08-13 17:12 | -27 | 2014-08-12 12:18 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | ITP not accepted prior to Subcontractor JTS commencing work on excavation blinding and steel fixing of dwarf compound wall for TW pumping station. Work was stopped by __ pending submission & acceptance of ITP. Following discussions at end of last week concrete was provisionally called off for Monday morning planned pour. However Subcontractor failed to follow their planned arrangements for inspection & test and missed a required hold point attendance by Crossrail for the pre pour inspection
| 01CV - Civils | Cxxx-NCR-000894 | NCR | Tunnel Drive H - First Stage Concrete - Failure to provide sufficient resource for UKAS sampling & Testing |  | Contr | HTM |  |  | 2014-09-09 | 2014-09-08 14:04 | -1 | 2014-08-12 12:41 | Tunnelling - Linings - In-situ Concrete | 500 |  | Planning | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | During insitu Trial of first Stage concrete on 8th August 2014 at WSB end of westbound Tunnel drive 1 (PLU-WSB) with planned acceptance of trial for permanent work. __ technician providing UKAS accredited sampling and testing for subcontractor __ Formwork left site at the end of his normal working hours leaving the subcontractor without sufficient resources to sample the remainder of the concrete pour.
| 01CV - Civils | Cxxx-NCR-000895 | NCR | Tunnel Drive H - First Stage Concrete - Failure to saw cut expansion joint resulting in uncontrolled crack generating in Trial poured 8th August. |  | Contr | HTM |  |  | 2014-09-09 | 2014-08-27 11:54 | -13 | 2014-08-12 14:57 | Tunnelling - Linings - In-situ Concrete | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Management Problem - Improper resource allocation | Completed |  | During insitu Trial of first Stage concrete on 8th August 2014 at WSB end of westbound Tunnel drive 1 (PLU-WSB) with planned acceptance of trial for permanent work. Saw cutting of expansion joint in addition to use of crack inducers was not carried out in accordance with planned arrangements.
| 01CV - Civils | Cxxx-NCR-000896 | NCR | WSB - 28 Day Cube Failures (Central and Eastern Box Platfrom Walls, Eastern Box Platform Slab) |  | Contr | HTM |  |  | 2014-08-26 | 2014-08-19 15:07 | -7 | 2014-08-12 14:16 | Civil - Civil Engineering General | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | There have been a number of 28 day cube failures for the concreting works at Woolwich Station Box. These are summarised in the attached table.
| 01CV - Civils | Cxxx-NCR-000897 | NCR | WSB - Damage to smoke duct during transport/delivery |  | Contr | HTM |  |  | 2014-08-26 | 2014-08-26 17:02 | 0 | 2014-08-12 17:02 | Civil - Civil Engineering General | 1000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Supervision - Insufficient supervision | Completed |  | During delivery/transportation, one of the smoke ducts delivered on 11/08/14 was damaged along one edge (heavily chipped)
| 01CV - Civils | Cxxx-NCR-000898 | NCR | NWP - Cracked Staircase Corbel - Phase 3 |  | Contr | HTM | NOW - North Woolwich Portal (East) |  | 2014-08-26 | 2014-08-26 17:10 | 0 | 2014-08-12 17:07 | Civil - Civil Engineering General | 1000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Supervision - Insufficient supervision | Completed |  | During removal of the temporary propping in Phase 3 the prop struck the RC corbel for the intervention staircase and a hairline crack was formed.
| 01CV - Civils | Cxxx-NCR-000899 | NCR | WSB - Concrete Finish to Central Box Platform Walls WB W6 |  | Contr | HTM |  |  | 2014-08-26 | 2014-08-26 17:01 | 0 | 2014-08-12 17:11 | Civil - Civil Engineering General | 1000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The south face of the central box wall WB W6 shows signs of grout loss and large blow holes throughout the surface finish of the wall. It is a similar finish to the NCR - Cxxx-NCR-000891.
| 01CV - Civils | Cxxx-NCR-000900 | NCR | WSB - Damaged wall starter bars at 200mm secondary wall in Eastern Box |  | Contr | HTM |  |  | 2014-08-27 | 2014-08-27 15:34 | 0 | 2014-08-13 14:54 | Civil - Civil Engineering General | 1000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Improper preservation of material after installation | Completed |  | A number of reinforcement starter bars for the 200mm in the east box have been damaged beyond repair - snapped at slab level with inadequate length exposed to utilise couplers. Please see attached photo and location sketch.
| 01CV - Civils | Cxxx-NCR-000902 | NCR | WSB - East Box - Missing Service Duct Boxout |  | Contr | HTM |  |  | 2014-08-28 | 2014-08-27 15:35 | -1 | 2014-08-14 15:50 | Civil - Civil Engineering General | 1000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Requirements on drawing required 6 no. box outs installed in wall EB-BP-W50 in the East Box. 5 no. box outs had been installed instead.
| 01CV - Civils | Cxxx-NCR-000903 | NCR | WSB - ITP Records Incomplete |  | Contr | HTM |  |  | 2014-08-28 | 2014-08-27 16:29 | -1 | 2014-08-14 16:39 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Following a __ surveillance, the ITP verification records for Eastern Box tunnel collar and Eastern Box high RC walls were incomplete. In some instances these pours were completed in February and March 2014 - but most in June-July 2014. Records have not been acquired from __ for concrete testing both on and off site. Post pour inspections had not been carried out in a timely manner. Refer to Cxxx-HTM-O4-RGN-CR147-50043 for details.
| 01CV - Civils | Cxxx-NCR-000904 | NCR | Tunnel Drive H - First Stage Concrete - Pumstead to Woolwich Box Westbound - Levels exeeding Tolerance in Trial sample to be included in permanent works |  | Contr | HTM |  |  | 2014-09-12 | 2014-09-05 16:30 | -7 | 2014-08-15 15:55 | Tunnelling - Linings - In-situ Concrete | 2000 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | First Stage concrete permanent works Trial Rings 780 - 816 Westbound Tunnel PLU - WSB As built survey of levels (attached) shows areas of first stage concrete exceeding level tolerance +0/-10
| 01CV - Civils | Cxxx-NCR-000905 | NCR | Tunnel Drive H - First Stage Concrete - Bay 1 Westbound Tunnel a Plumstead - last 900mm of bay insufficient concrete to finish to design level. |  | Contr | HTM |  |  | 2014-09-16 | 2014-08-27 17:18 | -20 | 2014-08-19 11:29 | Tunnelling - Linings - In-situ Concrete | 1000 |  | Planning | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Pour date 18/08/14 - Bay 1 Westbound Tunnel a Plumstead - last 900mm of bay insufficient concrete to finish to design level. Approximate concrete shortage 0.3 m3
| 01CV - Civils | Cxxx-NCR-000906 | NCR | Tunnel Drive H - Tunnel Collar Eastbound - Woolwich Station Box East - Insitu cast Concrete Honeycombed. |  | Contr | HTM |  |  | 2014-11-21 | 2014-11-21 11:18 | 0 | 2014-08-27 10:36 | Tunnelling - Linings - In-situ Concrete | 4000 |  | Workmanship | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Witnessed on August Senior Management Quality Tour Insitu Concrete Collar exiting into WSB from Eastbound Tunnel. - Insitu concrete finishes - Honeycombed and resulting leakage of groundwater above and below 1st stage concrete level. Repair has been made to area covering defect prior to agreement with Crossrail Inspector on extent of damage. Photo of original condition prior to repair attached.
| 01CV - Civils | Cxxx-NCR-000907 | NCR | PP - Miss out the Kiwkastrip for the mid height stair landing in Wall 5. |  | Contr | HTM |  |  | 2014-09-16 | 2014-09-19 16:18 | 3 | 2014-09-02 17:23 | Civil - Civil Engineering General | 2500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During Concrete wall pour on 27/08/2014 Miss out the Kiwkastrip for the mid height stair landing wall 5
| 01CV - Civils | Cxxx-NCR-000908 | NCR | NCR- __ - Pumping Station - RC Retaining wall 5 and RC base for retaining wall 3 pour without UKAS sampling of concrete |  | Contr | HTM |  |  | 2014-10-02 | 2014-09-19 13:46 | -13 | 2014-09-04 11:24 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Repair | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | It is notice the above concrete pour on 03/09/2014 with out UKAS accredited sampling
| 01CV - Civils | Cxxx-NCR-000909 | NCR | PP- Kwikastrip not Installedin correctly in North & South capping beam soffit for lining wall |  | Contr | HTM |  |  | 2014-10-02 | 2014-09-18 09:19 | -14 | 2014-09-04 13:31 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During the pull out of inner reinforcement from Kwikastrip installed in capping beam soffit are not pull out straight (see attached picture)
| 01CV - Civils | Cxxx-NCR-000910 | NCR | WSB - Scaffold screed rails left in mass pour |  | Contr | HTM |  |  | 2014-09-19 | 2014-09-10 17:31 | -9 | 2014-09-05 15:40 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | During the east box mass pour from approx. E1 to Z3 (up to the underside of the cast in channel) the scaffold poles used as screed rails have been cast in to the concrete. __ attempted to remove the tubs but failed, on the south side. The tubes have been trimmed to concrete level.
| 01CV - Civils | Cxxx-NCR-000911 | NCR | WSB - Damaged steel hanger for smoke ducts |  | Contr | HTM |  |  | 2014-09-19 | 2014-09-08 14:08 | -11 | 2014-09-05 15:53 | Civil - Civil Engineering General | 750 |  | Damaged | Reject | 4 (0.5-3k) | Complete | Discipline/Workmanship - Not Defined | Completed |  | One of the steel hangers, delivered to site by __, was damaged. The lower T-section had been bent (see attached photo)
| 01CV - Civils | Cxxx-NCR-000912 | NCR | PP- installation of incorrect diameter Kwikastrip for the mid height stair landing in Wall 2 |  | Contr | HTM |  |  | 2014-10-03 | 2014-09-19 09:49 | -14 | 2014-09-05 16:13 | Civil - Civil Engineering General | 1500 |  | Supervision/Management | Repair | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | 12mm diameter Kwikastrip installed instead of 16mm diameter in the mid height stair landing in Wall 2
| 01CV - Civils | Cxxx-NCR-000913 | NCR | PP - water bar outside front face of South lining wall at base slabe 24/25 joint |  | Contr | HTM |  |  | 2014-10-07 | 2014-09-19 09:41 | -18 | 2014-09-09 11:24 | Civil - Civil Engineering General | 1000 |  | Supervision/Management | Repair | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | due to position of secant cut off wall at Marmadon section the Water bar installed at base slab joint 24/25 for lining wall was outside front face of lining wall (see attached photo)
| 01CV - Civils | Cxxx-NCR-000914 | NCR | Tunnel Drive H - Materials Compliance Record without a code {Hanson – Mix Design 32/40 (GGBFS) - F6 Flow class} |  | Contr | HTM |  |  | 2014-09-24 | 2014-09-18 14:24 | -6 | 2014-09-10 17:10 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | Materials Compliance Record - – Mix Design 32/40 (GGBFS) - F6 Flow class {Cxxx-HTM-C-CER-CR146_ST004-50087 Rev.1.0} was submitted to eB on the 2nd of September. The concrete was used on site in Tunnel 1(eastbound) on the 8th of September
| 01CV - Civils | Cxxx-NCR-000915 | NCR | WSB - Cracking to platform slab around column C2 |  | Contr | HTM |  |  | 2014-09-25 | 2014-09-29 12:51 | 4 | 2014-09-11 15:27 | Civil - Civil Engineering General | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The platform slab around column C2 (Central Box, Western End) has a number of hairline cracks across its surface. Initial investigations under the slab have shown that these cracks do not extend through the slab
| 01CV - Civils | Cxxx-NCR-000916 | NCR | WSB - Western Box platform wall concrete finish |  | Contr | HTM |  |  | 2014-09-25 | 2014-09-29 12:55 | 4 | 2014-09-11 16:09 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The concrete finish of the platform walls (below platform slab level) in the Western Box does not meet the requirements of the specification. There are a number of blow holes, slight grout loss at the kicker level and poor finish at the top of the wall in a number of locations. A section of a wall corner has also been 'chipped' away, presumably whilst removing the shutters.
| 01CV - Civils | Cxxx-NCR-000917 | NCR | WSB - Half landing couplers (Grid Z4-Z5) |  | Contr | HTM |  |  | 2014-09-26 | 2014-09-22 15:54 | -4 | 2014-09-12 12:57 | Civil - Civil Engineering General | 1500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Two couplers in the recess section of the half landings at grid line Z4-Z5, to receive threaded bar (bar mark 02), were set higher than they should be; following the line of the other top level couplers. Attached sketch shows the bar locations.
| 01CV - Civils | Cxxx-NCR-000918 | NCR | Plumstead Portal - Lining Wall - N10 - Segregation of Self Compacting Concrete |  | Contr | HTM |  |  | 2014-09-30 | 2014-09-19 16:31 | -11 | 2014-09-16 16:06 | Civil - Civil Engineering General | 2500 |  | Material | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Plumstead Portal - Lining Wall - N10 - Segregation of Self Compacting Concrete Pour date 15/09/14 - Segregation voids & surface finish. Following removal of shutter and inspection it was decided to break out to sound concrete areas of suspect concrete
| 01CV - Civils | Cxxx-NCR-000919 | NCR | TUNNEL DRIVE H - CRACK IN CONCRETE OF EAST BOUND CROSS PASSAGE 19 COLLAR (Tunnel 2) |  | Contr | HTM |  |  | 2015-03-27 | 2015-03-30 13:40 | 3 | 2014-10-28 17:45 | Civil - Tunnelling | 2500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | Cracks noticed at the eastbound collar of cross passage 19 after remedial works of grouting injection was done to cross passage 19.
| 01CV - Civils | Cxxx-NCR-000920 | NCR | WSB - Coupler positions for smoke ducts in Central Box (North section) |  | Contr | HTM |  |  | 2014-10-17 | 2014-10-20 15:41 | 3 | 2014-09-19 12:24 | Civil - Concrete Pavement | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Previous Construction - Other | Completed |  | The steel hanger installation, along the north side of the central box at Woolwich Station Box, has identified a number of coupler positions which are outside of the tolerance supplied to __ for the overall hanger installation. The couplers were installed by a previous contractor for CRL and the tolerances they worked to are unknown. __ have attempted to use some of the tolerance on the bolt holes to correct this problem but a number of the steel hangers are still out of tolerance overall. The hangers sit away from platform edge towards the tracks, and may cause few issues for next contract when installing platform doors. Attached is the __ survey data
| 01CV - Civils | Cxxx-NCR-000921 | NCR | PP - Damaged D Wall Couplers for pannel N7,N8 N9 & N10 |  | Contr | HTM |  |  | 2014-10-03 | 2014-10-03 14:41 | 0 | 2014-09-19 10:45 | Civil - Civil Engineering General | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Following the excavation of the portal in Phases 4 while installation of reinforcement cage a number of couplers have been identified as damaged.
| 01CV - Civils | Cxxx-NCR-000922 | NCR | Tunnel Drive H - Cross Passage 18 - Insitu Concrete for Upstands in Tunnel 1 - Concrete still being discharge 2hrs 15 minutes after batching |  | Contr | HTM |  |  | 2014-10-06 | 2014-09-30 12:00 | -6 | 2014-09-22 16:43 | Civil - Tunnelling | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | C32/40 F4 concrete mix was batched 08:25am for up stands in the Tunnel 1. Concrete was batched 08:25am. Flow test was done at 09:40am with a value of 520mm before batching. At 10:40am the concrete wagon was still on site discharging the same concrete for up stands.
| 01CV - Civils | Cxxx-NCR-000923 | NCR | PP- Between Roof slab R2 & R3 construction joint top and bottom bars are not staggered as per FCD 00875 |  | Contr | HTM |  |  | 2014-10-21 | 2014-10-08 15:59 | -13 | 2014-09-23 13:08 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The joints between roofslabs R2 and R3 in Plumstead Portal, on the FCD 00785 it states that the bars are staggered and this was not followed on-site. however top and bottom bars of RS3 terminate at the same length and all the lapping bars of the couplers have the same minimum lapping length. top 1350, bottom 1100 laps. ( please see attached photo)
| 01CV - Civils | Cxxx-NCR-000924 | NCR | WSB - Platfrom Wall 8 South West Box |  | Contr | HTM |  |  | 2014-10-07 | 2014-10-06 08:53 | -1 | 2014-09-23 16:24 | Civil - Civil Engineering General | 2000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | It has been discovered following as built surveys that WB-BP-W8 Wall in the western Box south side is partially out of alignment. Please see attached sketch which shows the As built (pink line) against the design alignment (black lines). The junction in the Wall has been built incorrectly by 200mm.
| 01CV - Civils | Cxxx-NCR-000925 | NCR | Plumstead portal - phase 2 south lining wall 24 concrete surface finishing and cold joint |  | Contr | HTM |  |  | 2014-10-23 | 2014-10-22 09:31 | -1 | 2014-09-25 17:44 | Civil - Civil Engineering General | 1000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | The concrete surface finish does not meet the requirements of the specification. There are Cold joint and minor surface blow holes
| 01CV - Civils | Cxxx-NCR-000926 | NCR | WSB - Straightness of C1-Y10 Platform Slab |  | Contr | HTM |  |  | 2014-10-10 | 2014-10-01 11:24 | -9 | 2014-09-26 08:22 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During the pouring of platform slab C1-Y10 there was some formwork displacement. An as built survey was carried out to assess the extent of the movement. Please refer to the attached survey data. The specification (NSCS Standard Specification 10.9.2 Edge Straightness) allows a permitted deviation of 8mm/m but no greater than 20mm. In one location the survey shows that this is exceeded by 1mm (deviation of 21mm)
| 01CV - Civils | Cxxx-NCR-000927 | NCR | WSB - WB Lift Shaft Kicker |  | Contr | HTM |  |  | 2014-10-14 | 2014-10-13 14:37 | -1 | 2014-09-30 10:54 | Civil - Civil Engineering General | 1000 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The concrete at the WB lift shaft kicker was not compacted sufficiently and does not meet the requirements of the specification. Initially it was thought that the shutter had moved but survey checks show that the as-built position is within 1mm of design (see attached survey data).
| 01CV - Civils | Cxxx-NCR-000928 | NCR | NWP - Missing Couplers from RS4 |  | Contr | HTM | NOW - North Woolwich Portal (East) |  | 2014-10-14 | 2014-10-13 14:49 | -1 | 2014-09-30 12:08 | Civil - Civil Engineering General | 1000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | Following on from Cxxx-NCR-000801, the roof slab installation has been carried out. Attached is a sketch which details the positions of the couplers that were omitted, due to being damaged beyond repair in the final installation (marked in red)
| 01CV - Civils | Cxxx-NCR-000929 | NCR | NWP - Missing coupler for flood wall across Roof Slab RS09 |  | Contr | HTM | NOW - North Woolwich Portal (East) |  | 2014-10-16 | 2014-10-07 13:11 | -9 | 2014-10-02 10:02 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | A coupler, cast into the roof slab RS09, can not be located. The 20mm coupler was to be used to lap with the 16mm vertical bar of the flood wall at this location. Please see attached photograph and sketch.
| 01CV - Civils | Cxxx-NCR-000930 | NCR | WSB - East Box W71, W72, W73, W74, W75 Tie in Reinforcement to Roof Slab |  | Contr | HTM |  |  | 2014-10-21 | 2014-10-15 10:20 | -6 | 2014-10-07 08:07 | Civil - Civil Engineering General | 1500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The 'U' bars at the top of the high level wall in the Eastern Box have been installed at the incorrect level. These bars tied the wall into the roof slab but, at their current level, are protruding into the top cover zone of the slab. The wall affected is the high level north wall which comprises W71, W72, W73, W74 and W75.
| 01CV - Civils | Cxxx-NCR-000931 | NCR | No concrete repair procedure produced for FSC works as requested during a CRL planned surveillance |  | Crossrail | XRL |  |  | 2014-11-18 | 2014-11-21 09:39 | 3 | 2014-10-07 09:05 | Tunnelling - Tunnelling General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | During a planned Crossrail surveillance on 16th September 2014 a review of the ITP Cxxx-HTM-C-ITP-CR146_ST005-50014 was carried out. Under inspection number 18 it states that after removal of formwork the concrete should be checked for honeycombing, unwanted marks or imperfections and finish in accordance with series 1700 clause 1708. SHW series 1700 ‘structural concrete’ clause 1708 details surface finish classes, however provides no information regarding concrete repairs and making good. Materials and Workmanship Specification ‘In-Situ Concrete’ KF10.3212 states a) “Concrete, which is honeycombed or fails to attain the specified characteristic strength, and concrete work which in any way fails to comply with the Specification, will be considered to be defective” and “the method statements shall include procedures for considering individual defects …”. A concrete repair procedure for FSC works that considers defects, appropriate repair methodologies and acceptable materials was requested for post surveillance review, however it was stated that to date nothing had been produced. Works Information Vol 2B part 20.4 states “The Contract Quality Plan shall be supported by comprehensive QSP’s … The primary activities addressed by QSP’s and to be implemented by the Contractor are to include;… preparation of QSP’s for design (including temporary works), procurement, manufacture, construction, installation and testing along with all management system processes”. This NCR was raised to ensure an appropriate repair procedure is produced appropriate to FSC works
| 01CV - Civils | Cxxx-NCR-000932 | NCR | Inadequate storage management and curing of concrete cube specimens before laboratory collection as witnessed during a planned CRL surveillance |  | Crossrail | XRL |  |  | 2014-10-24 | 2014-10-24 13:12 | 0 | 2014-10-07 09:07 | Tunnelling - Tunnelling General | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | During a planned Crossrail surveillance on 16th September 2014 the storage facility where concrete cubes are stored over night was reviewed. A thermometer was witnessed as being in place, however no records were being maintained to demonstrate the facilities compliance to the requirements set out in BS EN 12390-2:2009 Testing Hardened Concrete Part 2: Making and Curing Specimens for Strength Tests clause 5; “Leave the test specimens in the mould for at least 16 hours, but not longer than 3 days, protected against shock, vibration and dehydration at a temperature of (20±5) oC”. ISO 17025:2005 General Requirements for the Competence of Testing and Calibration Laboratories clause 5.3.2 states “The laboratory shall monitor, control and record environmental conditions as required by the relevant specifications, methods and procedures or where they influence the quality of the results”. As no records were being maintained the facilities on-going compliance to date could not be verified, i.e. daily records. Additionally, whilst reviewing the storage facility it was noted that __ cubes not associated to the FSC works were being stored in the container uncovered, with no protection from dehydration; this is against the requirements set out in BS EN 12390-2:2009 clause 5 detailed above.
| 01CV - Civils | Cxxx-NCR-000933 | NCR | Tunnel Drive H - Tunnel 1: Ring 483 - Nadir Catch pit - Ring Roll Alignment out of Tolerance |  | Contr | HTM |  |  | 2014-11-10 | 2014-11-10 15:21 | 0 | 2014-10-09 13:02 | Tunnelling - Linings - Precast | 1500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The Nadir Catch Pit (NCP) segment opening have been slightly rolled by the bellow factors: Tunnel 1: Ring 483 - ring roll approx. 90mm clockwise seen in advance direction. The new position may not be adequate for other permanent work interfaces. This may affect the Cxxx original reinforcement design Cxxx-OVE-C4-DDD-CR001_Z-24521 (C01 for the Catchpit . Roll Relative to Ring adjacent are within the specified 3mm due to the tight tolerances fixed by the Dowel system
| 01CV - Civils | Cxxx-NCR-000934 | NCR | PP - North lining wall 24 Leak through wall honeycomb and wet shrinkage crack |  | Contr | HTM |  |  | 2014-11-06 | 2014-10-22 12:21 | -15 | 2014-10-09 13:59 | Civil - Civil Engineering General | 2500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The concrete surface finish does not meet the requirements of the specification. on post inspection of North lining wall 24 it has been notice leakage through lining wall honeycomb and wet shrinkage crack as highlighted in attached photo
| 01CV - Civils | Cxxx-NCR-000935 | NCR | PP - North lining wall 22 void/grout loss on top of wall |  | Contr | HTM |  |  | 2014-11-20 | 2014-10-24 11:47 | -27 | 2014-10-09 14:51 | Civil - Civil Engineering General | 2500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The concrete surface finish does not meet the requirements of the specification. There are two voids/grout loss between top of lining wall and under side of capping beam. See attached photo.
| 01CV - Civils | Cxxx-NCR-000936 | NCR | 1st Stage Concrete in Tunnel 2 not conforming to Specification |  | Contr | HTM |  |  | 2014-10-23 | 2014-10-24 12:15 | 1 | 2014-10-09 16:23 | Civil - Civil Engineering General | 2500 |  | Material | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | 1st stage concrete for Tunnel 2(East), first pour was poured with an approved F6 mix. The mix was too wet and kept on flowing down the Tunnel. This led to an uneven slab in level on the last 15 rings of slab.
| 01CV - Civils | Cxxx-NCR-000937 | NCR | Tunnel Drive H - Tunnel 2: EB Ring 483 - Nadir Catch pit - Ring Roll Alignment out of Tolerance |  | Contr | HTM |  |  | 2014-11-10 | 2014-11-10 15:45 | 0 | 2014-10-09 17:05 | Tunnelling - Linings - Precast | 1500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | EB drive: Plumstead - Woolwich station Box Tunnel 2: Ring 483 - ring roll approx. 115mm anti-clockwise seen in advance direction
| 01CV - Civils | Cxxx-NCR-000938 | NCR | Tunnel Drive H - Tunnel 3: Ring 1252 - Nadir Catch pit - Ring Roll Alignment out of Tolerance |  | Contr | HTM |  |  | 2014-11-10 | 2014-11-10 15:53 | 0 | 2014-10-09 17:12 | Tunnelling - Linings - Precast | 1500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | As a result of the tunnel row, the Nadir Catch Pit (NCP) segment opening have been slightly rolled by the bellow factors: WB drive: Woolwich Station Box to North Woolwich Tunnel 3: Ring 1252 - ring roll approx. 160mm anti-clockwise seen in advance direction The new position may not be adequate for other permanent work interfaces. This may affect the Cxxx original reinforcement design Cxxx-OVE-C4-DDD-CR001_Z-24521 (C01 for the Catchpit. Roll Relative to Ring adjacent are within the specified 3mm due to the tight tolerances fixed by the Dowel system
| 01CV - Civils | Cxxx-NCR-000939 | NCR | Tunnel Drive H - Tunnel 4: Ring 1246 - Nadir Catch pit - Ring Roll Alignment out of Tolerance |  | Contr | HTM |  |  | 2014-11-10 | 2014-11-12 13:01 | 2 | 2014-10-09 17:16 | Tunnelling - Linings - Precast | 1500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | As a result of the tunnel row, the Nadir Catch Pit (NCP) segment opening have been slightly rolled by the bellow factors: Tunnel 4: Ring 1246 - ring roll approx. 75mm clockwise seen in advance direction The new position may not be adequate for other permanent work interfaces. This may affect the Cxxx original reinforcement design Cxxx-OVE-C4-DDD-CR001_Z-24521 (C01 for the Catchpit. Roll Relative to Ring adjacent are within the specified 3mm due to the tight tolerances fixed by the Dowel system
| 01CV - Civils | Cxxx-NCR-000940 | NCR | NWP - Changes to bar sizes in reinforcement for Flood Wall 9 (return wall) |  | Contr | HTM | NOW - North Woolwich Portal (East) |  | 2014-10-24 | 2014-10-15 15:28 | -9 | 2014-10-10 07:05 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | __ have installed reinforcement bars of a different diameter than detailed on the drawings on flood wall 9 for the vertical bars. The original drawing detailed B16 and B20 bars. The sub agent had agreed with CRL to change these to B25 bars but this does not seem to have been recorded on PTR. Finally, due to a shortage of B25 bars on site a number were replaced with B20.
| 01CV - Civils | Cxxx-NCR-000941 | NCR | 1ST STAGE CONCRETE DISCHARGE 4 HOURS AFTER B__HING ON A F6 C32/40 MIX |  | Contr | HTM |  |  | 2014-10-24 | 2014-10-15 12:56 | -9 | 2014-10-10 16:20 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The last load of concrete (Delivery Ticket 217479 dated 06/10/14) was batched 1643hours. The concrete load finished at 2018hours. The workability of the concrete is 3 hours from batch time.
| 01CV - Civils | Cxxx-NCR-000942 | NCR | PP - Damaged D Wall Couplers Not installed in roof slab construction for slab RS4, 5 & 6 |  | Contr | HTM |  |  | 2014-11-07 | 2014-10-20 14:25 | -18 | 2014-10-10 15:37 | Civil - Civil Engineering General | 1500 |  | Damaged | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Following the excavation of the portal in Phases 4 and while installation of D wall reinforcement cage a number of couplers have been identified as damaged or clash with temporary prop gallows bracket. The damaged couplers wear not connected to roof slab construction is as follows. Roof Slab 4: D wall panel N11- 2 numbers, S10B - 1 number, S11 - 1 number Roof Slab 5: D wall Panel N12b - 1number, S13 - 1 Number Roof Slab 6: D wall Panel N16 - 1Number, N19 - 2 Number, S16 - 1Number, S17 - 1Number, S19 - 3number
| 01CV - Civils | Cxxx-NCR-000943 | NCR | __ CONCRETE TECHNICAL REPRESENTATIVE NOT ON SITE WHEN 1st WAGON OF CONCRETE PLACED. |  | Contr | HTM |  |  | 2014-10-25 | 2014-10-24 13:14 | -1 | 2014-10-11 10:36 | Civil - Tunnelling | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | The 1st wagon of Concrete to Tunnel 2 slab infill works was placed by 0935hours. There was no __ representative present on site. No flow test and cubes on the F5 mix was made by __. __'s Formwork did make cubes out of the wagon.
| 01CV - Civils | Cxxx-NCR-000944 | NCR | WSB - East Box Basement Slab Z4-E6 Changes to Reinforcement |  | Contr | HTM |  |  | 2014-10-30 | 2014-10-30 14:17 | 0 | 2014-10-16 11:55 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Personnel Error - Violation of requirement or procedure | Completed |  | A number of bars detailed on the drawings for WSB - East Box Basement Slab Z4-E6 have not been installed. This is due to clashes with the beams at basement level - Beam EB11, EB12, EB13 and EB14. Whilst the straight bars of the top and bottom mat continue into the beam itself the U bars have not been installed in this heavily congested area. This has been checked with the __ designer but due to the late stage of the reporting has not been recorded in an FCD to the client. Cxxx-HTM-C-DWG-CR147-52060 (at North Beam) 6 no. BM05 not installed (NW corner of opening) 6 no. BM04 not installed (NW corner of opening) 6 no. BM05 not installed (SE corner of opening) 5 no. BM01 not installed (SE corner of opening) Cxxx-HTM-C-DWG-CR147-52061 (at South Beam) 6 no. BM05 not installed (SW corner of opening) 6 no. BM04 not installed (SW corner of opening) 6 no. BM05 not installed (NE corner of opening) 5 no. BM01 not installed (NE corner of opening)
| 01CV - Civils | Cxxx-NCR-000945 | NCR | PP - Missing D wall Couplers in foor slab RS7 |  | Contr | HTM |  |  | 2014-11-12 | 2014-10-20 15:24 | -23 | 2014-10-15 14:50 | Civil - Civil Engineering General | 1000 |  | Damaged | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Following on from Cxxx-NCR-000942, the roof slab 7 installation has been carried out and found missing one coupler in D wall panel S21 and one in D wall panel N21. The Attached sketch which details the positions of the couplers that were behind the gallows bracket or being damaged and beyond repair in the final installation. (see attached photo and detail)
| 01CV - Civils | Cxxx-NCR-000946 | NCR | PP - Phase 2 North & south flood wall 21&22 reinforcement installed incorrectly |  | Contr | HTM |  |  | 2014-10-29 | 2014-10-28 15:08 | -1 | 2014-10-15 15:42 | Civil - Civil Engineering General | 1500 |  | Supervision/Management | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During the construction of capping beam in Plumstead portal phase 2 the reinforcement being set out incorrectly for North & South Flood wall 21&22
| 01CV - Civils | Cxxx-NCR-000947 | NCR | NWP - Spine Wall 2 kicker - Failure of concreting procedure - none compliant concrete |  | Contr | HTM | NOW - North Woolwich Portal (East) |  | 2014-11-20 | 2014-11-14 16:30 | -6 | 2014-10-16 15:19 | Civil - Civil Engineering General | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | Approximately 1.5m3 of concrete, for the spine wall 2 kicker (9m length) was placed before the slump test was carried out on the load. When the slump test result was obtained it was recorded at 110mm. This is outside the acceptable range of an S4 concrete mix.
| 01CV - Civils | Cxxx-NCR-000948 | NCR | PP - Changes to bar sizes in reinforcement for Roof slab 6 (RS6) |  | Contr | HTM |  |  | 2014-11-14 | 2014-10-20 15:38 | -25 | 2014-10-17 10:10 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Error by manufacturer in shipping or marking | Completed |  | __ have installed reinforcement bars of a different diameter than detailed on the drawing no.Cxxx-CSY-S-DDL-CR148_PT005-02246 on roof slab 6 bottom B1 bar which was Poured on 09/10/14. The original drawing detailed bottom B1 as B25mm bars.The supplier has send B32 bar bundle instead of B25 on site. due to short time to change bar sub agent had agreed with CRL to change these to B32 bars but this does not seem to have been recorded on PTR but recorded in observation report.
| 01CV - Civils | Cxxx-NCR-000949 | NCR | PP - Missing D wall Couplers in Roof slab RS8 |  | Contr | HTM |  |  | 2014-11-14 | 2014-10-28 16:40 | -17 | 2014-10-17 12:56 | Civil - Civil Engineering General | 1000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The roof slab construction is on going at Plumstead portal and while exposing D wall couplers for the roof slab 8 and found missing one coupler in D wall panel S24 and one in D wall panel N24. The Attached sketch which details the positions of the couplers that were being damaged and beyond repair in the final installation. (see attached photo and detail)
| 01CV - Civils | Cxxx-NCR-000950 | NCR | Plumstead Portal - North lining wall NLW21 - Leak through wall honeycomb and wet shrinkage crack |  | Contr | HTM |  |  | 2014-11-17 | 2014-10-27 15:21 | -21 | 2014-10-17 14:16 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The concrete surface finish does not meet the requirements of the specification. on post inspection of North lining wall NLW21 .Leakage through lining wall honeycomb and wet shrinkage crack as highlighted in attached photo.
| 01CV - Civils | Cxxx-NCR-000951 | NCR | Plumstead Portal - Spine Walll - __ Concrete Mix 34R - C32/40 with Poly Fibres - Cube Failures 16th July & 1st Aug |  | Contr | HTM |  |  | 2014-11-17 | 2014-10-31 12:23 | -17 | 2014-10-17 14:53 | Civil - Civil Engineering General | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | Measured from a start location from Chainage 56m at the interface of Spine Wall 1 with the Twin Wall. NCR relates to Pour 2 on16/07/14 (Spine wall No.2 at ch. 70.4m - 84.8m approximate position adjacent to base slab B6.) and Pour no. 8 on 1/08/14 (Spine wall no. 8 Ch. 156.8 - 171.2 approx. position adjacent to Base slab B12) __ Mix 34R C32/40 Retarded with Poly Fibre 28 cubes failed Individual Mean Test Result against Criterion 2 & 1 BS EN 8500 & EN 206 Annex B additional requirements for Compressive Strength Identity Testing. B.3.1 Concrete under production control certification Identity of concrete is assessed for each individual strength test result and the average of n non-overlapping discrete results as identified in Table B1. Concrete is deemed to come from a conforming population if both the criteria in Table B.1 are satisfied for n results derived from strength tests on samples taken from the defined volume of concrete.
| 01CV - Civils | Cxxx-NCR-000952 | NCR | PP - RC Central Spine Wall 15 Pour Without UKAS Sampling of Concrete |  | Contr | HTM |  |  | 2014-11-17 | 2014-10-22 13:53 | -26 | 2014-10-20 18:23 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | It is notice the above spine wall concrete pour on 26/08/2014 without UKAS accredited sampling
| 01CV - Civils | Cxxx-NCR-000953 | NCR | Plumstead Portal - North lining wall NLW16 - honeycomb and surface blow holes |  | Contr | HTM |  |  | 2014-11-18 | 2014-10-28 15:16 | -21 | 2014-10-21 07:45 | Civil - Civil Engineering General | 1000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | On post inspection of North lining wall 16The concrete surface finish does not meet the requirements of the specification. There are minor defects includign honeycomb and surface blow holes
| 01CV - Civils | Cxxx-NCR-000954 | NCR | Plumstead Portal-Concrete finish to South Flood Wall 24 (SFW24) South face |  | Contr | HTM |  |  | 2014-11-18 | 2014-10-28 15:13 | -21 | 2014-10-21 08:10 | Civil - Civil Engineering General | 1500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | On the post concrete inspection it is found concrete surface finish does not meet the requirements of the specification. there is one Rough patch on south face of flood wall and minor voids by poor compaction
| 01CV - Civils | Cxxx-NCR-000955 | NCR | PP - Missing D wall Couplers in Roof slab RS9 |  | Contr | HTM |  |  | 2014-11-18 | 2014-10-28 15:08 | -21 | 2014-10-21 14:44 | Civil - Civil Engineering General | 1000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The roof slab construction is on going at Plumstead portal and while exposing D wall couplers for the roof slab 9 and found missing one coupler in D wall panel S29. The Attached sketch which details the positions of the coupler that were being damaged and beyond repair in the final installation. (see attached photo and detail)
| 01CV - Civils | Cxxx-NCR-000956 | NCR | NWP - Damaged couplers in reception chamber sump |  | Contr | HTM | NOW - North Woolwich Portal (East) |  | 2014-11-05 | 2014-10-24 11:53 | -12 | 2014-10-22 10:04 | Civil - Civil Engineering General | 2500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The majority of the couplers for the columns in reception chamber sump are damaged and unable to be utilised for the connecting bars. See attached photo.
| 01CV - Civils | Cxxx-NCR-000957 | NCR | WSB - Concrete pour for Eastern Box basement slab Z4-E6 |  | Contr | HTM |  |  | 2014-11-05 | 2014-10-24 12:14 | -12 | 2014-10-22 10:16 | Civil - Civil Engineering General | 1500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Following a __ observation, areas of possible cold jointing have been observed in the concrete pour for the Eastern Box basement slab Z4-E6. Investigation of the delivery documentation has identified a single delivery that exceeded the prescribed period between placement of loads of fresh concrete. The __ procedure, Cxxx-HTM-Z-GPD-CR148-50028 Production, Delivery & Control of Ready Mixed Concrete Operations, states in section 7.4 Placing of Concrete: "Fresh concrete shall not be placed against existing fresh in-situ concrete which has been in position for more than sixty minutes. When in-situ concrete has been in place for four hours or if the concrete has reached its initial set, no further concrete shall be placed against it for a further twenty four hours and a construction joint shall be formed" Load 34538400 arrived on site at 12:55. The next, and final, load 34538406 arrived on site at 14:50.
| 01CV - Civils | Cxxx-NCR-000958 | NCR | WSB - Concrete pour for Eastern Box basement slab Z2-Z4 |  | Contr | HTM |  |  | 2014-11-05 | 2014-10-24 11:57 | -12 | 2014-10-22 10:36 | Civil - Civil Engineering General | 1000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During the steel inspection for the basement slab Z2-Z4 a number of locations were identified where the cover was greater then the nominal 50mm specified. The worst case was 90mm. BSEN 13670 allows for a maximum cover of 66mm at this location.
| 01CV - Civils | Cxxx-NCR-000959 | NCR | Tunnel Drive H - Cross passage 17 Invert Slab Pour 5 on 20/10/14 - Delay to Supply in Concrete |  | Contr | HTM |  |  | 2014-11-24 | 2014-10-31 12:27 | -24 | 2014-10-23 15:15 | Tunnelling - Linings - In-situ Concrete | 2500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | Tunnel Drive H - Cross passage 17 Invert Slab - Monday the 20th October 2014 – Pour Ref 5 Pour started at Westbound end of Cross passage Area of collar to Shaft completed prior to delay. Some concrete placed to the Eastbound side of shaft. Load batched at 11:50 and wagon left site at 14:55 due to a combination of __ sending the wagon too early and also issues with the locomotives brakes. Load completely discharged into pour approx. 15:30 Delay of 3 hours before the next load of concrete entered the tunnel Pour Restarted 18:10hrs Ref. KF10.3211 Sequence of Pours marked up with Delays Cxxx-HTM-C-DWG-CR146-ST004_77201 20/10/14 Pour 5 Pour Mix 25 Volume 36m3 delivery to West Box - XP17 Invert Slab Pour rate 1 load per hour – 36m3 Delivery Ticket 21168178, 21168188, 21168190, 21168196, 21168210, 21168215, Cumulative 6.0m3 Batched 8:55 on site 09:35 off site 10:35 Cumulative 12.0m3 Batched 10:00 on site 10:25 off site 12:15 Cumulative 18.0m3 Batched 11:30 on site 12:00 off site 13:29 Cumulative 24.0m3 Batched 11:52 on site 12:10 off site 14:55 (waggon arrived 30 minutes early) Root cause batcher was not informed in delay for 1st 2 loads __ Schedule would have been supply up to 15:00hrs at a rate of 1 load + make up load as per call off. Cumulative 30.0m3 Batched 13:35 on site 15:20 off site 15:25 (returned load rejected 1hr 20min Time standing on site waiting for previous waggon to discharge. Additional load added to pour call off) immediate Cause - concrete available could not be placed in time. Cumulative 36.0m3 Batched 16:44 on site 17:25 off site 17:55 (non-conformance KF10.3203 delay in batching an placing 3hrs 10 mins) Supplier __ unable to provide waggons Cumulative 42.0m3 Batched 17:33 on site 18:15 off site 19:05 Cumulative 49.6m3 Batched 17:33 on site 18:15 off site 19:05 (load adjustment to complete 7.6m3 Total poured 49.6 – 6m3 rejected 43.6m3) During delay in supply Concrete was worked to avoid plastic set and maintain workability. The marked up drawing shows the approximate location of any potential cold joint.
| 01CV - Civils | Cxxx-NCR-000960 | NCR | Tunnel Drive H - Cross Passage - Ring Beam Reinforcement - Drainage Sumps - Contractors declaration / contractor rebar sign off certificate was not submitted prior to completing works |  | Contr | HTM |  |  | 2014-12-01 | 2014-11-27 13:55 | -4 | 2014-10-24 12:11 | Tunnelling - Linings - In-situ Concrete | 500 |  | System Defect | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | Process for sign of by Contractor - Contractors Declaration - Contractor Rebar Sign Off Certificate CRL1-XRL-O-ZTM-CR001-50002 was not completed prior to completion of RC work on Cross passages 17 & 18. Cross-passage 17, Plan and Profile, Sheet 1 of 3, Cxxx - Cxxx-OVE-C4-DDD-CR001_Z-23608 Contractors Drawings of Reinforcement detail • Cxxx –HTM-C-DWG-CR146_ST004-77431 rev 01 not submitted Drawing - Cross Passage 17 - RC Detail for Drainage Sump - Reinforcement of Ring Beam Sheet 1 of X • Cxxx –HTM-C-DWG-CR146_ST004-77432 rev 01 not submitted- Cross Passage 17 - RC Detail for Drainage Sump - Reinforcement of Ring Beam Sheet 2 of X Cross-passage 18, Plan and Profile, Sheet 1 of 3, Cxxx - Cxxx-OVE-C4-DDD-CR001_Z-23650 Contractors Drawings of Reinforcement detail • Cxxx –HTM-C-DWG-CR146_ST004-77424 Rev C01 Drawing - Cross Passage 18 - RC Detail for Drainage Sump - Reinforcement of Ring Beam Sheet 1 of 3 • Cxxx –HTM-C-DWG-CR146_ST004-77425 Rev 01 Drawing - Cross Passage 18 - RC Detail for Drainage Sump - Reinforcement of Ring Beam Sheet 1 of 3 • Cxxx –HTM-C-DWG-CR146_ST004-77426 Rev C01 Drawing - Cross Passage 18 - RC Detail for Drainage Sump - Reinforcement of Ring Beam Sheet 3 of 3
| 01CV - Civils | Cxxx-NCR-000961 | NCR | WSB - Kwikastrip incorrectly placed |  | Contr | HTM |  |  | 2014-11-11 | 2014-11-03 15:11 | -8 | 2014-10-28 08:25 | Civil - Civil Engineering General | 1500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Kwikstrip had been installed incorrectly on the side of the basement slab facing towards the stairwell as opposed to being placed on the top face of the slab.
| 01CV - Civils | Cxxx-NCR-000962 | NCR | Plumstead Portal - RC South Lining Wall 17 Concrete Cover |  | Contr | HTM |  |  | 2014-11-11 | 2014-10-28 16:43 | -14 | 2014-10-28 14:28 | Civil - Civil Engineering General | 1000 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | South lining wall 17 There was approx. 2.5m in length observed excess cover of 100 mm (see attached photographs for detail). The starter bar set out for lining wall at the time of construction base slab was as per correct alignment. The as built of capping beam above in the same location is encroaching 25mm of the 40mm original alignment set out to the minimum distance to rail track and kicker set out to the as constructed of capping beam in the area therefore the excess cover at the kicker level.
| 01CV - Civils | Cxxx-NCR-000963 | NCR | WSB - Concrete cover on basement slab - Eastern Box (E1-Z2) |  | Contr | HTM |  |  | 2014-11-12 | 2014-11-03 15:14 | -9 | 2014-10-29 13:01 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During final inspection with Crossrail, a number of locations were identified on the basement slab E1-Z2 where top cover exceeded the required nominal cover of 50mm. Worst case was 70mm. The maximum cover allowed in this case is 66mm; in accordance to NSCS for building construction (complying with BS EN 13670:2009)
| 01CV - Civils | Cxxx-NCR-000964 | NCR | PP - Damaged D wall Coupler in Roof slab 12 (RS12) |  | Contr | HTM |  |  | 2014-11-12 | 2014-10-31 17:16 | -12 | 2014-10-29 14:09 | Civil - Civil Engineering General | 1000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The roof slab construction is on going at Plumstead portal and while exposing D wall couplers for the roof slab 12 and found Damaged one coupler in D wall panel N40. The Attached sketch which details the positions of the coupler that were being damaged and beyond repair in the final installation. (see attached photo and detail)
| 01CV - Civils | Cxxx-NCR-000965 | NCR | WSB - East box - Gallows brackets embedded into beam |  | Contr | HTM |  |  | 2014-11-13 | 2014-11-06 12:48 | -7 | 2014-10-30 16:55 | Civil - Civil Engineering General | 2000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The gallows brackets supporting the Walers in the East Box are cast into the North and South side corner/edge beam at basement slab level.
| 01CV - Civils | Cxxx-NCR-000966 | NCR | WSB - Missing Void Formers |  | Contr | HTM |  |  | 2014-12-12 | 2014-12-08 14:10 | -4 | 2014-11-04 09:45 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | There are 4 missing void formers on the basement slab along the infill (see attached plan). A total of 3 have been installed; again see attached plan. These would be used to concrete the 200mm walls at platform level (Secondary walls) as stated per RFI 1296.
| 01CV - Civils | Cxxx-NCR-000967 | NCR | WSB Tunnel Collar (T3) - Concrete Surface Finish |  | Contr | HTM |  |  | 2014-11-18 | 2014-11-21 09:48 | 3 | 2014-11-04 11:13 | Civil - Civil Engineering General | 2000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | T3 collar produced a poor concrete finish. Signs of a few dry honeycomb patches that appears to be cosmetic as paste could be seen within close range of surface edge on the inside face of the tunnel collar adjacent to the tunnel ring. Also, grout loss especially at bottom joint. Blowholes - larger than 10cm.
| 01CV - Civils | Cxxx-NCR-000968 | NCR | Plumstead Portal - South Lining Wall 18 Concrete Cover |  | Contr | HTM |  |  | 2014-11-17 | 2014-11-06 14:13 | -11 | 2014-11-03 15:17 | Civil - Civil Engineering General | 1000 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Supervision - Other | Completed |  | South lining wall 18 There is approx. 2.5m in length observed excess cover of 90- 100 mm (see attached photographs). The starter bar installed for lining wall at the time of base slab construction was out of alignment in the short length of lining wall 18 therefore the excess cover at the kicker level.
| 01CV - Civils | Cxxx-NCR-000969 | NCR | __ - Pumping Station - Surface finish to concrete slab and different shade |  | Contr | HTM |  |  | 2015-01-12 | 2015-01-06 14:07 | -6 | 2014-11-05 17:44 | Civil - Civil Engineering General | 2500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The concrete surface finish does not meet the requirements of the specification.The concrete slab pour at pumping station has produced two different shade on the finish. is the approved supplier for JTS, however __ was used on the 16th of October due to the inability to get concrete from on this date. The __ concrete used was approved Mix 22 - C32/40 S2. See attached sketch for locations. There are also defect in concrete finish This includes, minor broken corner, some slightly crooked edging/joints, small gouges & bumps etc. in concrete pour.
| 01CV - Civils | Cxxx-NCR-000970 | NCR | Plumstead Portal - North lining wall NLW19 - grout loss and surface blow holes |  | Contr | HTM |  |  | 2014-12-09 | 2014-11-14 16:58 | -25 | 2014-11-11 08:33 | Civil - Civil Engineering General | 1500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The concrete surface finish does not meet the requirements of the specification. On post inspection of North lining wall 19 there are minor defects includign grout loss and surface blow holes. ( photos attach)
| 01CV - Civils | Cxxx-NCR-000971 | NCR | WSB - Roof slab levels |  | Contr | HTM |  |  | 2014-12-05 | 2014-11-26 16:49 | -9 | 2014-11-11 16:39 | Surveying - Surveying General | 1500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Following on from RFI 1486 and under NSCS clause 10.5.5, the permitted deviation of adjacent floors at is ±10mm. A number of points on the roof slab have exceeded the specified tolerance. Please see attached As-Built survey of roof slab E6-E1 Ease box Basement Slab.
| 01CV - Civils | Cxxx-NCR-000972 | NCR | Plumstead Portal - Reception Road Piling - CFA Piles - Reinforcement cage not to full depth |  | Contr | HTM |  |  | 2015-04-30 | 2015-04-08 14:05 | -22 | 2014-11-11 16:46 | Civil - Civil Engineering General | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | Reception Road CFA pile 5C toe level of steel is 3.870m above the design steel toe level.
| 01CV - Civils | Cxxx-NCR-000973 | NCR | Plumstead portal - Reception road piling work commenced without accepted Cntractor's declaration in place |  | Contr | HTM |  |  | 2014-12-10 | 2014-12-10 10:24 | 0 | 2014-11-12 18:24 | Civil - Civil Engineering General | 500 |  | System Defect | Repair | 4 (0.5-3k) | Complete | Procedure Problem - Other | Completed |  | Reception road piling work was commenced on 10th November 2014 without the agreed contractor's declaration document approved by CRL on basis of RFI submission.
| 01CV - Civils | Cxxx-NCR-000974 | NCR | WSB - Roof Slab levels (soffit) |  | Contr | HTM |  |  | 2014-11-27 | 2014-11-26 14:54 | -1 | 2014-11-13 11:37 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | On the soffit of the south side Basement/Roof Slab in the east box, coordinates show points where roof slab has exceeded specified tolerance of 10mm (clarified in RFI 1486) and are all lower than design. Please see attached plan with coordinates.
| 01CV - Civils | Cxxx-NCR-000975 | NCR | Plumstead Portal - missing coplers in Roof slab 17 & 18 |  | Contr | HTM |  |  | 2014-11-28 | 2014-11-27 13:37 | -1 | 2014-11-14 10:37 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | It has been found on pre pour inspection of roof slab 17 & 18 that the pre installed couplers in RC prop 28, 29 and in Capping beam for roof slab are not correct numbers as per the drawing. There are missing couplers. Please see attached mark up drawing for detail.
| 01CV - Civils | Cxxx-NCR-000976 | NCR | Plumstead Portal - Roof slab 16, 17, 18 & 19 hydrophilic water bar Expanded (hydrated) |  | Contr | HTM |  |  | 2014-12-15 | 2014-11-28 15:57 | -17 | 2014-11-17 11:32 | Civil - Civil Engineering General | 500 |  | Material | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Improper preservation of material after installation | Completed |  | Plumstead portal ROSCOR hydrophilic water bars installed in roof slab 16, 17,18 & 19 are expanded (hydrated) due to contact with rain water prior to concrete pour. please see attached photos.
| 01CV - Civils | Cxxx-NCR-000977 | NCR | Plumstead Portal - missing coplers in Roof slab 19 |  | Contr | HTM |  |  | 2014-12-01 | 2014-11-28 09:52 | -3 | 2014-11-17 15:42 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | As per the NCR 000975 It is similar situation for roof slab 19 that the pre installed couplers in RC prop 29, 30 and in Capping beam for roof slab 19 are not correct numbers as per the drawing. There are missing couplers. Please see attached mark up drawing for detail.
| 01CV - Civils | Cxxx-NCR-000978 | NCR | WSB - Concrete honeycombing |  | Contr | HTM |  |  | 2014-12-02 | 2014-11-26 16:07 | -6 | 2014-11-18 16:47 | Civil - Civil Engineering General | 1500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | On the west box high wall (plat. to basement level), a honeycomb patch along the corner/edge of the wall. Given the position of the honeycomb (along the corner/edge of the beam), there is still substantial cover to the re-bars, as cover along the corners are in excess of 50mm due to u-bars curvature.
| 01CV - Civils | Cxxx-NCR-000979 | NCR | Plumstead Portal - missing coplers in RC props and capping beams for Roof slab 20, 21 & 22 |  | Contr | HTM |  |  | 2014-12-19 | 2014-11-28 09:51 | -21 | 2014-11-21 14:18 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | As per the NCR 000977 It is similar situation for roof slab 20, 21, & 22 which was poured on 20/11/2014, that the pre installed couplers in RC props and in Capping beams for roof slabs are not correct numbers as per the drawing.There are missing couplers. Please see attached mark up drawing & position for detail.
| 01CV - Civils | Cxxx-NCR-000980 | NCR | Plumstead Portal - Reception Road CFA Piling (Roger Bullivant) - Pile 8b - Drop in fresh Concrete level during excavaion of adjacent pile 9a |  | Contr | HTM |  |  | 2015-01-09 | 2015-01-06 14:49 | -3 | 2014-11-21 14:17 | Geotechnical Engineering - Concrete - Bored Pile | 2500 |  | Design | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Plumstead Portal - Reception Road CFA Piling (Roger Bullivant) - Pile 8b - Drop in fresh Concrete level during excavaion of adjacent pile 9a - Pile 8b – while drilling pile 9a the banksmen noticed pile 8b (drilled and poured 30-60m prior) slump, it was estimated at 2m below platform level. As the concrete slumped the pile then filled with dirt and water.
| 01CV - Civils | Cxxx-NCR-000981 | NCR | Plumstead Portal - Reception Road CFA Piling (Roger Bullivant) - 55 Piles installed with incorrect Lap length |  | Contr | HTM |  |  | 2015-04-30 | 2015-04-08 14:00 | -22 | 2014-11-21 14:38 | Geotechnical Engineering - Concrete - Bored Pile | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | - 55 Piles see below (also attached map of piles) - installed with 1000mm lap while CRL drawings asked for 1290 lap, this was due to an error in the fabrication drawing. I have attached the CRL and the Roger Bullivant fabrication drawings for your reference. o 1-10A 13A 14A 16A 19A 21A 22A 23A 25A o 1-17B o 1-11C 13C 14C 16C 18C 20C 22C 23C 24C 26C
| 01CV - Civils | Cxxx-NCR-000982 | NCR | Plumstead Portal - Roof slab 23, 24, 25 & 26 hydrophilic water bar Expanded (hydrated) |  | Contr | HTM |  |  | 2014-12-08 | 2014-12-04 11:39 | -4 | 2014-11-24 17:48 | Civil - Civil Engineering General | 500 |  | Damaged | Use As-Is | 4 (0.5-3k) | Complete | External Phenomenon - Weather or ambient condition | Completed |  | Due to the heavy rain over the weekend the two layers of ROSCOR hydrophilic strip on roof slabs 23, 24, 25, 26 have fully expanded (hydrated) and come off the wall between the fixings. please see attached photos.
| 01CV - Civils | Cxxx-NCR-000983 | NCR | Plumstead Portal - missing coplers in RC props and capping beams for Roof slab 23, 24, 25 & 26 |  | Contr | HTM |  |  | 2014-12-10 | 2014-11-28 16:55 | -12 | 2014-11-26 13:29 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | As per the NCR 000979 It is similar situation for roof slab 23, 24, 25 & 26 which is being poured to day on 26/11/2014. The pre installed couplers in RC props and in Capping beams for roof slabs are not correct numbers as per the drawing.There are missing couplers. Please see attached mark up drawings & position for detail.
| 01CV - Civils | Cxxx-NCR-000984 | NCR | Tunnel Drive H - T2 tunnel collar water proofing – Omitted Grout Tube |  | Contr | HTM |  |  | 2015-01-09 | 2014-12-04 10:38 | -36 | 2014-11-27 10:01 | Tunnelling - Linings - In-situ Concrete | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Tunnel Drive H - T2 tunnel collar water proofing – Omitted Grout Tube Ref: FCD response 903 Item 3 (grout tube / channel not Installed) Installed detailed is the hydrophilic strip (7) which has been fixed to the concrete substrate with the hydrophilic paste (6) Ref: FCD response 903 __500S hydrophilic bedded on __ mastic. 1. Channel installed as per drawing 2. Hydrophilic installed as per drawing 3. Channel – omitted 4. Paste - installed as per drawing 5. Channel - Installed as per FCD 6. Paste - installed as per drawing 7. Hydrophilic installed but not required as per latest FCD 8. Hydrophilic - installed as per drawing 9. Channel - installed as per drawing
| 01CV - Civils | Cxxx-NCR-000985 | NCR | Quality Assurance (QA) records not available for roof slab waterproofing under a Crossrail planned surveillance |  | Crossrail | XRL | NOW - North Woolwich Portal (East) |  | 2015-01-09 | 2015-01-06 14:51 | -3 | 2014-11-27 15:04 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Repair | 4 (0.5-3k) | Complete | Procedure Problem - Defective or inadequate procedure | Completed |  | During a planned Crossrail surveillance dated 12th November 2014, it was detailed that when thickness patches, pull off tests or any identified pin holes are repaired, another spark test is carried out to ensure the areas which have undergone repair have achieved a fully water tight system. A post surveillance request was made for Quality Assurance (QA) records detailing pull off test locations, patch test locations and any identified pinhole locations from initial spark testing. Additionally a request was made for QA records demonstrating that spark testing had been carried out, and, if pin holes were highlighted and repairs undertaken, details of a further spark test being undertaken as required by ITP item number 12. A daily diary report was provided for the works completed on 11th November 2014; the extract detailed pull off results and a statement that spark testing had been completed, however no QA records were produced demonstrating that all of the above had been carried out, which should form part of the assurance documentation at hand over of the works. This NCR has been raised as appropriate records could not be produced demonstrating this. Works Information Vol 2B part 20.9 ‘Self Certification’, “The Contractor shall be responsible for demonstrating that the works have been completed in accordance with the requirements of the Works Information and shall produce records that provide clear evidence of conformance”. Part 13.2 ‘Assurance’ states “progressive assurance means that there will be continual confirmation of compliance by the generation of contemporaneous records”. Additionally, it was noted that the pull off (bond) testing and acceptance parameters were not detailed in the ITP as an inspection activity and as such this should be closed out as part of this NCR.
| 01CV - Civils | Cxxx-NCR-000986 | NCR | Plumstead Portal - RC Prop 37 Upstand |  | Contr | HTM |  |  | 2014-12-12 | 2014-12-04 11:27 | -8 | 2014-11-28 09:15 | Civil - Civil Engineering General | 2000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The RC prop 37 up stand kicker reinforcement installed during RC prop construction has not enough concrete cover on south/west corner of the up stand . See attach photo and drawing
| 01CV - Civils | Cxxx-NCR-000987 | NCR | Plumstead Portal - Reception Road Piling - CFA Piles 6C - Reinforcement cage projecting 250mm above Piling platform level. |  | Contr | HTM |  |  | 2014-12-30 | 2014-12-04 11:07 | -26 | 2014-12-02 08:14 | Civil - Civil Engineering General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Reception Road CFA pile 6C reinforcement cage not to full depth. As per the information form site engineer the detail of installed pile is as follows. 1. Installed Pile Toe Level: 14.3m below PPL (103.4m) 2. Installed Toe Level of reinforcement Cage: (13.0m-.25m) 12.75m below PPL (103.4m) 3. Design pile cut off level of 102.660m ATD will be achieved 4. The anchorage bar lengths specified on drawing Cxxx-OVE-C-DDL-CR148_Z-80112 will be achieved
| 01CV - Civils | Cxxx-NCR-000988 | NCR | Plumstead Portal - Reception Road Piling - CFA Piles 30A - Reinforcement cage projecting 750mm above Piling platform level. |  | Contr | HTM |  |  | 2014-12-30 | 2014-12-04 10:59 | -26 | 2014-12-02 08:20 | Civil - Civil Engineering General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Reception Road CFA pile 30A reinforcement cage not to full depth. As per the information form site engineer the detail of installed pile is as follows. 1. Installed Pile Toe Level: 14.6m below PPL (103.4m) 2. Installed Toe Level of reinforcement Cage: (13.5m-.75m) 12.75m below PPL (103.4m) 3. Design pile cut off level of 102.357m ATD will be achieved 4. The anchorage bar lengths specified on drawing Cxxx-OVE-C-DDL-CR148_Z-80112 will be achieved
| 01CV - Civils | Cxxx-NCR-000989 | NCR | Plumstead Portal - __ Pumping Station - MEICA - 3 No. ITP's not Submitted or accepted Prior to Site Installation. |  | Contr | HTM |  |  | 2014-12-19 | 2014-12-16 11:29 | -3 | 2014-12-05 12:14 | Utilities Engineering - Utilities General | 500 |  | System Defect | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Three no. Rev 1.0 issue ITPs were not submitted for to Site Installation of Equipment. ITPs were returned code 3. Installation Started 20th October. SAT Commissioning is was due to start 2nd Dec but has been delayed until W/C 8th Dec. ITP were returned code 3 1st December. ITP were submitted following Engineering discussions 13th November. Cxxx-HTM-U-ITP-CR148_PT005-50034 - Marmadon Sewer Pumping Station - MEICA Works - Mechanical Installation Cxxx-HTM-U-ITP-CR148_PT005-50035 - Marmadon Sewer Pumping Station - MEICA Works – Electrical Installation Cxxx-HTM-U-ITP-CR148_PT005-50036 - Marmadon Sewer Pumping Station - MEICA Works - Instrumentation, Controls and Automation
| 01CV - Civils | Cxxx-NCR-000990 | NCR | Plumstead Portal-Pumping station compound - Concrete finish to retaining wall 6 |  | Contr | HTM |  |  | 2015-01-30 | 2015-01-09 17:34 | -21 | 2014-12-08 18:12 | Civil - Civil Engineering General | 2000 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | On the post concrete inspection today it is found concrete surface finish to retaining wall 6 does not meet the requirements of the specification. there are Rough patch on retaining wall face, honeycomb, grout loss, voids and poor construction joint Please attached photo.
| 01CV - Civils | Cxxx-NCR-000991 | NCR | Plumstead Portal - Roof Slab - Lytag infill between RC Props - Surface finish Grout loss. |  | Contr | HTM |  |  | 2015-01-06 | 2015-01-06 11:52 | 0 | 2014-12-09 08:39 | Civil - Civil Engineering General | 1000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Plumstead Portal - Roof Slabs 18 - 26 - Lytag infill between RC Props - Surface finish Grout loss. Lytag Lightweight concrete placed as in-fill material between roof slab & RC Props displaying poor finishes exhibiting areas of grout loss, Loose lytag aggregate and exposed aggregate (rough surface which may affect the application and durability of waterproofing layer to be applied.
| 01CV - Civils | Cxxx-NCR-000992 | NCR | Plumstead - Rising Main Air Valve Chamber White Hart Road -TW Specified Manhole Cover installed is non compliant with Highway Works. |  | Contr | HTM |  |  | 2015-01-07 | 2015-01-06 11:53 | -1 | 2014-12-10 12:15 | Utilities Engineering - Water | 3000 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Error in equipment or material selection | Completed |  | The steel hinged manhole Covers Specified for __ Air Valve chamber does not need the specified requirements for Highways. The cover was installed without design review following a location change moving the Chamber from its original location in the pavement to a location within White Hart Road carriageway to avoid services. The original drawing “A041-A1-21771-Rev I” locates the air valve chamber in the footway adjacent the pumping station. In RFI No. “Cxxx-RFI-001415” __ proposed to move the air valve chamber to the high point which is in the highway (location of road crossing to MH06 / SOS), however revisions required to the finishing details (MH cover, clear opening, biscuit etc.) were not picked up in the RFI response.
| 01CV - Civils | Cxxx-NCR-000993 | NCR | WSB - Collar repairs prior to inspection |  | Contr | HTM |  |  | 2015-03-27 | 2015-03-12 12:16 | -15 | 2014-12-18 09:14 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Repairs were done prior to inspection on tunnel 4 collar. It seems that the concrete gang took it upon their own initiatives to carry out the repairs as they had previously just carried out similar cosmetic repairs due to the outcome of the NCR issued on T3.
| 01CV - Civils | Cxxx-NCR-000994 | NCR | NWP - Kerb Alignment on Albert Road CH 88710 to 88730 |  | Contr | HTM | NOW - North Woolwich Portal (East) |  | 2015-01-16 | 2015-01-13 09:33 | -3 | 2014-12-19 08:04 | Civil - Streets & Highways | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The kerb alignment at the south side of the Albert Road between chainages 88710 and 88730 deviates from the CRL approved kerb alignment (See attached sketch and photos). The location of the deviation is on the joint between the high containment kerbs and bullnose kerbs.
| 01CV - Civils | Cxxx-NCR-000995 | NCR | Plumstead Portal - Attenuation Tank - DI Drainage Pipe - Material Installed Prior to Acceptance. |  | Contr | HTM |  |  | 2015-02-10 | 2015-01-16 14:43 | -25 | 2015-01-13 13:54 | Materials - Approval | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | DI installed as cast in item to Attenuation Tank prior to MCR submission & acceptance
| 01CV - Civils | Cxxx-NCR-000996 | NCR | Plumstead Portal - Reception Road Slab 2, Incorrect Base Slab Blinding in the first 4.5m of the slab continuing on from Slab 1 |  | Contr | HTM |  |  | 2015-02-12 | 2015-01-28 13:46 | -15 | 2015-01-15 14:34 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The blinding in the first 4.5m of the slab continuing on from Slab 1 (poured 19/12/2014) to the point where Slab 2 steps down from a 700/815 thick slab to a 1200/1315 thick slab has been placed at a constant height of 102.585m instead of at a constant ~1% fall West to East as per design. Please note that the blinding following the step down was placed correctly with 1% fall West to East as per design ( see attach drawing 1& 2)
| 01CV - Civils | Cxxx-NCR-000997 | NCR | Plumstead portal - __ - Pumping Station Valve chamber leak in JV connection pipe |  | Contr | HTM |  |  | 2015-02-12 | 2015-01-27 16:44 | -16 | 2015-01-15 16:02 | Civil - Drainage | 2500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | up on the pressure test it was found the __ pipe connection was leak and it was identified that the incorrect __ was originally installed in the wall 4 of valve chamber. Please see attached photo.
| 01CV - Civils | Cxxx-NCR-000998 | NCR | NCR - NWP - Reception Chamber Sump Wall South Section |  | Contr | __ | NOW - North Woolwich Portal (East) |  | 2015-03-03 | 2015-03-04 11:57 | 1 | 2015-02-03 12:20 | Civil - Civil Engineering General | 2000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The concrete surface finish does not meet the requirements of the spec - honeycombing, exposed aggregate and large blow holes. Poor compaction seems to be the cause.
| 01CV - Civils | Cxxx-NCR-001000 | NCR | WSB- East Box - Stairwell Wall |  | Contr | HTM |  |  | 2015-02-13 | 2015-02-04 14:37 | -9 | 2015-01-23 10:53 | Civil - Civil Engineering General | 2500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | In order to install the pre-cast stairs in between 450 North and 100 North (See Attached); the 450 North wall was cut back 10mm in areas where wall inclination exceeded 15mm (See attached AB Survey). __ have therefore broken down as much as 10mm of the edge face of the wall to accommodate the installation of the Pre-cast stairs in between the western staircase walls (East Box). __’s wall was built in accordance to the NSCS specification in compliance with British Standards EN 13670:2009 where an allowed tolerance of 23mm is permitted (See section 10.5.2). The maximum level of inclination on the staircase wall was 19mm at 450 North (See Attached AB Survey). It is apparent that the fabrication of the pre-cast stairs did not take into consideration the permitted tolerance on the walls when designing, as there is only a 20mm gap between the width of the stairs compared to the width of the opening (See Attached DWG). This only allows a 10 mm deviation on each wall as opposed to the 23mm standardised by British Standards.
| 01CV - Civils | Cxxx-NCR-001001 | NCR | PUNCTURE TO WATERPROOF MEMBRANE IN CROSS PASSAGE 18 SHAFT |  | Contr | HTM |  |  | 2015-03-27 | 2015-03-30 13:42 | 3 | 2015-01-23 16:24 | Civil - Civil Engineering General | 2000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During the construction of Nadir Catch Pit and Directional Drilling, the membrane at the Auger bore opening (XP 18 shaft) was punctured
| 01CV - Civils | Cxxx-NCR-001003 | NCR | North Woolwich Portal - Comms Room - Fire Protection - Mix 4 without Poly fibre used. |  | Contr | HTM | NOW - North Woolwich Portal (East) |  | 2015-02-23 | 2015-02-06 12:26 | -17 | 2015-01-26 09:47 | Civil - Civil Engineering General | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Pour North Woolwich Tuesday 20th Ref RFI 1620 mix was poured prior to response to RFI clarifying mixes required Poly fibres. Mix 45 (offered in RFI as an option for the narrow wall pours with 10mm aggregate) was not used however the mix used (Accepted Mix 4) contained no fibres.
| 01CV - Civils | Cxxx-NCR-001004 | NCR | WSB- Cracks in Sealant -Smoke Ducts |  | Contr | HTM |  |  | 2015-02-12 | 2015-02-04 11:44 | -8 | 2015-01-29 09:38 | Civil - Civil Engineering General | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | While sealing the precast smoke ducts panels in Woolwich Box as per the procedure agreed in FCD 917, __ noticed some cracks in the sealant between the Smoke Ducts panels at two locations (see attached pictures). As a precaution __ stopped works and contacted a representative from the sealant supplier to arrange a site visit and review the installation procedure. During the inspection it was established that the backing rod which was being used was suitable for the task but the depth of the sealant was most likely the issue.
| 01CV - Civils | Cxxx-NCR-001005 | NCR | PP - Walkway Platform Construction - Work started without accepted ITP in place |  | Contr | HTM |  |  | 2015-03-03 | 2015-02-24 15:03 | -7 | 2015-02-03 14:22 | Civil - Civil Engineering General | 500 |  | System Defect | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | Inspection & Test Plan (ITP) - Plumstead Portal Completion (PPC) - Walkway Platform Construction Cxxx-HTM-C-ITP-CR148_PT005-50018 revision 1.0 submitted on 29/01/2015 and work started on 26/01/2015
| 01CV - Civils | Cxxx-NCR-001006 | NCR | PP - Twin Walls Headhouse |  | Contr | HTM |  |  | 2015-02-18 | 2015-02-06 17:20 | -12 | 2015-02-04 14:45 | Civil - Civil Engineering General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Bar mk. 39, 23 on drawing Cxxx-HTM-C-DWG-CR148_PT005-51500 have been inserted as B16 instead of B20 Bar mk. 39, 23 & 47 on drawing Cxxx-HTM-C-DWG-CR148_PT005-51501 have been inserted as B16 instead of B20.
| 01CV - Civils | Cxxx-NCR-001007 | NCR | NWP - Hard Hard Lining Wall - Honeycombing |  | Contr | HTM | NOW - North Woolwich Portal (East) |  | 2015-03-04 | 2015-03-04 12:01 | 0 | 2015-02-04 16:04 | Civil - Civil Engineering General | 2500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Honey combing on Hard Hard Lining Wall. Wall poured on Monday 2nd of Feb.
| 01CV - Civils | Cxxx-NCR-001008 | NCR | C__HPIT IN TUNNEL 4 IN WRONG POSITION AS PER DRAWING |  | Contr | HTM |  |  | 2015-03-13 | 2015-03-16 13:58 | 3 | 2015-02-06 11:22 | Civil - Tunnelling | 1500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During 1st stage concrete pour of invert slab Tunnel 4 (WBS to NW)eastbound, the catchpit on chainage 20201 moved and was displaced from what drawings stated
| 01CV - Civils | Cxxx-NCR-001009 | NCR | Plumstead Portal - Reception Road - Waterproofing - Bitumen Paint not applied to manufacturers recomended 2 coats |  | Contr | HTM |  |  | 2015-02-19 | 2015-02-23 17:34 | 4 | 2015-02-05 16:55 | Civil - Civil Engineering General | 2000 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Plumstead Portal - Reception Road - Waterproofing - Bitumen Paint not applied to manufacturers recomended 2 coats - Reception Road Slab 2. Area was covered up prior to second witness point confirming second coat had been applied
| 01CV - Civils | Cxxx-NCR-001010 | NCR | Plumstead Portal - Reception Road - Installation of Clayboard Void Former - Alternative Method of Collapsing board not identified in ITP or Method Statement |  | Contr | HTM |  |  | 2015-02-19 | 2015-02-23 17:39 | 4 | 2015-02-05 17:09 | Civil - Civil Engineering General | 500 |  | Incomplete Works | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Insufficient information made available to the worker. | Completed |  | ITP item 17 - Installation of Clayboard: Manufacturers Optional Void pack was not installed and water has not been added to the clayboard following hardening of concrete slab no. 2 & 3.
| 01CV - Civils | Cxxx-NCR-001011 | NCR | UPSTAND SIDE FACE PEELING OFF IN TUNNEL 4 |  | Contr | HTM |  |  | 2015-02-20 | 2015-02-27 17:21 | 7 | 2015-02-06 16:48 | Civil - Tunnelling | 1000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | When striking upstands in Tunnel 4, the concrete on the side face came off with the shutters. In the areas in question, upstands was poured in the afternoon and night shift struck shutters in the night.
| 01CV - Civils | Cxxx-NCR-001012 | NCR | PP - Colour diference in RC prop 37 and up stand |  | Contr | HTM |  |  | 2015-03-09 | 2015-03-09 16:07 | 0 | 2015-02-09 11:28 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The visual appearance of open to view concrete colour for RC prop 37 up stand is slightly darker shade then the existing RC prop 37
| 01CV - Civils | Cxxx-NCR-001013 | NCR | NCR- WSB- Discoloration and joint in the Beams 21 & 22 |  | Contr | HTM |  |  | 2015-03-30 | 2015-03-31 11:13 | 1 | 2015-02-16 09:24 | Architectural - Finishes | 5000 |  | Incorrect Installation | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Following the removal of the shutters in beams 21 & 22 in the west box it has been noticed that the joints between the basement slab and the beams are not straight. A grout check should have been installed during basement slab pour 1 to create a straight joint between the basement level and the beam which was to be poured afterwards leaving a rough joint, see attached pictures.
| 01CV - Civils | Cxxx-NCR-001014 | NCR | PP - South Lining wall 19 Pour Without __ UKAS Sampling of Concrete |  | Contr | HTM |  |  | 2015-03-12 | 2015-02-24 13:39 | -16 | 2015-02-12 17:09 | Civil - Civil Engineering General | 500 |  | Planning | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | While compiling Concrete cube results It is found that the South Lining wall 19 concrete poured on 10/11/2014 without __ UKAS accredited sampling
| 01CV - Civils | Cxxx-NCR-001015 | NCR | Plumstead Portal - East Bound Walk way 06 - damaged Concrete |  | Contr | HTM |  |  | 2015-03-12 | 2015-02-27 10:31 | -13 | 2015-02-12 18:25 | Civil - Civil Engineering General | 1500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | While striking formwork shutter form cantilever section of east bound walk way 06 concrete has been damaged at two location as shown in attached photo
| 01CV - Civils | Cxxx-NCR-001016 | NCR | Plumstead portal - East bound walk way 01 - Chamfer installed to top edge. |  | Contr | HTM |  |  | 2015-03-13 | 2015-03-09 16:25 | -4 | 2015-02-13 17:03 | Civil - Civil Engineering General | 1500 |  | Supervision/Management | Repair | 4 (0.5-3k) | Complete | Supervision - Other | Completed |  | Chamfer installed to top edge of East bound walk way 01 cantilever section was not specify in drawing
| 01CV - Civils | Cxxx-NCR-001017 | NCR | Plumstead Portal - Roof slab 20, 21 & 22 hydrophilic water bar Expanded (hydrated) |  | Contr | HTM |  |  | 2015-03-16 | 2015-02-23 16:14 | -21 | 2015-02-16 16:57 | Civil - Civil Engineering General | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | External Phenomenon - Weather or ambient condition | Completed |  | Plumstead portal ROSCOR hydrophilic water bars installed in roof slab 20, 21 & 22 are expanded (hydrated) due to contact with rain water prior to concrete poured on 20/11/2014. please see attached photos.
| 01CV - Civils | Cxxx-NCR-001018 | NCR | Plumstead Portal - East Bound Walk way 03 & 04 interface - Cantilever slab out of tolerence |  | Contr | HTM |  |  | 2015-03-17 | 2015-02-27 10:26 | -18 | 2015-02-17 10:45 | Civil - Civil Engineering General | 1000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | East bound walkway 03 & 04 interface cantilever slab out of tolerance increase from 150mm to 180mm thick please see attached photos. the drawing no. Cxxx-CSY-S-DDD-CR148_PT005-00631 shows vertical tolerance is -25, +0mm
| 01CV - Civils | Cxxx-NCR-001019 | NCR | PP - Damaged/missing head wall & D wall Coupler in Roof slab 1 |  | Contr | HTM |  |  | 2015-03-19 | 2015-03-09 16:26 | -10 | 2015-02-19 10:42 | Civil - Civil Engineering General | 1000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | while exposing head wall and D wall couplers for the roof slab 1 & 2 it was found Damaged one coupler in North D wall panel N01 and number of missing/damaged couplers in head wall. The Attached detail/layout which details the positions of the coupler that were being missing or damaged. (see attached detail layout)
| 01CV - Civils | Cxxx-NCR-001020 | NCR | UPSTANDS CONCRETE STILL PLACED AFTER 3HOURS |  | Contr | HTM |  |  | 2015-03-13 | 2015-03-04 13:17 | -9 | 2015-02-20 16:25 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Upstand Concrete was still placed after agreed concrete life time period passed in Tunnel 3 (rings 1392 to 1409). A set of 6 cubes was made about 1230hours. Concrete was called in for FSC Slab, and before the we could start pouring the slab, the pump line got blocked. In the process of clearing the pump line, the decision was made to use concrete on site for upstands with the dumper. These lead to the concrete being over the 3 hours concrete life time . Attached also is the 4 day result of the concrete.
| 01CV - Civils | Cxxx-NCR-001021 | NCR | PP - Miss out the Kiwkastrip for the mid height stair landing in Wall 6. |  | Contr | HTM |  |  | 2015-03-23 | 2015-03-09 16:47 | -14 | 2015-02-23 18:23 | Civil - Civil Engineering General | 2000 |  | Design | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | __ reinforcing drawing for wall 6 did not show the Kwikastrip in wall 06 hence Miss out the Kiwkastrip for the mid height stair landing. (please see attached mark up drawing)
| 01CV - Civils | Cxxx-NCR-001022 | NCR | PP - East bound walk way 1&2 construction joint - Omission of lapping A142 front face mesh |  | Contr | HTM |  |  | 2015-03-24 | 2015-02-27 17:20 | -25 | 2015-02-24 13:39 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Supervision - Other | Completed |  | __ omitted lapping A142 steel mesh to front face of East bound walk way 1 & 2 construction joint
| 01CV - Civils | Cxxx-NCR-001023 | NCR | __ Marmadon Sewer Pumping Station - Rising Main - DI Pipe Connection MH06 - SOS - Ponding identified in CCTV Survey |  | Contr | HTM |  |  | 2015-03-26 | 2015-03-11 11:18 | -15 | 2015-02-26 17:07 | Civil - Utilities Engineering | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Ponding was viewed on the camera survey of the pipe at the __ connection. The ponding runs from the step at the __ coupling where it connects with the sewer wall, over the 1m rocker pipe and feathering out along the preceding 5.5m long pipe. The pipeline is formed of ductile iron pressure pipework laid to gradients to accommodate the flow from an upstream pumping station. There are no other gravity fed connections on the line. The upstream point being MH6 which was the termination chamber for the 400 OD PE pumping main and incorporated an internal backdrop pipe to take the flow from the pumping main height down to the invert level of the gravity sewer. The as-constructed pipework end to end is 25m long and has a fall of approx 350mm, giving a gradient in excess of 1 in 70m fall, far exceeding the minimum self cleansing gradients required for drainage pipework.
| 01CV - Civils | Cxxx-NCR-001024 | NCR | Tunnel Drive H - PP-T1 West bound tunnel collar water proofing – Omitted Grout Tube |  | Contr | HTM |  |  | 2015-03-30 | 2015-03-12 12:14 | -18 | 2015-03-02 13:01 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | T1 west bound tunnel collar - omitted grout tube under side of segment. installed additional hydrophilic strip instead Ref: FCD response 903
| 01CV - Civils | Cxxx-NCR-001025 | NCR | Cxxx TUH Crosspagge 17 sump base waterproofing membrane puncture and leak |  | Crossrail | XRL |  |  | 2015-03-23 | 2015-03-27 17:09 | 4 | 2015-03-09 14:50 | Tunnelling - Linings - In-situ Concrete | 1500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | On 04Mar2015 after __ waterproofing membrane subcontractor Russetts installed the new repair patch of membrane arround the Naylor pipe end at sump base of CP17, CRL field engineer inspecting the patch repair work and found a new puncture hole on waterproofing membrane and ground water flowing out continuosly.
| 01CV - Civils | Cxxx-NCR-001026 | NCR | Tunnel Drive H - First Stage Concrete - Plumstead to North Woolwich - Westbound (T1) - Tunnel Drainage - Ist Catch Pit Not Cast in. |  | Contr | HTM |  |  | 2015-04-08 | 2015-04-13 12:24 | 5 | 2015-03-11 10:26 | Civil - Civil Engineering General | 1500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | 1 no. catch pit (Type 5) at chain age 22643.000 was not installed in the FSC Slab in WB Tunnel FSC Slab on the first 5 no. Rings was poured on 5th of March 2015.It was noticed on 6th of March (after the pour) that the 1 no. catch pit (Type 5) at above chainage was not installed.
| 01CV - Civils | Cxxx-NCR-001027 | NCR | Plumstead Portal - Incorrect installation and missing coplers in RC capping beams for reception road Run on Slab |  | Contr | HTM |  |  | 2015-04-09 | 2015-03-23 16:55 | -17 | 2015-03-12 17:14 | Civil - Civil Engineering General | 2000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | 1) The bottom Couplers installed in RC Capping beam for run on slab was incorrect level which was below bottom B1 reinforcement. And also about 12nos couplers were installed 20mm instead 25mm (see attach mark up drawing) 2) The couplers were not installed in one of the capping beam 16 (NCR-00549).
| 01CV - Civils | Cxxx-NCR-001028 | NCR | C__H PIT INSTALLATION AT CHAINAGE 22556 IN TUNNEL PLUMSTEAD TO WOOLWICH BOX(EASTBOUND) |  | Contr | HTM |  |  | 2015-04-01 | 2015-03-20 11:24 | -12 | 2015-03-18 10:11 | Civil - Tunnelling | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | NCR Details: Catch pit (Type 5) installation at chainage 22556 in Tunnel 2 Please refer to the attached as built survey for a comparison b/w design and the as built position of the catch Pit. (Out of tolerance measurements are highlighted, max.32mm on one side)
| 01CV - Civils | Cxxx-NCR-001029 | NCR | No Cubes made on Infill Concrete round clay pipe of XP17 Sump by __ |  | Contr | HTM |  |  | 2015-05-14 | 2015-05-15 11:11 | 1 | 2015-03-18 11:46 | Civil - Tunnelling | 1500 |  | Incomplete Works | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | XP17 sump infill round clay pipe was poured on the 9th of March. __ did not come to site(but they were booked to come), __ made cubes.
| 01CV - Civils | Cxxx-NCR-001030 | NCR | Plumstead Portal - South walk way slab reinforcement installed 300mm lap length instead 400mm specify in drawing |  | Contr | HTM |  |  | 2015-04-15 | 2015-03-23 16:13 | -23 | 2015-03-18 12:25 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | On pre inspection check it was found that the South walk way chainage 92020 - 91983. the slab distribution reinforcement installed 300mm lap length instead 400 specify in __ drawing for slab concrete poured on 17/03/2015. (please see attach drawing)
| 01CV - Civils | Cxxx-NCR-001031 | NCR | Plumsted Portal - Head house wall 17 couplers moved |  | Contr | HTM |  |  | 2015-04-17 | 2015-03-26 14:13 | -22 | 2015-03-20 15:04 | Civil - Civil Engineering General | 1500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | On exposing head house wall 17 coupler it was found that the bottom couplers installed within wall 17 moved during the pour, causing them to have insufficient cover if extended.(Please see attach sketch)
| 01CV - Civils | Cxxx-NCR-001032 | NCR | Plumstead Portal - Twin Walll spaly 5th - __ Concrete Mix 34R - C32/40 with Poly Fibres - Cube Failures of 13/08/14 |  | Contr | HTM |  |  | 2015-04-20 | 2015-03-26 14:34 | -25 | 2015-03-23 10:48 | Civil - Civil Engineering General | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | While compiling twin walls cube result it has found that the concrete pour on 13/08/14 the one set of average concrete cube result failed
| 01CV - Civils | Cxxx-NCR-001034 | NCR | WSB - Precast Stairs & Landing - Cores cut trough Precast Stairs & landing without acceptance in place. |  | Contr | HTM |  |  | 2015-04-10 | 2015-04-13 12:38 | 3 | 2015-03-27 17:08 | Civil - Civil Engineering General | 500 |  | System Defect | Repair | 4 (0.5-3k) | Complete | Procedure Problem - Lack of procedure | Completed |  | Three core holes in WSBF 9 & 10. Precast Stairs & landing without acceptance in place.
| 01CV - Civils | Cxxx-NCR-001035 | NCR | PP - Opening cast incorrectly in lift shaft wall 06 & 07 |  | Contr | HTM |  |  | 2015-04-28 | 2015-04-10 16:57 | -18 | 2015-03-31 12:07 | Civil - Civil Engineering General | 2500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Plumstead portal lift shaft wall 06 & 07 opening casted incorrectly which are not as per __ reinforcement drawing. The opening in lift shaft wall 06 cast as per lift shaft wall 07 and visa versa. Please refer to attach CRL drawing Cxxx-CSY-S-DDC-CR148_PT005-01156 C01 ( Opening number reference)
| 01CV - Civils | Cxxx-NCR-001036 | NCR | C__H PIT MISSED OUT WHEN POURING THE 1ST FIVE RINGS INVERT SLAB IN TUNNEL 1(PLUMSTEAD TO WOOLWICH BOX(WESTBOUND) |  | Contr | HTM |  |  | 2015-04-15 | 2015-04-16 16:58 | 1 | 2015-04-01 09:03 | Civil - Tunnelling | 2500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | When pouring the 1st five rings FSC invert slab, the catch pit was missed out in Tunnel 1 from Plumstead to Woolwich Box (Westbound)
| 01CV - Civils | Cxxx-NCR-001037 | NCR | No Cubes made when pouring XP17 sump dividing wall by __ |  | Contr | HTM |  |  | 2015-06-05 | 2015-06-04 15:40 | -1 | 2015-04-01 09:28 | Civil - Tunnelling | 1500 |  | Incomplete Works | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | XP17 sump dividing wall was cast and __ was not present to make cubes.
| 01CV - Civils | Cxxx-NCR-001038 | NCR | No cubes made by __ when pouring Ring 1 to 5 of Tunnel 2 Plumstead to Woolwich Box (Eastbound) |  | Contr | HTM |  |  | 2015-05-13 | 2015-05-15 12:56 | 2 | 2015-04-01 09:42 | Civil - Tunnelling | 1500 |  | Incomplete Works | Rework | 4 (0.5-3k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | __ was not on site when rings 1 to 5 of Tunnel 2 Plumstead to Woolwich Box (Eastbound) was poured, so no cubes were made
| 01CV - Civils | Cxxx-NCR-001039 | NCR | OUT OF TOLERANCE LEVEL FOR FSC IN TUNNEL 1 (WESTBOUND) PLUMSTEAD TO WOOLWICH BOX |  | Contr | HTM |  |  | 2015-05-28 | 2015-07-14 09:18 | 47 | 2015-04-02 12:05 | Civil - Tunnelling | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | As built survey of FSC in Tunnel 1(Plumstead to Woolwich Box Westbound) shows it on the average low. Survey attached
| 01CV - Civils | Cxxx-NCR-001040 | NCR | OUT OF TOLERANCE LEVEL FOR FSC IN TUNNEL 2 (EASTBOUND) PLUMSTEAD TO WOOLWICH BOX |  | Contr | HTM |  |  | 2015-04-21 | 2015-04-24 12:28 | 3 | 2015-04-07 09:18 | Civil - Tunnelling | 1500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | As built survey of FSC in Tunnel 2(Plumstead to Woolwich Box Eastbound) shows it on the average low. Survey attached
| 01CV - Civils | Cxxx-NCR-001041 | NCR | WSB- Levels 1st Stage Concrete- West Box |  | Contr | HTM |  |  | 2015-05-20 | 2015-05-11 17:31 | -9 | 2015-04-08 10:26 | Civil - Civil Engineering General | 1500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Attached is a level survey of the FSC in the Woolwich West Box @ T4 entrance. The concrete level has been laid incorrectly and is outside normal tolerance of +-10mm.
| 01CV - Civils | Cxxx-NCR-001042 | NCR | NWP - Bay E12 - North Flood Wall - Grade of Reinforcement |  | Contr | HTM | NOW - North Woolwich Portal (East) |  | 2015-04-23 | 2015-04-10 17:10 | -13 | 2015-04-09 14:41 | Civil - Civil Engineering General | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Error by manufacturer in shipping or marking | Completed |  | As per the response to the Cxxx-FCD-000941, the reinforcement to be used should be Grade B500 and not H as supplied by Cxxx.
| 01CV - Civils | Cxxx-NCR-001044 | NCR | NWP - North Comms Walls - 28 day cube failure |  | Contr | HTM | NOW - North Woolwich Portal (East) |  | 2015-04-23 | 2015-04-14 10:08 | -9 | 2015-04-09 15:07 | Civil - Civil Engineering General | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | See attached cube results for North Comms Walls. Mix 34 failure at 28days (tested at 30days). Specified Strength = 40N/mm at 28days. Also see attached mark up of affected area & slump record.
| 01CV - Civils | Cxxx-NCR-001045 | NCR | NWP - 300mm Rising Main |  | Contr | HTM | NOW - North Woolwich Portal (East) |  | 2015-05-14 | 2015-05-15 11:09 | 1 | 2015-04-09 17:21 | Civil - Civil Engineering General | 1500 |  | Design | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The services step in the capping beam next to the riser shaft in Roof Slab 1 has not been cast in line with the 300mm rising main (see attached). __ propose to break a section of the capping beam 450mm wide by 200mm deep to allow the rising main to be installed. After breaking the capping beam will be made good to provide cover to the reinforcement. Can Crossrail please confirm this is acceptable?
| 01CV - Civils | Cxxx-NCR-001046 | NCR | Plumstead Portal- Concrete finish toHead house wall 30 |  | Contr | HTM |  |  | 2015-05-07 | 2015-05-08 15:15 | 1 | 2015-04-09 18:36 | Civil - Civil Engineering General | 2500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | On the post concrete inspection today it is found concrete surface finish to head house wall 30 does not meet the requirements of the specification. The stop end shutter moved and create belly in concrete see attach photos.
| 01CV - Civils | Cxxx-NCR-001047 | NCR | Tunnel Drive H - East & Westbound Tunnels - FSC Drainage Temporary Catchpit Covers. Plywood used is not fireproofed Timber. |  | Contr | HTM |  |  | 2015-05-12 | 2015-05-11 17:25 | -1 | 2015-04-14 08:51 | Civil - Civil Engineering General | 2000 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | Temporary works construction of East & Westbound Tunnels - FSC Drainage. Temporary Catchpit Covers were risk assessed as a temporary material in Plywood However the Plywood used is not fireproofed in accordance with requirements for use of Timber underground.
| 01CV - Civils | Cxxx-NCR-001048 | NCR | Plumstead Portal- Concrete finish to West bound walk way slab |  | Contr | HTM |  |  | 2015-05-14 | 2015-05-01 11:36 | -13 | 2015-04-16 17:09 | Civil - Civil Engineering General | 2000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | In some locations the Concrete finish to the top surface of South walk way slab does not meet the required U1 finish. please see attach mark up sketches.
| 01CV - Civils | Cxxx-NCR-001049 | NCR | Plumstead Portal - Reception Road CFA Piling (Roger Bullivant) Out of tolerances |  | Contr | HTM |  |  | 2015-05-14 | 2015-05-05 14:55 | -9 | 2015-04-16 17:53 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Plumstead Portal - Reception Road CFA Pile no. 1B, 3B, 5B, 5C, 8A, 8B, 13B, 15A, 17B, 18B, 19A, 20B are marginally out of tolerances in plan position
| 01CV - Civils | Cxxx-NCR-001050 | NCR | Plumstead portal - Run on slab CFA Pile 317 Unable to Locat the rig computer printout |  | Contr | HTM |  |  | 2015-05-14 | 2015-04-24 12:49 | -20 | 2015-04-16 18:31 | Civil - Civil Engineering General | 500 |  | System Defect | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | CFA Pile number 317 was installed on 16/02/2015 have been unable to locate the rig computer printout (pile log)
| 01CV - Civils | Cxxx-NCR-001051 | NCR | Plumstead Portal - Transition slab - top Concrete Cover |  | Contr | HTM |  |  | 2015-05-18 | 2015-05-01 10:09 | -17 | 2015-04-20 15:05 | Civil - Civil Engineering General | 1000 |  | Supervision/Management | Repair | 4 (0.5-3k) | Complete | Supervision - Supervisor not familiar with the work | Completed |  | At transition slab observed excess cover of 100- 120 mm at the whole width of slab stop end and gradually decrease down to 40mm in 750mm length (see attached photographs).
| 01CV - Civils | Cxxx-NCR-001052 | NCR | Plumstead Portal - Concrete finish to Transition slab |  | Contr | HTM |  |  | 2015-05-22 | 2015-05-08 15:30 | -14 | 2015-04-24 15:43 | Civil - Civil Engineering General | 1000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The transition slab top concrete surface finish at couple of places does not meet the requirements of the specification. There are unfinished surface due to concrete gone stiff. Please see attach photo.
| 01CV - Civils | Cxxx-NCR-001053 | NCR | NWP - Precast Intervention Stairs - Hair Line Crack |  | Contr | HTM | NOW - North Woolwich Portal (East) |  | 2015-05-11 | 2015-05-15 12:57 | 4 | 2015-04-27 17:41 | Civil - Civil Engineering General | 2000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | After installing the pre cast intervention stair case it was noticed that a hair line crack had formed across the underside of the stairs in the transverse direction (see attached). The crack was measured at the widest point and appears to be approx 0.25mm. (see attached photos). Upon discussions and inspection by Cxxx it was agreed that the crack does not impose any issues to the structural integrity of the staircase.
| 01CV - Civils | Cxxx-NCR-001054 | NCR | Plumstead portal - Non-continuous concrete pour operation – Headshunt Capping Beam Stage 4 West. |  | Contr | HTM |  |  | 2015-05-26 | 2015-04-29 09:18 | -27 | 2015-04-28 09:53 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | due to 20-30min. delay due to crane allocation time the concrete pour was not continuous but concrete was discharged within the 2 hour duration from batching. (see attach Concrete ticket)
| 01CV - Civils | Cxxx-NCR-001055 | NCR | Plumstead Portal - No fines concrete was placed in excess of 2 hours from the time it was batched |  | Contr | HTM |  |  | 2015-05-27 | 2015-05-01 11:37 | -26 | 2015-04-29 14:21 | Civil - Civil Engineering General | 1500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Plumstead Portal no fine concrete place to cover west bound pressure release drainage pipe along Diaphragm wall was placed in excess of 2 hours from the time it was batched
| 01CV - Civils | Cxxx-NCR-001056 | NCR | NWP - Intervention Stairs - Position |  | Contr | HTM | NOW - North Woolwich Portal (East) |  | 2015-05-14 | 2015-05-08 15:21 | -6 | 2015-04-30 10:46 | Civil - Civil Engineering General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | From response to Cxxx-RFI-001699 for the position of the Intervention Stairs, __ constructed to the SOPs 1,2 3 & 4 given on the drawing Cxxx-CSY-S-DDL-CR146_PT004-02211 rev P04.1. This gave an overall length of 5.925m. The actual over all length of the precast stairs is 5.900m, (25mm of a difference). This resulted in the stairs plinth standing 25mm proud- see attached photo. The wall & precast stairs are in the correct position.
| 01CV - Civils | Cxxx-NCR-001057 | NCR | Plumsted Portal - Head house wall 15 & 16 couplers moved/damaged |  | Contr | HTM |  |  | 2015-06-03 | 2015-05-22 18:15 | -12 | 2015-05-06 15:40 | Civil - Civil Engineering General | 1500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | When exposing the couplers that were placed in wall 15 and 16, there was excessive cover on the coupler face (20-30mm) where the couplers had come away from the shutter face. The breaking of this concrete resulted in damage of some of the coupler trends and __ were unable to place the male couplers for the roof slab construction. There was also a number of couplers that twisted during the placing of the concrete, if the male couplers where placed to these twisted female, the coupler leg would be protruding through either the top or bottom of the slab itself.
| 01CV - Civils | Cxxx-NCR-001058 | NCR | Plumstead Portal - Incorrect installation of dimpled membrane in track drainage |  | Contr | HTM |  |  | 2015-06-03 | 2015-05-22 18:13 | -12 | 2015-05-06 17:02 | Civil - Civil Engineering General | 1000 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Concrete form work shutter installed and secured to form a track drainage profile without installation of dimple membrane. The membrane installed between D wall and shutter are tucked inside the shutter and poured concrete. while separating membrane from concrete after striking shutter it was locally break out concrete to separate membrane and concrete surface has to make good. Please see attach photo
| 01CV - Civils | Cxxx-NCR-001059 | NCR | AS BUILT DIRECTION OF NADIR (XP18) CLAY PIPE IN C__H PIT TYPE 2 OF TUNNEL 1 & 2 (PLUMSTEAD TO WOOLWICH BOX WESTBOUND & EASTBOUND) |  | Contr | HTM |  |  | 2015-05-22 | 2015-05-22 18:08 | 0 | 2015-05-08 09:07 | Civil - Tunnelling | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | __ constructed the Nadir catchpit in T1 & T2 as per drawing Cxxx-OVE-C4-DDD-CR001_Z-24517. However, __ did not review the first stage concrete drawings before installing the DN 200 vitrified clay pipes between the catchpit and the shaft in Cross Passage 18. This has resulted in the clay pipe not being centralised in the finished catchpit location. To remediate this __ would like to propose forming a recess in the first stage concrete at the level of the clay pipe, as per the attached as built sketch’s. Please confirm that is acceptable.
| 01CV - Civils | Cxxx-NCR-001060 | NCR | PP – Omit rocker pipe from MHC401 on existin sewer 381dia. sewer |  | Contr | HTM |  |  | 2015-06-05 | 2015-06-04 15:13 | -1 | 2015-05-08 13:47 | Civil - Drainage | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | __ have cast a mass concrete base for the retaining wall west of the attenuation tank at Plumstead Portal. The revised drainage design includes a manhole (MH C401) which is to be constructed north of the retaining wall on the line of the 381mm diameter sewer. At the connection of the 381 sewer and MH C401 a rocker pipe is specified. However the mass concrete base has been poured prior to the construction of MH C401 and no allowance was made for a rocker pipe on the south side. On the north side a concrete surround from a previous repair is impeding the installation of a rocker pipe. Please note the repair was carried out using flexseal couplings as shown in attach sketch.
| 01CV - Civils | Cxxx-NCR-001061 | NCR | Plumstead Portal - __ - February 2015 Concrete Supply from Angerstien Plant - Traceability of Records |  | Contr | HTM |  |  | 2015-06-08 | 2015-06-11 13:46 | 3 | 2015-05-11 14:59 | Civil - Civil Engineering General | 500 |  | System Defect | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Lack or improper material identification and traceability | Completed |  | Pours recorded with incorrect characteristic strength due to error in __ purchasing & batching system.
| 01CV - Civils | Cxxx-NCR-001063 | NCR | Tunnel Collars Plumstead North Woolwich & Woolwich Box Portals - Reinjectable Grout tubes |  | Contr | HTM |  |  | 2015-06-08 | 2015-05-22 18:09 | -17 | 2015-05-11 14:50 | Civil - Civil Engineering General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Installed Tubes have been injected and cannot be re-injected.
| 01CV - Civils | Cxxx-NCR-001066 | NCR | PP - Opening cast incorrectly in Head house wall 40 |  | Contr | HTM |  |  | 2015-06-08 | 2015-05-15 16:54 | -24 | 2015-05-11 14:00 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Plumstead portal Head house wall 40 opening 100x100mm casted incorrectly Please see attach sketch.
| 01CV - Civils | Cxxx-NCR-001067 | NCR | NWP – Grout Check on top of Walkway Slab |  | Contr | HTM | NOW - North Woolwich Portal (East) |  | 2015-05-25 | 2015-05-15 16:57 | -10 | 2015-05-11 14:27 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | __ have included a grout check on the top side of the walkway slab (track side edge). This should not have been included.
| 01CV - Civils | Cxxx-NCR-001068 | NCR | Pumstead Portal - Damaged precast stair steps edge |  | Contr | HTM |  |  | 2015-06-10 | 2015-05-22 18:01 | -19 | 2015-05-13 16:16 | Civil - Civil Engineering General | 2000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | It has been noticed there are few places the precast stairs step are damaged.
| 01CV - Civils | Cxxx-NCR-001069 | NCR | NWP - CBGM No Fines Concrete Cube Failure at 28days |  | Contr | HTM | NOW - North Woolwich Portal (East) |  | 2015-05-28 | 2015-05-26 14:29 | -2 | 2015-05-14 09:51 | Civil - Civil Engineering General | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | 28 day cube failure - see attached. C8/10 at 28 days required. Also see cubes made by supplier.
| 01CV - Civils | Cxxx-NCR-001071 | NCR | AS BUILT SURVEY OF C__H PITS (TUNNEL DRAINAGE) IN RELATION TO DESIGN CHAINAGE |  | Contr | HTM |  |  | 2015-06-01 | 2015-05-26 17:36 | -6 | 2015-05-18 11:50 | Civil - Tunnelling | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Attached is as built survey of Tunnels from Plumstead to North Woolwich (eastbound and westbound).Highlighted in pink is the off set in relation to design catch pit chainage from the drawing Cxxx-OVE-D-DDD-CR001_Z-53032 Rev C02
| 01CV - Civils | Cxxx-NCR-001072 | NCR | Flood Wall – Gate 7 – Damaged Couplers in Base Slab |  | Contr | HTM | NOW - North Woolwich Portal (East) |  | 2015-06-02 | 2015-06-01 17:43 | -1 | 2015-05-19 16:44 | Civil - Civil Engineering General | 1500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Upon inspection of a small section of the B16 & B32 couplers in the base slab, it was noticed that one of the B16 couplers was damaged and beyond use. See attached location of single B16 that has been affected.
| 01CV - Civils | Cxxx-NCR-001073 | NCR | Tunnel Drive H - Westbound Plumstead to Woolwich Box (T1) - Tunnel Drainage Catchpit as built positions |  | Contr | HTM |  |  | 2015-06-03 | 2015-06-04 14:28 | 1 | 2015-05-20 10:20 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Westbound (T1) – PLU - WSB Ch. 22644 – 21330 Ref. PLU – NWP Catch Pit As-Built Survey Report - Cxxx-HTM-C-RGN-CR146_ST004-50055 Rev 1.0 Offsets > +/-25mm compared to design WB-SE-21378 WB-SE-22558 Chainage > +/-25mm compared to design WB-SE-21920 WB-SE-22520 WB-SE-22598 Dimension > +/-10 mm compared to design WB-SE-21378 WB-SE-21628 WB-SE-21920
| 01CV - Civils | Cxxx-NCR-001074 | NCR | Plumstead Portal - Surface finish to track drainage mass concrete |  | Contr | HTM |  |  | 2015-06-17 | 2015-06-11 16:40 | -6 | 2015-05-20 17:02 | Civil - Civil Engineering General | 2000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | On post concrete inspection of track drainage it is found concrete surface finish to the face of track drainage does not meet the requirements of the specification. there are honeycomb, grout loss, one on WB drainage approx. CH:91815 and EB approx. CH:90040 Please attached photo.
| 01CV - Civils | Cxxx-NCR-001075 | NCR | PLumstead Portal - 28 Day Compressive Cube Strength Fail for D wall North Capping beam 06 |  | Contr | HTM |  |  | 2015-06-18 | 2015-05-26 14:52 | -23 | 2015-05-21 10:32 | Civil - Civil Engineering General | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The C40/50 Design Mix 23 concrete used to form the top of the D wall capping beams 06, do not meet the requirements of BS EN 206-1. Refer to attached document for a summary of the cube results and the relevant locations within the works
| 01CV - Civils | Cxxx-NCR-001076 | NCR | Tunnel Drive H - First Stage Concrete Upstand - Difference in cast level - Interface Tunnel Portal Collar at Plumstead, |  | Contr | HTM |  |  | 2015-06-04 | 2015-06-04 14:40 | 0 | 2015-05-21 16:50 | Tunnelling - Linings - In-situ Concrete | 1000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | FSC upstand at the Plumstead Portal end of the Westbound T1 & Eastbound (T2) Tunnel Collars - 100mm step in the upstand Photo attached
| 01CV - Civils | Cxxx-NCR-001077 | NCR | Cxxx TUH Cross Passage 17 twin wall duct damaged and blocked duct passage under the Western Collar Slab |  | Crossrail | XRL | NOW - North Woolwich Portal (East) |  | 2015-06-05 | 2015-06-08 09:04 | 3 | 2015-05-22 17:24 | Tunnelling - Linings - In-situ Concrete | 2000 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Inadequate/insufficient tooling. | Completed |  | Poly twin wall duct found out to be damaged, collaped and blocked the duct passage under the Xp17 westbound collar floor. From the recent CCTV joint surveilance found out that there is a section of damaged of 450mm still remain inside the passage. DMI team has attempt to remove the damage duct using their extended drill attachement but not success due to the duct passage alignment found out to be not straight ( duct centre section lifted during concreting).
| 01CV - Civils | Cxxx-NCR-001079 | NCR | Cxxx North Woolwich Portal NWP Drainage Duct Joint Remedial Work |  | Crossrail | XRL | NOW - North Woolwich Portal (East) |  | 2015-06-05 | 2015-06-04 14:39 | -1 | 2015-05-22 17:39 | Civil - Drainage | 2500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | North Woolwich Portal drainage duct reference 100.009 and 102.009 connection joint to the track slab concrete drainage trench showing the bottom half of the circular surface area has been filled with concrete.
| 01CV - Civils | Cxxx-NCR-001080 | NCR | Plumstead - Reopen NCR-001023 RE: __ Marmadon Sewer Pumping Station - Rising Main - DI Pipe Connection MH06 - SOS - Ponding identified in CCTV Survey |  | Contr | HTM |  |  | 2015-06-10 | 2015-06-02 11:47 | -8 | 2015-05-27 09:24 | Civil - Utilities Engineering | 2500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Ref NCR Cxxx-NCR-001023 Ponding was viewed on the camera survey of the pipe at the __ connection. The ponding runs from the step at the __ coupling where it connects with the sewer wall, over the 1m rocker pipe and feathering out along the preceding 5.5m long pipe. The pipeline is formed of ductile iron pressure pipework laid to gradients to accommodate the flow from an upstream pumping station. There are no other gravity fed connections on the line. The upstream point being MH6 which was the termination chamber for the 400 OD PE pumping main and incorporated an internal backdrop pipe to take the flow from the pumping main height down to the invert level of the gravity sewer. The as-constructed pipework end to end is 25m long and has a fall of approx. 350mm, giving a gradient in excess of 1 in 70m fall, far exceeding the minimum self cleansing gradients required for drainage pipework.
| 01CV - Civils | Cxxx-NCR-001081 | NCR | Tunnel Drive H - Eastbound Crosspassage 17, Nadir - Sump drain - Water infiltrating Clay Pipe. |  | Contr | HTM |  |  | 2015-06-07 | 2015-06-08 12:48 | 1 | 2015-05-28 07:40 | Civil - Drainage | 2000 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Eastbound Crosspassage 17, Nadir - Sump drain - Water infiltrating Clay Pipe. Following prelim CCTV & Air Test water being made in the pipe run and not from the sumps or has been recorded. Approximate infiltration 80ltrs per hour over a 66m pipe Run. Full report to be submitted.
| 01CV - Civils | Cxxx-NCR-001083 | NCR | Plumstead Portal - Eastbound and Westbound walk way Out of tolerances |  | Contr | HTM |  |  | 2015-06-15 | 2015-07-14 09:46 | 29 | 2015-06-01 14:22 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Plumstead portal - eastbound and west bound walk ways as shown in as built survey report are marginally out of tolerances in plan position and vertical. As per the drawing No. Cxxx-CSY-S-DDD-CR148_PT005-00631 Construction tolerance on gauge for walkway edges = -0, +10mm horizontally (-ve towards track) -25. +0mm vertically.
| 01CV - Civils | Cxxx-NCR-001084 | NCR | NWP - Track Drainage T4 - Phase 1 - Damaged Concrete |  | Contr | HTM | NOW - North Woolwich Portal (East) |  | 2015-06-09 | 2015-06-04 14:37 | -5 | 2015-06-02 09:45 | Civil - Civil Engineering General | 500 |  | Damaged | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The top edge of concrete drainage slab became damaged when striking. See attached photo.
| 01CV - Civils | Cxxx-NCR-001085 | NCR | Tunnel Drive H - Eastbound - FSC Upstand - drainage Fall of Top Surface - isolated rings with negative slope |  | Contr | HTM |  |  | 2015-06-10 | 2015-06-08 12:56 | -2 | 2015-06-03 17:39 | Tunnelling - Linings - In-situ Concrete | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Eastbound PLU - WSB slope between survey reference point 1 & 2 Ring 246, 248,250,286, 816 slope between survey reference point 8 & 9 Ring 258 & 260
| 01CV - Civils | Cxxx-NCR-001086 | NCR | Omission of box out in Mass concrete foundation for 381 drainage pipe |  | Contr | HTM |  |  | 2015-06-17 | 2015-06-24 16:34 | 7 | 2015-06-03 17:56 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | __ has cast mass concrete foundation above 381 sewer pipe without box out above 381 sewer pipe. the box out was required for allowance of rocker pipe connection to MH C401.
| 01CV - Civils | Cxxx-NCR-001087 | NCR | Tunnel Drive H - First Stage concrete Upstand - Eastbound - Top Surface Slope - Isolated rings where slope gradient exceeds acceptable range 1:20 to 1:60 |  | Contr | HTM |  |  | 2015-06-10 | 2015-06-08 15:23 | -2 | 2015-06-03 18:02 | Tunnelling - Linings - In-situ Concrete | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | unnel Drive H - First Stage concrete Upstand - Eastbound - Top Surface Slope - Isolated rings where slope gradient exceeds acceptable range 1:20 to 1:60 Eastbound PLU - WSB Gradient of slope exceeds allowable range between survey points 1 & 2 or 8 & 9 see attached list of Rings
| 01CV - Civils | Cxxx-NCR-001088 | NCR | Portals and Woolwich Box - Tunnel Collar to Final Ring Mastic Sealant - Replace material for LUL Compliance |  | Crossrail | PDP |  |  | 2015-06-10 | 2015-06-11 16:39 | 1 | 2015-06-04 10:13 | Civil - Civil Engineering General | 1000 |  | Material | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | For the collar to final ring connection, in the Woolwich Box collars, the design requires a backing rod with a mastic seal as shown in Cxxx-OVE-T-DDL-CR001_Z-73461 Rev C01, Detail 3. A similar detail applies to the collars in the portal. Works were undertaken by the Portals and Box team, and a polysulphide sealant product called Geocel 201 was used as per MCR Cxxx-HTM-C-CER-CR148-50112 Rev 2.0. On further review of the product used, it is rated as Class F for fire resistance. As the product in located in the tunnel area, it is not compliant with LUL standards or Cxxx requirements as per CEDS Part 1 Clause 1.16 Fire Design (CRL1-XRL-O6-STD-CR001-00003) and Cxxx KT10 Clause KF10.1401 Fire Resistance (Cxxx-OVE-Z4-RSP-CR001-00001).
| 01CV - Civils | Cxxx-NCR-001089 | NCR | Plumstead portal - head housse drainage - The alignment of the DN100 ventilation pipework |  | Contr | HTM |  |  | 2015-06-10 | 2015-06-11 13:49 | 1 | 2015-06-08 08:25 | Civil - Drainage | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Conflicting information on drawings | Completed |  | The alignment of the DN100 ventilation pipework shown on section Cxxx-CSY-D-DDD-CR148_PT005-01011 (drainage drawing) did not match the position of the drainage opening within the roof slab shown on Cxxx-CSY-S-DDA-CR148_PT005-01203 (structural drawing). To match the pipework at the top and bottom, two 90 degree bends were added as shown in the attached mark up drawing ‘Ventilation and roof outlet solution.
| 01CV - Civils | Cxxx-NCR-001090 | NCR | Plumstead portal - head house drainage - Seepage pipework |  | Contr | HTM |  |  | 2015-06-22 | 2015-06-11 14:04 | -11 | 2015-06-08 08:46 | Civil - Drainage | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | The seepage pipework shown on Cxxx-CSY-D-DDD-CR148_PT005-01205 is not practical to construct as shown due to the push fit sockets needing to be pushed in opposite directions over a fixed length. For constructability __ installed 1 no. straight coupling on the vertical section against the headwall. See attached mark up drawing ‘Seepage pipework solution’ for details
| 01CV - Civils | Cxxx-NCR-001091 | NCR | Plumstead Portal - Rising main alignment and pipework |  | Contr | HTM |  |  | 2015-06-22 | 2015-06-11 13:54 | -11 | 2015-06-08 09:00 | Civil - Drainage | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | There are a number of issues with the rising main design shown on Cxxx-CSY-D-DDL-CR148_PT005-01013 and the scheduled pipework on Cxxx-CSY-D-DDL-CR148_PT005-01014. The issues were: 1). the socket spigot lengths detailed as RM4 (6000 mm) were longer than what was readily available from our suppliers, 5500 mmm long lengths were the longest available. 2). 30 degree push fit bends are not a standard item in DN300 DI pipework, 22.5 degree bends are available. 3). The scheduled lengths on drawing Cxxx-CSY-D-DDL-CR148_PT005-01014 do not match the required lengths of pipe to construct the rising main. ie RM 8 is shown to be 1640 mm long however this distance is longer than 4000 mm when scaled. Alternative lengths and additional pipe were needed to construct the rising main. 4). The alignment of the rising main clashed with the base of MH 401 and needed to be moved north to avoid this manhole; additional pipework was required. To work around the issues above, __ have installed the rising main as shown in the attached marked up drawing and photo labelled ‘Rising main solution 1’ and ‘Rising main solution2’.
| 01CV - Civils | Cxxx-NCR-001092 | NCR | Plumstead Portal - Rising main drainage - Thrust block construction |  | Contr | HTM |  |  | 2015-06-10 | 2015-06-16 15:47 | 6 | 2015-06-08 09:09 | Civil - Drainage | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | The thrust blocks shown on Cxxx-CSY-D-DDD-CR148_PT005-01204 are impractical to safely construct and form up inside a trench, nor do they provide the restraint required to insert the pipes within the socket joints. Thrust blocks 1 and 2 needed to be enlarged to allow the pipework on the 22.5 degree bends to be restrained while the next section of pipe was inserted in the socket. Thrust block 1 was constructed in two pours to allow the next length of pipe to be inserted in the 22.5 degree socket joint. The thrust blocks were constructed as detailed in the attached mark up drawing ‘Rising main solution 1’.
| 01CV - Civils | Cxxx-NCR-001093 | NCR | Plumstead Portal - Head house drainage - Roof outlet drainage |  | Contr | HTM |  |  | 2015-06-22 | 2015-06-16 16:16 | -6 | 2015-06-08 09:25 | Civil - Drainage | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | The roof drainage shown on drawing Cxxx-CSY-D-DDD-CR148_PT005-01201, Section D-D and Section E-E clashed with the ventilation pipework once set out as per the structural drawing Cxxx-CSY-S-DDA-CR148_PT005-01203. To avoid this clash, __ installed the outlet drainage vertically as shown in the attached mark up drawing ‘Ventilation and roof outlet solution
| 01CV - Civils | Cxxx-NCR-001094 | NCR | Tunnel Drive H - FSC - Eastbound Tunnels - List of UTX measured short extending above Upstand |  | Contr | HTM |  |  | 2015-06-15 | 2015-06-11 16:43 | -4 | 2015-06-08 10:00 | Tunnelling - Linings - In-situ Concrete | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Attached list of extensions of UTX measured above the FSC upstand which are shorter than the minimum specified length by more than 25mm.
| 01CV - Civils | Cxxx-NCR-001095 | NCR | Plumstead Portal - Locally reduced fireproofing thickness in order to install seepage pipework |  | Contr | HTM |  |  | 2015-06-23 | 2015-06-18 17:18 | -5 | 2015-06-09 08:55 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | In order to install the pipework as per the IFC drawings, __ locally reduced the thickness of the fireproofing by 15mm.
| 01CV - Civils | Cxxx-NCR-001096 | NCR | Plumstead Portal - Head House Rool Level - Revised Detail to Cantilever Upstands not covered in FCD |  | Contr | HTM |  |  | 2015-06-17 | 2015-06-16 16:17 | -1 | 2015-06-10 10:04 | Civil - Civil Engineering General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Detail Change not agreed in FCD before works completed on site.
| 01CV - Civils | Cxxx-NCR-001097 | NCR | Plumstead Portal - Drainage Connection Attenuation tank - MHC312 - Incorrect materials DI to Plastic Flange adapter |  | Contr | HTM |  |  | 2015-06-17 | 2015-06-18 17:14 | 1 | 2015-06-10 10:16 | Civil - Drainage | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Design Problem - Conflicting information on drawings | Completed |  | Incomplete Works due to selection procurement and installation of incompatible materials. Unable to connect DI to Plastic Drainage wit 225mm Flange adapter as detailed on Drawing because Plastic Pipe installed is incompatible with Flange adapter use.
| 01CV - Civils | Cxxx-NCR-001098 | NCR | Incompletion of Pressure Testing to Pipe Work at Plumstead Portals |  | Crossrail | XRL |  |  | 2015-06-24 | 2015-06-19 16:20 | -5 | 2015-06-10 19:15 | Civil - Civil Engineering General | 500 |  | Incomplete Works | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Pressure testing is incomplete to the following pipe work at Plumstead Portal: 1) 225mm pipe work from attenuation tank to MH C312 2) 225mm pipe work from MH C312 to existing MH on cobbled road 3) pipe work from CP to attenuation tank 4) 375mm dia. ductile pipe work from track drainage to portal sump 5) 100mm dia. ductile pipe from lift shaft to portal sump 6) 100mm dia. ductile pipe seepage drainage lines from headhouse to portal sump Pressure testing of pipe work is to be completed following installation of pipe work, and is detailed as a "hold" point on the ITP.
| 01CV - Civils | Cxxx-NCR-001099 | NCR | Plumsread Portal - discrepancies in CRL head house roof slab reinforcement drawing |  | Contr | HTM |  |  | 2015-07-10 | 2015-06-23 14:57 | -17 | 2015-06-12 15:57 | Civil - Civil Engineering General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | On the pre pour inspection of head house upper roof slab at 100.030 poured on 19/05/2015 the discrepancies in CRL reinforcement drawing were picked up at the pre-pour inspection. the discrepancy was the open link omitted for up stand reason being the __ has installed the U bar in the wall below for the up stand already and was difficult to installed the link. Please see attach mark up detailed drawing.
| 01CV - Civils | Cxxx-NCR-001100 | NCR | Plumstead portal - 375 dia discharge pipe air test fail |  | Contr | HTM |  |  | 2015-06-30 | 2015-06-19 16:26 | -11 | 2015-06-16 17:39 | Civil - Drainage | 1500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | East bound and west bound 375mm dia. track drainage discharge pipe air test fail. neither of pipes hold the air test for 5 minutes as per requirement of specification/ITP. the test has been witnessed by Paul Gorman (CRL field engineer) west bound pipe dropped the pressure after a period of 3 minutes & 5 seconds East bound pipe dropped the pressure after a period of 2 minutes & 40 seconds
| 01CV - Civils | Cxxx-NCR-001101 | NCR | Plumstead portal - North & South Capping Beam - application of additional protection to burried concrete |  | Contr | HTM |  |  | 2015-07-08 | 2015-07-09 13:01 | 1 | 2015-07-01 12:04 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Ref. Cxxx- PWK 00111 PP- North and South capping beam - application of additional protection to buried concrete PP- North and South capping beam CH:92060 to 92232 - application of additional protection to buried concrete (Black Bitumen Paint) construction of capping beam was completed at Plumstead portal and the ground level was not confirm at that time RC work completion, therefore application Black Bitumen Paint was not done. Application of black bitumen completed by exposing most of the capping beam but could not be applied below the level of the blinding.
| 01CV - Civils | Cxxx-NCR-001102 | NCR | Plumstead Portal- Concrete finish to West bound walk way slab |  | Contr | HTM |  |  | 2015-07-14 | 2015-07-10 09:35 | -4 | 2015-07-07 09:35 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Ref. Cxxx-PWK-00141 finish to portal walkways does not meet the specified U1 finish; remedial proposal to “use as is”.
| 01CV - Civils | Cxxx-NCR-000054 | NCR | Incomplete Material Approval Application |  | Contr |  | CON - Connaught Tunnel (East) |  | 2011-12-16 | 2012-03-06 10:57 | 81 | 2011-12-12 | Civil - Fill | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | Use of Type 1 backfill material before formally being accepted by CRL
| 01CV - Civils | Cxxx-NCR-000055 | NCR | Failure to notify of witness point in ITP |  | Contr |  | CON - Connaught Tunnel (East) |  | 2011-12-16 | 2012-03-06 11:00 | 81 | 2011-12-12 | Civil - Fill | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | Failure to notify of witness point in ITP
| 01CV - Civils | Cxxx-NCR-000068 | NCR | Use of unapproved material |  | Contr |  | CON - Connaught Tunnel (East) |  | 2012-01-17 | 2012-04-27 18:08 | 101 | 2012-01-10 | Civil - Fill | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | 6F2 material was used to backfill the Archaeology hole in the west site before material approval.
| 01CV - Civils | Cxxx-NCR-000096 | NCR | Failure to notify witness points |  | Contr |  | CON - Connaught Tunnel (East) |  | 2012-02-28 | 2012-05-24 08:53 | 86 | 2012-02-14 | Surveying - Instrumentation and Monitoring | 500 |  |  | Use As-Is |  | Complete |  | Completed |  | Failure to notify witness points for installation of 3 separate Automated Total Stations (two in east single tunnel, one on East End tunnel wall to monitor DLR viaduct).
| 01CV - Civils | Cxxx-NCR-000097 | NCR | 6F5 material was used at site without Project Manager's approval |  | Contr |  | CON - Connaught Tunnel (East) |  | 2012-02-20 | 2012-03-02 16:41 | 11 | 2012-02-15 | Civil - Fill | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | 6F5 material was placed at 4 Piling Mat locations at the below chainages; IRF 032 - Chainage SE 18700 IRF 034 - Chainage SE 18970 IRF 035 - Chainage SE 18950 IRF 036 - Chainage SE 18930 6F5 was not approved at the time of placement and also contained organic materials inclusive of; grass, soil, wood pieces and tree roots.
| 01CV - Civils | Cxxx-NCR-000117 | NCR | Concrete for Controlled Modulus Column (CMC) |  | Contr |  | CON - Connaught Tunnel (East) |  | 2012-03-16 | 2012-04-26 09:37 | 41 | 2012-03-05 | Civil - Civil Engineering General | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | Specification KF10.3221(b) and general good practice requires that ready mixed concrete is laid in its final position within 2 hours of the introduction of cement to the aggregate (i.e. batching time), unless a different time is agreed with the Project Manager. The concrete for the CMC test piles on East Surface Rail on 15/02/2012 exceeded this 2 hour limit. The time of batching for ticket No. 629376 was 11.26 and the time of discharge completion was 15:10. Records show that drilling for the final pile began at 14:51.
| 01CV - Civils | Cxxx-NCR-000120 | NCR | Concrete for Controlled Modulus Column (CMC) |  | Contr |  | CON - Connaught Tunnel (East) |  | 2012-03-16 | 2012-04-26 15:26 | 41 | 2012-03-06 | Civil - Civil Engineering General | 500 |  | System Defect | Use As-Is |  | Complete |  | Completed |  | Delivered concrete for CFA Test Pile on 01/03/2012 did not conform with CFA concrete on two occasions. Delivery tickets checked at approximately 10am and 2.30pm. Approved concrete for CFA piles has Grade C32/40, but delivered concrete had Grade 20/25.
| 01CV - Civils | Cxxx-NCR-000125 | NCR | Pile Testing |  | Contr |  | CON - Connaught Tunnel (East) |  | 2012-05-01 | 2012-05-15 11:35 | 14 | 2012-04-30 | Civil - Civil Engineering General | 500 |  | Design | Use As-Is |  | Complete |  | Completed |  | The zone tests and isolated plate tests we have carried out are a combination of the ICE Ground Treatment 1987 specification and Crossrail specific criteria. Therefore the UKAS certification of __ does not directly cover these test, nor would any other test company. __ / PMC have been used to carry out the isolated plate test and zone tests. Their accreditation (attached) covers plate test loading (BS 1377-9:1990) (pg 5 1of accreditation)and static load testing (ICE SPERW: 2007) (Pg 44 of accreditation) , in fact they are the only company within the UK that can carry out static load tests with UKAS accreditation.
| 01CV - Civils | Cxxx-NCR-000131 | NCR | Commencement of Piling |  | Contr |  | CON - Connaught Tunnel (East) |  | 2012-03-23 | 2012-04-03 18:00 | 11 | 2012-03-16 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | Although the correct documentation was submitted to Crossrail in advance of the piling operation, the permit to load had not been signed. The document was signed and the piling works then commenced before a member from Crossrail came to site and viewed the signed documentation. There was a period of approximately half an hour between piling starting and Crossrail signing the IRF releasing the hold point
| 01CV - Civils | Cxxx-NCR-000134 | NCR | Formation Bay W6 & W5 |  | Contr |  | CON - Connaught Tunnel (East) |  | 2012-12-20 | 2012-11-20 15:43 | -30 | 2012-11-08 | Civil - Geotechnical Engineering | 500 |  | Damaged | Rework |  | Complete |  | Completed |  | Formation is damaged after being exposed to the weather in Bay W6. Area will have to be scraped to remove 'slush' resulting in formation being out of level toelrance.
| 01CV - Civils | Cxxx-NCR-000136 | NCR | CMC Test Piles - Reinforcement not central within pile |  | Contr |  | CON - Connaught Tunnel (East) |  | 2012-03-25 | 2012-03-29 11:38 | 4 | 2012-03-20 | Civil - Civil Engineering General | 500 |  | System Defect | Repair |  | Complete |  | Completed |  | Please see attached sketch Cxxx-SK-0059 UXO and Trial Pile Co-ordinates West Compound. This shows the locations and references of CMC Test piles in the West Compound. Pile references TW1, TW2, TW3, TW4, TW7 were shown to have had reinforcement installed too high within the pile. From this it could be observed that TW1, TW2, TW3 and TW7 had reinforcement which was not central within the pile. Please see attached photographs for TW1, TW2, TW3, TW4, TW7.
| 01CV - Civils | Cxxx-NCR-000137 | NCR | CMC Test Piles - Reinforcement level outside tolerance |  | Contr |  | CON - Connaught Tunnel (East) |  | 2012-03-26 | 2012-03-29 11:47 | 3 | 2012-03-20 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | Please see attached sketch Cxxx-SK-0059 UXO and Trial Pile Co-ordinates West Compound. This shows the locations and references of CMC Test piles in the West Compound. Pile references TW1, TW2, TW3, TW4, TW7 were shown to have had reinforcement installed too high within the pile. (please see attached photographs) The deviation from the trimming level of the pile were TW1: +1.047mm TW2: +347m TW3: +485mm TW4: +651mm TW7: +44mm
| 01CV - Civils | Cxxx-NCR-000138 | NCR | CMC Test Piles - Necking of piles |  | Contr |  | CON - Connaught Tunnel (East) |  | 2012-03-26 | 2012-04-03 18:00 | 8 | 2012-03-20 | Civil - Civil Engineering General | 500 |  | System Defect | Repair |  | Complete |  | Completed |  | Please see attached sketch Cxxx-SK-0059 UXO and Trial Pile Co-ordinates West Compound. This shows the locations and references of CMC Test piles in the West Compound. Pile references TW7 and TW9 have experiences necking within the pile. This has created voids around the sides of the pile. Please see photographs ‘TW6a’ and ‘TW9’
| 01CV - Civils | Cxxx-NCR-000139 | NCR | CMC Test Piles - Pile diameter too small |  | Contr |  | CON - Connaught Tunnel (East) |  | 2012-03-28 | 2012-04-03 18:05 | 6 | 2012-03-20 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | Please see attached sketch Cxxx-SK-0059 UXO and Trial Pile Co-ordinates West Compound. This shows the locations and references of CMC Test piles in the West Compound. TW2 and TW3 have a diameter which are less than 320mm in one orientation. These diameters are 260mm and 290mm respectively. Please see photographs ‘TW2’ and photograph ‘TW3’ •Pile T2 has diameters of 300mm and 260mm and an approximate cross sectional area of 0.062m2 •Pile T3 has diameters of 390mm and 290mm and an approximate cross sectional area of 0.091m2 •The designed pile should have diameters of 320mm and a cross sectional area of 0.080m2
| 01CV - Civils | Cxxx-NCR-000146 | NCR | Commencement of grouting works |  | Contr |  | CON - Connaught Tunnel (East) |  | 2012-03-30 | 2012-03-29 12:03 | -1 | 2012-03-28 | Civil - Civil Engineering General | 500 |  |  | Use As-Is |  | Complete |  | Completed |  | On Friday 23rd March 2012 the piling subcontractor Vibro __ wished to carry out remedial works to CMC test piles in the west compound. This involved updating the current trial pile method statement (reference: Cxxx-VIN-C-GMS-CR146_ST003-50053 rev7) On the morning of Friday 23rd March there was a power cut in the site offices meaning that the document could not be printed, signed and uploaded to eB. The methodology had been verbally approved by __ and Paul Edwards and a verbal agreement was in place between CRL and __ for the work to commence. The works were carried out before the document had been signed and uploaded to eB.
| 01CV - Civils | Cxxx-NCR-000147 | NCR | Reinforcement out of tolerance |  | Contr |  | CON - Connaught Tunnel (East) |  | 2012-03-30 | 2012-04-30 09:31 | 31 | 2012-03-28 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | The reinforcement for B5 is 287mm high.
| 01CV - Civils | Cxxx-NCR-000149 | NCR | Reinforcement depth not achieved |  | Contr |  | CON - Connaught Tunnel (East) |  | 2012-04-06 | 2012-04-13 16:20 | 7 | 2012-03-29 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | Pile numbers B4 and B5 do not achieve the depth within the gravels as required. Existing levels are as follows B4 gravel depth: 96.5m B4 reinforcement depth: 95.58m B4 Depth achieved: 920mm B5 gravel depth: 96.5m B5 reinforcement depth: 95.59m B5 depth achieved: 910mm These results show that these two piles have not achieved the required 925mm
| 01CV - Civils | Cxxx-NCR-000155 | NCR | Gravel Depth Estimation |  | Contr |  | CON - Connaught Tunnel (East) |  | 2012-06-14 | 2012-06-12 14:40 | -2 | 2012-04-04 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | The works were not carried out in accordance with the approved method statement. The CFA piles were installed to estimated depths, based on the ground information, interpolated from boreholes CH42CPT, CH43CPT and CH44CPT. During installation a reliable estimate of the gravel level could not be determined by rig data provided to the driver.
| 01CV - Civils | Cxxx-NCR-000156 | NCR | Reinforcement too high CMC East Trial Piles. |  | Contr |  | CON - Connaught Tunnel (East) |  | 2012-04-05 | 2012-04-30 09:13 | 25 | 2012-04-02 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | Piles TE3, TE4, TE7, TE11, TE12, TE13 in the east CMC trial pile area have reinforcement which has been installed too high. TE3:84mm too high TE4: 425mm too high TE7: 74mm too high TE11: 229mm too high TE12: 667mm too high TE13: 258mm too high
| 01CV - Civils | Cxxx-NCR-000157 | NCR | Reinforcement not central - East CMC Trial Piles |  | Contr |  | CON - Connaught Tunnel (East) |  | 2012-04-05 | 2012-04-30 09:15 | 25 | 2012-04-02 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | Piles TE3, TE11, TE13 in the east CMC trial pile area have reinforcement which has not been installed within the tolerance. TE3:95m outside tolerance TE11: 35mm outside tolerance TE13: 25mm outside tolerance
| 01CV - Civils | Cxxx-NCR-000159 | NCR | Piling Rig Calibration |  | Contr |  | CON - Connaught Tunnel (East) |  | 2012-04-11 | 2012-07-13 09:02 | 93 | 2012-04-04 | Civil - Civil Engineering General | 500 |  | Equipment Breakdown | Rework |  | Complete |  | Completed |  | __ has not provided evidence that equipment fitted to the piling rig and used for monitoring is calibrated at the start of the works. This includes equipment for measuring the volume of concrete pumped (volume pumped in each pump stroke) and pile verticality.
| 01CV - Civils | Cxxx-NCR-000165 | NCR | CFA Pile Integrity Testing |  | Contr |  | CON - Connaught Tunnel (East) |  | 2012-04-27 | 2012-04-30 16:34 | 3 | 2012-04-13 | Civil - Civil Engineering General | 500 |  | Planning | Use As-Is |  | Complete |  | Completed |  | As of Friday 17th April, no integrity testing has been undertaken for CFA piles installed. As such, piles B1 to B55 inclusive and C1 to C41 inclusive, which were installed between 13th March 2012 and 26th March 2012 have not been subject to integrity testing between the 7-21 days time window.
| 01CV - Civils | Cxxx-NCR-000180 | NCR | Failing to follow required test procedure on first plate load test on single CMC on 17/04/2012 |  | Contr |  | CON - Connaught Tunnel (East) |  | 2012-04-30 | 2012-05-08 16:50 | 8 | 2012-04-25 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | 1. First test on TW5 started before CRL arrive on site to inspect (sub contractor commenced the test even before __ on site , IRF has been sent to CRL and __ accompanied CRL engineers) 2. Technicians not following exact requiremnts as per ICE specification ( they use the correct load but did not follow exact deflection monitoring procedure) 3. Technicians were not briefed on approved MS and ITP.
| 01CV - Civils | Cxxx-NCR-000193 | NCR | CMC Test Piles for East Zone Test 1 |  | Contr |  | CON - Connaught Tunnel (East) |  | 2012-05-04 | 2012-05-01 08:13 | -3 | 2012-04-30 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | Following the preparation of the CMC head piles in order to proceed with the zone test it was found that TE1, TE2, TE4 have an inadequate pile head diameter. column head size: TE1: 320 x 240mm – Av 310mm dia TE2: 320 x 175mm – Av 270mm dia TE4: 300 x 240mm – Av 300mm dia
| 01CV - Civils | Cxxx-NCR-000196 | NCR | Damage to CMC TE6 |  | Contr |  | CON - Connaught Tunnel (East) |  | 2012-05-02 | 2012-05-23 14:46 | 21 | 2012-05-01 | Civil - Civil Engineering General | 500 |  | Damaged | Rework |  | Complete |  | Completed |  | A crack has been formed approx 1m below cut off level. The crack was a clean horizontal fracture. It will not affect the results of the isolated plate load test.
| 01CV - Civils | Cxxx-NCR-000197 | NCR | CMC Test Pile TE7 |  | Contr |  | CON - Connaught Tunnel (East) |  | 2012-08-13 | 2012-08-02 10:31 | -11 | 2012-05-01 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | Following the preparation of the CMC head in order to proceed with the zone test it was found that TE7 column had the minimum diameter of 320mm however a void approx 40mm diameter was present just below cut off level approx 80mm and clay was observed within the column. This should not affect the settlement of the column. Integrity test has been caried out (see attached) no defects found.
| 01CV - Civils | Cxxx-NCR-000211 | NCR | Pile 68F Installed in the wrong place |  | Contr |  | CON - Connaught Tunnel (East) |  | 2012-05-18 | 2012-05-29 16:57 | 11 | 2012-05-14 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Reject |  | Complete |  | Completed |  | Pile number 68F was installed co-ordinates X=91369.286, Y=35424.378 which are the co-ordinates from Ground Improvement drawing Cxxx-OVE-C-DDA-CR001_Z-31125 C02. This pile has been relocated for the purpose of OHLE piles. The actual position was installed and now this pile is redundant.
| 01CV - Civils | Cxxx-NCR-000214 | NCR | Over-excavation using of invert reprofiling |  | Contr |  | CON - Connaught Tunnel (East) |  | 2012-05-25 | 2012-07-30 14:09 | 66 | 2012-05-17 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | In remote places between chainages 18485 and 18510 on the Eastern approach ramp, the invert has been reprofiled down between 60mm and 110mm (15mm-65mm out of tolerance)
| 01CV - Civils | Cxxx-NCR-000223 | NCR | Use of unapproved Material to Backfill Zone Test 1 on East |  | Contr |  | CON - Connaught Tunnel (East) |  | 2012-06-26 | 2012-07-06 16:18 | 10 | 2012-05-30 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | Unapproved reclaimed material from the tunnel invert was reused to backfill Zone Test 1 on the East, Systemand possible material failure
| 01CV - Civils | Cxxx-NCR-000226 | NCR | CMC Test Pile TE10 |  | Contr |  | CON - Connaught Tunnel (East) |  | 2012-05-30 | 2012-05-24 14:26 | -6 | 2012-05-23 | Civil - Civil Engineering General | 500 |  | Damaged | Reject |  | Complete |  | Completed |  | Following break down and preparation of the CMC head it was found that two of the piles (TE12 & TE13) had necking and TE10 had clay inclusions within the pile it was found that TE10 was fractured at the top of the pile.
| 01CV - Civils | Cxxx-NCR-000228 | NCR | CMC Test Pile TE6 |  | Contr |  | CON - Connaught Tunnel (East) |  | 2012-05-24 | 2012-06-21 09:02 | 28 | 2012-05-23 | Civil - Civil Engineering General | 500 |  | Damaged | Reject |  | Complete |  | Completed |  | TE7 did not meet the necessary specification of maximum 15mm settlement at 250% working load. It had a recorded settlement of 21.58mm but due to the instrument setup __ could not acheive any further readings.
| 01CV - Civils | Cxxx-NCR-000237 | NCR | Grouting - Deviation from approved Method Statement |  | Contr |  | CON - Connaught Tunnel (East) |  | 2012-06-01 | 2012-06-12 15:07 | 11 | 2012-05-28 | Civil - Civil Engineering General | 500 |  | Planning | Use As-Is |  | Complete |  | Completed |  | As per the attached observation report, __ were observed deviating from their approved Method Statement following changes to assumed site conditions. These deviations were: - Stuffing box not being installed in an area of dense clay - Cutting shoe being used instead of a 'lost bit' technique - 0.5m long casings being used, not 1m. - Drill casing withdrawn before insertion of TaM. Other than the reduced casings size, these were all due to encountering stiff clay immediately behind the tunnel wall .
| 01CV - Civils | Cxxx-NCR-000246 | NCR | Concrete used for CMC on East without Approved MCR |  | Contr |  | CON - Connaught Tunnel (East) |  | 2012-08-13 | 2012-08-09 16:55 | -4 | 2012-06-18 | Civil - Civil Engineering General | 500 |  | System Defect | Use As-Is |  | Complete |  | Completed |  | CMC Concrete without an approved MCR was used (Same mix design but different batching plant) . The concrete was used in the following columns: 514 ABC 513 ABC 512 ABC 511 ABC 510 ABC 509 ABC 508 AB 478 BC 477 ABC 476 ABC
| 01CV - Civils | Cxxx-NCR-000248 | NCR | CFA test pile - Gravel depth |  | Contr |  | CON - Connaught Tunnel (East) |  | 2012-06-15 | 2012-06-14 13:34 | -1 | 2012-06-11 | Civil - Civil Engineering General | 500 |  | Planning | Use As-Is |  | Complete |  | Completed |  | During installation a reliable estimate of the gravel level could not be determined by rig data provided to the driver.
| 01CV - Civils | Cxxx-NCR-000259 | NCR | __ cables between CMC lines 166 and 167 ( west compound) |  | Contr |  | CON - Connaught Tunnel (East) |  | 2012-08-13 | 2012-08-17 13:35 | 4 | 2012-06-14 | Civil - Civil Engineering General | 500 |  | Workmanship | Rework |  | Complete |  | Completed |  | The Survey information of the concrete surround on the serco cables provided to CRL (under PMI_0032) is not correct.
| 01CV - Civils | Cxxx-NCR-000268 | NCR | Fail to raise an IRF prior to commence the test on CFA trial pile |  | Contr |  | CON - Connaught Tunnel (East) |  | 2012-06-22 | 2012-07-19 13:34 | 27 | 2012-06-18 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | __ did not raise formal Inspection Request to CRL(witness inspection prior to static load test) , However CRL was made aware about the test start time and request to do an inspection (verbally).
| 01CV - Civils | Cxxx-NCR-000270 | NCR | Incorrect Trial Hole Data submitted for __ Power Cables Trial Hole 9 |  | Contr |  | CON - Connaught Tunnel (East) |  | 2012-11-30 | 2012-11-13 12:02 | -17 | 2012-10-17 | Civil - Civil Engineering General | 500 |  | Workmanship | Rework |  | Complete |  | Completed |  | Conflicting information for the line of the __ cable was provided on the drawing submitted to Crossrail for Trial Hole 9, to verify the line trial hole 9 was re excavated and on excavation it was found that not only was the line incorrect but the level recorded for the service was incorrect. Most likely cause for error was error in setup of the machine,
| 01CV - Civils | Cxxx-NCR-000271 | NCR | Damage to CMC 623F Bay E16 |  | Contr |  | CON - Connaught Tunnel (East) |  | 2012-11-21 | 2012-11-01 17:12 | -20 | 2012-10-17 | Civil - Geotechnical Engineering | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | During excavation of the downstand beam close to row F, column 623F has been damaged causing a crack around the perimeter approximately 500mm below COL
| 01CV - Civils | Cxxx-NCR-000272 | NCR | Installation of CMC 383C whilst currently on Hold |  | Contr |  | CON - Connaught Tunnel (East) |  | 2012-07-26 | 2012-08-01 09:17 | 6 | 2012-07-04 | Civil - Civil Engineering General | 500 |  | System Defect | Use As-Is |  | Complete |  | Completed |  | CMC 383C was installed on 15/06/2012 whilst rows 333 -383 were still on hold. Cause - Surveyor had marked out an extra column, this was not checked by the engineer.
| 01CV - Civils | Cxxx-NCR-000273 | NCR | Invert Reprofile Low Spots 17687-17658 |  | Contr |  | CON - Connaught Tunnel (East) |  | 2012-07-31 | 2012-08-01 12:26 | 1 | 2012-06-19 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | In certain areas, as detailed in the attached spreadsheet, sketch and IRF between the chainages 17687 and 17658 on the western approach ramp, the invert was reprofiled lower than the allowable tolerance by up to 50mm.
| 01CV - Civils | Cxxx-NCR-000278 | NCR | Reduced diameter column within the permanent zone test area-column number 140C |  | Contr |  | CON - Connaught Tunnel (East) |  | 2012-08-13 | 2012-08-17 13:37 | 4 | 2012-06-20 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | CMC 140C (one of the column on permanent zone test area) has reduced diameter at its cut off level. Based on the circumference of 803mm equivalent diameter is 256mm
| 01CV - Civils | Cxxx-NCR-000291 | NCR | Position and size of column 115A |  | Contr |  | CON - Connaught Tunnel (East) |  | 2012-07-20 | 2012-07-02 14:50 | -18 | 2012-06-22 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | 1.Design position of the column no 115A is 91454.228, 35426.499 and the installed position is 91454.143, 35426.562. These coordinates suggest column 115A is 105.8mm off from the design position 2. The measured perimeter of the column 115A is 985mm.Diameter of a circular shape equivalent to 985mm perimeter is 313.5mm;
| 01CV - Civils | Cxxx-NCR-000292 | NCR | Column no 115B size and tolerance |  | Contr |  | CON - Connaught Tunnel (East) |  | 2012-07-20 | 2012-07-03 15:30 | -17 | 2012-06-22 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | Design position of the column no 115B is 91453.9894, 35424.714and the installed position is 91453.789, 35424.728. These coordinates suggest column 115B is 200.8mm off from the design position The measured perimeter of the column 115B is 970mm.Diameter of a circular shape equivalent to 970mm perimeter is 308mm
| 01CV - Civils | Cxxx-NCR-000295 | NCR | Column no 116B position |  | Contr |  | CON - Connaught Tunnel (East) |  | 2012-07-20 | 2012-07-24 17:09 | 4 | 2012-06-22 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | Design position of the column no 116B is 91455.775, 35424.443 and the installed position is 91455.783, 35424.557. These coordinates suggest column 116B is 114mm off from the design position
| 01CV - Civils | Cxxx-NCR-000301 | NCR | Tunnel Mechanical Services - Workign without an approved ITP |  | Contr |  | CON - Connaught Tunnel (East) |  | 2012-07-20 | 2012-07-03 14:31 | -17 | 2012-06-25 | Civil - Civil Engineering General | 500 |  | Planning | Use As-Is |  | Complete |  | Completed |  | Following numerous meetings between __, __ and CRL, both the mechanical and electrical ITP's were updated togerther. Unfortunately a communication error led to only the electrical ITP being updated, and upon approval work commenced. The mechanical installation commenced before the error was realised.
| 01CV - Civils | Cxxx-NCR-000310 | NCR | Mechanical Services Installation missed inspection point |  | Contr |  | CON - Connaught Tunnel (East) |  | 2012-08-03 | 2012-08-01 12:30 | -2 | 2012-07-03 | Civil - Civil Engineering General | 500 |  | Planning | Use As-Is |  | Complete |  | Completed |  | This NCR is further to NCR 301 which details the mix up between the Mechanical and Electrical ITPs. The Electrical ITP does not have a 'Witness' point for for Inspection 8, whilst the Mechinical ITP does. The same sequence of works was followed as per the Electrical ITP and consequently Inspection 8 of the Mechanical ITP was missed. The subcontractor 'Hold' and __ 'Witness' were both carried out.
| 01CV - Civils | Cxxx-NCR-000314 | NCR | Column no 140B tolerance |  | Contr |  | CON - Connaught Tunnel (East) |  | 2012-08-13 | 2012-08-17 13:43 | 4 | 2012-07-06 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | The design position of the column no 140B is E=91498.4101, N= 35416.7312 and the installed position is E=91498.390, N=35416.585. These coordinates suggest that the column 140B is 147.5mm out of the design position.
| 01CV - Civils | Cxxx-NCR-000315 | NCR | Column no 140C Tolerance |  | Contr |  | CON - Connaught Tunnel (East) |  | 2012-08-13 | 2012-08-17 13:41 | 4 | 2012-07-06 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | The design position of the column no 140C is E=91498.0779, N= 35414.6919 and the installed position is E=91498.067, N=35414.804. These coordinates suggest that the column 140C is 158.3mm out of the design position (at the cut off level)
| 01CV - Civils | Cxxx-NCR-000317 | NCR | Position of Column no 138B at cut off level |  | Contr |  | CON - Connaught Tunnel (East) |  | 2012-08-13 | 2012-08-09 11:49 | -4 | 2012-07-09 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | Design position of the column no 138B is 91494.875, 35417.449 and the installed position is 91494.741, 35417.427. These coordinates suggest column 138B is 135.8mm off from the design position @ cut off level
| 01CV - Civils | Cxxx-NCR-000324 | NCR | Piles 524A and 524F installed in wrong place |  | Contr |  | CON - Connaught Tunnel (East) |  | 2012-09-01 | 2012-08-30 08:33 | -2 | 2012-07-12 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Reject |  | Complete |  | Completed |  | The piles have been installed the the following co-ordinates 524A: 92666.917, 34514.358 524F: 92665.643, 34507.266 These are 1m away from the correct location. This non conformance has occured due to confusion between numerous sources of information.
| 01CV - Civils | Cxxx-NCR-000335 | NCR | M&E equipment installed in tunnel without approved MCR |  | Contr |  | CON - Connaught Tunnel (East) |  | 2012-07-27 | 2012-08-01 13:05 | 5 | 2012-07-17 | Electrical - Electrical Engineering General | 500 |  |  | Use As-Is |  | Complete |  | Completed |  | An approved Material Compliance Record is required before use of material in the works.
| 01CV - Civils | Cxxx-NCR-000338 | NCR | Surface Rail Trial Panel - Incomplete works at inspection time |  | Contr |  | CON - Connaught Tunnel (East) |  | 2012-07-18 | 2012-07-20 09:42 | 2 | 2012-07-17 | Civil - Civil Engineering General | 500 |  | Planning | Use As-Is |  | Complete |  | Completed |  | Works at time of planned inspection were incomplete due to cover issues and reinforcement misplacement.
| 01CV - Civils | Cxxx-NCR-000339 | NCR | Surface Rail Trial Panel - Honeycombing |  | Contr |  | CON - Connaught Tunnel (East) |  | 2012-08-13 | 2012-08-13 16:11 | 0 | 2012-07-18 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | Honeycombing to 2 locations of Trial Panel wall: 1) Base of wall at joint with kicker on front face of wall (1.5m long, max 60mm high, depth to be determined) 2) Panel joint on bottom right handside of front face of wall (650m long, max 20mm high, depth to be determined)
| 01CV - Civils | Cxxx-NCR-000340 | NCR | Surface Rail Trial Panel - Timber in concrete face |  | Contr |  | CON - Connaught Tunnel (East) |  | 2012-08-13 | 2012-08-13 16:31 | 0 | 2012-07-18 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | Timber splinters left in concrete face on back face of Trial Panel wall from shutters and around tie hole.
| 01CV - Civils | Cxxx-NCR-000341 | NCR | Surface Rail Trial Panel - Additioanl holes in slab |  | Contr |  | CON - Connaught Tunnel (East) |  | 2012-08-13 | 2012-08-13 16:28 | 0 | 2012-07-18 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | 2No additional 12mm holes drilled into Trial Panel slab for formwork support.
| 01CV - Civils | Cxxx-NCR-000342 | NCR | Surface Rail Trial Panel - Dowel Bars |  | Contr |  | CON - Connaught Tunnel (East) |  | 2012-08-13 | 2012-08-13 16:20 | 0 | 2012-07-18 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | 3No dowel bars projecting out of the Trial Panel wall are not perpendicular to the stop end of the wall.
| 01CV - Civils | Cxxx-NCR-000343 | NCR | Exposing __ Main without a Permit to Work |  | Contr |  | CON - Connaught Tunnel (East) |  | 2012-08-23 | 2012-07-24 16:32 | -30 | 2012-07-18 | Civil - Drainage | 500 |  | Supervision/Management | Rework |  | Complete |  | Completed |  | East temporaray sewer connection commenced before permit was granted
| 01CV - Civils | Cxxx-NCR-000344 | NCR | Column 515B |  | Contr |  | CON - Connaught Tunnel (East) |  | 2012-09-12 | 2012-09-10 15:46 | -2 | 2012-07-18 | Civil - Civil Engineering General | 500 |  | Damaged | Repair |  | Complete |  | Completed |  | The column reference 515BA has a crack in the column head which has resulted in a piece of the concrete breaking away at the head and side of the column. Removing this cracked piece has created a smaller pile head and also a void to the side of the column. The width and depth of the spalled concrete are 120mm and 150mm respectively. The column head has diameters of 200mm x 300mm (It should be noted that the column has achieved the correct diameter and only the head has a smaller diameter.)
| 01CV - Civils | Cxxx-NCR-000345 | NCR | Column 442B |  | Contr |  | CON - Connaught Tunnel (East) |  | 2012-09-12 | 2012-09-11 18:23 | -1 | 2012-07-18 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | The columns has been installed to 92521.749,34541.323. This is 107mm out of position. As the tolerance is 100mm, this is 7mm out of tolerance
| 01CV - Civils | Cxxx-NCR-000346 | NCR | Column 444B |  | Contr |  | CON - Connaught Tunnel (East) |  | 2012-09-03 | 2012-09-05 16:36 | 2 | 2012-07-19 | Civil - Civil Engineering General | 500 |  | Workmanship | Rework |  | Complete |  | Completed |  | The column reference 444B has been installed with the correct diameter, however the crack inducer has been installed offset to one side. This has caused the head to crack as shown in the attached sketch c315-SK-253. This has caused a smaller diameter at the head of the pile of 260mm
| 01CV - Civils | Cxxx-NCR-000347 | NCR | Pile 515A and 516A |  | Contr |  | CON - Connaught Tunnel (East) |  | 2012-09-03 | 2012-09-03 17:04 | 0 | 2012-07-19 | Civil - Civil Engineering General | 500 |  | Workmanship | Rework |  | Complete |  | Completed |  | The column references 515A and 516A, have a crack in the column head which have resulted in a piece of the concrete breaking away at the head and side of the column. Removing these cracked pieces have created a smaller pile head and also a void to the side of the column. The sizes of the cracked concrete and the diameters of the column heads are shown below. (It should be noted that the column has achieved the correct diameter and only the head has a smaller diameter.) 515A: Spalled concrete 90mm(width) x 150mm (depth) Column head = 320mm x 200mm 516A: Spalled concrete 12mm(width) x 150mm (depth) Column head = 200mm x 300mm
| 01CV - Civils | Cxxx-NCR-000348 | NCR | Column 516B |  | Contr |  | CON - Connaught Tunnel (East) |  | 2012-09-03 | 2012-09-04 12:05 | 1 | 2012-07-19 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | Columnn 516B has an average diameter of 274mm
| 01CV - Civils | Cxxx-NCR-000349 | NCR | Rebar Tracebility |  | Contr |  | CON - Connaught Tunnel (East) |  | 2012-09-28 | 2012-10-03 10:23 | 5 | 2012-07-19 | Civil - Civil Engineering General | 500 |  | System Defect | Use As-Is |  | Complete |  | Completed |  | The Quality Management System could not demonstrate during the CRL surveillance of 13th June 2012 that the specified requirement for implementing BS 4449 with respect to reinforcement steel traceability was met
| 01CV - Civils | Cxxx-NCR-000350 | NCR | Pile 442A |  | Contr |  | CON - Connaught Tunnel (East) |  | 2012-09-12 | 2012-09-03 16:50 | -9 | 2012-07-19 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | Column 442A has an average diameter of 293mm.
| 01CV - Civils | Cxxx-NCR-000353 | NCR | Cracked Column Heads Rows 536-538 |  | Contr |  | CON - Connaught Tunnel (East) |  | 2012-09-03 | 2012-09-05 16:39 | 2 | 2012-07-25 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | The column references 536C, 536E, 537C, 537E, 537F, 538E, 538F, have a crack in the column head which have resulted in a piece of the concrete breaking away at the head and side of the column. Removing these cracked pieces have created a smaller pile head and also a void to the side of the column. The sizes of the cracked concrete and the diameters of the column heads are shown on the attached spreadsheet. (It should be noted that the column has achieved the correct diameter and only the head has a smaller diameter.)
| 01CV - Civils | Cxxx-NCR-000357 | NCR | Invert Reprofiling - West |  | Contr |  | CON - Connaught Tunnel (East) |  | 2012-08-14 | 2012-08-17 15:02 | 3 | 2012-07-24 | Civil - Civil Engineering General | 500 |  | Planning | Use As-Is |  | Complete |  | Completed |  | In some localised areas (see attached drawings) there are areas out of tolerance.
| 01CV - Civils | Cxxx-NCR-000358 | NCR | Cracked Head Pile Rows 532-535 |  | Contr |  | CON - Connaught Tunnel (East) |  | 2012-09-05 | 2012-08-10 08:23 | -26 | 2012-07-25 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | The column references 532B, 532C, 532F, 533B, 533C, 534A, 534C, 534F, 535B, 535F have a crack in the column head which have resulted in a piece of the concrete breaking away at the head and side of the column. Removing these cracked pieces have created a smaller pile head and also a void to the side of the column. The sizes of the cracked concrete and the diameters of the column heads are shown on the attached spreadsheet. (It should be noted that the column has achieved the correct diameter and only the head has a smaller diameter.)
| 01CV - Civils | Cxxx-NCR-000359 | NCR | Cracked Column Head Rows 529 - 531 |  | Contr |  | CON - Connaught Tunnel (East) |  | 2012-09-05 | 2012-08-13 16:39 | -23 | 2012-07-25 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | The column references 529A, 529B, 529E, 530E, 530F, 531A, 531E have a crack in the column head which have resulted in a piece of the concrete breaking away at the head and side of the column. Removing these cracked pieces have created a smaller pile head and also a void to the side of the column. The sizes of the cracked concrete and the diameters of the column heads are shown on the attached spreadsheet. (It should be noted that the column has achieved the correct diameter and only the head has a smaller diameter.)
| 01CV - Civils | Cxxx-NCR-000360 | NCR | Reduced Column Diameter Rows 536-538 |  | Contr |  | CON - Connaught Tunnel (East) |  | 2012-09-05 | 2012-08-09 13:24 | -27 | 2012-07-25 | Civil - Civil Engineering General | 500 |  | System Defect | Use As-Is |  | Complete |  | Completed |  | Columns 538C and 536D have average diameters of 290mm and 315mm respectively
| 01CV - Civils | Cxxx-NCR-000361 | NCR | Reduced Column Diameter rows 532-535 |  | Contr |  | CON - Connaught Tunnel (East) |  | 2012-09-05 | 2012-08-09 11:50 | -27 | 2012-07-25 | Civil - Civil Engineering General | 500 |  | System Defect | Use As-Is |  | Complete |  | Completed |  | Columns 535C and 533A have average diameters of 315mmmm and 310mm respectively
| 01CV - Civils | Cxxx-NCR-000362 | NCR | Reduced Column Diameter rows 529 - 531 |  | Contr |  | CON - Connaught Tunnel (East) |  | 2012-09-05 | 2012-08-09 11:47 | -27 | 2012-07-25 | Civil - Civil Engineering General | 500 |  | System Defect | Use As-Is |  | Complete |  | Completed |  | Column 530D has an average diameter of 315mm
| 01CV - Civils | Cxxx-NCR-000363 | NCR | Columns out of positional tolerance rows 532-535 |  | Contr |  | CON - Connaught Tunnel (East) |  | 2012-09-14 | 2012-09-12 11:22 | -2 | 2012-07-25 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | The column 535A and 535D are out of positional tolerance. The as built co-ordinates of these columns are 535A: 92686.545, 34511.767 532D: 92680.404, 34507.508 These are 134mm (535A) and 102mm (532D) away from the designed co-ordinate. As the tolerance is 100mm, these are 34mm and 2mm out of tolerance respectively
| 01CV - Civils | Cxxx-NCR-000364 | NCR | Columns out of Positional Tolerance in rows 529-531 |  | Contr |  | CON - Connaught Tunnel (East) |  | 2012-09-28 | 2012-09-05 15:20 | -23 | 2012-07-26 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | The column 531D is out of positional tolerance. The as built co-ordinates of this column is 531D: 92678.716, 34507.808 This is 179mm away from the designed co-ordinate. As the tolerance is 100mm, this is 79mm out of tolerance.
| 01CV - Civils | Cxxx-NCR-000365 | NCR | Column 38B Cracked Head and Reduced Diameter |  | Contr |  | CON - Connaught Tunnel (East) |  | 2012-09-05 | 2012-09-05 16:59 | 0 | 2012-07-25 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | The column reference 538B has a crack in the column head which has resulted in a piece of the concrete breaking away at the head and side of the column. Removing this cracked piece has created a smaller pile head and also a void to the side of the column. The width and depth of the spalled concrete are 100mm and 150mm respectively. The column head has diameters of 300mm x 270mm (It should be noted that the column has achieved the correct diameter and only the head has a smaller diameter.) This column also has an average smaller diameter of 310mm
| 01CV - Civils | Cxxx-NCR-000366 | NCR | Column 536B Cracked Head and Reduced Diameter |  | Contr |  | CON - Connaught Tunnel (East) |  | 2012-09-05 | 2012-08-30 13:59 | -6 | 2012-07-25 | Civil - Civil Engineering General | 500 |  |  | Use As-Is |  | Complete |  | Completed |  | The column reference 536B has a crack in the column head which has resulted in a piece of the concrete breaking away at the head and side of the column. Removing this cracked piece has created a smaller pile head and also a void to the side of the column. The width and depth of the spalled concrete are 90mm and 130mm respectively. The column head has diameters of 260mm x 280mm (It should be noted that the column has achieved the correct diameter and only the head has a smaller diameter.) This column also has an average smaller diameter of 310mm
| 01CV - Civils | Cxxx-NCR-000367 | NCR | Column 534B Cracked Head and Reduced Diameter |  | Contr |  | CON - Connaught Tunnel (East) |  | 2012-09-05 | 2012-08-30 13:56 | -6 | 2012-07-25 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | The column reference 534B has a crack in the column head which has resulted in a piece of the concrete breaking away at the head and side of the column. Removing this cracked piece has created a smaller pile head and also a void to the side of the column. The width and depth of the spalled concrete are 70mm and 40mm respectively. The column head has diameters of 220mm x 320mm (It should be noted that the column has achieved the correct diameter and only the head has a smaller diameter.) This column also has an average smaller diameter of 286mm
| 01CV - Civils | Cxxx-NCR-000368 | NCR | Invert Reprofiling - East |  | Contr |  | CON - Connaught Tunnel (East) |  | 2012-08-15 | 2012-08-17 15:03 | 2 | 2012-07-25 | Civil - Civil Engineering General | 500 |  | Planning | Use As-Is |  | Complete |  | Completed |  | There are some localised areas (see attachments) that are out of tolerance.
| 01CV - Civils | Cxxx-NCR-000369 | NCR | Column 533F Cracked Head and Reduced Diameter |  | Contr |  | CON - Connaught Tunnel (East) |  | 2012-09-05 | 2012-09-04 14:21 | -1 | 2012-07-25 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | The column reference 533 F has a crack in the column head which has resulted in a piece of the concrete breaking away at the head and side of the column. Removing this cracked piece has created a smaller pile head and also a void to the side of the column. The width and depth of the spalled concrete are 70mm x 100mm respectively. The column head has diameters of 280mm x 320mm (It should be noted that the column has achieved the correct diameter and only the head has a smaller diameter.) This column also has an average smaller diameter of 315mm
| 01CV - Civils | Cxxx-NCR-000370 | NCR | Column 533E Cracked Head and Reduced Diameter |  | Contr |  | CON - Connaught Tunnel (East) |  | 2012-09-05 | 2012-09-04 14:20 | -1 | 2012-07-25 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | The column reference 533 E has a crack in the column head which has resulted in a piece of the concrete breaking away at the head and side of the column. Removing this cracked piece has created a smaller pile head and also a void to the side of the column. The width and depth of the spalled concrete are 80mm x 130mm respectively. The column head has diameters of 220mm x 300mm (It should be noted that the column has achieved the correct diameter and only the head has a smaller diameter.) This column also has an average smaller diameter of 300mm
| 01CV - Civils | Cxxx-NCR-000371 | NCR | Column 530C Cracked Head and Reduced Diameter |  | Contr |  | CON - Connaught Tunnel (East) |  | 2012-09-05 | 2012-09-05 17:00 | 0 | 2012-07-25 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | The column reference 530 C has a crack in the column head which has resulted in a piece of the concrete breaking away at the head and side of the column. Removing this cracked piece has created a smaller pile head and also a void to the side of the column. The width and depth of the spalled concrete are 110mm x 150mm respectively. The column head has diameters of 210mm x 300mm (It should be noted that the column has achieved the correct diameter and only the head has a smaller diameter.) This column also has an average smaller diameter of 290mm
| 01CV - Civils | Cxxx-NCR-000372 | NCR | Column 530A Cracked Head and Reduced Diameter |  | Contr |  | CON - Connaught Tunnel (East) |  | 2012-09-05 | 2012-09-05 17:02 | 0 | 2012-07-25 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | The column reference 530 A has a crack in the column head which has resulted in a piece of the concrete breaking away at the head and side of the column. Removing this cracked piece has created a smaller pile head and also a void to the side of the column. The width and depth of the spalled concrete are 110mm x 160mm respectively. The column head has diameters of 190mm x 290mm (It should be noted that the column has achieved the correct diameter and only the head has a smaller diameter.) This column also has an average smaller diameter of 305mm
| 01CV - Civils | Cxxx-NCR-000373 | NCR | Column 537A Cracked Head and Out of Position |  | Contr |  | CON - Connaught Tunnel (East) |  | 2012-09-14 | 2012-09-13 11:04 | -1 | 2012-07-25 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | The column reference 537 A has a crack in the column head which has resulted in a piece of the concrete breaking away at the head and side of the column. Removing this cracked piece has created a smaller pile head and also a void to the side of the column. The width and depth of the spalled concrete are 110mm x 160mm respectively. The column head has diameters of 190mm x 290mm (It should be noted that the column has achieved the correct diameter and only the head has a smaller diameter.) This column is also out of positional tolerance. The as built co-ordinate of this column is 92690.122, 34511.121. This is 131mm away from the designed co-ordinate. As the tolerance is 100mm, this is 31mm out of tolerance.
| 01CV - Civils | Cxxx-NCR-000374 | NCR | Column 536F Cracked Head and Out of Position |  | Contr |  | CON - Connaught Tunnel (East) |  | 2012-09-14 | 2012-09-12 11:33 | -2 | 2012-07-25 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | The column reference 536 F has a crack in the column head which has resulted in a piece of the concrete breaking away at the head and side of the column. Removing this cracked piece has created a smaller pile head and also a void to the side of the column. The width and depth of the spalled concrete are 100mm x 210mm respectively. The column head has diameters of 220mm x 320mm (It should be noted that the column has achieved the correct diameter and only the head has a smaller diameter.) This column is also out of positional tolerance. The as built co-ordinate of this column is 92686.68, 34502.522. This is 149mm away from the designed co-ordinate. As the tolerance is 100mm, this is 49mm over the tolerance.
| 01CV - Civils | Cxxx-NCR-000375 | NCR | Column 532E Cracked Head and Out of Position |  | Contr |  | CON - Connaught Tunnel (East) |  | 2012-09-14 | 2012-09-12 11:39 | -2 | 2012-07-25 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | The column reference 532 E has a crack in the column head which has resulted in a piece of the concrete breaking away at the head and side of the column. Removing this cracked piece has created a smaller pile head and also a void to the side of the column. The width and depth of the spalled concrete are 70mm x 170mm respectively. The column head has diameters of 250mm x 310mm (It should be noted that the column has achieved the correct diameter and only the head has a smaller diameter.) This column is also out of positional tolerance. The as built co-ordinate of this column is 92680.099, 34505.73. This is 112mm away from the designed co-ordinate. As the tolerance is 100mm, this is 12mm over the tolerance.
| 01CV - Civils | Cxxx-NCR-000376 | NCR | Column 531F Cracked Head and Out of Position |  | Contr |  | CON - Connaught Tunnel (East) |  | 2012-09-14 | 2012-09-13 08:58 | -1 | 2012-07-25 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | The column reference 531 F has a crack in the column head which has resulted in a piece of the concrete breaking away at the head and side of the column. Removing this cracked piece has created a smaller pile head and also a void to the side of the column. The width and depth of the spalled concrete are 100mm x 130mm respectively. The column head has diameters of 250mm x 310mm (It should be noted that the column has achieved the correct diameter and only the head has a smaller diameter.) This column is also out of positional tolerance. The as built co-ordinate of this column is 92677.828, 34504.129. This is 137mm away from the designed co-ordinate. As the tolerance is 100mm, this is 37mm over the tolerance.
| 01CV - Civils | Cxxx-NCR-000377 | NCR | Column 530B Cracked Head and Out of Position |  | Contr |  | CON - Connaught Tunnel (East) |  | 2012-09-05 | 2012-09-04 16:50 | -1 | 2012-07-25 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | The column reference 530 B has a crack in the column head which has resulted in a piece of the concrete breaking away at the head and side of the column. Removing this cracked piece has created a smaller pile head and also a void to the side of the column. The width and depth of the spalled concrete are 90mm x 190mm respectively. The column head has diameters of 240mm x 320mm (It should be noted that the column has achieved the correct diameter and only the head has a smaller diameter.) This column is also out of positional tolerance. The as built co-ordinate of this column is 92677.422, 34511.325. This is 143mm away from the designed co-ordinate. As the tolerance is 100mm, this is 43mm over the tolerance.
| 01CV - Civils | Cxxx-NCR-000378 | NCR | Column 529F Cracked HEad and Out of Position |  | Contr |  | CON - Connaught Tunnel (East) |  | 2012-09-05 | 2012-09-04 14:24 | -1 | 2012-07-25 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | The column reference 529 F has a crack in the column head which has resulted in a piece of the concrete breaking away at the head and side of the column. Removing this cracked piece has created a smaller pile head and also a void to the side of the column. The width and depth of the spalled concrete are 70mm x 140mm respectively. The column head has diameters of 250mm x 340mm (It should be noted that the column has achieved the correct diameter and only the head has a smaller diameter.) This column is also out of positional tolerance. The as built co-ordinate of this column is 92674.331, 34504.777. This is 110mm away from the designed co-ordinate. As the tolerance is 100mm, this is 10mm over the tolerance.
| 01CV - Civils | Cxxx-NCR-000379 | NCR | Column 327 E Cracked Head and Out of Position |  | Contr |  | CON - Connaught Tunnel (East) |  | 2012-09-06 | 2012-09-05 15:21 | -1 | 2012-07-26 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | The column reference 327 E has a crack in the column head which has resulted in a piece of the concrete breaking away at the head and side of the column. Removing this cracked piece has created a smaller pile head and also a void to the side of the column. The width and depth of the spalled concrete are 50mm x 140mm respectively. The column head has diameters of 270mm x 330mm (It should be noted that the column has achieved the correct diameter and only the head has a smaller diameter.) This column is also out of positional tolerance. The as built co-ordinate of this column is 92324.195, 34598.862. This is 111mm away from the designed co-ordinate. As the tolerance is 100mm, this is 11mm over the tolerance.
| 01CV - Civils | Cxxx-NCR-000380 | NCR | Column 326C Cracked Head and Out of Position |  | Contr |  | CON - Connaught Tunnel (East) |  | 2012-09-06 | 2012-09-10 08:27 | 4 | 2012-07-26 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | The column reference 326 C has a crack in the column head which has resulted in a piece of the concrete breaking away at the head and side of the column. Removing this cracked piece has created a smaller pile head and also a void to the side of the column. The width and depth of the spalled concrete are 50mm x 110mm respectively. The column head has diameters of 290mm x 320mm (It should be noted that the column has achieved the correct diameter and only the head has a smaller diameter.) This column is also out of positional tolerance. The as built co-ordinate of this column is 92324.233, 34602.693. This is 146mm away from the designed co-ordinate. As the tolerance is 100mm, this is 46mm over the tolerance.
| 01CV - Civils | Cxxx-NCR-000381 | NCR | Columns 326E and 326F Out of Positon |  | Contr |  | CON - Connaught Tunnel (East) |  | 2012-09-06 | 2012-08-09 11:39 | -28 | 2012-07-26 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | The column 326E and 326F are out of positional tolerance. The as built co-ordinates of these columns are 326E: 92322.602, 34599.668 326F: 92321.691, 34598.054 These are 139mm (326EA) and 130mm (326F) away from the designed co-ordinate. As the tolerance is 100mm, these are 39mm and 30mm out of tolerance respectively
| 01CV - Civils | Cxxx-NCR-000382 | NCR | Column 529D Cracked Head and Out of Position |  | Contr |  | CON - Connaught Tunnel (East) |  | 2012-09-06 | 2012-09-06 10:44 | 0 | 2012-07-26 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | The column reference 529 D has a crack in the column head which has resulted in a piece of the concrete breaking away at the head and side of the column. Removing this cracked piece has created a smaller pile head and also a void to the side of the column. The width and depth of the spalled concrete are 50mm x 50mm respectively. The column head has diameters of 270mm x 320mm (It should be noted that the column has achieved the correct diameter and only the head has a smaller diameter.) This column is also out of positional tolerance. The as built co-ordinate of this column is 92675.097, 34508.384. This is 109mm away from the designed co-ordinate. As the tolerance is 100mm, this is 9mm over the tolerance.
| 01CV - Civils | Cxxx-NCR-000383 | NCR | Column 533D Reduced Diameter and Out of Position |  | Contr |  | CON - Connaught Tunnel (East) |  | 2012-09-24 | 2012-09-13 11:26 | -11 | 2012-07-26 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | The column 533D has an average smaller diameter of 305mm This column is also out of positional tolerance. The as built co-ordinate of this column is 92682.272, 34507.178. This is 193mm away from the designed co-ordinate. As the tolerance is 100mm, this is 93mm over the tolerance.
| 01CV - Civils | Cxxx-NCR-000384 | NCR | Column 537B Cracked Head Out of Positional Tolerance and Reduced Diameter |  | Contr |  | CON - Connaught Tunnel (East) |  | 2012-09-06 | 2012-09-06 10:46 | 0 | 2012-07-26 | Civil - Civil Engineering General | 500 |  | Workmanship | Rework |  | Complete |  | Completed |  | Cracked Head The column reference 537 B has a crack in the column head which has resulted in a piece of the concrete breaking away at the head and side of the column. Removing this cracked piece has created a smaller pile head and also a void to the side of the column. The width and depth of the spalled concrete are 90mm x 100mm respectively. The column head has diameters of 250mm x 310mm (It should be noted that the column has achieved the correct diameter and only the head has a smaller diameter.) Out of positional Tolerance This column is also out of positional tolerance. The as built co-ordinate of this column is 92689.871 ; 34509.204. This is 104mm away from the designed co-ordinate. As the tolerance is 104mm, this is 04mm over the tolerance. Reduced Diameter The column has an average diameter of 300mm
| 01CV - Civils | Cxxx-NCR-000385 | NCR | Column 536A Cracked Head Out of Tolerance and Trimming Level too Low |  | Contr |  | CON - Connaught Tunnel (East) |  | 2012-09-20 | 2012-09-17 08:20 | -3 | 2012-08-09 | Civil - Civil Engineering General | 500 |  | Workmanship | Rework |  | Complete |  | Completed |  | Cracked Head The column reference 536 A has a crack in the column head which has resulted in a piece of the concrete breaking away at the head and side of the column. Removing this cracked piece has created a smaller pile head and also a void to the side of the column. The width and depth of the spalled concrete are 100mm x 170mm respectively. The column head has diameters of 230mm x 340mm (It should be noted that the column has achieved the correct diameter and only the head has a smaller diameter.) Out of positional Tolerance This column is also out of positional tolerance. The as built co-ordinate of this column is 92688.326; 34511.456. This is 142mm away from the designed co-ordinate. As the tolerance is 100mm, this is 42mm over the tolerance. Trimming Level too Low The trimming level is 30mm too low
| 01CV - Civils | Cxxx-NCR-000386 | NCR | Column 532A Cracked Head Reduced Diameter and Out of Postion |  | Contr |  | CON - Connaught Tunnel (East) |  | 2012-09-07 | 2012-09-06 11:13 | -1 | 2012-07-26 | Civil - Civil Engineering General | 500 |  | Workmanship | Rework |  | Complete |  | Completed |  | Cracked Head The column reference 532 A has a crack in the column head which has resulted in a piece of the concrete breaking away at the head and side of the column. Removing this cracked piece has created a smaller pile head and also a void to the side of the column. The width and depth of the spalled concrete are 80mm x 140mm respectively. The column head has diameters of 270mm x 300mm (It should be noted that the column has achieved the correct diameter and only the head has a smaller diameter.) Out of positional Tolerance This column is also out of positional tolerance. The as built co-ordinate of this column is 92681.361 ; 34512.56. This is 133mm away from the designed co-ordinate. As the tolerance is 100mm, this is 33mm over the tolerance. Reduced Diameter The column 532A has an average smaller diameter of 305mm
| 01CV - Civils | Cxxx-NCR-000387 | NCR | Backfill of Trial Hole 5 (PMI-187) prior to Crossrail inspection |  | Contr |  | CON - Connaught Tunnel (East) |  | 2012-08-20 | 2012-08-15 11:36 | -5 | 2012-07-27 | Civil - Fill | 500 |  | Planning | Rework |  | Complete |  | Completed |  | Contractor submitted IRF hold point __-IR 0524. Crossrail attended site at time and date specified, but trial hole had already been backfilled.
| 01CV - Civils | Cxxx-NCR-000389 | NCR | Column 537D Trimming Level too Low |  | Contr |  | CON - Connaught Tunnel (East) |  | 2012-09-06 | 2012-09-05 16:19 | -1 | 2012-07-27 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | The column 537D has a trimming level of 100.941. The designed trimming level is 101.037 which makes this column 96mm low
| 01CV - Civils | Cxxx-NCR-000390 | NCR | Columns with cracked heads within rows 523-528 |  | Contr |  | CON - Connaught Tunnel (East) |  | 2012-09-09 | 2012-09-06 11:21 | -3 | 2012-07-30 | Civil - Civil Engineering General | 500 |  | Workmanship | Rework |  | Complete |  | Completed |  | Within column rows 523-528 which were inspected on 26th July 2012, the following columns have a crack in the column head which have resulted in a piece of the concrete breaking away at the head and side of the column. 523C, 523B, 524C, 525A, 525E, 525F, 526A, 526B, 526C, 526E, 526F, 527D, 527E, 528B, 528E, 528F. Removing these cracked pieces have created a smaller pile head and also a void to the side of the column. The sizes of the cracked concrete and the diameters of the column heads are shown on the attached spreadsheet. (It should be noted that the column has achieved the correct diameter and only the head has a smaller diameter.)
| 01CV - Civils | Cxxx-NCR-000391 | NCR | Columns out of positional tolerance within rows 523-528 |  | Contr |  | CON - Connaught Tunnel (East) |  | 2012-09-09 | 2012-09-06 15:07 | -3 | 2012-07-29 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | Columns 523D, 524A, 525C, 525D are out of positional tolerance. As built co-ordinates are as follows 523D: 92664.502 ; 34510.3 142mm away from the centre and therefore 42mm out of positional tolerance 524A: 92666.043 ; 34514.591. 123mm away from the centre and therefore 23mm out of positional tolerance 525C: 92668.336 ; 34511.212 160mm away from the centre and therefore 60mm out of positional tolerance 525D: 92668.026 ; 34509.68. 118mm away from the centre and therefore 18mm out of positional tolerance
| 01CV - Civils | Cxxx-NCR-000392 | NCR | Columns 525B and 528D Reduced Diameter |  | Contr |  | CON - Connaught Tunnel (East) |  | 2012-09-09 | 2012-09-10 15:32 | 1 | 2012-07-30 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | Columns 525B and 528D have average diameters of 300mm and 310mm respectively
| 01CV - Civils | Cxxx-NCR-000393 | NCR | Column 524B Cracked Head and Reduced Diameter |  | Contr |  | CON - Connaught Tunnel (East) |  | 2012-09-09 | 2012-09-04 16:52 | -5 | 2012-07-30 | Civil - Civil Engineering General | 500 |  | Workmanship | Rework |  | Complete |  | Completed |  | Column 524 B has a crack in the column head which has resulted in a piece of the concrete breaking away at the head and side of the column. Removing this cracked piece has created a smaller pile head and also a void to the side of the column. The size of the spalled concrete is 90mm width and 120mm depth and the diameters of the pile head is 210mm x 300mm. (It should be noted that the column has achieved the correct diameter and only the head has a smaller diameter.) The column also has a reduced average diameter of 290mm
| 01CV - Civils | Cxxx-NCR-000394 | NCR | Column 526D Cracked Head and Reduced Diameter |  | Contr |  | CON - Connaught Tunnel (East) |  | 2012-09-09 | 2012-09-10 15:34 | 1 | 2012-07-30 | Civil - Civil Engineering General | 500 |  | Workmanship | Rework |  | Complete |  | Completed |  | Column 526 D has a crack in the column head which has resulted in a piece of the concrete breaking away at the head and side of the column. Removing this cracked piece has created a smaller pile head and also a void to the side of the column. The size of the spalled concrete is 160mm width and 50mm depth and the diameters of the pile head is 220mm x 310mm. (It should be noted that the column has achieved the correct diameter and only the head has a smaller diameter.) The column also has a reduced average diameter of 310mm
| 01CV - Civils | Cxxx-NCR-000395 | NCR | Column 527B Cracked Head and Out of Positional Tolerance |  | Contr |  | CON - Connaught Tunnel (East) |  | 2012-09-09 | 2012-09-10 15:36 | 1 | 2012-07-30 | Civil - Civil Engineering General | 500 |  | Workmanship | Rework |  | Complete |  | Completed |  | Column 527B has a crack in the column head which has resulted in a piece of the concrete breaking away at the head and side of the column. Removing this cracked piece has created a smaller pile head and also a void to the side of the column. The size of the spalled concrete is 120mm width and 120mm depth and the diameters of the pile head is 210mm x 280mm. (It should be noted that the column has achieved the correct diameter and only the head has a smaller diameter.) The column is also out of positional tolerance. As built co-ordinates are as follows 527B: 92672.157 ; 34512.504. This is 135mm away from the centre and therefore 35mm out of positional tolerance
| 01CV - Civils | Cxxx-NCR-000396 | NCR | Column 527C Cracked Head and Out of Position |  | Contr |  | CON - Connaught Tunnel (East) |  | 2012-09-09 | 2012-09-10 15:38 | 1 | 2012-07-30 | Civil - Civil Engineering General | 500 |  | Workmanship | Rework |  | Complete |  | Completed |  | Column 527 C has a crack in the column head which has resulted in a piece of the concrete breaking away at the head and side of the column. Removing this cracked piece has created a smaller pile head and also a void to the side of the column. The size of the spalled concrete is 100mm width and 120mm depth and the diameters of the pile head is 220mm x 320mm. (It should be noted that the column has achieved the correct diameter and only the head has a smaller diameter.) The column is also out of positional tolerance. As built co-ordinates are as follows 527C: 92672.026 ; 34510.561. This is 143mm away from the centre and therefore 43mm out of positional tolerance
| 01CV - Civils | Cxxx-NCR-000397 | NCR | Column 527F Cracked Head and Out of Positional Tolerance |  | Contr |  | CON - Connaught Tunnel (East) |  | 2012-09-09 | 2012-09-10 15:39 | 1 | 2012-07-30 | Civil - Civil Engineering General | 500 |  | Workmanship | Rework |  | Complete |  | Completed |  | Column 527 F has a crack in the column head which has resulted in a piece of the concrete breaking away at the head and side of the column. Removing this cracked piece has created a smaller pile head and also a void to the side of the column. The size of the spalled concrete is 80mm width and 160mm depth and the diameters of the pile head is 250mm x 330mm. (It should be noted that the column has achieved the correct diameter and only the head has a smaller diameter.) The column is also out of positional tolerance. As built co-ordinates are as follows 527F: 92670.784 ; 34505.417. This is 109mm away from the centre and therefore 9mm out of positional tolerance
| 01CV - Civils | Cxxx-NCR-000398 | NCR | Column 523A out of Positional Tolerance and Trimming Level too Low |  | Contr |  | CON - Connaught Tunnel (East) |  | 2012-09-12 | 2012-09-05 16:30 | -7 | 2012-08-01 | Civil - Civil Engineering General | 500 |  | Workmanship | Rework |  | Complete |  | Completed |  | Out of Positional Tolerance This column is out of positional tolerance. The as built co-ordinate of this column is 92665.237 ; 34515.633. This is 175mm away from the designed co-ordinate. As the tolerance is 100mm, this is 75mm over the tolerance. Trimming Level too Low The trimming level of the column is 10.845 which is 142mm below the designed trimming level.
| 01CV - Civils | Cxxx-NCR-000399 | NCR | Column 527A Cracked Head and Trimming Level too Low |  | Contr |  | CON - Connaught Tunnel (East) |  | 2012-09-12 | 2012-09-11 18:25 | -1 | 2012-08-01 | Civil - Civil Engineering General | 500 |  | Workmanship | Rework |  | Complete |  | Completed |  | Cracked Head The column reference 527A has a crack in the column head which has resulted in a piece of the concrete breaking away at the head and side of the column. Removing this cracked piece has created a smaller pile head and also a void to the side of the column. The width and depth of the spalled concrete are 90mm and 110mm respectively. The column head has diameters of 250mm x 330mm (It should be noted that the column has achieved the correct diameter and only the head has a smaller diameter.) Trimming Level too Low The trimming level of the column is 100.941which is 60mm below the designed trimming level.
| 01CV - Civils | Cxxx-NCR-000400 | NCR | Column 528A Cracked Head and Trimming Level too Low |  | Contr |  | CON - Connaught Tunnel (East) |  | 2012-09-12 | 2012-09-11 18:27 | -1 | 2012-08-01 | Civil - Civil Engineering General | 500 |  | Workmanship | Rework |  | Complete |  | Completed |  | Cracked Head The column reference 528A has a crack in the column head which has resulted in a piece of the concrete breaking away at the head and side of the column. Removing this cracked piece has created a smaller pile head and also a void to the side of the column. The width and depth of the spalled concrete are 80mm and 160mm respectively. The column head has diameters of 240mm x 320mm (It should be noted that the column has achieved the correct diameter and only the head has a smaller diameter.) Trimming Level too Low The trimming level of the column is 100.945 which is 60mm below the designed trimming level.
| 01CV - Civils | Cxxx-NCR-000401 | NCR | Column 523 F Cracked Head, Reduced Diameter, Out of Positional Tolerance and Reinforcement too high |  | Contr |  | CON - Connaught Tunnel (East) |  | 2012-09-12 | 2012-09-11 18:29 | -1 | 2012-08-01 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | Cracked Head The column reference 523 F has a crack in the column head which has resulted in a piece of the concrete breaking away at the head and side of the column. Removing this cracked piece has created a smaller pile head and also a void to the side of the column. The width and depth of the spalled concrete are 100mm x 60mm respectively. The column head has diameters of 220mm x 300mm (It should be noted that the column has achieved the correct diameter and only the head has a smaller diameter.) Out of positional Tolerance This column is also out of positional tolerance. The as built co-ordinate of this column is 92663.858 ; 34506.726. This is 143mm away from the designed co-ordinate. As the tolerance is 100mm, this is 43mm over the tolerance. Reduced Diameter The column also average smaller diameter of 305mm Reinforcement The reinforcement is 121mm too high. The top of the reinforcement is at 101.033. The embedment of the reinforcement into the gravels is 1.205m and so the reinforcement has achieved the requirement of being embedding within the river terrace deposits a minimum of 925mm.
| 01CV - Civils | Cxxx-NCR-000402 | NCR | Continuation of invert replacement works through a hold point |  | Contr |  | CON - Connaught Tunnel (East) |  | 2012-08-31 | 2012-08-20 15:55 | -11 | 2012-08-02 | Civil - Civil Engineering General | 500 |  | Planning | Use As-Is |  | Complete |  | Completed |  | __: Following a meeting between CRL, __ and __ on Tuesday 24/07/12, the installation of the temporary works for the west single tunnel invert replacement works were discussed. Progression of the works was agreed, however the temporary works design had not been approved by CRL and so work continued without releasing the hold point. CRL: The meeting between CRL, __ and __ on Tuesday 24/07/12 agreed that in support of Contractor’s progress works prior to loading were able to continue despite the Design Check Certificate not being complete and the Third Party Checker as __ yet to be agreed. This agreement however did not relinquish the requirement for the design to be accepted by Crossrail in accordance with the Hold Point on the ITP.
| 01CV - Civils | Cxxx-NCR-000413 | NCR | Columns number 523C-524B-529B trimming level too low |  | Contr |  | CON - Connaught Tunnel (East) |  | 2012-09-20 | 2012-09-12 11:40 | -8 | 2012-08-09 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | 523C: Trimming level is 100.927, 60mm below design trimming level 524B: Trimming level is 100.930, 61mm below design trimming level (mechanical damage) 529B: Trimming level is 100.936, 73mm below design trimming level
| 01CV - Civils | Cxxx-NCR-000414 | NCR | Cracked head 535A |  | Contr |  | CON - Connaught Tunnel (East) |  | 2012-09-20 | 2012-09-13 11:23 | -7 | 2012-08-10 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | The column reference 535A has a crack in the column head which has resulted in a piece of the concrete breaking away at the head and side of the column. Removing this cracked piece has created a smaller pile head and also a void to the side of the column. The width and depth of the spalled concrete is 80mm x 100mm . The column head has diameters of 220mm x 280mm (It should be noted that the column has achieved the correct diameter and only the head has a smaller diameter.)
| 01CV - Civils | Cxxx-NCR-000416 | NCR | Total Station Accuracy |  | Contr |  | CON - Connaught Tunnel (East) |  | 2013-02-28 | 2013-03-01 11:49 | 1 | 2012-08-14 | Surveying - Surveying General | 500 |  | Material | Rework |  | Complete |  | Completed |  | The total station being used by __ (__ TCRP 1205) to check position and level of CMCs is 2mm + 2ppm in reflectorless mode (i.e. to a surface, without a prism). The total station used by __ to perform manual monitoring (__ TS 06, serial number 1321599) has an accuracy of 1.5mm + 2ppm.
| 01CV - Civils | Cxxx-NCR-000417 | NCR | Total Station Instrument Checks |  | Contr |  | CON - Connaught Tunnel (East) |  | 2012-09-20 | 2012-11-13 10:50 | 54 | 2012-08-14 | Surveying - Surveying General | 500 |  | System Defect | Rework |  | Complete |  | Completed |  | The checksheet applicable for total station used by __ to perform manual monitoring (__ TS 06, serial number 1321599) shows that for May, June and July, only horizontal and vertical collimation checks were undertaken. The checksheets are incomplete for plate bubble, trunnion axis and optical plummet checks. Further, the checksheets are not kept in a single location – each Engineer has their own folder.
| 01CV - Civils | Cxxx-NCR-000418 | NCR | Incomplete Measuring and Test Equipment Register |  | Contr |  | CON - Connaught Tunnel (East) |  | 2012-09-20 | 2012-10-15 11:14 | 25 | 2012-08-14 | Surveying - Surveying General | 500 |  | System Defect | Rework |  | Complete |  | Completed |  | The register provided by the Contractor has the following non-conformances: - Following instruments are missing off the register: total Station used by __ surveyor (serial number 1335710), laser level used during invert reprofiling checking, any staffs, pogo sticks, tape measures, piling rigs etc. Note, this list is not exclusive. - Checking method for total stations lists only plate bubble test. Further test methods need to be included such as optical plummet, vertical and horizontal collimation etc - Test method and frequency column states that no regular checks are to be performed on gas monitors. This is in contradiction to the manufacturers guidelines
| 01CV - Civils | Cxxx-NCR-000419 | NCR | Formation Overdug |  | Contr |  | CON - Connaught Tunnel (East) |  | 2012-09-24 | 2012-10-02 11:18 | 8 | 2012-08-15 | Geotechnical Engineering - Geotechnical Engineering - General | 500 |  | Workmanship | Rework |  | Complete |  | Completed |  | The Formation at CMC Rows 537-538 has been overdug by upto 100mm, due to incorrect setting up of laser level
| 01CV - Civils | Cxxx-NCR-000420 | NCR | Formation Low Spots |  | Contr |  | CON - Connaught Tunnel (East) |  | 2012-09-24 | 2012-10-08 16:23 | 14 | 2012-08-15 | Civil - Geotechnical Engineering | 500 |  | Damaged | Rework |  | Complete |  | Completed |  | Low spots which are upto 50mm outside tolerence between Rows 525 and 536 have developed due to formaton being exposed to the elements whilst awaiting closure of NCR's for multiple column defects as per attached photo
| 01CV - Civils | Cxxx-NCR-000421 | NCR | CATIII Checker Approval |  | Contr |  | CON - Connaught Tunnel (East) |  | 2012-09-28 | 2012-11-15 09:07 | 48 | 2012-08-16 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | Tony Gee was accepted by the Project Manager to carry out structural assessments of the tunnel. Tony Gee were also used by __ to complete a CAT III check of the working platform for the surface rail piling. Originally __ intended on a CAT II check however DLR (adjacent to the work are) required a CAT III check. Due to the short notice requirement of a CAT III check, Tony Gee was used as they were already approved to complete structural assessments on the project. Tony Gee had not been submitted to the Project Manager for approval as a CAT III design checker.
| 01CV - Civils | Cxxx-NCR-000423 | NCR | CMC 520A cracked head |  | Contr |  | CON - Connaught Tunnel (East) |  | 2012-09-27 | 2012-09-04 12:10 | -23 | 2012-08-17 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | The column reference 520A has a crack in the column head which has resulted in a piece of the concrete breaking away at the head and side of the column. Removing this cracked piece has created a smaller pile head and also a void to the side of the column. The width and depth of the spalled concrete are 170mm x 300mm respectively. The column head has diameters of 150mm x 320mm (It should be noted that the column has achieved the correct diameter and only the head has a smaller diameter.) The column has a shape on top which is less than 200mm equivalent diameter.
| 01CV - Civils | Cxxx-NCR-000424 | NCR | CMC 515D, 516D out of position |  | Contr |  | CON - Connaught Tunnel (East) |  | 2012-10-11 | 2012-09-13 08:59 | -28 | 2012-09-12 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | Column 515D is 34mm out of positional tolerance Column 516D is 87mm out of positional tolerance
| 01CV - Civils | Cxxx-NCR-000425 | NCR | CMC 520C cracked head- out of position |  | Contr |  | CON - Connaught Tunnel (East) |  | 2012-09-27 | 2012-09-04 11:36 | -23 | 2012-08-17 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | Cracked Head The column reference 520F has a crack in the column head which has resulted in a piece of the concrete breaking away at the head and side of the column. Removing this cracked piece has created a smaller pile head and also a void to the side of the column. The width and depth of the spalled concrete are 130mm (width) x 200mm (depth) respectively. The column head has diameters of 300mm x 210mm Column out of position The columns has been installed to (92659.497 ; 34512.807) This is 176 mm away from the designed co-ordinate. As the tolerance is 100mm, this is 76 mm out of tolerance
| 01CV - Civils | Cxxx-NCR-000426 | NCR | CMC rows 153-154 – cracked heads |  | Contr |  | CON - Connaught Tunnel (East) |  | 2012-11-29 | 2012-11-12 14:17 | -17 | 2012-10-26 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | The column references 153A / 154AF, have a crack in the column head which have resulted in a piece of the concrete breaking away at the head and side of the column. Removing these cracked pieces has created a smaller pile head and also a void to the side of the column. The sizes of the cracked concrete and the diameters of the column heads are shown on the attached spreadsheet. (It should be noted that the column has achieved the correct diameter and only the head has a smaller diameter.)
| 01CV - Civils | Cxxx-NCR-000429 | NCR | CMC 521A cracked head - out of position |  | Contr |  | CON - Connaught Tunnel (East) |  | 2012-09-27 | 2012-09-04 12:12 | -23 | 2012-08-17 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | Cracked Head The column reference 521A has a crack in the column head which has resulted in a piece of the concrete breaking away at the head and side of the column. Removing this cracked piece has created a smaller pile head and also a void to the side of the column. The width and depth of the spalled concrete are 130mm (width) x 180mm (depth) respectively. The column head has diameters of 320mm x 210mm Column out of position The columns has been installed to (92661.842 ; 34516.231) This is 161 mm away from the designed co-ordinate. As the tolerance is 100mm, this is 61 mm out of tolerance
| 01CV - Civils | Cxxx-NCR-000430 | NCR | CMC 521B cracked head - diameter too small |  | Contr |  | CON - Connaught Tunnel (East) |  | 2012-09-27 | 2012-09-04 12:13 | -23 | 2012-08-17 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | Cracked Head The column reference 521B has a crack in the column head which has resulted in a piece of the concrete breaking away at the head and side of the column. Removing this cracked piece has created a smaller pile head and also a void to the side of the column. The width and depth of the spalled concrete are 100mm (width) x 240mm (depth) respectively. The column head has diameters of 300mm x 190mm Diameter too small The installed column has an average diameter of 310mm
| 01CV - Civils | Cxxx-NCR-000431 | NCR | CMC rows 467-459 - Multiple issues |  | Contr |  | CON - Connaught Tunnel (East) |  | 2012-10-22 | 2012-10-16 09:00 | -6 | 2012-09-18 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | Cracked Head Column NCR (Applicable to 459ACE / 460ABCEF / 461A-F / 462ACE / 463BCDE / 464ADE / 465ABC / 466ABCE / 467ABCEF ) The columns from row 459 to 467 , have a crack in the column head which have resulted in a piece of the concrete breaking away at the head and side of the column. Removing these cracked pieces has created a smaller pile head and also a void to the side of the column. The sizes of the cracked concrete and the diameters of the column heads are shown on the attached spreadsheet. (It should be noted that the column has achieved the correct diameter and only the head has a smaller diameter.) Out of Position (Applicable to 459ACD / 460ACE / 461AF / 462AC / 464A / 465AC / 466AD / 467A) The columns have been installed as per the attached spreadsheet This is distance from the designed co-ordinate is stated. Reduced Diameter (Applicable to 459ACDE / 460ABCEF / 461A-E / 462ACE / 463BCDE / 464AE / 465AB / 466A-E / 467ABCEF ) The installed columns have diameters as stated in the attached spreadsheet Reinforcement too high (Applicable to 464D ) The reinforcement is per the attached schedule. The reinforcement has achieved the requirement of being embedding within the river terrace deposits a minimum of 925mm. Mechanical damage applicable to 459E / 460E / 461D / 463B / 463D / 465C
| 01CV - Civils | Cxxx-NCR-000432 | NCR | CMC 522F cracked head - diameter too small |  | Contr |  | CON - Connaught Tunnel (East) |  | 2012-09-27 | 2012-09-04 12:17 | -23 | 2012-08-17 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | Cracked Head The column reference 522F has a crack in the column head which has resulted in a piece of the concrete breaking away at the head and side of the column. Removing this cracked piece has created a smaller pile head and also a void to the side of the column. The width and depth of the spalled concrete are 110mm (width) x 140mm (depth) respectively. The column head has diameters of 320mm x 330mm The remaining area at the top of the column is less than 200mm equivalent diameter. Diameter too small The installed column has an average diameter of 305mm
| 01CV - Civils | Cxxx-NCR-000433 | NCR | CMC rows 501 -510 - multiple issues |  | Contr |  | CON - Connaught Tunnel (East) |  | 2012-10-12 | 2012-10-13 16:33 | 1 | 2012-09-13 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | Cracked Head Column NCR. (Applicable to all columns between 501 and 510 with the exception of 506D, 507D, 508E and 510E). The columns between rows 501 and 510, have a crack in the column head which have resulted in a piece of the concrete breaking away at the head and side of the column. Removing these cracked pieces has created a smaller pile head and also a void to the side of the column. The sizes of the cracked concrete and the diameters of the column heads are shown on the attached spreadsheet. (It should be noted that the column has achieved the correct diameter and only the head has a smaller diameter.) Out of Position NCR (Applicable to 501A/C/D/E, 503A, 505B/D, 506A/C/D, 507D/F/B, 509A/D/E, 510D/F) The columns have been installed as per the attached spreadsheet The distance from the designed co-ordinate is stated on the spreadsheet Reduced Diameter NCR (Applicable to 501A/B/F, 502A/B/D/F, 503A/B/C, 504B/C/F, 505A/B/C/F, 506A/B/C/F, 507A/B/C/F, 508A/C/F, 509A/B/C/E/F, 510A/B/C/F) The installed columns have diameters as stated in the attached spreadsheet As well as experiencing a cracked head, the following columns have experienced a surface crack in the head due to excavation. These are501D, 503A, 508A, 508B, 509D, 510F.
| 01CV - Civils | Cxxx-NCR-000434 | NCR | CMC 522B cracked head - diameter too small |  | Contr |  | CON - Connaught Tunnel (East) |  | 2012-09-27 | 2012-09-05 16:40 | -22 | 2012-08-17 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | Cracked Head The column reference 522B has a crack in the column head which has resulted in a piece of the concrete breaking away at the head and side of the column. Removing this cracked piece has created a smaller pile head and also a void to the side of the column. The width and depth of the spalled concrete are 140mm (width) x 170mm (depth) respectively. The column head has diameters of 310mm x 180mm Diameter too small The installed column has an average diameter of 300mm
| 01CV - Civils | Cxxx-NCR-000435 | NCR | CMC 506D, 507D out of position |  | Contr |  | CON - Connaught Tunnel (East) |  | 2012-10-12 | 2012-10-04 12:11 | -8 | 2012-09-13 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | 506D is 10mm out of positional tolerance. 507D is 16mm out of positional tolerance. (shown on schedule attached)
| 01CV - Civils | Cxxx-NCR-000436 | NCR | CMC 521F out of position |  | Contr |  | CON - Connaught Tunnel (East) |  | 2012-09-27 | 2012-09-13 11:28 | -14 | 2012-08-17 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | The columns has been installed to (92660.135; 34507.248) This is 190 mm away from the designed co-ordinate. As the tolerance is 100mm, this is 90 mm out of tolerance
| 01CV - Civils | Cxxx-NCR-000437 | NCR | CMC 501-510 - cracked head |  | Contr |  | CON - Connaught Tunnel (East) |  | 2012-10-12 | 2012-10-13 15:33 | 1 | 2012-09-13 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | The column references 502 CE, 503 DEF, 504 ADE, 505E, 506E, 507E, 508D, have a crack in the column head which have resulted in a piece of the concrete breaking away at the head and side of the column. Removing these cracked pieces has created a smaller pile head and also a void to the side of the column. The sizes of the cracked concrete and the diameters of the column heads are shown on the attached spreadsheet. (It should be noted that the column has achieved the correct diameter and only the head has a smaller diameter.)
| 01CV - Civils | Cxxx-NCR-000439 | NCR | Inspection not carried out correctly |  | Contr |  | CON - Connaught Tunnel (East) |  | 2012-09-29 | 2012-09-13 11:32 | -16 | 2012-08-21 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | For activity number 2 'Inspection of Works' for Cxxx-VIN-C-ITP-CR146_ST003-50024, __ carried out an inspection on column heads yet CRL found more NCRs upon thier inspection
| 01CV - Civils | Cxxx-NCR-000443 | NCR | Witness point passed before time notified to CRL |  | Contr |  | CON - Connaught Tunnel (East) |  | 2012-09-20 | 2012-09-20 16:52 | 0 | 2012-08-20 | Civil - Civil Engineering General | 500 |  | Planning | Rework |  | Complete |  | Completed |  | Contractors IRF for the works (__-IR 0542)was submitted with a planned date and time of the works of 17/08/12 0830. CRL were informed verbally that the works would not commence until 1030. When visiting site to carry out an unrelated inspection at approx. 0930 it was noted that the works had commenced.
| 01CV - Civils | Cxxx-NCR-000446 | NCR | CMC rows 500-490 - multiple issues |  | Contr |  | CON - Connaught Tunnel (East) |  | 2012-10-23 | 2012-10-13 15:32 | -10 | 2012-09-13 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | Cracked Head Column NCR (Applicable to 490C/F, 491A/B/F, 492A/E/F, 493B/C/, 494A/C/E/F, 495C/D/E, 496A/C/D/E, 497A/D/E/F, 498B/D/E/F, 499C/F, 500A/B/E/F) The column between rows 500 to 490, have a crack in the column head which have resulted in a piece of the concrete breaking away at the head and side of the column. Removing these cracked pieces has created a smaller pile head and also a void to the side of the column. The sizes of the cracked concrete and the diameters of the column heads are shown on the attached spreadsheet. (It should be noted that the column has achieved the correct diameter and only the head has a smaller diameter.) Out of Position (Applicable to 490C/F, 491B/F, 492E/F, 493B/C/E, 494A, 495C, 496B, 497B/F, 499F) The columns have been installed as per the attached spreadsheet This is distance from the designed co-ordinate is stated. Reduced Diameter (Applicable to 490F, 491A/F, 492A/F, 493E, 494C/E/F, 495C/D/E, 496A/B/C/D/E, 497A/B/C/E/F, 498B/D/E/F, 499/C, 500A/B/E/F) The installed columns have diameters as stated in the attached spreadsheet Reinforcement too high (Applicable to 499F) The reinforcement is per the attached schedule. The reinforcement has achieved the requirement of being embedding within the river terrace deposits a minimum of 925mm.
| 01CV - Civils | Cxxx-NCR-000449 | NCR | CMC rows 500-490 - reduced diameter |  | Contr |  | CON - Connaught Tunnel (East) |  | 2012-10-23 | 2012-10-02 16:58 | -21 | 2012-09-13 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | The follwoing columns have a reduced diameter 490E 494D 495F 499B The installed columns have diameters as stated in the attached spreadsheet
| 01CV - Civils | Cxxx-NCR-000450 | NCR | CMC rows 489-479 - Cracked heads |  | Contr |  | CON - Connaught Tunnel (East) |  | 2012-10-23 | 2012-10-13 15:23 | -10 | 2012-09-13 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | Cracked Heads (Applicable to 479C/D, 482C, 484A/D, 485A, 486D, 489C, 489D) The column from row 489 to 479, have a crack in the column head which have resulted in a piece of the concrete breaking away at the head and side of the column. Removing these cracked pieces has created a smaller pile head and also a void to the side of the column. The sizes of the cracked concrete and the diameters of the column heads are shown on the attached spreadsheet. (It should be noted that the column has achieved the correct diameter and only the head has a smaller diameter.)
| 01CV - Civils | Cxxx-NCR-000451 | NCR | CMC 517E diameter too small |  | Contr |  | CON - Connaught Tunnel (East) |  | 2012-10-11 | 2012-09-12 16:54 | -29 | 2012-09-12 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | The installed column has an average diameter of 290mm
| 01CV - Civils | Cxxx-NCR-000453 | NCR | CMC rows 478-468 - out of position |  | Contr |  | CON - Connaught Tunnel (East) |  | 2012-10-17 | 2012-10-13 14:01 | -4 | 2012-09-14 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | The column 473E have been installed as per the attached spreadsheet This is distance from the designed co-ordinate is stated.
| 01CV - Civils | Cxxx-NCR-000454 | NCR | CMC 518B-518D-519C-521D cracked heads |  | Contr |  | CON - Connaught Tunnel (East) |  | 2012-10-03 | 2012-09-12 16:56 | -21 | 2012-09-12 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | The column references 518B-518D-519C-521D have a crack in the column head which has resulted in a piece of the concrete breaking away at the head and side of the column. Removing this cracked piece has created a smaller pile head and also a void to the side of the column. -518B: cracked head 260x 280mm. Spalled concrete: 90(width)x220mm(depth) -518D: cracked head 250x 320mm. Spalled concrete: 90(width)x130mm(depth) -519C: cracked head 230x 290mm. Spalled concrete: 100(width)x290mm(depth) -521D: cracked head 210x 340mm. Spalled concrete: 90(width)x120mm(depth) (It should be noted that the column has achieved the correct diameter and only the head has a smaller diameter.)
| 01CV - Civils | Cxxx-NCR-000456 | NCR | CMC rows 478 to 468 - Multiple issues |  | Contr |  | CON - Connaught Tunnel (East) |  | 2012-10-03 | 2012-10-13 13:26 | 10 | 2012-09-14 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | Cracked Head Column NCR (Applicable to 468ABDE / 469ACEF / 470B-F / 471A-F / 472ABEF / 473ABCF / 474ABD / 475A-E / 476ABE / 477ABCEF / 478F ) The columns from row 468to 478 , have a crack in the column head which have resulted in a piece of the concrete breaking away at the head and side of the column. Removing these cracked pieces has created a smaller pile head and also a void to the side of the column. The sizes of the cracked concrete and the diameters of the column heads are shown on the attached spreadsheet. (It should be noted that the column has achieved the correct diameter and only the head has a smaller diameter.) Out of Position (Applicable to 468AD / 470ABF / 471ADF / 472A / 473ACD / 476F / 477F / 478F ) The columns have been installed as per the attached spreadsheet This is distance from the designed co-ordinate is stated. Reduced Diameter (Applicable to 468ABDE / 469ACEF / 470A-F / 471A-F / 472ABEF / 473ABCDF / 474ABD / 475A-E / 476ABEF / 477ABCE / 478F ) The installed columns have diameters as stated in the attached spreadsheet Mechanical damage (Applicable to 469A / 471D / 473C / 475D)
| 01CV - Civils | Cxxx-NCR-000459 | NCR | CMC rows 500-490 - Cracked heads |  | Contr |  | CON - Connaught Tunnel (East) |  | 2012-10-23 | 2012-10-13 15:18 | -10 | 2012-09-13 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | Cracked heads (Applicable to 490A/B 491D, 492B, 493A, 493D, 493F, 494B, 495A/B, 498A/C, 499A/E, 500C) The column from row 500 to 490, have a crack in the column head which have resulted in a piece of the concrete breaking away at the head and side of the column. Removing these cracked pieces has created a smaller pile head and also a void to the side of the column. The sizes of the cracked concrete and the diameters of the column heads are shown on the attached spreadsheet. (It should be noted that the column has achieved the correct diameter and only the head has a smaller diameter.)
| 01CV - Civils | Cxxx-NCR-000460 | NCR | CFA piles West 3C - 5C out of position |  | Contr |  | CON - Connaught Tunnel (East) |  | 2012-10-22 | 2012-10-17 15:52 | -5 | 2012-09-12 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | Pile 3C have been installed with the coordinates (91252.446 ; 35431.967), with a vector of 0.134m Pile 5C have been installed with the coordinates (91255.865 ; 35431.791), with a vector of 0.132m
| 01CV - Civils | Cxxx-NCR-000463 | NCR | Temperature for curing of concrete test specimens |  | Contr |  | CON - Connaught Tunnel (East) |  | 2012-09-22 | 2012-11-19 16:35 | 58 | 2012-08-22 | Civil - Civil Engineering General | 500 |  | System Defect | Use As-Is |  | Complete |  | Completed |  | During a joint Crossrail-Contractor surveillance of __ Concrete Testing Lab in Uxbridge on 21/08/12, __ stated that due to the recent hot weather, the hot climate rule was being applied, allowing newly made cubes to be stored up to 30°C, not 25°C.
| 01CV - Civils | Cxxx-NCR-000471 | NCR | Rough (Uneven) CMC heads Bay 13: 538A,B,D,E,F & 537B,F |  | Contr |  | CON - Connaught Tunnel (East) |  | 2012-10-05 | 2012-09-04 14:06 | -31 | 2012-08-24 | Geotechnical Engineering - Geotechnical Engineering - General | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | The current column head surface would cause damage to the geotextile strength specified in the long term.
| 01CV - Civils | Cxxx-NCR-000477 | NCR | Invert Replacement - Overbreak |  | Contr |  | CON - Connaught Tunnel (East) |  | 2012-10-11 | 2012-11-07 09:35 | 27 | 2012-08-31 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Rework |  | Complete |  | Completed |  | Excavation continued further under the wall than expected by up to 300mm. Area is indicated on attached sketch. Overbreak is only located on the West end of Trial Bay 1.
| 01CV - Civils | Cxxx-NCR-000487 | NCR | Failure of Contractors quality system to find defect - CMC 498D |  | Contr |  | CON - Connaught Tunnel (East) |  | 2012-10-03 | 2012-10-04 15:22 | 1 | 2012-09-05 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Repair |  | Complete |  | Completed |  | The works in question are carried out under ITP ref: Cxxx-VIN-C-ITP-CR146_ST003-50024 CMC remedials At the time of CRL grout pouring inspection to column ref: 498D there was significant soil on the substrate of the column which was to grouted. The contractor had failed to rectify this during his inspection at the previous intervention point under the ITP (3-Column head) prepared for grouting.
| 01CV - Civils | Cxxx-NCR-000488 | NCR | Failure of Contractors quality system to find defect - E12 Formation |  | Contr |  | CON - Connaught Tunnel (East) |  | 2012-10-03 | 2012-10-04 15:33 | 1 | 2012-09-05 | Civil - Excavation | 500 |  | Supervision/Management | Repair |  | Complete |  | Completed |  | The works in question are carried out under ITP ref: Cxxx-VIN-O4-ITP-CR146_ST003-50004 Inspection and Test Plan - Load Transfer Platform At the time of CRL ITP Point 12 (Check Formation/Pile positions, condition and levels) it was found that the levels of the formation were not within tolerance. The contractor had failed to rectify this during his inspection. CRL had been invited to inspect the works under IRP ref: 0387
| 01CV - Civils | Cxxx-NCR-000496 | NCR | Incomplete M&TE Register - Laser Level missing |  | Contr |  | CON - Connaught Tunnel (East) |  | 2012-09-30 | 2012-10-17 08:10 | 17 | 2012-09-06 | Civil - Civil Engineering General | 500 |  | System Defect | Rework |  | Complete |  | Completed |  | Laser level (Rugby 400, serial no. 74220, calibration no. C53642) in use on West Surface Rail checking level of excavation for CFA cut-off and engineering fill layer formation, does not appear on the M&TE Register.
| 01CV - Civils | Cxxx-NCR-000500 | NCR | Damage to CFA pile heads during cutting them down |  | Contr |  | CON - Connaught Tunnel (East) |  | 2012-10-31 | 2012-10-17 15:23 | -14 | 2012-09-08 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | The following pile heads got chipped ( damaged) during cutting down .Pile no 1B,Pile no 1C, Pile no 2B, Pile no 3B, Pile no 4B, Pile no 5B, Pile 5C, Pile 7C , refer to attached Cxxx-SK-351 to 354 for details
| 01CV - Civils | Cxxx-NCR-000503 | NCR | Debonding foam below cut-off on West CFA Piles (Rows B, C and 1 – 10) |  | Contr |  | CON - Connaught Tunnel (East) |  | 2012-10-11 | 2012-10-19 14:43 | 8 | 2012-09-11 | Civil - Civil Engineering General | 500 |  | Damaged | Rework |  | Complete |  | Completed |  | The following CFA piles have voids around a number of the reinforcement bars, where the debonding foam has encroached below cut-off level: 6B, 8B, 8C, 10C. The following CFA piles have debonding foam inside the concrete surrounding a number of reinforcement bars, below cut-off level: 1B, 2B, 5C, 7B, 7C.
| 01CV - Civils | Cxxx-NCR-000505 | NCR | CMC rows 489-479 - Multiple issues |  | Contr |  | CON - Connaught Tunnel (East) |  | 2012-10-23 | 2012-10-13 15:15 | -10 | 2012-09-13 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | Cracked Head Column NCR (Applicable to 479B/E/F, 480B/E/F, 481A/B/F, 482A/B/D/F, 483B/C/D/E/F, 484E, 485B/C/E/F, 486C/F, 487A/B/C/E, 488A/B/C/D/E, 489B) The column between rows 489 to 479, have a crack in the column head which have resulted in a piece of the concrete breaking away at the head and side of the column. Removing these cracked pieces has created a smaller pile head and also a void to the side of the column. The sizes of the cracked concrete and the diameters of the column heads are shown on the attached spreadsheet. (It should be noted that the column has achieved the correct diameter and only the head has a smaller diameter.) Out of Position (Applicable to 480E, 481A, 485E, 486F, 488A, 489A/F) The columns have been installed as per the attached spreadsheet This is distance from the designed co-ordinate is stated. Reduced Diameter (Applicable to 479B/E/F, 480B/F, 481A/B/F, 482A/B/D/F, 483B/C/D/E/F, 484E, 485B/C/E/F, 486C/F, 487A/B/C/E, 488B/C/D/E, 489B/F) The installed columns have diameters as stated in the attached spreadsheet Column 487C has also experienced a surface crack due to excavation
| 01CV - Civils | Cxxx-NCR-000506 | NCR | CMC rows 489-479 - Out of position |  | Contr |  | CON - Connaught Tunnel (East) |  | 2012-10-23 | 2012-10-13 15:11 | -10 | 2012-09-13 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | The column references 481D and 486A are 11mm and 70m out of positional tolerance The columns have been installed as per the attached spreadsheet This is distance from the designed co-ordinate is stated.
| 01CV - Civils | Cxxx-NCR-000507 | NCR | CMC rows 489-479 - Reduced diameter |  | Contr |  | CON - Connaught Tunnel (East) |  | 2012-10-23 | 2012-10-13 15:00 | -10 | 2012-09-13 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | The following column have reduced diameters, 479A, 480A, 481E, 482E, 483A, 484B/C/F, 485D, 486B/E, 487f The installed columns have diameters as stated in the attached spreadsheet
| 01CV - Civils | Cxxx-NCR-000508 | NCR | CMC rows 478-468 - Cracked head |  | Contr |  | CON - Connaught Tunnel (East) |  | 2012-10-23 | 2012-10-13 16:38 | -10 | 2012-09-18 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | Craked heads(applicable to 468F / 474E / 474F / 475F / 478A / 478C / 478D) The column from row 478 to 468, have a crack in the column head which have resulted in a piece of the concrete breaking away at the head and side of the column. Removing these cracked pieces has created a smaller pile head and also a void to the side of the column. The sizes of the cracked concrete and the diameters of the column heads are shown on the attached spreadsheet. (It should be noted that the column has achieved the correct diameter and only the head has a smaller diameter.)
| 01CV - Civils | Cxxx-NCR-000509 | NCR | CMC rows 478-468 - Reduced diameter |  | Contr |  | CON - Connaught Tunnel (East) |  | 2012-10-23 | 2012-10-13 14:08 | -10 | 2012-09-14 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | The installed columns 468C / 469BD / 472CD / 476C / 478B / 478E have diameters as stated in the attached spreadsheet
| 01CV - Civils | Cxxx-NCR-000512 | NCR | CMC rows 467-459 - Cracked head |  | Contr |  | CON - Connaught Tunnel (East) |  | 2012-10-23 | 2012-10-13 13:58 | -10 | 2012-09-18 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | Cracked heads (Applicable to 459B / 459F / 460D / 462B / 464C / 464F / 465F / 466F) The column from row 467 to 459, have a crack in the column head which have resulted in a piece of the concrete breaking away at the head and side of the column. Removing these cracked pieces has created a smaller pile head and also a void to the side of the column. The sizes of the cracked concrete and the diameters of the column heads are shown on the attached spreadsheet. (It should be noted that the column has achieved the correct diameter and only the head has a smaller diameter.)
| 01CV - Civils | Cxxx-NCR-000513 | NCR | CMC rows 467-459 - Reduced diameter |  | Contr |  | CON - Connaught Tunnel (East) |  | 2012-10-23 | 2012-10-13 13:55 | -10 | 2012-09-18 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | The installed columns 462D / 462F / 463A / 464B / 467D have diameters as stated in the attached spreadsheet
| 01CV - Civils | Cxxx-NCR-000515 | NCR | CMC rows 142-152 – cracked heads |  | Contr |  | CON - Connaught Tunnel (East) |  | 2012-11-29 | 2012-11-19 08:50 | -10 | 2012-10-26 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | The column references 142AF / 144E / 145E / 147AF / 148A / 149C / 151AF / 152A, have a crack in the column head which have resulted in a piece of the concrete breaking away at the head and side of the column. Removing these cracked pieces has created a smaller pile head and also a void to the side of the column. The sizes of the cracked concrete and the diameters of the column heads are shown on the attached spreadsheet. (It should be noted that the column has achieved the correct diameter and only the head has a smaller diameter.)
| 01CV - Civils | Cxxx-NCR-000518 | NCR | Columns 511A, 511E, 514C,517B Cracked Head |  | Contr |  | CON - Connaught Tunnel (East) |  | 2012-09-26 | 2012-09-13 11:07 | -13 | 2012-09-12 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Repair |  | Complete |  | Completed |  | Cracked Head The columns have a crack in the column head which has resulted in a piece of the concrete breaking away at the head and side of the columns. Removing these cracked pieces has created a smaller pile head and also a void to the side of the column.
| 01CV - Civils | Cxxx-NCR-000519 | NCR | Columns with Multiple Issues between rows 511-522 |  | Contr |  | CON - Connaught Tunnel (East) |  | 2012-09-26 | 2012-10-10 15:20 | 14 | 2012-09-13 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | 511B: Cracked Head and Reduced Diameter • Drilling log contained within execution report for 6th June 2012. 511C: Cracked Head and Reduced Diameter • Drilling log contained within execution report for 6th June 2012. 511D: Cracked Head and Reduced Diameter • Drilling log contained within execution report for 28th May 2012. 511F: Cracked Head and Reduced Diameter and Out of Positional Tolerance • Drilling log contained within execution report for 30th May 2012. 512A: Cracked Head and Reduced Diameter • Drilling log contained within execution report for 6th June 2012. 512B: Cracked Head and Reduced Diameter • Drilling log contained within execution report for 6th June 2012. 512C: Cracked Head and Reduced Diameter • Drilling log contained within execution report for 6th June 2012. 512D: Cracked Head and Trimming Level too Low • Drilling log contained within execution report for 29th May 2012. 512F: Cracked Head and Out of Positional Tolerance • Drilling log contained within execution report for 30th May 2012. 513A: Cracked Head and Reduced Diameter • Drilling log contained within execution report for 6th June 2012. 513B: Cracked Head and Reduced Diameter • Drilling log contained within execution report for 6th June 2012. 513E: Cracked Head and Reduced Diameter and Out of Positional Tolerance • Drilling log contained within execution report for 30th May 2012 513F: Cracked Head and Reduced Diameter • Drilling log contained within execution report for 30th May 2012 514B: Cracked Head and Reduced Diameter • Drilling log contained within execution report for 6th June 2012. 514E: Cracked Head and Out of Positional Tolerance • Drilling log contained within execution report for 30th May 2012. 514F: Cracked Head and Reduced Diameter • Drilling log contained within execution report for 30th May 2012. 515F: Cracked Head and Reduced Diameter • Drilling log contained within execution report for 30th May 2012. 516F: Cracked Head and Reduced Diameter • Drilling log contained within execution report for 30th May 2012 517A: Cracked Head and Reduced Diameter • Drilling log contained within execution report for 6th June 2012 517C: Cracked Head and Out of Positional Tolerance • Drilling log contained within execution report for 6th June 2012 517D: Reduced Diameter and Out of Positional Tolerance • Drilling log contained within execution report for 28th May 2012 517F: Cracked Head and Reduced Diameter and Out of Positional Tolerance • Drilling log contained within execution report for 30th May 2012 518A: Cracked Head and Reduced Diameter and Trimming Level too Low • Drilling log contained within execution report for 6th June 2012 518C: Cracked Head and Reduced Diameter • Drilling log contained within execution report for 6th June 2012 518E: Cracked Head and Reduced Diameter • Drilling log contained within execution report for 30th May 2012 518F: Cracked Head and Out of Positional Tolerance • Drilling log contained within execution report for 30th May 2012 519A: Cracked Head and Out of Positional Tolerance • Drilling log contained within execution report for 6th June 2012 519B: Cracked Head and Reduced Diameter and Out of Positional Tolerance • Drilling log contained within execution report for 6th June 2012 519E: Cracked Head and Reduced Diameter • Drilling log contained within execution report for 30th May 2012 520B: Cracked Head and Reduced Diameter and Out of Positional Tolerance • Drilling log contained within execution report for 6th June 2012 520D: Cracked Head and Reduced Diameter • Drilling log contained within execution report for 28th May 2012 520E: Cracked Head and Reduced Diameter • Drilling log contained within execution report for 30th May 2012 520F: Cracked Head and Reduced Diameter and Out of Positional Tolerance • Drilling log contained within execution report for 30th May 2012 521C: Cracked Head and Reduced Diameter • Drilling log contained within execution report for 6th June 2012 521E: Cracked Head and Reduced Diameter and Reinforcement too High • Drilling log contained within execution report for 30th May 2012 522A: Cracked Head and Reduced Diameter and Out of Positional Tolerance • Drilling log contained within execution report for 6th June 2012 522C: Cracked Head and Out of Positional Tolerance • Drilling log contained within execution report for 6th June 2012 522E: Cracked Head and Out of Positional Tolerance • Drilling log contained within execution report for 30th May 2012
| 01CV - Civils | Cxxx-NCR-000522 | NCR | Column 496F Cracked Head and Reduced Diameter |  | Contr |  | CON - Connaught Tunnel (East) |  | 2012-09-28 | 2012-10-13 14:58 | 15 | 2012-09-14 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | Coumn 496F has a cracked head and a reduced diameter. The width and deth of the cracked sections of concrete are 110mm and 200mm repectively leaving the size of the column head 180mm x 110mm. The diameter of the column is also reduced at 200mm.
| 01CV - Civils | Cxxx-NCR-000528 | NCR | Concrete Spacing outside of Tolerance |  | Contr |  | CON - Connaught Tunnel (East) |  | 2012-10-02 | 2012-10-18 14:17 | 16 | 2012-09-18 | Tunnelling - Linings - In-situ Concrete | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | At the time of the CRL inspection for Bay 1 of the Trial Invert Replacement, post Gallaghers and __ Inspection it was identified by CRL that the concrete cover ranged between 55mm and 80mm. Hence up to 19mm outside of the tolerance. To facilitate Self Certification the Contractor must identify any defects, and correct them prior to proceeding with the works or inviting CRL to inspection as appropriate.
| 01CV - Civils | Cxxx-NCR-000529 | NCR | Concrete spacer bar not approved |  | Contr |  | CON - Connaught Tunnel (East) |  | 2012-10-09 | 2012-10-08 16:14 | -1 | 2012-09-18 | Tunnelling - Linings - In-situ Concrete | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | The spacer bars used in trial bays 1 & 2 had dimensions of approximately 75mm x 75mm (as advised by Gallaghers).
| 01CV - Civils | Cxxx-NCR-000531 | NCR | CFA piles West 21B out of position |  | Contr |  | CON - Connaught Tunnel (East) |  | 2012-10-31 | 2012-10-17 08:12 | -14 | 2012-09-20 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | Pile 21B has been installed to the coordinates at trimming level:(91284.772 ; 35433.574) with a vector form design coordinates of 0.109 The piling platform level was 102.60 and the design trim level is 101.3. The allowable tolerance beiing 0.0923, the pile is installed 0.017 out of tolerance
| 01CV - Civils | Cxxx-NCR-000532 | NCR | C32/40- concrete strength below requirement |  | Contr |  | CON - Connaught Tunnel (East) |  | 2012-10-31 | 2012-11-21 09:29 | 21 | 2012-10-01 | Civil - Civil Engineering General | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | Test cubes taken the 3/4/12 for piles E14-16 have only achieved and average of 37.7N/mm2 @ 28 days not the specified 40N/mm2 required. At 56 days, the concrete strength is still 38.9 N/mm2 < 40N/mm2
| 01CV - Civils | Cxxx-NCR-000533 | NCR | Damage to CFA pile heads during cutting them down |  | Contr |  | CON - Connaught Tunnel (East) |  | 2012-10-31 | 2012-10-19 15:59 | -12 | 2012-09-19 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | The following pile heads got chipped ( damaged) during cutting down .Pile no 9B,Pile no 10C, Pile no 11B refer to attached Cxxx-SK-353
| 01CV - Civils | Cxxx-NCR-000546 | NCR | Letterbox in invert replacement trial bay walls |  | Contr |  | CON - Connaught Tunnel (East) |  | 2012-11-02 | 2012-11-13 11:47 | 11 | 2012-10-02 | Civil - Civil Engineering General | 500 |  | Equipment Breakdown | Repair |  | Complete |  | Completed |  | During the pour, the ply guillotine did not work as it was being pushed back into the pour itself and so it was removed completely. This left the entire birdsmouth concrete block atatched to the wall. The day after the pour, the birdsmouth was removed with the low vibration air breaker and broken back past the finished concrete level (max25mm) - leaving an area the full size of the birdsmouth to be made good.
| 01CV - Civils | Cxxx-NCR-000558 | NCR | Bent/snapped CFA rebar in Bays W1a and W2a |  | Contr |  | CON - Connaught Tunnel (East) |  | 2012-11-23 | 2012-11-22 14:06 | -1 | 2012-10-09 | Civil - Civil Engineering General | 500 |  | Damaged | Repair |  | Complete |  | Completed |  | CFA 38C rebar has been bent and several bars have snapped above pile cut-off level. CFA 34B - 1 No. bar is bent OHLE CFA 4b has bent bars due to excavator trafficking OHLE CFA 6 has bent bars due to excavator trafficking See attached photos for evidence.
| 01CV - Civils | Cxxx-NCR-000562 | NCR | CFA pile no 38C |  | Contr |  | CON - Connaught Tunnel (East) |  | 2012-11-30 | 2012-11-22 13:43 | -8 | 2012-10-06 | Civil - Civil Engineering General | 500 |  | Damaged | Repair |  | Complete |  | Completed |  | On pile no 38C 6 number reinforcement bars were cut during trimming down due to non-presence of the deboning foam (see attached sketch Cxxx-SK-374/1 and Cxxx-SK-374/2)
| 01CV - Civils | Cxxx-NCR-000563 | NCR | Engineering fill between eb ch 17227 and ch 17248 |  | Contr |  | CON - Connaught Tunnel (East) |  | 2012-11-30 | 2012-10-10 15:09 | -51 | 2012-10-06 | Civil - Civil Engineering General | 500 |  | Workmanship | Rework |  | Complete |  | Completed |  | The area between EB ch 17227 and EB ch 17248 excavated 70mm below the formation level removing the soft ground caused by rainwater. refe to Cxxx-SK-376 and Cxxx-SK-367/2
| 01CV - Civils | Cxxx-NCR-000564 | NCR | Damage to CFA pile heads during cutting them down |  | Contr |  | CON - Connaught Tunnel (East) |  | 2012-11-30 | 2012-10-19 14:55 | -42 | 2012-10-06 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | The following pile heads got chipped ( damaged) during cutting down .Pile no 27B,Pile no 31C, Pile no 37B and pile 34B refer to attached Cxxx-SK-367, Cxxx-SK-372,Cxxx-SK-373, Cxxx-SK-375/1
| 01CV - Civils | Cxxx-NCR-000566 | NCR | OHLE VFA Piles 59 & 60 in Bay E12 |  | Contr |  | CON - Connaught Tunnel (East) |  | 2012-10-31 | 2012-10-23 16:13 | -8 | 2012-10-08 | Civil - Geotechnical Engineering | 500 |  | Workmanship | Rework |  | Complete |  | Completed |  | During Pile Breakdown works the angle of the saw cut was not horizontal resulting in the level of the CFA pile being -45mm in places
| 01CV - Civils | Cxxx-NCR-000568 | NCR | Plate Bearing Test 17 East LTP Bay E12 |  | Contr |  | CON - Connaught Tunnel (East) |  | 2012-11-12 | 2012-10-24 14:10 | -19 | 2012-10-08 | Civil - Geotechnical Engineering | 500 |  | Design | Rework |  | Complete |  | Completed |  | Stiffness acheived on Test 17 was 23.8MPa further tests were carried out on the centre rip of the LTP as per attached sketch and schedule with passes and failures. Compaction was carried out in accordance with the ITP, NDM's were carried out on Layers 1 & 2 on the outer edges only. It was decided to carry out an NDM test on the Centre and the initial NDM test passed. It was decided to remove the entire centre rip and replace with newly imported 6N whilst gradings and tests were taken on the removed material
| 01CV - Civils | Cxxx-NCR-000579 | NCR | Plate Bearing Test 13 East LTP Bay E10 |  | Contr |  | CON - Connaught Tunnel (East) |  | 2012-11-06 | 2012-10-17 09:05 | -20 | 2012-10-09 | Geotechnical Engineering - Geotechnical Engineering - General | 500 |  | Design | Rework |  | Complete |  | Completed |  | Plate Bearing Test 13 on the LTP in Bay E10 has failed to acheive stiffness of 50MPa, A further test was carried out at Locaton 13A which also failed to achiece stiffness of 50MPa. However Test 14 acheived 60MPa. Please find attached summary of results and plan location of tests. Please note Test 13I was carried out on Layer 2 which was subsequently removed and relaid and is provided for information only
| 01CV - Civils | Cxxx-NCR-000582 | NCR | Formation Bay E9 |  | Contr |  | CON - Connaught Tunnel (East) |  | 2012-11-06 | 2012-10-17 08:33 | -20 | 2012-10-09 | Civil - Geotechnical Engineering | 500 |  | Damaged | Rework |  | Complete |  | Completed |  | Formation is damaged after being exposed to the weather between Rows 438-458 approx in Bay E9. Area will have to be scraped to remove 'slush' resulting in formation being out of level toelrance.
| 01CV - Civils | Cxxx-NCR-000585 | NCR | Damage to CFA pile heads during cutting them down (20B) |  | Contr |  | CON - Connaught Tunnel (East) |  | 2012-11-30 | 2012-10-28 14:15 | -33 | 2012-10-10 | Civil - Civil Engineering General | 500 |  |  | Repair |  | Complete |  | Completed |  | The following pile heads got chipped ( damaged) during cutting down .Pile no 20B (photo attached)
| 01CV - Civils | Cxxx-NCR-000586 | NCR | OHLE CFA Piles 65 & 66 in Bay E16 |  | Contr |  | CON - Connaught Tunnel (East) |  | 2012-11-07 | 2012-10-24 16:33 | -14 | 2012-10-10 | Civil - Geotechnical Engineering | 500 |  | Planning | Repair |  | Complete |  | Completed |  | The piling platform was installed to a level of 500mm above CMC COL to allow installation of CMC Columns resulting in the platform being 50mm above CFA COL. Generally Piles are cast at least 300mm above COL to ensure sound concrete at COL. This was not picked up for the installation of the CFA Piles until the cages were being levelled. Approximately 100mm of concrete was removed to "sound" concrete resulting in OHLE Pile 65 being 77mm below COL and OHLE Pile being 50mm below COL.
| 01CV - Civils | Cxxx-NCR-000587 | NCR | CMC rows 458 to 448 - out of position |  | Contr |  | CON - Connaught Tunnel (East) |  | 2012-11-15 | 2012-10-23 16:17 | -23 | 2012-10-15 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | The columns 451C and 453C have been installed as per the attached spreadsheet This is distance from the designed co-ordinate is stated.
| 01CV - Civils | Cxxx-NCR-000590 | NCR | CMC rows 458 to 448 - reduced diameter |  | Contr |  | CON - Connaught Tunnel (East) |  | 2012-11-21 | 2012-10-23 16:22 | -29 | 2012-10-15 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | Reduced diameter (Applicable to 448AD / 453D / 455D / 456DE / 457D / 458F ) The installed columns have diameters as stated in the attached spreadsheet
| 01CV - Civils | Cxxx-NCR-000591 | NCR | CMC rows 458 to 448 – cracked heads |  | Contr |  | CON - Connaught Tunnel (East) |  | 2012-11-21 | 2012-11-08 16:49 | -13 | 2012-10-15 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | The column references 448F / 449B / 450F / 451AE / 452E, have a crack in the column head which have resulted in a piece of the concrete breaking away at the head and side of the column. Removing these cracked pieces has created a smaller pile head and also a void to the side of the column. The sizes of the cracked concrete and the diameters of the column heads are shown on the attached spreadsheet. (It should be noted that the column has achieved the correct diameter and only the head has a smaller diameter.)
| 01CV - Civils | Cxxx-NCR-000592 | NCR | CMC rows 458 to 448 - multiple issues |  | Contr |  | CON - Connaught Tunnel (East) |  | 2012-11-21 | 2012-11-08 16:49 | -13 | 2012-10-15 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | Cracked Head Column NCR (Applicable to 448BCE / 449ACDEF / 450ABCDE / 451B / 452ABCDF / 453ABEF / 454ABCDEF / 455ABCEF / 456ABCF / 457ABCEF / 458ABCDE) The columns from row 458 to 448 have a crack in the column head which have resulted in a piece of the concrete breaking away at the head and side of the column. Removing these cracked pieces has created a smaller pile head and also a void to the side of the column. The sizes of the cracked concrete and the diameters of the column heads are shown on the attached spreadsheet. (It should be noted that the column has achieved the correct diameter and only the head has a smaller diameter.) Out of Position (Applicable to 448BC / 450AC / 451B / 452C / 453ABF / 454ACF / 455ABC / 456ABC / 457ABCE / 458ABCD / 459ACD / 460ACE) The columns have been installed as per the attached spreadsheet This is distance from the designed co-ordinate is stated. Reduced Diameter (Applicable to 448CE / 449ACDEF / 450BCDE / 452ABCDF / 453AEF / 454A-F / 455ABCEF / 456ABCF / 457ABF / 458ABDE) The installed columns have diameters as stated in the attached spreadsheet Columns too low / Mechanical damage (Applicable to 449C/450D / 451B / 454E / 455E )
| 01CV - Civils | Cxxx-NCR-000593 | NCR | CMC rows 447 to 436 - cracked heads |  | Contr |  | CON - Connaught Tunnel (East) |  | 2012-11-21 | 2012-11-08 16:51 | -13 | 2012-10-15 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | The column references 436AB / 437AD / 438AE / 439B / 442F / 443AB / 445E / 446AE / 447F have a crack in the column head which have resulted in a piece of the concrete breaking away at the head and side of the column. Removing these cracked pieces has created a smaller pile head and also a void to the side of the column. The sizes of the cracked concrete and the diameters of the column heads are shown on the attached spreadsheet. (It should be noted that the column has achieved the correct diameter and only the head has a smaller diameter.)
| 01CV - Civils | Cxxx-NCR-000594 | NCR | CMC rows 447 to 436 - reduced diameter |  | Contr |  | CON - Connaught Tunnel (East) |  | 2012-11-21 | 2012-10-23 16:25 | -29 | 2012-10-15 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | Reduced diameter (Applicable to 437E / 438B / 442E / 443C / 447C ) The installed columns have diameters as stated in the attached spreadsheet
| 01CV - Civils | Cxxx-NCR-000595 | NCR | CMC rows 447 to 436 - multiple issues |  | Contr |  | CON - Connaught Tunnel (East) |  | 2012-11-21 | 2012-11-08 16:29 | -13 | 2012-10-15 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | Cracked Head Column NCR (Applicable to 436CDEF / 437BC / 438CDF / 439ACDEF / 440ABCDEF / 441ACEF / 442ABCD / 443DEF / 444CDEF / 445ABCDF / 446ABCDF / 447ABDE ) The columns from row 447 to 436 , have a crack in the column head which have resulted in a piece of the concrete breaking away at the head and side of the column. Removing these cracked pieces has created a smaller pile head and also a void to the side of the column. The sizes of the cracked concrete and the diameters of the column heads are shown on the attached spreadsheet. (It should be noted that the column has achieved the correct diameter and only the head has a smaller diameter.) Out of Position (Applicable to 437C / 438CDF / 439ACEF / 440ABDF / 441AC / 442B / 443E / 445AC / 447A) The columns have been installed as per the attached spreadsheet This is distance from the designed co-ordinate is stated. Reduced Diameter (Applicable to 436CDEF / 437BC / 438F / 439CDEF / 440CDEF / 441CEF / 442ACD / 443DEF / 444CDEF / 445ABCDF / 446BCDF / 447ABDE ) The installed columns have diameters as stated in the attached spreadsheet Columns too low / Mechanical damage (Applicable to 445A /445C / 446A / 446C/ 440AF / 436C / 437BC ) Trimming level is as per the attached spread sheet Reinforcement too high (Applicable to 445B) The reinforcement is per the attached schedule. The reinforcement has achieved the requirement of being embedding within the river terrace deposits a minimum of 925mm.
| 01CV - Civils | Cxxx-NCR-000596 | NCR | CFA pile cut off level outside the tolerance |  | Contr |  | CON - Connaught Tunnel (East) |  | 2012-11-30 | 2012-10-29 12:10 | -32 | 2012-10-11 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | During the trimming down works some of the piles got trimmed below the cut off level (as per the attched schedule)
| 01CV - Civils | Cxxx-NCR-000597 | NCR | CFA Pile OHLE 54 in Bay E9 |  | Contr |  | CON - Connaught Tunnel (East) |  | 2012-12-07 | 2012-12-06 12:26 | -1 | 2012-10-11 | Civil - Civil Engineering General | 500 |  | Damaged | Repair |  | Complete |  | Completed |  | During Pile Breakdown of OHLE 54 4 No 16mm Starter Bars were damaged at cut of level
| 01CV - Civils | Cxxx-NCR-000598 | NCR | Bending rebar manually |  | Contr |  | CON - Connaught Tunnel (East) |  | 2012-11-30 | 2012-10-29 11:57 | -32 | 2012-10-12 | Civil - Civil Engineering General | 500 |  | Workmanship | Rework |  | Complete |  | Completed |  | Following the cutting down of CFA piles, (bay w1a and bay w2a) some of the reinforcement bars have been bent manually to achieve the splice using a site made hickey type re bar bending tool with a scaffold tube
| 01CV - Civils | Cxxx-NCR-000600 | NCR | Debonding foam below the pile cut off level on surface rail west (Rows B,C 10-55) |  | Contr |  | CON - Connaught Tunnel (East) |  | 2012-11-30 | 2012-10-28 14:19 | -33 | 2012-10-11 | Civil - Civil Engineering General | 500 |  | Damaged | Repair |  | Complete |  | Completed |  | On following CFAs debonding foam has encroached below cut off level (maximum up to 25mm) 12B, 14C, 15A, 15B,16C, 17B, 17C,18B,19C,20C,22B,23B,23C,24C,25C,28C,29B,30B,52C,55B
| 01CV - Civils | Cxxx-NCR-000606 | NCR | CMCs 72B, 118F, 146C outside of verticality tolerance |  | Contr |  | CON - Connaught Tunnel (East) |  | 2012-12-01 | 2012-10-19 15:10 | -43 | 2012-10-12 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | Considering the CMC logs, three CMCs constructed were found to have exceeded the verticality limit: 72B, 1.0° in Y direction 118F, -3.0° in Y direction 146C, 1.0° in Y direction NB. The attached drilling logs labelled 119F and 147C are correct for CMCs 118F and 146C respectively – they were labelled incorrectly and the pile reference/log reference comparison is shown in the attached file.
| 01CV - Civils | Cxxx-NCR-000611 | NCR | Toe Depth of M&E Building CFA Pile - P8 |  | Contr |  | CON - Connaught Tunnel (East) |  | 2012-11-16 | 2012-11-01 17:06 | -15 | 2012-10-17 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | Pile reinforcement cage for pile P8 of the M&E Building installed 80mm high (30mm outside specified tolerance) due to being unable to sink cage any further within the fully bored pile. Actual toe level of pile reinforcement = 95.280m ATD
| 01CV - Civils | Cxxx-NCR-000612 | NCR | Toe Depth of M&E Building CFA Pile - P6 |  | Contr |  | CON - Connaught Tunnel (East) |  | 2012-11-16 | 2012-11-09 17:11 | -7 | 2012-10-17 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | Pile reinforcement cage for pile P6 of the M&E Building installed 355mm high (305mm outside specified tolerance) due to being unable to sink cage any further within the fully bored pile. Attempt made to remove cage to rebore pile but the lift capacity required to pull the cage out exceeded the piling rig's SWL. Actual toe level of pile reinforcement = 95.555m ATD
| 01CV - Civils | Cxxx-NCR-000613 | NCR | M&E Building Pile Reinforcement Cage - 4 No. bars cut |  | Contr |  | CON - Connaught Tunnel (East) |  | 2012-11-16 | 2012-10-29 16:24 | -18 | 2012-10-18 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | Whilst cutting the 7 No. cages for piles P23, P25, P27, P29, P30, P31 and P32 (as required by FCD-Cxxx-00575) an 8th cage started to be cut. 4 No. consecutive Bar Mark 01 bars were cut 850mm from the bottom of the cage. Leaving 8 No. full length bars and 4 No. bars 850mm short.
| 01CV - Civils | Cxxx-NCR-000615 | NCR | Formation Bay E8 |  | Contr |  | CON - Connaught Tunnel (East) |  | 2012-11-30 | 2012-11-27 08:52 | -3 | 2012-10-18 | Civil - Geotechnical Engineering | 500 |  | Damaged | Repair |  | Complete |  | Completed |  | Formation is damaged after being exposed to the weather in Bay E8. Area will have to be scraped to remove 'slush' resulting in formation being out of level toelrance.
| 01CV - Civils | Cxxx-NCR-000617 | NCR | Failure by Contractor to identify defect - Slab E12 Reinforcement |  | Contr |  | CON - Connaught Tunnel (East) |  | 2012-11-23 | 2012-11-13 10:35 | -10 | 2012-11-10 | Civil - Civil Engineering General | 500 |  | Workmanship | Rework |  | Complete |  | Completed |  | The works in question are carried out under ITP ref: Cxxx-VIN-C-ITP-CR146_ST003-50011 Inspection and Test Plan - Surface Rail RC Works At the time of CRL ITP Point 4.06 (Pre-pour Inspection) it was found that there was reduced cover to BM07 at various locations along the base of the wall. CRL had been invited to inspect the works under IRP ref: 0669
| 01CV - Civils | Cxxx-NCR-000618 | NCR | Depth of Bay 12 slab reinforcment out of tolerance |  | Contr |  | CON - Connaught Tunnel (East) |  | 2012-11-16 | 2012-10-31 08:37 | -16 | 2012-10-22 | Civil - Civil Engineering General | 500 |  | Design | Rework |  | Complete |  | Completed |  | On inspection of Bay E12 slab reinforcement, the __ Inspector highlighted that the depth between the top and bottom mats of slab reinforcement was between 320mm and 330mm in most places over the area of the slab. On further inspection the size of chairs dictating the depth of slab were bent correctly to the bending schedule (275mm +/-5mm).
| 01CV - Civils | Cxxx-NCR-000627 | NCR | CMC rows 130-141 – cracked heads |  | Contr |  | CON - Connaught Tunnel (East) |  | 2012-12-04 | 2012-11-19 08:50 | -15 | 2012-10-26 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | The column references 130AE / 131AF / 132AF / 134B / 135A / 136B / 139BF / 140F / 141CE, have a crack in the column head which have resulted in a piece of the concrete breaking away at the head and side of the column. Removing these cracked pieces has created a smaller pile head and also a void to the side of the column. The sizes of the cracked concrete and the diameters of the column heads are shown on the attached spreadsheet. (It should be noted that the column has achieved the correct diameter and only the head has a smaller diameter.)
| 01CV - Civils | Cxxx-NCR-000629 | NCR | CMC rows 130-141 - multiple issues |  | Contr |  | CON - Connaught Tunnel (East) |  | 2012-12-04 | 2012-11-19 08:51 | -15 | 2012-10-31 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | Cracked Head Column NCR (Applicable to 130BCD / 131BCD / 132BCE / 133A-F / 134ACDE / 135BCDEF / 136ACDEF / 137DEF / 138AEF / 140ADE / 141F) The columns from row 130-141 have a crack in the column head which have resulted in a piece of the concrete breaking away at the head and side of the column. Removing these cracked pieces has created a smaller pile head and also a void to the side of the column. The sizes of the cracked concrete and the diameters of the column heads are shown on the attached spreadsheet. (It should be noted that the column has achieved the correct diameter and only the head has a smaller diameter.) Out of Position (Applicable to 130CF / 131CD / 132E / 133BCD / 134CDEF / 135BCEF / 136C / 137DEF / 138A / 140AD / 141A) The columns have been installed as per the attached spreadsheet This is distance from the designed co-ordinate is stated. Reduced Diameter (Applicable to 130BC / 131__C / 132BE / 133ABEF / 134ADEF / 136ACDE / 137DEF / 138DEF / 141F) The installed columns have diameters as stated in the attached spreadsheet Columns too low / Mechanical damage (Applicable to 130D / 132C / 135D / 136F / 137DF / 138AD / 140DE) Reinforcement too high (Applicable to 130F / 134F / 135B / 136D / 141A ) The reinforcement is per the attached schedule. The reinforcement has achieved the requirement of being embedding within the river terrace deposits a minimum of 925mm.
| 01CV - Civils | Cxxx-NCR-000630 | NCR | CMC rows 153-154 - multiple issues |  | Contr |  | CON - Connaught Tunnel (East) |  | 2013-01-16 | 2013-01-21 15:02 | 5 | 2012-10-31 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | Cracked Head Column NCR (Applicable to 153CDEF / 154BCDE) The columns from row 153-154 have a crack in the column head which have resulted in a piece of the concrete breaking away at the head and side of the column. Removing these cracked pieces has created a smaller pile head and also a void to the side of the column. The sizes of the cracked concrete and the diameters of the column heads are shown on the attached spreadsheet. (It should be noted that the column has achieved the correct diameter and only the head has a smaller diameter.) Out of Position (Applicable to 153BCDE / 154BDE) The columns have been installed as per the attached spreadsheet This is distance from the designed co-ordinate is stated. Reduced Diameter (Applicable to 153BF / 154CDE) The installed columns have diameters as stated in the attached spreadsheet Columns too low / Mechanical damage (Applicable to 153E / 154BCD )
| 01CV - Civils | Cxxx-NCR-000631 | NCR | CMC rows 130-141 - out of position |  | Contr |  | CON - Connaught Tunnel (East) |  | 2012-12-04 | 2012-11-07 09:29 | -27 | 2012-10-31 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | The columns 131E / 137BC / 138C / 139AE / 140BC / 141B / 141D have been installed as per the attached spreadsheet This is distance from the designed co-ordinate is stated.
| 01CV - Civils | Cxxx-NCR-000632 | NCR | CMC rows 142-152 - out of position |  | Contr |  | CON - Connaught Tunnel (East) |  | 2012-12-04 | 2012-11-07 09:31 | -27 | 2012-10-31 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | The columns 143C / 145AF / 148E / 150E / 151BD have been installed as per the attached spreadsheet This is distance from the designed co-ordinate is stated.
| 01CV - Civils | Cxxx-NCR-000633 | NCR | CMC rows 142-152 - multiple issues |  | Contr |  | CON - Connaught Tunnel (East) |  | 2012-12-04 | 2012-11-19 08:51 | -15 | 2012-10-31 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | Cracked Head Column NCR (Applicable to 142CD / 143ABF / 144AB / 145B / 146BCDEF / 147BCE / 148B / 149A 150BCDF / 151CE / 152BCDEF) The columns from row 142-152 have a crack in the column head which have resulted in a piece of the concrete breaking away at the head and side of the column. Removing these cracked pieces has created a smaller pile head and also a void to the side of the column. The sizes of the cracked concrete and the diameters of the column heads are shown on the attached spreadsheet. (It should be noted that the column has achieved the correct diameter and only the head has a smaller diameter.) Out of Position (Applicable to 142CD / 143F / 144AB / 145BC / 146ACDF / 147E / 149B / 150BDF / 151CE / 152BDEF) The columns have been installed as per the attached spreadsheet This is distance from the designed co-ordinate is stated. Reduced Diameter (Applicable to 142D / 146B / 152CE) The installed columns have diameters as stated in the attached spreadsheet Columns too low / Mechanical damage (Applicable to 142CD / 143B / 145B / 146CDE / 147BCE / 148B / 149AB / 150C / 151C / 152CD ) Reinforcement too high (Applicable to 143A / 144A / 145C / 146AC) The reinforcement is per the attached schedule. The reinforcement has achieved the requirement of being embedding within the river terrace deposits a minimum of 925mm. Reinforcement not achieving the required embedment (Applicable to 143A / 144A / 146A ) The reinforcement is per the attached schedule. The reinforcement has not achieved the requirement of being embedding within the river terrace deposits a minimum of 925mm. The embedment is between 0.81 and 0.89m
| 01CV - Civils | Cxxx-NCR-000659 | NCR | Column CMC 434D |  | Contr |  | CON - Connaught Tunnel (East) |  | 2012-11-30 | 2012-11-08 15:38 | -22 | 2012-10-31 | Civil - Geotechnical Engineering | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | Bay 8 Defect Inspection IR 990 @ 08:00, CMC 434D crack inducer was still in CMC column 222mm below COL
| 01CV - Civils | Cxxx-NCR-000660 | NCR | Integrity Testing before time on IR |  | Contr |  | CON - Connaught Tunnel (East) |  | 2012-11-30 | 2012-11-09 17:14 | -21 | 2012-10-31 | Civil - Geotechnical Engineering | 500 |  | System Defect | Rework |  | Complete |  | Completed |  | IR 980 was submitted to CRL on 15/10/2012 for witnessing Integrity Tests on CMC 440F,433C & 432C on 16/10/2012 @ 08:30 prior to grouting. These tests were carried out @ 08:20 without giving CRL an opportuinty to witness.
| 01CV - Civils | Cxxx-NCR-000661 | NCR | Column 434D Crack Inducer too Low |  | Contr |  | CON - Connaught Tunnel (East) |  | 2012-11-30 | 2012-10-31 13:39 | -30 | 2012-10-31 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | The crack inducer for 434D has been installed too low which has resulted in the column trimming level too low. Trimming level: 100.472 Top of reinforcement: 100.536
| 01CV - Civils | Cxxx-NCR-000664 | NCR | OHLE piles 4b and 6. Bent reinforcement bars |  | Contr |  | CON - Connaught Tunnel (East) |  | 2012-11-30 | 2012-11-22 13:45 | -8 | 2012-10-31 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | The reinforcement in OHLE piles 4b and 6 have been manually bent which creates a risk that the bar has been over stressed.
| 01CV - Civils | Cxxx-NCR-000666 | NCR | Bay E16 Downstand Wall Concrete Quality |  | Contr |  | CON - Connaught Tunnel (East) |  | 2013-01-30 | 2013-03-18 12:26 | 47 | 2012-10-31 | Civil - Civil Engineering General | 500 |  | Material | Repair |  | Complete |  | Completed |  | On striking the north and south downstand walls on Bay E16 it was found that concrete finish was not to specification with colour change and surface pitting. On closer inspection it was found that the surface of the concrete had small 'air holes' in it.
| 01CV - Civils | Cxxx-NCR-000673 | NCR | Tunnel Concrete Mix Trial Cubes |  | Contr |  | CON - Connaught Tunnel (East) |  | 2013-01-18 | 2012-11-05 10:35 | -74 | 2012-11-02 | Civil - Civil Engineering General | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | Only 1No set of 9 cubes was taken prior to the MCR (Cxxx-VIN-C-RSP-CR146_ST003-50088)being submitted and approved Code 1. All concrete cubes that were tested were above strength (see attached MCR showing 28 day strength ~56N/mm2)
| 01CV - Civils | Cxxx-NCR-000677 | NCR | CMC 144D reinforcement too high |  | Contr |  | CON - Connaught Tunnel (East) |  | 2012-12-17 | 2012-11-08 16:43 | -39 | 2012-11-05 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | The reinforcement has been installed 115mm above tolerance (100.215mOD). The reinforcement has achieved the requirement of being embedding within the river terrace deposits a minimum of 925mm (1.2m).
| 01CV - Civils | Cxxx-NCR-000679 | NCR | CMC 430B - out of position |  | Contr |  | CON - Connaught Tunnel (East) |  | 2012-12-17 | 2012-11-08 16:41 | -39 | 2012-11-06 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | The columns have been installed at the following coordinates:( 92500.256 ; 34543.518) Vector 0.109 This is distance from the designed co-ordinate is stated.
| 01CV - Civils | Cxxx-NCR-000680 | NCR | CMC rows 435-424 - cracked heads |  | Contr |  | CON - Connaught Tunnel (East) |  | 2013-01-16 | 2013-01-15 09:24 | -1 | 2012-11-06 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | The column references 429B / 432A / 433A / 435A / 435E have a crack in the column head which have resulted in a piece of the concrete breaking away at the head and side of the column. Removing these cracked pieces has created a smaller pile head and also a void to the side of the column. The sizes of the cracked concrete and the diameters of the column heads are shown on the attached spreadsheet. (It should be noted that the column has achieved the correct diameter and only the head has a smaller diameter.)
| 01CV - Civils | Cxxx-NCR-000681 | NCR | CMC rows 435 to 424 - reduced diameter |  | Contr |  | CON - Connaught Tunnel (East) |  | 2012-12-17 | 2012-11-07 09:36 | -40 | 2012-11-06 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | Reduced diameter (Applicable to 425C / 425D / 429D ) The installed columns have diameters as stated in the attached spreadsheet
| 01CV - Civils | Cxxx-NCR-000682 | NCR | CMC rows 435 to 424 - multiple issues |  | Contr |  | CON - Connaught Tunnel (East) |  | 2013-01-16 | 2013-01-15 09:26 | -1 | 2012-11-06 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | Cracked Head Column NCR (Applicable to 424ABCDEF / 425AF / 426BCDEF / 427ABCDEF / 428ABCDEF / 429ACE / 430ACDEF / 431ABCDEF / 432BCDEF / 433BCDEF / 434ABCF / 435BCDF) The columns from row 435 to 424, have a crack in the column head which have resulted in a piece of the concrete breaking away at the head and side of the column. Removing these cracked pieces has created a smaller pile head and also a void to the side of the column. The sizes of the cracked concrete and the diameters of the column heads are shown on the attached spreadsheet. (It should be noted that the column has achieved the correct diameter and only the head has a smaller diameter.) Out of Position (Applicable to 424AC / 426DEF / 427ABDE / 428BCDEF / 429AF / 430A / 431ABD / 432BF / 433CDEF / 434ABCF / 435BCD) The columns have been installed as per the attached spreadsheet This is distance from the designed co-ordinate is stated. Reduced Diameter (Applicable to 424DEF / 425AF / 426CDEF / 427ADEF / 428ABD / 429ACEF / 430CDEF / 431ADEF / 432CDEF / 433BDE / 435CDF ) The installed columns have diameters as stated in the attached spreadsheet Columns too low / Mechanical damage (Applicable to424C / 426B / 427C / 428C / 429C / 430C / 431C / 432C / 433C / 434B / 434C) Trimming level is as per the attached spread sheet
| 01CV - Civils | Cxxx-NCR-000683 | NCR | CMC rows 598-595 - out of position |  | Contr |  | CON - Connaught Tunnel (East) |  | 2012-12-17 | 2012-11-28 10:26 | -19 | 2012-11-06 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | The columns 596D / 597B / 598B / 598F have been installed as per the attached spreadsheet This is distance from the designed co-ordinate is stated.
| 01CV - Civils | Cxxx-NCR-000684 | NCR | CMC rows 623 – 599 out of position |  | Contr |  | CON - Connaught Tunnel (East) |  | 2012-12-17 | 2012-11-26 11:54 | -21 | 2012-11-06 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | The columns 602A / 605B / 606ADF / 608BF / 609CE / 610AE / 611C / 612CD / 613F / 620D / 621C / 622F / 623ADEF have been installed as per the attached spreadsheet This is distance from the designed co-ordinate is stated.
| 01CV - Civils | Cxxx-NCR-000689 | NCR | Bay W1a Blinding Levels |  | Contr |  | CON - Connaught Tunnel (East) |  | 2012-11-30 | 2012-11-15 09:30 | -15 | 2012-11-06 | Civil - Civil Engineering General | 500 |  | Workmanship | Rework |  | Complete |  | Completed |  | Witihin Bay W1a there are 2No localised areas of blinding concrete (8mx1m & 3mx1m sections along the southern face of slab) which are lower than the designed level greater than 30mm (max 40mm lower than design).
| 01CV - Civils | Cxxx-NCR-000696 | NCR | Plate Bearing Test on East LTP Bay E9 Location 441E |  | Contr |  | CON - Connaught Tunnel (East) |  | 2012-12-20 | 2012-12-07 08:54 | -13 | 2012-11-08 | Civil - Geotechnical Engineering | 500 |  | System Defect | Rework |  | Complete |  | Completed |  | Plate Bearing Tests were carried out in bay E9 as per locations agreed in PTR 667. Tests 457C, 453B & 446C were carried out on 02/11/2012 and minimum stiffness was achieved on the second cycle. Test 441 E was carried out on 05/11/2012 and failed to achieve 50MPa on second cycle
| 01CV - Civils | Cxxx-NCR-000697 | NCR | Non-Accepted Temporary Works Design being used at site |  | Contr |  | CON - Connaught Tunnel (East) |  | 2012-11-27 | 2012-11-15 17:49 | -12 | 2012-11-08 | Tunnelling - Linings - In-situ Concrete | 500 |  | Design | Use As-Is |  | Complete |  | Completed |  | The Temporary Works design being used at site is Cxxx-VIN-C-RGN-CR146_ST003-50739 Rev 2.0 (Design 21 - Formwork for Wall Systems and Ties). Rev 2.0 has not been accepted by Crossrial to date and thus a non-accepted design is being implemented at site.
| 01CV - Civils | Cxxx-NCR-000698 | NCR | Commencement of Bay 10 without accepted Design |  | Contr |  | CON - Connaught Tunnel (East) |  | 2012-11-20 | 2012-11-19 12:55 | -1 | 2012-11-08 | Tunnelling - Linings - In-situ Concrete | 500 |  | Design | Use As-Is |  | Complete |  | Completed |  | Bay 10 rebar installation has commenced and materials have been procured prior to submission and acceptance of the Rebar Detail Drawings.
| 01CV - Civils | Cxxx-NCR-000699 | NCR | Rebar being modified at site and not as per Design |  | Contr |  | CON - Connaught Tunnel (East) |  | 2012-12-01 | 2012-11-19 12:56 | -12 | 2012-11-08 | Tunnelling - Linings - In-situ Concrete | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | Rebar (Bar Mark 11) is being bent at site to accomodate combined diameter of the lacers (BM 07) and U-bars (BM 15) at the most easterly 1m of Bay 11 North Twin Tunnel Wall. This is a deviation from the design and also from the specification (KF10.3103 a)).
| 01CV - Civils | Cxxx-NCR-000705 | NCR | CMC rows 423-419 - cracked heads |  | Contr |  | CON - Connaught Tunnel (East) |  | 2013-01-16 | 2013-01-15 09:52 | -1 | 2012-11-20 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | The column references 414CDEF / 415F / 416E / 418B / 421B have a crack in the column head which have resulted in a piece of the concrete breaking away at the head and side of the column. Removing these cracked pieces has created a smaller pile head and also a void to the side of the column. The sizes of the cracked concrete and the diameters of the column heads are shown on the attached spreadsheet. (It should be noted that the column has achieved the correct diameter and only the head has a smaller diameter.)
| 01CV - Civils | Cxxx-NCR-000706 | NCR | CMC rows 423-419 - reduced diameter |  | Contr |  | CON - Connaught Tunnel (East) |  | 2012-12-21 | 2012-11-21 14:04 | -30 | 2012-11-20 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | The installed columns have diameters as stated in the attached spreadsheet
| 01CV - Civils | Cxxx-NCR-000707 | NCR | CMC rows 423 - 419 - out of position |  | Contr |  | CON - Connaught Tunnel (East) |  | 2012-12-21 | 2012-12-18 13:55 | -3 | 2012-11-20 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | The columns 414A / 415C have been installed as per the attached spreadsheet This is distance from the designed co-ordinate is stated.
| 01CV - Civils | Cxxx-NCR-000708 | NCR | CMC rows 423-419 - multiple issues |  | Contr |  | CON - Connaught Tunnel (East) |  | 2013-01-16 | 2013-01-15 09:53 | -1 | 2012-11-20 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | Cracked Head Column NCR (Applicable to 414B / 415ADE / 416ABC / 417ABDE / 418ADF / 419ADEF / 420ABCDF / 421ADEF / 422ABDEF / 423ADEF ) The columns from row 423 to 419, have a crack in the column head which have resulted in a piece of the concrete breaking away at the head and side of the column. Removing these cracked pieces has created a smaller pile head and also a void to the side of the column. The sizes of the cracked concrete and the diameters of the column heads are shown on the attached spreadsheet. (It should be noted that the column has achieved the correct diameter and only the head has a smaller diameter.) Out of Position (Applicable to 414B / 415DE / 416ABC / 417BDF / 418AD / 419AF / 420BCD / 421A / 422AB / 423AB) The columns have been installed as per the attached spreadsheet This is distance from the designed co-ordinate is stated. Reduced Diameter (Applicable to 415A / 416AF / 417ACDEF / 418ACDF / 419ADEF / 420ADF / 421DEF / 422ADEF / 423ACDEF) The installed columns have diameters as stated in the attached spreadsheet Columns too low / Mechanical damage (Applicable to 416F / 417F / 418C / 420C / 423B / 423C) Trimming level is as per the attached spread sheet
| 01CV - Civils | Cxxx-NCR-000709 | NCR | CMC rows 423-419 – Suspected Mechanical damage |  | Contr |  | CON - Connaught Tunnel (East) |  | 2013-01-16 | 2013-01-15 09:54 | -1 | 2012-11-20 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | Suspected Mechanical damage (Applicable 419C / 421C / 422C) Trimming level is as per the attached spread sheet
| 01CV - Civils | Cxxx-NCR-000710 | NCR | Bay E16 Downstand External Wall Finish |  | Contr |  | CON - Connaught Tunnel (East) |  | 2013-01-25 | 2013-02-12 13:25 | 18 | 2012-11-12 | Civil - Civil Engineering General | 500 |  | Material | Repair |  | Complete |  | Completed |  | On striking the formwork on the external faces of the downstand walls on Bay E16 there are areas of surface pitting and pins holes.
| 01CV - Civils | Cxxx-NCR-000726 | NCR | CMC 417C Mechanical Damage |  | Contr |  | CON - Connaught Tunnel (East) |  | 2012-12-20 | 2012-12-18 13:19 | -2 | 2012-12-12 | Civil - Civil Engineering General | 500 |  | Damaged | Repair |  | Complete |  | Completed |  | CMC has a reduced pile diameter of 285mm and pile has potential mechanical damage to a depth of 660mm below design cut off level
| 01CV - Civils | Cxxx-NCR-000728 | NCR | CMC 124F- out of position |  | Contr |  | CON - Connaught Tunnel (East) |  | 2012-12-21 | 2013-01-15 10:14 | 25 | 2012-12-13 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | The column 124F have been installed as per the attached spreadsheet This is distance from the designed co-ordinate is stated.
| 01CV - Civils | Cxxx-NCR-000729 | NCR | CMC rows 115-129 EF - cracked heads |  | Contr |  | CON - Connaught Tunnel (East) |  | 2013-01-16 | 2013-01-22 14:26 | 6 | 2012-12-14 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | The column references 117E / 119E / 120F / 123E / 125F, have a crack in the column head which have resulted in a piece of the concrete breaking away at the head and side of the column. Removing these cracked pieces has created a smaller pile head and also a void to the side of the column. The sizes of the cracked concrete and the diameters of the column heads are shown on the attached spreadsheet. (It should be noted that the column has achieved the correct diameter and only the head has a smaller diameter.)
| 01CV - Civils | Cxxx-NCR-000730 | NCR | CMC 129F – rebar too high |  | Contr |  | CON - Connaught Tunnel (East) |  | 2013-01-16 | 2013-01-15 10:15 | -1 | 2012-12-14 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | Reinforcement too high (Applicable to 129F ) The reinforcement is installed at 100.337, 114mm above tolerance. The reinforcement has achieved the requirement of being embedding within the river terrace deposits a minimum of 925mm. (950mm)
| 01CV - Civils | Cxxx-NCR-000731 | NCR | CMC 128F- diameter too small |  | Contr |  | CON - Connaught Tunnel (East) |  | 2013-01-16 | 2013-01-21 15:05 | 5 | 2012-12-14 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | Reduced Diameter (Applicable to 128F) The installed column has a diameter of 290mm average
| 01CV - Civils | Cxxx-NCR-000732 | NCR | CMC rows 115-129EF – mechanical damage |  | Contr |  | CON - Connaught Tunnel (East) |  | 2013-01-30 | 2013-01-21 15:00 | -9 | 2012-12-14 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | Mechanical damage (Applicable to 122F / 124E / 125E)
| 01CV - Civils | Cxxx-NCR-000733 | NCR | CMC rows 115-129EF - multiple issues |  | Contr |  | CON - Connaught Tunnel (East) |  | 2013-01-16 | 2013-01-25 14:13 | 9 | 2012-12-14 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | Cracked Head Column NCR (Applicable to 115E / 117F / 118EF / 121E / 126EF / 127E / 129E) The columns from row 130-141 have a crack in the column head which have resulted in a piece of the concrete breaking away at the head and side of the column. Removing these cracked pieces has created a smaller pile head and also a void to the side of the column. The sizes of the cracked concrete and the diameters of the column heads are shown on the attached spreadsheet. (It should be noted that the column has achieved the correct diameter and only the head has a smaller diameter.) Out of Position (Applicable to 115E / 116E / 121E / 121F / 126F / 127F / 129E) The columns have been installed as per the attached spreadsheet This is distance from the designed co-ordinate is stated. Reduced Diameter (Applicable to 116E / 117F / 118EF / 120E / 122E / 126E / 127EF / 128E) The installed columns have diameters as stated in the attached spreadsheet Columns too low / Mechanical damage (Applicable to 120E / 121F / 122E / 127F / 128E) Reinforcement too high (Applicable to 129E ) The reinforcement is per the attached schedule. The reinforcement has achieved the requirement of being embedding within the river terrace deposits a minimum of 925mm.
| 01CV - Civils | Cxxx-NCR-000736 | NCR | Engineering Fill Bay E16 |  | Contr |  | CON - Connaught Tunnel (East) |  | 2012-12-20 | 2012-12-12 16:20 | -8 | 2012-11-20 | Civil - Fill | 500 |  | System Defect | Use As-Is |  | Complete |  | Completed |  | Further to PTR COT-CRL-RFI-Cxxx-0551 it was agreed to carry out NDM tests on the 6F5 piling platform post scraping to FL prior to installation of the LTP. This NDM test was not carried out as the original piling platform was temporaray works and installed using method spec compaction and a plate bearing test carried out for the permit to load.
| 01CV - Civils | Cxxx-NCR-000741 | NCR | CMC 128B – cracked head |  | Contr |  | CON - Connaught Tunnel (East) |  | 2013-01-03 | 2013-01-15 10:22 | 12 | 2012-12-14 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | The column reference128B, have a crack in the column head which have resulted in a piece of the concrete breaking away at the head and side of the column. Removing these cracked pieces has created a smaller pile head and also a void to the side of the column. The sizes of the cracked concrete and the diameters of the column heads are shown on the attached spreadsheet. (It should be noted that the column has achieved the correct diameter and only the head has a smaller diameter.)
| 01CV - Civils | Cxxx-NCR-000744 | NCR | CMC rows 126-129 D-A – mechanical damage |  | Contr |  | CON - Connaught Tunnel (East) |  | 2013-01-03 | 2013-01-15 10:23 | 12 | 2012-12-14 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | Mechanical damage (Applicable to 126D / 127D / 128A / 128D)
| 01CV - Civils | Cxxx-NCR-000745 | NCR | CMC 126A – rebar too high |  | Contr |  | CON - Connaught Tunnel (East) |  | 2013-01-03 | 2013-01-21 16:59 | 18 | 2012-12-14 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | Reinforcement too high (Applicable to 129F ) The reinforcement is installed at 100.532, 288mm above tolerance. The reinforcement has achieved the requirement of being embedding within the river terrace deposits a minimum of 925mm. (1.18m)
| 01CV - Civils | Cxxx-NCR-000747 | NCR | CMC rows 126-129 A-D - multiple issues |  | Contr |  | CON - Connaught Tunnel (East) |  | 2013-01-03 | 2013-01-22 15:17 | 19 | 2012-12-14 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | Cracked Head Column NCR (Applicable to 126B/ 126C / 127BC / 128C / 129ABC) The columns from row 126-129 have a crack in the column head which have resulted in a piece of the concrete breaking away at the head and side of the column. Removing these cracked pieces has created a smaller pile head and also a void to the side of the column. The sizes of the cracked concrete and the diameters of the column heads are shown on the attached spreadsheet. (It should be noted that the column has achieved the correct diameter and only the head has a smaller diameter.) Out of Position (Applicable to 126B / 126C / 127B /128C) The columns have been installed as per the attached spreadsheet This is distance from the designed co-ordinate is stated. Reduced Diameter (Applicable to 126C / 127C / 128C / 129ABC) The installed columns have diameters as stated in the attached spreadsheet Columns too low / Mechanical damage (Applicable to 129C)
| 01CV - Civils | Cxxx-NCR-000748 | NCR | CMC rows 413-404- multiple issues |  | Contr |  | CON - Connaught Tunnel (East) |  | 2013-01-03 | 2013-01-24 16:54 | 21 | 2012-11-26 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | Cracked Head Column NCR (Applicable to 404ADEF / 405BC / 406A / 407ABF / 408ADEF / 409ABDEF / 410ABCDF / 411AEF / 412ABDEF / 413ACDE ) The columns from rows 404 to 413 have a crack in the column head which have resulted in a piece of the concrete breaking away at the head and side of the column. Removing these cracked pieces has created a smaller pile head and also a void to the side of the column. The sizes of the cracked concrete and the diameters of the column heads are shown on the attached spreadsheet. (It should be noted that the column has achieved the correct diameter and only the head has a smaller diameter.) Out of Position (Applicable to 404AC / 405BF / 407A / 408D / 409DE / 410C / 411F / 412DE / 413E ) The columns have been installed as per the attached spreadsheet This is distance from the designed co-ordinate is stated. Reduced Diameter (Applicable to 404DE / 405BCF / 406A / 407ABF / 408ABCEF / 409 A-F / 410 ABCDF / 411AEF / 412A-F / 413A-E ) The installed columns have diameters as stated in the attached spreadsheet Columns too low / Mechanical damage (Applicable to 404C / 408B / 408C / 409C / 412C / 413B ) Trimming level is as per the attached spread sheet
| 01CV - Civils | Cxxx-NCR-000749 | NCR | CMC rows 413-404- cracked heads |  | Contr |  | CON - Connaught Tunnel (East) |  | 2013-01-03 | 2013-01-21 14:55 | 18 | 2012-11-26 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | The column reference 413F / 405AE / 406BDE has a crack in the column head which have resulted in a piece of the concrete breaking away at the head and side of the column. Removing these cracked pieces has created a smaller pile head and also a void to the side of the column. The sizes of the cracked concrete and the diameters of the column heads are shown on the attached spreadsheet. (It should be noted that the column has achieved the correct diameter and only the head has a smaller diameter.)
| 01CV - Civils | Cxxx-NCR-000750 | NCR | CMC rows 413-404- reduced diameter |  | Contr |  | CON - Connaught Tunnel (East) |  | 2013-01-03 | 2012-12-18 13:38 | -16 | 2012-11-26 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | Reduced diameter (Applicable to 411D / 410E / 406F ) The installed columns have diameters as stated in the attached spreadsheet
| 01CV - Civils | Cxxx-NCR-000754 | NCR | CMC 407D- out of position |  | Contr |  | CON - Connaught Tunnel (East) |  | 2013-01-03 | 2012-12-18 13:35 | -16 | 2012-11-26 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | The column 407D has been installed as per the attached spreadsheet This is distance from the designed co-ordinate is stated.
| 01CV - Civils | Cxxx-NCR-000756 | NCR | CMC rows 413-404– Mechanical damage |  | Contr |  | CON - Connaught Tunnel (East) |  | 2013-01-03 | 2013-01-24 15:22 | 21 | 2012-12-12 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | Columns too low / Potential Mechanical damage (Applicable to 411C / 406C / 407C) Trimming level is as per the attached spread sheet
| 01CV - Civils | Cxxx-NCR-000758 | NCR | Non compliant geotextile wrap used around water diversion sleeve |  | Contr |  | CON - Connaught Tunnel (East) |  | 2013-01-16 | 2013-01-31 13:30 | 15 | 2012-11-23 | Utilities Engineering - Water | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | The material used is a Lotrak Geotextiles 100 nonwoven geotextile. This product is not that specified for use.
| 01CV - Civils | Cxxx-NCR-000766 | NCR | CMC 124C – cracked head |  | Contr |  | CON - Connaught Tunnel (East) |  | 2013-01-07 | 2013-01-22 14:27 | 15 | 2012-12-13 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | The column reference 124C, have a crack in the column head which have resulted in a piece of the concrete breaking away at the head and side of the column. Removing these cracked pieces has created a smaller pile head and also a void to the side of the column. The sizes of the cracked concrete and the diameters of the column heads are shown on the attached spreadsheet. (It should be noted that the column has achieved the correct diameter and only the head has a smaller diameter.)
| 01CV - Civils | Cxxx-NCR-000767 | NCR | CMC 122D- diameter too small |  | Contr |  | CON - Connaught Tunnel (East) |  | 2013-01-07 | 2013-01-15 09:20 | 8 | 2012-12-14 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | The installed column has a diameter of 305mm average
| 01CV - Civils | Cxxx-NCR-000768 | NCR | CMC 122C, 123A, 123B, 123C &125B out of position |  | Contr |  | CON - Connaught Tunnel (East) |  | 2013-01-07 | 2013-01-22 14:37 | 15 | 2012-12-14 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | The column 122C / 123A / 123B / 123C / 125B have been installed as per the attached spreadsheet This is distance from the designed co-ordinate is stated.
| 01CV - Civils | Cxxx-NCR-000770 | NCR | CMC rows 125-122 A-D - multiple issues |  | Contr |  | CON - Connaught Tunnel (East) |  | 2013-01-07 | 2013-01-22 14:41 | 15 | 2012-12-13 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | Cracked Head Column NCR (Applicable to 122AB / 124AB / 125CD) The columns from row 122-125 have a crack in the column head which have resulted in a piece of the concrete breaking away at the head and side of the column. Removing these cracked pieces has created a smaller pile head and also a void to the side of the column. The sizes of the cracked concrete and the diameters of the column heads are shown on the attached spreadsheet. (It should be noted that the column has achieved the correct diameter and only the head has a smaller diameter.) Out of Position (Applicable to 122AB / 124D / 125ACD) The columns have been installed as per the attached spreadsheet This is distance from the designed co-ordinate is stated. Reduced Diameter (Applicable to 122B / 124AB / 125C) The installed columns have diameters as stated in the attached spreadsheet Columns too low / Mechanical damage (Applicable to 124D / 125ACD)
| 01CV - Civils | Cxxx-NCR-000775 | NCR | CMC 400F- reduced diameter |  | Contr |  | CON - Connaught Tunnel (East) |  | 2013-01-10 | 2012-12-12 16:28 | -29 | 2012-12-10 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | The installed column has an average diameter of 305mm
| 01CV - Civils | Cxxx-NCR-000776 | NCR | CMC 403C– Mechanical damage |  | Contr |  | CON - Connaught Tunnel (East) |  | 2013-01-10 | 2013-01-24 15:20 | 14 | 2012-12-12 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | Potential Mechanical damage (applicable to 403C) Trimming level is as per the attached spread sheet
| 01CV - Civils | Cxxx-NCR-000778 | NCR | CMC rows 399-403- multiple issues |  | Contr |  | CON - Connaught Tunnel (East) |  | 2013-01-10 | 2013-01-24 15:21 | 14 | 2012-12-10 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | Cracked Head Column NCR (Applicable to 399ABCE / 400BDE / 401E / 402BDEF / 403ABDEF ) The columns from rows 404 to 413 have a crack in the column head which have resulted in a piece of the concrete breaking away at the head and side of the column. Removing these cracked pieces has created a smaller pile head and also a void to the side of the column. The sizes of the cracked concrete and the diameters of the column heads are shown on the attached spreadsheet. (It should be noted that the column has achieved the correct diameter and only the head has a smaller diameter.) Out of Position (Applicable to 399ABD / 400D / 401DF / 402D / 403AF ) The columns have been installed as per the attached spreadsheet This is distance from the designed co-ordinate is stated. Reduced Diameter (Applicable to 399CDE / 400BDE / 401CDEF / 402BDEF / 403ABDEF ) The installed columns have diameters as stated in the attached spreadsheet Columns too low / Mechanical damage (Applicable to 401C ) Trimming level is as per the attached spread sheet
| 01CV - Civils | Cxxx-NCR-000780 | NCR | CMC rows 399-403- cracked heads |  | Contr |  | CON - Connaught Tunnel (East) |  | 2013-01-10 | 2013-01-22 14:42 | 12 | 2012-12-10 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | The columns references 399F/400C/400B/402A have a crack in the column head which have resulted in a piece of the concrete breaking away at the head and side of the column. Removing these cracked pieces has created a smaller pile head and also a void to the side of the column. The sizes of the cracked concrete and the diameters of the column heads are shown on the attached spreadsheet. (It should be noted that the column has achieved the correct diameter and only the head has a smaller diameter.)
| 01CV - Civils | Cxxx-NCR-000782 | NCR | Temporary works |  | Contr |  | CON - Connaught Tunnel (East) |  | 2012-12-17 | 2012-12-12 16:33 | -5 | 2012-12-03 | Civil - Civil Engineering General | 500 |  | Design | Use As-Is |  | Complete |  | Completed |  | shutter design deviated from temporary works drawing. No re-submission of drawing to suit site conditions. Furthermore no evidence of signed permit to load on site and concrete pour has commenced.
| 01CV - Civils | Cxxx-NCR-000783 | NCR | CMC rows 118 to 121 A-D - multiple issues |  | Contr |  | CON - Connaught Tunnel (East) |  | 2013-01-14 | 2013-01-22 14:43 | 8 | 2012-12-13 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | Cracked Head Column NCR (Applicable to 118C / 119AB / 120ABC / 121BC) The columns from row 130-141 have a crack in the column head which have resulted in a piece of the concrete breaking away at the head and side of the column. Removing these cracked pieces has created a smaller pile head and also a void to the side of the column. The sizes of the cracked concrete and the diameters of the column heads are shown on the attached spreadsheet. (It should be noted that the column has achieved the correct diameter and only the head has a smaller diameter.) Out of Position (Applicable to 118C / 119BCD / 120ABC / 121BC) The columns have been installed as per the attached spreadsheet This is distance from the designed co-ordinate is stated. Reduced Diameter (Applicable to 118B / 119AD) The installed columns have diameters as stated in the attached spreadsheet Columns too low / Mechanical damage (Applicable to 119C) Reinforcement too high (Applicable to 118B) The reinforcement is per the attached schedule. The reinforcement has achieved the requirement of being embedding within the river terrace deposits a minimum of 925mm.
| 01CV - Civils | Cxxx-NCR-000784 | NCR | CMC rows 118A 120D & 121A – cracked head |  | Contr |  | CON - Connaught Tunnel (East) |  | 2013-01-14 | 2013-01-22 14:57 | 8 | 2012-12-13 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | The columns references 118A / 120D / 121A , have a crack in the column head which have resulted in a piece of the concrete breaking away at the head and side of the column. Removing these cracked pieces has created a smaller pile head and also a void to the side of the column. The sizes of the cracked concrete and the diameters of the column heads are shown on the attached spreadsheet. (It should be noted that the column has achieved the correct diameter and only the head has a smaller diameter.)
| 01CV - Civils | Cxxx-NCR-000785 | NCR | CMC 121D – mechanical damage |  | Contr |  | CON - Connaught Tunnel (East) |  | 2013-01-14 | 2013-01-22 14:58 | 8 | 2012-12-13 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | Mechanical damage (Applicable to 121D)
| 01CV - Civils | Cxxx-NCR-000789 | NCR | CMC rows 114A-F - 115 to 117A-D- multiple issues |  | Contr |  | CON - Connaught Tunnel (East) |  | 2013-01-16 | 2013-01-24 15:28 | 8 | 2012-12-13 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | Cracked Head Column NCR (Applicable to 114ABCE / 115BCD / 116ABCD / 117ABCD) The columns from row 114 to 117 have a crack in the column head which have resulted in a piece of the concrete breaking away at the head and side of the column. Removing these cracked pieces has created a smaller pile head and also a void to the side of the column. The sizes of the cracked concrete and the diameters of the column heads are shown on the attached spreadsheet. (It should be noted that the column has achieved the correct diameter and only the head has a smaller diameter.) Out of Position (Applicable to 114B / 115AB / 116B) The columns have been installed as per the attached spreadsheet This is distance from the designed co-ordinate is stated. Reduced Diameter (Applicable to 114ABCEF / 115ABC / 116ABCD / 117ABC) The installed columns have diameters as stated in the attached spreadsheet Columns too low / Mechanical damage (Applicable to 114F / 115D / 116D)
| 01CV - Civils | Cxxx-NCR-000790 | NCR | CMC 114D – cracked head |  | Contr |  | CON - Connaught Tunnel (East) |  | 2013-01-16 | 2013-01-22 14:52 | 6 | 2012-12-13 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | The column reference 114D, has a crack in the column head which have resulted in a piece of the concrete breaking away at the head and side of the column. Removing these cracked pieces has created a smaller pile head and also a void to the side of the column. The sizes of the cracked concrete and the diameters of the column heads are shown on the attached spreadsheet. (It should be noted that the column has achieved the correct diameter and only the head has a smaller diameter.)
| 01CV - Civils | Cxxx-NCR-000792 | NCR | CFA piles West 30E-34E-50E-51E- out of position |  | Contr |  | CON - Connaught Tunnel (East) |  | 2013-01-16 | 2013-01-22 14:53 | 6 | 2012-12-13 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | Pile 30E has been installed with the coordinates (91301.002, 35424.879), with a vector of 0.123 m Pile 34E has been installed with the coordinates (91308.308, 35425.086), with a vector of 0.122 m Pile 50E has been installed with the coordinates (91336.978, 35426.173), with a vector of 0.125 m Pile 51E has been installed with the coordinates (91338.791, 35426.26), with a vector of 0.121 m
| 01CV - Civils | Cxxx-NCR-000793 | NCR | OLE 3a CFA pile cage bar diameter |  | Contr |  | CON - Connaught Tunnel (East) |  | 2013-06-07 | 2013-06-13 17:34 | 6 | 2013-03-04 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | B16 reinforcement used for OLE 3a CFA cage (as per adjacent Load Case 3 OLE piles). B16 reinforcement scheduled on Cxxx-VIN-C-DWG-CR146_ST003-50021 rev 2 "CFA OHLE Pile Reinforcement Drawing" received Code 2 03-Jul-12. Discrepancy only came to light Dec-12 after installation on site completed.
| 01CV - Civils | Cxxx-NCR-000796 | NCR | Bay 11 west. Extra cover to BM12 splay bar |  | Contr |  | CON - Connaught Tunnel (East) |  | 2012-12-25 | 2012-12-21 10:29 | -4 | 2012-12-06 | Civil - Tunnelling | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | Please see attached as-built survey showing extra cover to the splay bar (BM12) in bay 11 west side. The bars have moved during the preceding concrete pour (upper walls) in a localized area, as shown on the attachment. We proposed to either : 1. Leave as is, with extra cover 2. Install H25 in the area, on the face to reduce the cover.
| 01CV - Civils | Cxxx-NCR-000797 | NCR | CMC rows 398-394- cracked heads |  | Contr |  | CON - Connaught Tunnel (East) |  | 2013-01-17 | 2013-01-22 14:58 | 5 | 2012-12-10 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | The columns references 395A / 397AC / 398AB have a crack in the column head which have resulted in a piece of the concrete breaking away at the head and side of the column. Removing these cracked pieces has created a smaller pile head and also a void to the side of the column. The sizes of the cracked concrete and the diameters of the column heads are shown on the attached spreadsheet. (It should be noted that the column has achieved the correct diameter and only the head has a smaller diameter.)
| 01CV - Civils | Cxxx-NCR-000798 | NCR | CMC rows 398-394- multiple issues |  | Contr |  | CON - Connaught Tunnel (East) |  | 2013-01-17 | 2013-01-24 15:35 | 7 | 2012-12-10 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | Cracked Head Column NCR (Applicable to 394DE / 395BDEF / 396ABEF / 397BDF / 398DEF ) The columns from rows 394 to 398 have a crack in the column head which have resulted in a piece of the concrete breaking away at the head and side of the column. Removing these cracked pieces has created a smaller pile head and also a void to the side of the column. The sizes of the cracked concrete and the diameters of the column heads are shown on the attached spreadsheet. (It should be noted that the column has achieved the correct diameter and only the head has a smaller diameter.) Out of Position (Applicable to 394BD / 395BF / 396A / 397B) The columns have been installed as per the attached spreadsheet This is distance from the designed co-ordinate is stated. Reduced Diameter (Applicable to 394BEF / 395BDEF / 396AEF / 397BDF / 398DEF ) The installed columns have diameters as stated in the attached spreadsheet
| 01CV - Civils | Cxxx-NCR-000799 | NCR | CMC rows 398-394– Mechanical damage |  | Contr |  | CON - Connaught Tunnel (East) |  | 2013-01-17 | 2013-01-24 15:37 | 7 | 2012-12-12 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | Potential Mechanical damage (applicable to 394C-396C-398C) Trimming level is as per the attached spread sheet
| 01CV - Civils | Cxxx-NCR-000800 | NCR | CMC 396D-397E- reduced diameter |  | Contr |  | CON - Connaught Tunnel (East) |  | 2013-01-17 | 2012-12-12 16:38 | -36 | 2012-12-10 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | Reduced diameter (Applicable to 396D-397E-) 396D has an average diameter of 285mm 397E has an average diameter of 290mm
| 01CV - Civils | Cxxx-NCR-000801 | NCR | Excavation below formation level West Surface Rail Bay 5 |  | Contr |  | CON - Connaught Tunnel (East) |  | 2012-12-20 | 2013-01-22 15:00 | 33 | 2012-12-10 | Civil - Excavation | 500 |  | Workmanship | Rework |  | Complete |  | Completed |  | CMC pile lines 114 to 118 exposed formation found to contain soft areas. CMC pile lines 122 to 125 formation exposed to weather resulting in damage.
| 01CV - Civils | Cxxx-NCR-000804 | NCR | Concrete finish West Surface Rail W1a slab |  | Contr |  | CON - Connaught Tunnel (East) |  | 2012-12-14 | 2013-01-24 15:25 | 41 | 2012-12-07 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | Concrete finish contains: 1) shutter face delamination marks 2) shallow voids (larger than surface pitting or small blemishes)
| 01CV - Civils | Cxxx-NCR-000807 | NCR | Bay E11 & E10 Waterproofing |  | Contr |  | CON - Connaught Tunnel (East) |  | 2013-02-11 | 2013-02-12 13:45 | 1 | 2012-12-11 | Civil - Civil Engineering General | 500 |  | Workmanship | Rework |  | Complete |  | Completed |  | 2 coats of mulseal were applied on the same shift (within 24 hours)
| 01CV - Civils | Cxxx-NCR-000808 | NCR | Bay E11 & E10 Surface Finish |  | Contr |  | CON - Connaught Tunnel (East) |  | 2013-03-11 | 2013-03-14 15:37 | 3 | 2012-12-13 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | Concrete finish contains: 1) shutter face delamination marks 2) shallow voids (larger than surface pitting or small blemishes)
| 01CV - Civils | Cxxx-NCR-000809 | NCR | Finish on Top Surface of Slab E11 |  | Contr |  | CON - Connaught Tunnel (East) |  | 2013-02-28 | 2013-01-15 10:16 | -44 | 2012-12-11 | Civil - Civil Engineering General | 500 |  | Workmanship | Rework |  | Complete |  | Completed |  | Footprints on top surface of concrete on eastern side of slab E11 (3m x 1m area as shown on attached photos). Existing cover in footprints are 1) 58mm, 2) 58mm, 3) 55mm.
| 01CV - Civils | Cxxx-NCR-000810 | NCR | Concrete on Starter Bars Bay E11 & E10 |  | Contr |  | CON - Connaught Tunnel (East) |  | 2013-01-21 | 2013-01-25 16:41 | 4 | 2012-12-11 | Civil - Civil Engineering General | 500 |  | Workmanship | Rework |  | Complete |  | Completed |  | Wall starter bars were not cleaned post concrte pour on Slab leaving dried concrete on sections of the exposed wall reinforcement.
| 01CV - Civils | Cxxx-NCR-000811 | NCR | CMC 110F – 111F – 113F – cracked heads |  | Contr |  | CON - Connaught Tunnel (East) |  | 2013-01-21 | 2013-01-22 15:05 | 1 | 2012-12-10 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | The column references 110F – 111F – 113F, have a crack in the column head which have resulted in a piece of the concrete breaking away at the head and side of the column. Removing these cracked pieces has created a smaller pile head and also a void to the side of the column. The sizes of the cracked concrete and the diameters of the column heads are shown on the attached spreadsheet. (It should be noted that the column has achieved the correct diameter and only the head has a smaller diameter.)
| 01CV - Civils | Cxxx-NCR-000812 | NCR | CMC 110D – 112C – 112D – reduced diameter |  | Contr |  | CON - Connaught Tunnel (East) |  | 2013-01-21 | 2012-12-12 17:06 | -40 | 2012-12-10 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | Reduced Diameter (Applicable to 110D / 112C / 112D) The column 110D has a diameter of 300mm average The column 112C has a diameter of 315mm average The column 112D has a diameter of 290mm average
| 01CV - Civils | Cxxx-NCR-000813 | NCR | CMC rows 110-113 - multiple issues |  | Contr |  | CON - Connaught Tunnel (East) |  | 2013-01-21 | 2013-01-24 16:57 | 3 | 2012-12-13 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | Cracked Head Column NCR (Applicable to 110ABCE / 111ABCE / 112ABEF / 113ABCDE) The columns from row 110-113 have a crack in the column head which have resulted in a piece of the concrete breaking away at the head and side of the column. Removing these cracked pieces has created a smaller pile head and also a void to the side of the column. The sizes of the cracked concrete and the diameters of the column heads are shown on the attached spreadsheet. (It should be noted that the column has achieved the correct diameter and only the head has a smaller diameter.) Out of Position (Applicable to 110AB / 111AB / 112BEF / 113BCDE) The columns have been installed as per the attached spreadsheet This is distance from the designed co-ordinate is stated. Reduced Diameter (Applicable to 110ABCE / 111BCE / 112AEF / 113ACDE) The installed columns have diameters as stated in the attached spreadsheet
| 01CV - Civils | Cxxx-NCR-000814 | NCR | Concrete finish West Surface Rail W2a slab |  | Contr |  | CON - Connaught Tunnel (East) |  | 2012-12-17 | 2013-02-14 08:52 | 59 | 2012-12-10 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | 1) Shallow voids (larger than surface pitting or samll blemishes. 2) Inprint of formwork "nogging" and surface finish below on wall kicker.
| 01CV - Civils | Cxxx-NCR-000816 | NCR | Placing of Concrete at Twin Tunnel Bay 6 Wall |  | Contr |  | CON - Connaught Tunnel (East) |  | 2012-12-20 | 2013-01-15 09:28 | 26 | 2012-12-11 | Tunnelling - Linings - In-situ Concrete | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | Concrete (1st load) being poured at Bay 6 East from a height of circa 2.5m. __ supervisor notified immediately. __: Shutter height 2.4m, kicker height 0.15m, chute resting on shutter hence greatest pour height of 2.25m.
| 01CV - Civils | Cxxx-NCR-000817 | NCR | CMC 389E-392B- reduced diameter |  | Contr |  | CON - Connaught Tunnel (East) |  | 2013-01-22 | 2012-12-18 13:19 | -35 | 2012-12-12 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | Reduced diameter (Applicable to 389E-392B 389E has an average diameter of 300mm 392B has an average diameter of 300mm
| 01CV - Civils | Cxxx-NCR-000819 | NCR | CMC rows 393-388- cracked heads |  | Contr |  | CON - Connaught Tunnel (East) |  | 2013-01-22 | 2013-01-24 15:38 | 2 | 2012-12-12 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | The columns references 389A / 390AC / 391ABE / 392A / 393A have a crack in the column head which have resulted in a piece of the concrete breaking away at the head and side of the column. Removing these cracked pieces has created a smaller pile head and also a void to the side of the column. The sizes of the cracked concrete and the diameters of the column heads are shown on the attached spreadsheet. (It should be noted that the column has achieved the correct diameter and only the head has a smaller diameter.)
| 01CV - Civils | Cxxx-NCR-000820 | NCR | CMC rows 390F / 391C / 393C – Mechanical damage |  | Contr |  | CON - Connaught Tunnel (East) |  | 2013-01-22 | 2013-01-24 15:45 | 2 | 2012-12-12 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | Potential Mechanical damage (applicable to 390F / 391C / 393C) Trimming level is as per the attached spread sheet
| 01CV - Civils | Cxxx-NCR-000821 | NCR | CMC rows 393 - 388- multiple issues |  | Contr |  | CON - Connaught Tunnel (East) |  | 2013-01-22 | 2013-01-24 15:46 | 2 | 2012-12-12 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | Cracked Head Column NCR (Applicable to 388BDF / 389BF / 392DE / 393BF) The columns from rows 393 to 388 have a crack in the column head which have resulted in a piece of the concrete breaking away at the head and side of the column. Removing these cracked pieces has created a smaller pile head and also a void to the side of the column. The sizes of the cracked concrete and the diameters of the column heads are shown on the attached spreadsheet. (It should be noted that the column has achieved the correct diameter and only the head has a smaller diameter.) Out of Position (Applicable to 388BF / 389B / 391D / 393BF) The columns have been installed as per the attached spreadsheet This is distance from the designed co-ordinate is stated. Reduced Diameter (Applicable to 388DF/ 389BF / 390B / 392DE / 393F ) The installed columns have diameters as stated in the attached spreadsheet Columns too low / Mechanical damage (Applicable to 390B / 391D ) Trimming level is as per the attached spread sheet
| 01CV - Civils | Cxxx-NCR-000822 | NCR | CMC rows 393-388- out of position |  | Contr |  | CON - Connaught Tunnel (East) |  | 2013-01-22 | 2012-12-18 13:58 | -35 | 2012-12-12 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | The columns 388A / 389D / 390D / 392C have been installed as per the attached spreadsheet This is distance from the designed co-ordinate is stated.
| 01CV - Civils | Cxxx-NCR-000823 | NCR | W1b CFA pile head crack at cut-off level |  | Contr |  | CON - Connaught Tunnel (East) |  | 2012-12-14 | 2012-12-21 10:30 | 7 | 2012-12-12 | Civil - Civil Engineering General | 500 |  | Damaged | Rework |  | Complete |  | Completed |  | Damage to pile head below cut-off level whilst trimming.
| 01CV - Civils | Cxxx-NCR-000826 | NCR | W2b CFA pile head crack at cut-off level |  | Contr |  | CON - Connaught Tunnel (East) |  | 2012-12-18 | 2012-12-21 10:31 | 3 | 2012-12-12 | Civil - Civil Engineering General | 500 |  | Damaged | Rework |  | Complete |  | Completed |  | Damage to pile head below cutt-off level whilst trimming.
| 01CV - Civils | Cxxx-NCR-000828 | NCR | CMC 108F – cracked head |  | Contr |  | CON - Connaught Tunnel (East) |  | 2013-01-28 | 2013-01-22 15:05 | -6 | 2012-12-20 | Civil - Civil Engineering General | 500 |  |  | Repair |  | Complete |  | Completed |  | The column references 108F, has a crack in the column head which have resulted in a piece of the concrete breaking away at the head and side of the column. Removing these cracked pieces has created a smaller pile head and also a void to the side of the column. The sizes of the cracked concrete and the diameter of the column head are shown on the attached spreadsheet. (It should be noted that the column has achieved the correct diameter and only the head has a smaller diameter.)
| 01CV - Civils | Cxxx-NCR-000829 | NCR | CMC 106D / 109D – reduced diameter |  | Contr |  | CON - Connaught Tunnel (East) |  | 2013-01-28 | 2013-01-22 15:06 | -6 | 2012-12-20 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | Reduced Diameter (Applicable to 106D / 109D) The column 106D has a diameter of 305mm average The column 109D has a diameter of 290mm average
| 01CV - Civils | Cxxx-NCR-000830 | NCR | CMC rows 109-106- multiple issues |  | Contr |  | CON - Connaught Tunnel (East) |  | 2013-01-28 | 2013-01-25 14:25 | -3 | 2012-12-20 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | Cracked Head Column NCR (Applicable to 106ABCF /107ABCE /108ABCE /109ABCEF) The columns from row 106 to 109 have a crack in the column head which have resulted in a piece of the concrete breaking away at the head and side of the column. Removing these cracked pieces has created a smaller pile head and also a void to the side of the column. The sizes of the cracked concrete and the diameters of the column heads are shown on the attached spreadsheet. (It should be noted that the column has achieved the correct diameter and only the head has a smaller diameter.) Out of Position (Applicable to 106AE /107EF /108ACD /109CE) The columns have been installed as per the attached spreadsheet This is distance from the designed co-ordinate is stated. Reduced Diameter (Applicable to 106ABCEF /107A-F /108ABDE /109ABCEF) The installed columns have diameters as stated in the attached spreadsheet Columns too low / Mechanical damage (Applicable to 107D / 107F)
| 01CV - Civils | Cxxx-NCR-000832 | NCR | CMC rows 387-385- cracked heads |  | Contr |  | CON - Connaught Tunnel (East) |  | 2013-01-30 | 2013-01-25 14:23 | -5 | 2013-01-18 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | The columns references 385CD / 386ACDE have a crack in the column head which have resulted in a piece of the concrete breaking away at the head and side of the column. Removing these cracked pieces has created a smaller pile head and also a void to the side of the column. The sizes of the cracked concrete and the diameters of the column heads are shown on the attached spreadsheet. (It should be noted that the column has achieved the correct diameter and only the head has a smaller diameter.)
| 01CV - Civils | Cxxx-NCR-000833 | NCR | CMC 387A- reduced diameter |  | Contr |  | CON - Connaught Tunnel (East) |  | 2013-01-30 | 2013-01-24 17:14 | -6 | 2013-01-18 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | Reduced diameter (Applicable to 387A) 387A has an average diameter of 310mm
| 01CV - Civils | Cxxx-NCR-000834 | NCR | CMC rows 387-385- multiple issues |  | Contr |  | CON - Connaught Tunnel (East) |  | 2013-02-28 | 2013-01-30 17:20 | -29 | 2013-01-18 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | Cracked Head Column NCR (Applicable to 385ABEF / 386BF / 387BCDEF) The columns from rows 387 to 385 have a crack in the column head which have resulted in a piece of the concrete breaking away at the head and side of the column. Removing these cracked pieces has created a smaller pile head and also a void to the side of the column. The sizes of the cracked concrete and the diameters of the column heads are shown on the attached spreadsheet. (It should be noted that the column has achieved the correct diameter and only the head has a smaller diameter.) Out of Position (Applicable to 385A / 385E) The columns have been installed as per the attached spreadsheet This is distance from the designed co-ordinate is stated. Reduced Diameter (Applicable Applicable to 385ABEF / 386BF / 387BCDEF ) The installed columns have diameters as stated in the attached spreadsheet
| 01CV - Civils | Cxxx-NCR-000838 | NCR | Folded Waterbar Splay/Soffit pour Bays 9-11 West |  | Contr |  | CON - Connaught Tunnel (East) |  | 2013-02-15 | 2013-02-16 14:33 | 1 | 2013-01-03 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | A concrete chute was located close to the __ Edgetie water bar and has led to a 2m section of it folding over (see attached photograph)
| 01CV - Civils | Cxxx-NCR-000841 | NCR | CMC 103E-105E – cracked head |  | Contr |  | CON - Connaught Tunnel (East) |  | 2013-02-15 | 2013-01-30 17:31 | -16 | 2013-01-09 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | The column references 103E-105E, have a crack in the column head which have resulted in a piece of the concrete breaking away at the head and side of the column. Removing these cracked pieces has created a smaller pile head and also a void to the side of the column. The sizes of the cracked concrete and the diameter of the columns heads are shown on the attached spreadsheet. (It should be noted that the columns have achieved the correct diameter and only the head has a smaller diameter.)
| 01CV - Civils | Cxxx-NCR-000845 | NCR | CMC rows 102-105- multiple issues |  | Contr |  | CON - Connaught Tunnel (East) |  | 2013-02-15 | 2013-01-31 10:36 | -15 | 2013-01-09 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | Cracked Head Column NCR (Applicable to 102 A-F / 103 ABCDF / 104 A-F / 105 ABCDF) The columns from row 102 to 105 have a crack in the column head which have resulted in a piece of the concrete breaking away at the head and side of the column. Removing these cracked pieces has created a smaller pile head and also a void to the side of the column. The sizes of the cracked concrete and the diameters of the column heads are shown on the attached spreadsheet. (It should be noted that the column has achieved the correct diameter and only the head has a smaller diameter.) Out of Position (Applicable to 102 ABF / 103 ABF / 104 F / 105 C) The columns have been installed as per the attached spreadsheet This is distance from the designed co-ordinate is stated. Reduced Diameter (Applicable to 102 BCDEF / 103 CD / 104 ABCDEF / 105 ABCDF) The installed columns have diameters as stated in the attached spreadsheet
| 01CV - Civils | Cxxx-NCR-000850 | NCR | CMC 98E – reduced diameter |  | Contr |  | CON - Connaught Tunnel (East) |  | 2013-02-19 | 2013-01-24 17:13 | -26 | 2013-01-09 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | Reduced Diameter (Applicable to 98E) The column 98E has a diameter of 315mm average
| 01CV - Civils | Cxxx-NCR-000851 | NCR | CMC 98F-99C – cracked head |  | Contr |  | CON - Connaught Tunnel (East) |  | 2013-02-19 | 2013-02-01 16:09 | -18 | 2013-01-09 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | The columns references 98F-99C, have a crack in the column head which have resulted in a piece of the concrete breaking away at the head and side of the column. Removing these cracked pieces has created a smaller pile head and also a void to the side of the column. The sizes of the cracked concrete and the diameter of the columns heads are shown on the attached spreadsheet. (It should be noted that the columns have achieved the correct diameter and only the head has a smaller diameter.)
| 01CV - Civils | Cxxx-NCR-000852 | NCR | CMC 100D – mechanical damage |  | Contr |  | CON - Connaught Tunnel (East) |  | 2013-02-19 | 2013-02-01 11:07 | -18 | 2013-01-09 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | Mechanical damage (Applicable to 100D)
| 01CV - Civils | Cxxx-NCR-000853 | NCR | CMC rows 98-101 - multiple issues |  | Contr |  | CON - Connaught Tunnel (East) |  | 2013-02-19 | 2013-02-01 16:11 | -18 | 2013-01-09 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | Cracked Head Column NCR (Applicable to 98ABCD / 99ADF / 100ABCEF / 101ABCEF ) The columns from row 98 to 101 have a crack in the column head which have resulted in a piece of the concrete breaking away at the head and side of the column. Removing these cracked pieces has created a smaller pile head and also a void to the side of the column. The sizes of the cracked concrete and the diameters of the column heads are shown on the attached spreadsheet. (It should be noted that the column has achieved the correct diameter and only the head has a smaller diameter.) Out of Position (Applicable to 98C / 99BDEF / 100BC / 101AE) The columns have been installed as per the attached spreadsheet This is distance from the designed co-ordinate is stated. Reduced Diameter (Applicable to 98ABCD / 99ABE / 100ABCEF / 101ABE) The installed columns have diameters as stated in the attached spreadsheet Columns too low / Mechanical damage (Applicable to 99B / 99E)
| 01CV - Civils | Cxxx-NCR-000855 | NCR | Faliure to notify to witness point in ITP |  | Contr |  | CON - Connaught Tunnel (East) |  | 2013-02-08 | 2013-02-06 11:00 | -2 | 2013-01-10 | Civil - Fill | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | Faliure to notify whitness point 17, Compaction of LTP (Load Transfer Platform) West Surface Rail, Bay 5, First LTP Layer at 200mm,
| 01CV - Civils | Cxxx-NCR-000858 | NCR | CMC rows 94-97 – cracked head |  | Contr |  | CON - Connaught Tunnel (East) |  | 2013-02-28 | 2013-02-08 15:38 | -20 | 2013-01-18 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | The columns references 94A, 94F, 95A, 95C, have a crack in the column head which have resulted in a piece of the concrete breaking away at the head and side of the column. Removing these cracked pieces has created a smaller pile head and also a void to the side of the column. The sizes of the cracked concrete and the diameter of the columns heads are shown on the attached spreadsheet. (It should be noted that the columns have achieved the correct diameter and only the head has a smaller diameter.)
| 01CV - Civils | Cxxx-NCR-000859 | NCR | CMC 96E – reduced diameter |  | Contr |  | CON - Connaught Tunnel (East) |  | 2013-02-22 | 2013-01-24 17:13 | -29 | 2013-01-18 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | Reduced Diameter (Applicable to 96E) The column 98E has a diameter of 295mm average
| 01CV - Civils | Cxxx-NCR-000860 | NCR | CMC 94C – 95F – mechanical damage |  | Contr |  | CON - Connaught Tunnel (East) |  | 2013-02-22 | 2013-02-08 15:33 | -14 | 2013-01-18 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | Mechanical damage (Applicable to 94C – 95F)
| 01CV - Civils | Cxxx-NCR-000861 | NCR | CMC rows 94-97 - multiple issues |  | Contr |  | CON - Connaught Tunnel (East) |  | 2013-02-28 | 2013-02-08 15:32 | -20 | 2013-01-18 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | Cracked Head Column NCR (Applicable to 94BDE / 95BD / 96ABCDF / 97ABCDEF) The columns from row 94 to 97 have a crack in the column head which have resulted in a piece of the concrete breaking away at the head and side of the column. Removing these cracked pieces has created a smaller pile head and also a void to the side of the column. The sizes of the cracked concrete and the diameters of the column heads are shown on the attached spreadsheet. (It should be noted that the column has achieved the correct diameter and only the head has a smaller diameter.) Out of Position (Applicable to 94DE / 95B / 96ACF / 97A) The columns have been installed as per the attached spreadsheet This is distance from the designed co-ordinate is stated. Reduced Diameter (Applicable to 94BDE / 95DE / 96ABCD / 97ABCDEF) The installed columns have diameters as stated in the attached spreadsheet Columns too low / Mechanical damage (Applicable to 95E)
| 01CV - Civils | Cxxx-NCR-000863 | NCR | CMC rows 90-93 – cracked head |  | Contr |  | CON - Connaught Tunnel (East) |  | 2013-02-25 | 2013-02-04 16:49 | -21 | 2013-01-18 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | The columns references 90C / 91A&F / 92E&F / 93E&F, have a crack in the column head which have resulted in a piece of the concrete breaking away at the head and side of the column. Removing these cracked pieces has created a smaller pile head and also a void to the side of the column. The sizes of the cracked concrete and the diameter of the columns heads are shown on the attached spreadsheet. (It should be noted that the columns have achieved the correct diameter and only the head has a smaller diameter.)
| 01CV - Civils | Cxxx-NCR-000864 | NCR | CMC rows 93-90 - multiple issues |  | Contr |  | CON - Connaught Tunnel (East) |  | 2013-02-28 | 2013-02-08 16:11 | -20 | 2013-01-18 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | Cracked Head Column NCR (Applicable to 90ABDEF / 91BCE / 92ABCD / 93BCD) The columns from row 90 to 93 have a crack in the column head which have resulted in a piece of the concrete breaking away at the head and side of the column. Removing these cracked pieces has created a smaller pile head and also a void to the side of the column. The sizes of the cracked concrete and the diameters of the column heads are shown on the attached spreadsheet. (It should be noted that the column has achieved the correct diameter and only the head has a smaller diameter.) Out of Position (Applicable to 91E / 92CD / 93A) The columns have been installed as per the attached spreadsheet This is distance from the designed co-ordinate is stated. Reduced Diameter (Applicable to 90ABDEF / 91BCE / 92AB / 93ABCD) The installed columns have diameters as stated in the attached spreadsheet Columns too low / Mechanical damage (Applicable to 91DEF / 92ABCDEF / 93ABCDEF) Reinforcement too high (Applicable to 91D) The reinforcement is per the attached schedule. The reinforcement has achieved the requirement of being embedding within the river terrace deposits a minimum of 925mm.
| 01CV - Civils | Cxxx-NCR-000874 | NCR | CMC rows 86-89 – cracked head |  | Contr |  | CON - Connaught Tunnel (East) |  | 2013-02-28 | 2013-02-14 08:59 | -14 | 2013-01-18 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | The columns references 86E&F / 87D&E / 88CE&F / 89DE&F, have a crack in the column head which have resulted in a piece of the concrete breaking away at the head and side of the column. Removing these cracked pieces has created a smaller pile head and also a void to the side of the column. The sizes of the cracked concrete and the diameter of the columns heads are shown on the attached spreadsheet. (It should be noted that the columns have achieved the correct diameter and only the head has a smaller diameter.)
| 01CV - Civils | Cxxx-NCR-000875 | NCR | CMC rows 86-89 - multiple issues |  | Contr |  | CON - Connaught Tunnel (East) |  | 2013-02-28 | 2013-02-25 09:21 | -3 | 2013-01-18 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | Cracked Head Column NCR (Applicable to 86ABCD / 87ABCF / 88ABD / 89ABC) The columns from row 86 to 89 have a crack in the column head which have resulted in a piece of the concrete breaking away at the head and side of the column. Removing these cracked pieces has created a smaller pile head and also a void to the side of the column. The sizes of the cracked concrete and the diameters of the column heads are shown on the attached spreadsheet. (It should be noted that the column has achieved the correct diameter and only the head has a smaller diameter.) Out of Position (Applicable to 87AB / 88A) The columns have been installed as per the attached spreadsheet This is distance from the designed co-ordinate is stated. Reduced Diameter (Applicable to 86ABCD / 87ACF / 88ABD / 89ABC) The installed columns have diameters as stated in the attached spreadsheet
| 01CV - Civils | Cxxx-NCR-000878 | NCR | OHLE CFA No. 12 Bay 5 West |  | Contr |  | CON - Connaught Tunnel (East) |  | 2013-02-28 | 2013-02-06 08:38 | -22 | 2013-01-18 | Civil - Civil Engineering General | 500 |  | Damaged | Repair |  | Complete |  | Completed |  | CFA Pile cut off level 200mm too low, pile muncher set too low, below level of debonding, caushing broken concrete around top of CFA reinforcement cage. see sketch and photos attached
| 01CV - Civils | Cxxx-NCR-000884 | NCR | OHLE CFA No. 11 Bay 5 West |  | Contr |  | CON - Connaught Tunnel (East) |  | 2013-02-21 | 2013-02-06 08:39 | -15 | 2013-01-21 | Civil - Civil Engineering General | 500 |  | Damaged | Repair |  | Complete |  | Completed |  | CFA Pile outer diameter damaged missing triangular section approx 60mm wide, depth of 50mm and a length of 120mm into the pile. see photos attached
| 01CV - Civils | Cxxx-NCR-000885 | NCR | CFA pile West OHLE 12 out of position |  | Contr |  | CON - Connaught Tunnel (East) |  | 2013-03-05 | 2013-02-06 08:14 | -27 | 2013-01-29 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | Pile OHLE 12 has been installed to the coordinates at trimming level:(91444.992, 35428.619) with a vector from design coordinates of 0.151m The piling platform level was 103.0 and the design trim level is 100.869. The allowable tolerance beiing 0.128m, the pile is installed 0.023m out of tolerance
| 01CV - Civils | Cxxx-NCR-000887 | NCR | CMC rows 384-381- cracked heads |  | Contr |  | CON - Connaught Tunnel (East) |  | 2013-03-06 | 2013-02-12 13:36 | -22 | 2013-01-29 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | The columns references 383CD / 384 BCDEF have a crack in the column head which have resulted in a piece of the concrete breaking away at the head and side of the column. Removing these cracked pieces has created a smaller pile head and also a void to the side of the column. The sizes of the cracked concrete and the diameters of the column heads are shown on the attached spreadsheet. (It should be noted that the column has achieved the correct diameter and only the head has a smaller diameter.)
| 01CV - Civils | Cxxx-NCR-000888 | NCR | CMC 381E & F /382B & E – Mechanical damage |  | Contr |  | CON - Connaught Tunnel (East) |  | 2013-03-06 | 2013-02-12 13:38 | -22 | 2013-01-29 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | Mechanical damage (applicable to 381E & F /382B & E) Trimming level is as per the attached spread sheet
| 01CV - Civils | Cxxx-NCR-000889 | NCR | CMC 383B - multiple issues |  | Contr |  | CON - Connaught Tunnel (East) |  | 2013-03-06 | 2013-02-12 13:39 | -22 | 2013-01-29 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | Cracked Head Column NCR (Applicable to 383B) The column 383B has a crack in the column head which have resulted in a piece of the concrete breaking away at the head and side of the column. Removing these cracked pieces has created a smaller pile head and also a void to the side of the column. The sizes of the cracked concrete and the diameters of the column heads are shown on the attached spreadsheet. (It should be noted that the column has achieved the correct diameter and only the head has a smaller diameter.) Reduced Diameter (Applicableto 383B ) The installed columns have diameters as stated in the attached spreadsheet
| 01CV - Civils | Cxxx-NCR-000890 | NCR | CMC rows 381-384- out of position |  | Contr |  | CON - Connaught Tunnel (East) |  | 2013-03-06 | 2013-02-12 15:37 | -22 | 2013-01-29 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | Out of Position The columns 381AC / 383A / 384A have been installed as per the attached spreadsheet This is distance from the designed co-ordinate is stated.
| 01CV - Civils | Cxxx-NCR-000891 | NCR | CMC 383F – Trimming level too low |  | Contr |  | CON - Connaught Tunnel (East) |  | 2013-03-06 | 2013-02-14 09:06 | -20 | 2013-01-29 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | Columns too low (Applicable to 383F) Trimming level is 100.314, 105mm below design trimming level
| 01CV - Civils | Cxxx-NCR-000900 | NCR | OLE Pile Caps 15a, 13b, 14b |  | Contr |  | CON - Connaught Tunnel (East) |  | 2013-03-15 | 2013-02-05 09:27 | -38 | 2013-01-30 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | Concrete cover survey shows concrete exceeding cover tollerances (see survey sheets attached), concrete larger at bottom forming a trapazoidal shape.
| 01CV - Civils | Cxxx-NCR-000901 | NCR | OLE pile 15b |  | Contr |  | CON - Connaught Tunnel (East) |  | 2013-03-22 | 2013-03-21 14:26 | -1 | 2013-01-30 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | Excess concrete cover, trapazoidal shape to pile cap, inappropriate concrete spacer bar used leading to concrete voiding. (please see attached photo and cover survey)
| 01CV - Civils | Cxxx-NCR-000903 | NCR | CMC 376D-378D- reduced diameter |  | Contr |  | CON - Connaught Tunnel (East) |  | 2013-03-15 | 2013-02-14 09:07 | -29 | 2013-02-01 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | Reduced diameter (Applicable to 376D-378D) 376D has an average diameter of 300mm 378D has an average diameter of 310mm
| 01CV - Civils | Cxxx-NCR-000904 | NCR | CMC rows 376-380- cracked heads |  | Contr |  | CON - Connaught Tunnel (East) |  | 2013-03-08 | 2013-02-14 09:15 | -22 | 2013-02-01 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | The columns references 376E / 377ACEF / 378AC have a crack in the column head which have resulted in a piece of the concrete breaking away at the head and side of the column. Removing these cracked pieces has created a smaller pile head and also a void to the side of the column. The sizes of the cracked concrete and the diameters of the column heads are shown on the attached spreadsheet. (It should be noted that the column has achieved the correct diameter and only the head has a smaller diameter.)
| 01CV - Civils | Cxxx-NCR-000905 | NCR | CMC 380A to F & 379E – Mechanical damage |  | Contr |  | CON - Connaught Tunnel (East) |  | 2013-03-15 | 2013-02-14 09:17 | -29 | 2013-02-01 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | Mechanical damage (applicable to 379E & 380A to F) Trimming level is as per the attached spread sheet
| 01CV - Civils | Cxxx-NCR-000906 | NCR | CMC rows 376-380- multiple issues |  | Contr |  | CON - Connaught Tunnel (East) |  | 2013-03-08 | 2013-02-14 09:24 | -22 | 2013-02-01 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | Cracked Head Column NCR (Applicable to 376ABCF / 377B / 378BF) The columns from rows 376 to 378 have a crack in the column head which have resulted in a piece of the concrete breaking away at the head and side of the column. Removing these cracked pieces has created a smaller pile head and also a void to the side of the column. The sizes of the cracked concrete and the diameters of the column heads are shown on the attached spreadsheet. (It should be noted that the column has achieved the correct diameter and only the head has a smaller diameter.) Out of Position (Applicable to 376BC / 377B / 378BF / 379BC) The columns have been installed as per the attached spreadsheet This is distance from the designed co-ordinate is stated. Reduced Diameter (Applicable to 376AF ) The installed columns have diameters as stated in the attached spreadsheet Columns too low / Mechanical damage (Applicable to 379BC ) Trimming level is as per the attached spread sheet
| 01CV - Civils | Cxxx-NCR-000910 | NCR | Settlement of UTX Water main Sleeve After Installation |  | Contr |  | CON - Connaught Tunnel (East) |  | 2013-03-01 | 2013-03-01 13:12 | 0 | 2013-01-31 | Civil - Sewage/Water services | 500 |  | Design | Rework |  | Complete |  | Completed |  | The southern end of the water main UTX connection is currently 86mm below design level.
| 01CV - Civils | Cxxx-NCR-000916 | NCR | Bayy 11 soffit rebar out of position |  | Contr |  | CON - Connaught Tunnel (East) |  | 2013-03-30 | 2013-02-21 14:21 | -37 | 2013-02-04 | Civil - Tunnelling | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | The reinforcement couplers are lower than designed/ out of postion
| 01CV - Civils | Cxxx-NCR-000920 | NCR | Bay W5 Pile cap reinforcement |  | Contr |  | CON - Connaught Tunnel (East) |  | 2013-03-28 | 2013-02-06 10:57 | -50 | 2013-02-05 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Rework |  | Complete |  | Completed |  | Top mat steel sitting over pile cap, due to U bars sitting externally to pile cap, and excess top mat steelwork, causing excessive cover to surrounding top mat steel. (see attached picture.)
| 01CV - Civils | Cxxx-NCR-000921 | NCR | CMC 371C-373F – Trimming level too low |  | Contr |  | CON - Connaught Tunnel (East) |  | 2013-04-02 | 2013-02-16 14:36 | -45 | 2013-02-06 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | Columns too low (Applicable to 371C-373F) 371C: Trimming level is 100.312, 100mm below design trimming level 373F: Trimming level is 100.355, 80mm below design trimming level
| 01CV - Civils | Cxxx-NCR-000922 | NCR | CMC 374A- out of position |  | Contr |  | CON - Connaught Tunnel (East) |  | 2013-04-02 | 2013-02-15 09:14 | -46 | 2013-02-06 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | The column 374A has been installed at the following coordinates: (92403.626 ; 34570.714) The distance from the designed co-ordinate is 104mm, 4mm out of tolerance.
| 01CV - Civils | Cxxx-NCR-000923 | NCR | CMC rows 371-375- multiple issues |  | Contr |  | CON - Connaught Tunnel (East) |  | 2013-04-02 | 2013-02-14 08:54 | -47 | 2013-02-06 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | Cracked Head Column NCR (Applicable to 373BCE / 374CE / 375ACEF) The columns from rows 371 to 375 have a crack in the column head which have resulted in a piece of the concrete breaking away at the head and side of the column. Removing these cracked pieces has created a smaller pile head and also a void to the side of the column. The sizes of the cracked concrete and the diameters of the column heads are shown on the attached spreadsheet. (It should be noted that the column has achieved the correct diameter and only the head has a smaller diameter.) Out of Position (Applicable to 373BC / 374CE / 375C) The columns have been installed as per the attached spreadsheet This is distance from the designed co-ordinate is stated. Reduced Diameter (Applicable to 373E / 374E / 375AEF ) The installed columns have diameters as stated in the attached spreadsheet
| 01CV - Civils | Cxxx-NCR-000924 | NCR | CMC 373A – Mechanical damage |  | Contr |  | CON - Connaught Tunnel (East) |  | 2013-04-02 | 2013-02-16 14:33 | -45 | 2013-02-06 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | 373A: Trimming level is 100.235, 200mm below design trimming level
| 01CV - Civils | Cxxx-NCR-000925 | NCR | CMC rows 371-375 - cracked heads |  | Contr |  | CON - Connaught Tunnel (East) |  | 2013-04-02 | 2013-02-14 08:57 | -47 | 2013-02-06 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | The columns references 371ABDEF / 372DE / 373D / 374BDF / 375BD have a crack in the column head which have resulted in a piece of the concrete breaking away at the head and side of the column. Removing these cracked pieces has created a smaller pile head and also a void to the side of the column. The sizes of the cracked concrete and the diameters of the column heads are shown on the attached spreadsheet. (It should be noted that the column has achieved the correct diameter and only the head has a smaller diameter.)
| 01CV - Civils | Cxxx-NCR-000926 | NCR | Slab E8 - Geotextile wrapped up against brick corbel |  | Contr |  | CON - Connaught Tunnel (East) |  | 2013-03-19 | 2013-03-11 09:54 | -8 | 2013-02-05 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | The geotextile material wrapped over the sides and top of the LTP have folded up on the surface of the brick corbel formwork in 4No locations along the north and south sides of Slab E8. Sections of the geotextile have become embedded within the concrete face of the brick corbel. Please see attached photos which give details and locations.
| 01CV - Civils | Cxxx-NCR-000940 | NCR | central box- Soffit beam supports |  | Contr |  | CON - Connaught Tunnel (East) |  | 2013-05-31 | 2013-06-12 09:02 | 12 | 2013-02-25 | Civil - Tunnelling | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | At present the temporary works soffit beams 1-40 are installed onto the new RC soffit/ splay which has been poured against the existing brick arch. The existing temporary works design 24 (roof support during break out) shows a 20mm plate onto of the flat 800mm thick slab but the new concrete is cast against the existing brick arch which makes the soffit slab 900mm thick and with an arch surface. The soffit beams are installed directly onto the RC soffit slab with Hardwood timber wedges filling the void in between the steel beam and RC soffit.
| 01CV - Civils | Cxxx-NCR-000941 | NCR | CMC 56F-57A&F – cracked heads |  | Contr |  | CON - Connaught Tunnel (East) |  | 2013-04-11 | 2013-02-25 09:09 | -45 | 2013-02-15 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | The columns references 56F-57A&F, have a crack in the column head which have resulted in a piece of the concrete breaking away at the head and side of the column. Removing these cracked pieces has created a smaller pile head and also a void to the side of the column. The sizes of the cracked concrete and the diameters of the column heads are shown on the attached spreadsheet. (It should be noted that the column has achieved the correct diameter and only the head has a smaller diameter.)
| 01CV - Civils | Cxxx-NCR-000942 | NCR | CMC 56A- diameter too small |  | Contr |  | CON - Connaught Tunnel (East) |  | 2013-04-11 | 2013-02-25 09:08 | -45 | 2013-02-15 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | Reduced Diameter (Applicable to 56A) The installed column has a diameter of 290mm average
| 01CV - Civils | Cxxx-NCR-000943 | NCR | CMC 58C– mechanical damage |  | Contr |  | CON - Connaught Tunnel (East) |  | 2013-03-28 | 2013-03-01 13:02 | -27 | 2013-02-15 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | Mechanical damage (Applicable to 58C)
| 01CV - Civils | Cxxx-NCR-000945 | NCR | CMC rows 56-59 - multiple issues |  | Contr |  | CON - Connaught Tunnel (East) |  | 2013-03-28 | 2013-03-01 13:03 | -27 | 2013-02-15 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | Cracked Head Column NCR (Applicable to 56CDE / 57BCDE / 58ABDE / 59A-F) The columns from row 56 to 59 have a crack in the column head which have resulted in a piece of the concrete breaking away at the head and side of the column. Removing these cracked pieces has created a smaller pile head and also a void to the side of the column. The sizes of the cracked concrete and the diameters of the column heads are shown on the attached spreadsheet. (It should be noted that the column has achieved the correct diameter and only the head has a smaller diameter.) Out of Position (Applicable to 56BCD / 57C / 58AB / 59CF) The columns have been installed as per the attached spreadsheet This is distance from the designed co-ordinate is stated. Reduced Diameter (Applicable to 56BDE / 57BCDE / 58DE / 59A-E) The installed columns have diameters as stated in the attached spreadsheet Columns too low (Applicable to 58E) / Mechanical damage (Applicable to 56B)
| 01CV - Civils | Cxxx-NCR-000946 | NCR | Incorrect Survey |  | Contr |  | CON - Connaught Tunnel (East) |  | 2013-03-29 | 2013-03-14 14:51 | -15 | 2013-02-15 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | Survey was not taken from centre, causing an NCR to be raised for out of position pile. Note all over survey carried out this day have been rechecked.
| 01CV - Civils | Cxxx-NCR-000949 | NCR | Geotextile lap into concrete W6 |  | Contr |  | CON - Connaught Tunnel (East) |  | 2013-05-17 | 2013-05-22 13:53 | 5 | 2013-02-18 | Civil - Civil Engineering General | 500 |  | Workmanship | Rework |  | Complete |  | Completed |  | with an overdig of LTP layer by 200mm, the geotextile wraps around LTP layer with 700-900mm on top of the LTP layer but only ~500mm of geotextile under concrete slab. see sketch attached. There arew two isolated areas, where geotextile into concrete slab reduces to 400mm, at the North side at CH. 17418 tand South side at Ch. 17417.
| 01CV - Civils | Cxxx-NCR-000952 | NCR | Works proceeding without NCR implementation in place |  | Contr |  | CON - Connaught Tunnel (East) |  | 2013-03-19 | 2013-03-13 11:49 | -6 | 2013-02-19 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | Remdial works have been undertaken before NCR 949 has reached implementation stage.
| 01CV - Civils | Cxxx-NCR-000953 | NCR | CMC 86D - Multiple issues |  | Contr |  | CON - Connaught Tunnel (East) |  | 2013-05-03 | 2013-03-04 09:45 | -60 | 2013-02-20 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | Cracked Head Column NCR (Applicable to 86D) The CMC column 86D have a crack in the column head which have resulted in a piece of the concrete breaking away at the head and side of the column. Removing this cracked piece has created a smaller pile head and also a void to the side of the column. The size of the cracked concrete and the diameters of the column head are shown on the attached spreadsheet. (It should be noted that the column has achieved the correct diameter and only the head has a smaller diameter.) Out of Position (Applicable to 86D) The column have been installed as per the attached spreadsheet The distance from the designed co-ordinates is stated. Reduced Diameter (Applicable to 86D) The installed column's diameter is stated in the attached spreadsheet
| 01CV - Civils | Cxxx-NCR-000954 | NCR | Installation of Horizontal Props Sequence |  | Contr |  | CON - Connaught Tunnel (East) |  | 2013-06-05 | 2013-06-07 17:15 | 2 | 2013-02-20 | Tunnelling - Excavation - Hand | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | Props are not being fully and permanently installed prior to intermediate holes being drilled.
| 01CV - Civils | Cxxx-NCR-000955 | NCR | CMC rows 60-74– cracked heads |  | Contr |  | CON - Connaught Tunnel (East) |  | 2013-05-17 | 2013-03-04 09:02 | -74 | 2013-02-20 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | The columns references 60CF / 62BC / 63A / 64BCF / 65AF / 66ABF / 67CF / 68BCEF / 69CF / 70CF / 71BCEF / 72F / 73ACDEF / 74F, have a crack in the column head which have resulted in a piece of the concrete breaking away at the head and side of the column. Removing these cracked pieces has created a smaller pile head and also a void to the side of the column. The sizes of the cracked concrete and the diameters of the column heads are shown on the attached spreadsheet. (It should be noted that the column has achieved the correct diameter and only the head has a smaller diameter.)
| 01CV - Civils | Cxxx-NCR-000956 | NCR | CMC 63F / 66C / 70D- diameter too small |  | Contr |  | CON - Connaught Tunnel (East) |  | 2013-04-03 | 2013-03-04 09:44 | -30 | 2013-02-20 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | Reduced Diameter (Applicable to 63F / 66C / 70D) CMC 63F : The installed column has a diameter of 310mm average CMC 66C : The installed column has a diameter of 310mm average CMC 70D: The installed column has a diameter of 300mm average
| 01CV - Civils | Cxxx-NCR-000957 | NCR | CMC rows 60-74– mechanical damage |  | Contr |  | CON - Connaught Tunnel (East) |  | 2013-05-17 | 2013-03-04 10:07 | -74 | 2013-02-21 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | Mechanical damage (Applicable to 63C / 64E / 68A / 69B / 71D)
| 01CV - Civils | Cxxx-NCR-000958 | NCR | CMC rows 60-74- multiple issues |  | Contr |  | CON - Connaught Tunnel (East) |  | 2013-05-17 | 2013-03-04 10:11 | -74 | 2013-02-20 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | Cracked Head Column NCR (Applicable to 60ABE / 61ABE / 62DEF / 63BDE / 64AD / 65BCE / 66E / 67AE / 68D / 69ADE / 70AB / 71A / 72ABCDE / 73B / 74ABCE) The columns from row 60 to 74 have a crack in the column head which have resulted in a piece of the concrete breaking away at the head and side of the column. Removing these cracked pieces has created a smaller pile head and also a void to the side of the column. The sizes of the cracked concrete and the diameters of the column heads are shown on the attached spreadsheet. (It should be noted that the column has achieved the correct diameter and only the head has a smaller diameter.) Out of Position (Applicable to 60AD / 61A / 62AF / 63B 64A / 65C / 66E / 67ABD / 69A / 70B / 72B / 74AD) The columns have been installed as per the attached spreadsheet This is distance from the designed co-ordinate is stated. Reduced Diameter (Applicable to 60BDE / 61BCDEF / 62DE / 63BDE / 64D / 65BDE / 66D / 67DE / 68D / 69DE / 70ABE / 71A / 72ABCDE / 73B / 74ABCDE) The installed columns have diameters as stated in the attached spreadsheet Columns too Low / Mechanical damage (Applicable to 61CDF / 62A / 65D / 66D / 67B / 70E)
| 01CV - Civils | Cxxx-NCR-000960 | NCR | Non Attendance of Contractor Representative for HOLD Point - Clean Water Diversion Inspection |  | Contr |  | CON - Connaught Tunnel (East) |  | 2013-03-12 | 2013-03-14 15:38 | 2 | 2013-02-27 | Civil - Sewage/Water services | 500 |  | System Defect | Use As-Is |  | Complete |  | Completed |  | The inspection was carried out by the client, TWUL and the contractor's sub contractor but without the contractor in attendance.
| 01CV - Civils | Cxxx-NCR-000962 | NCR | Damaged Waterproofing System |  | Contr |  | CON - Connaught Tunnel (East) |  | 2013-03-07 | 2013-03-27 14:36 | 20 | 2013-02-21 | Tunnelling - Linings - In-situ Concrete | 500 |  | Damaged | Repair |  | Complete |  | Completed |  | Edgetite waterproofing system has been damaged at the easterly end of Bay 11 northern splay (See attached photo). Also at isolated areas joint connections appear to be becoming disconnected.
| 01CV - Civils | Cxxx-NCR-000963 | NCR | Cofferdam Fill Material - Arriving at site without acceptance |  | Contr |  | CON - Connaught Tunnel (East) |  | 2013-03-18 | 2013-03-29 08:59 | 11 | 2013-02-21 | Civil - Civil Engineering General | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | Fill material for the cofferdam is being delivered at site prior to test results being available and Project Manager acceptance.
| 01CV - Civils | Cxxx-NCR-000965 | NCR | CMC 64E -Minimum rebar cover not achieved |  | Contr |  | CON - Connaught Tunnel (East) |  | 2013-05-17 | 2013-03-14 15:39 | -64 | 2013-02-22 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | Rebar outside of the column 600mm below the design trimming level. Minimum cover not achieved
| 01CV - Civils | Cxxx-NCR-000967 | NCR | CMC rows 76D-77F– mechanical damage |  | Contr |  | CON - Connaught Tunnel (East) |  | 2013-05-17 | 2013-03-14 15:40 | -64 | 2013-02-22 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | Mechanical damage (Applicable to 76D-77F)
| 01CV - Civils | Cxxx-NCR-000968 | NCR | CMC rows 75-79– cracked heads |  | Contr |  | CON - Connaught Tunnel (East) |  | 2013-05-17 | 2013-03-04 12:54 | -74 | 2013-02-22 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | The columns references 75ABCF / 77C / 78C / 79A, have a crack in the column head which have resulted in a piece of the concrete breaking away at the head and side of the column. Removing these cracked pieces has created a smaller pile head and also a void to the side of the column. The sizes of the cracked concrete and the diameters of the column heads are shown on the attached spreadsheet. (It should be noted that the column has achieved the correct diameter and only the head has a smaller diameter.)
| 01CV - Civils | Cxxx-NCR-000970 | NCR | CMC rows 75-79- multiple issues |  | Contr |  | CON - Connaught Tunnel (East) |  | 2013-04-05 | 2013-03-04 12:52 | -32 | 2013-02-22 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | Cracked Head Column NCR (Applicable to 75DE / 76ABCEF / 77ABDE / 78ABDEF / 79BCDEF) The columns from row 75 to 79 have a crack in the column head which have resulted in a piece of the concrete breaking away at the head and side of the column. Removing these cracked pieces has created a smaller pile head and also a void to the side of the column. The sizes of the cracked concrete and the diameters of the column heads are shown on the attached spreadsheet. (It should be noted that the column has achieved the correct diameter and only the head has a smaller diameter.) Out of Position (Applicable to 76AF/ 77AB / 78ABF / 79F) The columns have been installed as per the attached spreadsheet This is distance from the designed co-ordinate is stated. Reduced Diameter (Applicable to 75DE / 76BCE / 77ABDE / 78DE / 79BCD) The installed columns have diameters as stated in the attached spreadsheet
| 01CV - Civils | Cxxx-NCR-000973 | NCR | CMC 84DEF / 85EF – cracked heads |  | Contr |  | CON - Connaught Tunnel (East) |  | 2013-05-24 | 2013-03-14 15:46 | -71 | 2013-02-26 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | The columns references 80EF/81F/84DEF / 85EF have a crack in the column head which have resulted in a piece of the concrete breaking away at the head and side of the column. Removing these cracked pieces has created a smaller pile head and also a void to the side of the column. The sizes of the cracked concrete and the diameters of the column heads are shown on the attached spreadsheet. (It should be noted that the column has achieved the correct diameter and only the head has a smaller diameter.)
| 01CV - Civils | Cxxx-NCR-000974 | NCR | CMC rows 81D– mechanical damage |  | Contr |  | CON - Connaught Tunnel (East) |  | 2013-05-24 | 2013-03-14 15:47 | -71 | 2013-02-26 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | Mechanical damage (Applicable to 81D)
| 01CV - Civils | Cxxx-NCR-000975 | NCR | CMC 85D - out of position |  | Contr |  | CON - Connaught Tunnel (East) |  | 2013-05-24 | 2013-03-14 15:49 | -71 | 2013-02-26 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | The column 85D has been installed at the following coordinates: (91399.954; 35426.764), Vector 0.142, 42mm outside of allowable tolerance. This is distance from the designed co-ordinate is stated.
| 01CV - Civils | Cxxx-NCR-000976 | NCR | CMC rows 80-85 DEF- multiple issues |  | Contr |  | CON - Connaught Tunnel (East) |  | 2013-05-24 | 2013-03-14 15:49 | -71 | 2013-02-26 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | Cracked Head Column NCR (Applicable to 80D / 81E / 82DEF / 83DEF) The columns from row 80 to 85 DEF have a crack in the column head which have resulted in a piece of the concrete breaking away at the head and side of the column. Removing these cracked pieces has created a smaller pile head and also a void to the side of the column. The sizes of the cracked concrete and the diameters of the column heads are shown on the attached spreadsheet. (It should be noted that the column has achieved the correct diameter and only the head has a smaller diameter.) Out of Position (Applicable to 80D / 81E / 82D / 83DEF) The columns have been installed as per the attached spreadsheet This is distance from the designed co-ordinate is stated. Reduced Diameter (Applicable to 80D / 81E / 82DE) The installed columns have diameters as stated in the attached spreadsheet Columns too low (Applicable to 82EF)
| 01CV - Civils | Cxxx-NCR-000980 | NCR | CMC 82AC – cracked heads |  | Contr |  | CON - Connaught Tunnel (East) |  | 2013-05-31 | 2013-03-15 11:11 | -77 | 2013-02-27 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | The columns references 82AC have a crack in the column head which have resulted in a piece of the concrete breaking away at the head and side of the column. Removing these cracked pieces has created a smaller pile head and also a void to the side of the column. The sizes of the cracked concrete and the diameters of the column heads are shown on the attached spreadsheet. (It should be noted that the column has achieved the correct diameter and only the head has a smaller diameter.)
| 01CV - Civils | Cxxx-NCR-000981 | NCR | CMC rows 80-85 ABC- multiple issues |  | Contr |  | CON - Connaught Tunnel (East) |  | 2013-05-31 | 2013-03-15 11:21 | -77 | 2013-02-27 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | Cracked Head Column NCR (Applicable to 80ABC / 81ABC / 82B / 83AB / 84ABC / 85BC) The columns from row 80 to 85 ABC have a crack in the column head which have resulted in a piece of the concrete breaking away at the head and side of the column. Removing these cracked pieces has created a smaller pile head and also a void to the side of the column. The sizes of the cracked concrete and the diameters of the column heads are shown on the attached spreadsheet. (It should be noted that the column has achieved the correct diameter and only the head has a smaller diameter.) Out of Position (Applicable to 80BC / 81ABC / 83AC / 84ABC / 85ABC) The columns have been installed as per the attached spreadsheet This is distance from the designed co-ordinate is stated. Reduced Diameter (Applicable to 80ABC / 81C / 82B / 83ABC / 84B / 85ABC) The installed columns have diameters as stated in the attached spreadsheet Mechanical damage (Applicable to 83C / 85A)
| 01CV - Civils | Cxxx-NCR-000982 | NCR | Bay 7 LTP layer Overdig and geotextile issues |  | Contr |  | CON - Connaught Tunnel (East) |  | 2013-04-11 | 2013-03-25 10:56 | -17 | 2013-02-27 | Civil - Civil Engineering General | 500 |  |  | Repair |  | Complete |  | Completed |  | LTP varies width throughout bay with a maximum of approximately 1100mm from design, see survey of overdig attached. Geotextile has been punctured with Stakes at approximately every 2m along bay.
| 01CV - Civils | Cxxx-NCR-000983 | NCR | West Bay 6 OLE butress wall / pile cap alignment |  | Contr |  | CON - Connaught Tunnel (East) |  | 2013-03-28 | 2013-03-25 12:33 | -3 | 2013-02-27 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | As constructed OLE Pile cap 15a (Bay 6 north side) has 490mm to face of concrete on the proposed buttress alignment northeast corner (500mm northwest). Correct dimension should be 500mm. As constructed OLE Pile cap 15b (Bay 6 south side) has excess cover to the reinforcement (See NCR 901)
| 01CV - Civils | Cxxx-NCR-000984 | NCR | Bay 3W Overdig |  | Contr |  | CON - Connaught Tunnel (East) |  | 2013-03-28 | 2013-03-27 14:37 | -1 | 2013-02-28 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | Overdig of Bay 3W varies along bay, please see survey attached.
| 01CV - Civils | Cxxx-NCR-000993 | NCR | Head House Shaft Base Concrete Finish |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2014-09-30 | 2014-09-29 13:19 | -1 | 2013-03-07 | Civil - Civil Engineering General | 3000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | The finished level of the concrete is 80.700m ATD which provides the required 55mm cover, however the concrete appears to have settled between the bars of the top mat of the reinforcement. Using a 1m striaght edge the maximum deviation in flatness found was 22mm (as shown in the attached photograph). Possible plastic settlement.
| 01CV - Civils | Cxxx-NCR-000996 | NCR | Bay E15 Downstand Wall - Insufficent Cover |  | Contr |  | CON - Connaught Tunnel (East) |  | 2013-05-03 | 2013-04-19 16:34 | -14 | 2013-03-14 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | 1) The brick corbel between chainage 19122 & 19126 was not poured up to design level which has resulted in insufficient cover to the top of the reinforcement link. 2&3) Reinforcement part exposed in construction joint with <20mm clear surround for aggregate passage. 4&5) Shrinkage cracks within construction joint where reinforcement bars are too close to the surface.
| 01CV - Civils | Cxxx-NCR-000997 | NCR | Bay 8 East Overdig |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2013-07-26 | 2013-07-29 09:07 | 3 | 2013-03-13 | Civil - Civil Engineering General | 3500 |  |  | Repair | 3 (3-6k) | Complete |  | Completed |  | LTP extends outside of design outwards from slab as per attached survey. There are areas that comprise of 'seperated geotextile' in these areas are evidenced in the attached LTP Geotextile NCR.pdf Photo survey.
| 01CV - Civils | Cxxx-NCR-000998 | NCR | Extra cover to reinforcment in soffit bays 1-3 |  | Contr |  | CON - Connaught Tunnel (East) |  | 2013-05-31 | 2013-06-07 16:01 | 7 | 2013-03-13 | Civil - Tunnelling | 500 |  | Workmanship | Rework |  | Complete |  | Completed |  | Please find attached photos and drawings of bays 1 and 3, showing extra cover to the near face splay B40 couplers. When the concrete ports in the splay (bays 1-3) were used to concrete the splay and upper walls, the reinforcement was lifted under the pumping pressure and due to the congestion of the reinforcement. This extra cover covers 2.5m section around each port. The maximum cover is 110mm
| 01CV - Civils | Cxxx-NCR-000999 | NCR | West Cofferdam Fill |  | Contr |  | CON - Connaught Tunnel (East) |  | 2013-03-29 | 2013-03-29 09:00 | 0 | 2013-03-16 | Civil - Fill | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | __ started fill operation (on 15 Mar 2013 circa 20:00) and overlooked CRL HOLD points 6.1 and 6.3 of aforementioned ITP. CRL not notified of operation; H point IR raised day after fill operation started.
| 01CV - Civils | Cxxx-NCR-001003 | NCR | Bay 5 overdig |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2013-07-01 | 2013-07-03 09:59 | 2 | 2013-03-18 | Civil - Civil Engineering General | 3000 |  |  | Repair | 4 (0.5-3k) | Complete |  | Completed |  | LTP protruding from slab edges as per survey attached. This NCR covers part of bay 6 up to CH:17416. Please note along the noth and south edges there are areas with 'separated geotextie' where the geotextile lap that is pinned under the concrete slab is separate from the layer that wraps around the sides and underneath the LTP layer.
| 01CV - Civils | Cxxx-NCR-001008 | NCR | CMC rows 362-370 - cracked heads |  | Contr |  | CON - Connaught Tunnel (East) |  | 2013-05-01 | 2013-04-26 17:10 | -5 | 2013-03-21 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | The columns references 362CD / 363ABD / 364AE / 365ABD / 366DE / 368CDF / 369ADE / 370DE have a crack in the column head which have resulted in a piece of the concrete breaking away at the head and side of the column. Removing these cracked pieces has created a smaller pile head and also a void to the side of the column. The sizes of the cracked concrete and the diameters of the column heads are shown on the attached spreadsheet. (It should be noted that the column has achieved the correct diameter and only the head has a smaller diameter.)
| 01CV - Civils | Cxxx-NCR-001009 | NCR | CMC rows 367D / 369B - reduced diameter |  | Contr |  | CON - Connaught Tunnel (East) |  | 2013-05-10 | 2013-04-26 17:10 | -14 | 2013-03-21 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | Reduced diameter (Applicable to 367D / 369B) - 367D : average diameter 300mm - 369B: average diameter 300mm
| 01CV - Civils | Cxxx-NCR-001010 | NCR | CMC 365F / 370C- out of position |  | Contr |  | CON - Connaught Tunnel (East) |  | 2013-05-01 | 2013-04-26 17:17 | -5 | 2013-03-21 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | The columns references 365F / 370C have been installed at the following coordinates: 365F: (92385.475 ; 34569.06) ; Vector 0.147 370C: ( 92395.844 ; 34569.783) ; Vector 0.105 The distance from the designed co-ordinate is stated.
| 01CV - Civils | Cxxx-NCR-001011 | NCR | CMC rows 362-370- multiple issues |  | Contr |  | CON - Connaught Tunnel (East) |  | 2013-05-01 | 2013-04-26 17:18 | -5 | 2013-03-21 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | Cracked Head Column NCR (Applicable to 362BE / 363C / 364CD / 365CE / 366BF / 367E / 368AE / 369C / 370BF) The columns from rows 362 to 370 have a crack in the column head which have resulted in a piece of the concrete breaking away at the head and side of the column. Removing these cracked pieces has created a smaller pile head and also a void to the side of the column. The sizes of the cracked concrete and the diameters of the column heads are shown on the attached spreadsheet. (It should be noted that the column has achieved the correct diameter and only the head has a smaller diameter.) Out of Position (Applicable to 362BE / 364C / 367F / 368 / 369C / 370B) The columns have been installed as per the attached spreadsheet This is distance from the designed co-ordinate is stated. Reduced Diameter (Applicable to 363CE / 364D / 365CE / 366BF / 367EF / 368AE / 369 / 370F ) The installed columns have diameters as stated in the attached spreadsheet Columns too low / Mechanical damage (Applicable to 363E ) Trimming level is as per the attached spread sheet
| 01CV - Civils | Cxxx-NCR-001012 | NCR | CMC 366C – Mechanical damage |  | Contr |  | CON - Connaught Tunnel (East) |  | 2013-05-01 | 2013-04-26 17:19 | -5 | 2013-03-21 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | Mechanical damage (applicable to 366C) See attached schedule
| 01CV - Civils | Cxxx-NCR-001013 | NCR | BAY 3 CH. 17315.5-17309 OVERDIG |  | Contr |  | CON - Connaught Tunnel (East) |  | 2013-04-25 | 2013-04-05 14:41 | -20 | 2013-03-21 | Civil - Civil Engineering General | 500 |  |  | Repair |  | Complete |  | Completed |  | See attached survey, steel work down.
| 01CV - Civils | Cxxx-NCR-001022 | NCR | Damage to LTP Layer Geotextile, Bay 11 & 12 East |  | Contr |  | CON - Connaught Tunnel (East) |  | 2013-05-17 | 2013-05-22 08:45 | 5 | 2013-03-26 | Civil - Civil Engineering General | 500 |  | Damaged | Repair |  | Complete |  | Completed |  | Damage to LTP layer geotextile at NORTH SIDE BAY 11 CH88198, 900mm section of damage. At NORTH SIDE BAY 12 CH88244 by 1000mm section and CH88246 by 600mm section damaged. see attached photographs. Damage has occured at the corbel edge. Please note further NCR to be raised regarding overdig in this area.
| 01CV - Civils | Cxxx-NCR-001023 | NCR | Plate Bearing Tests Bay E15 |  | Contr |  | CON - Connaught Tunnel (East) |  | 2013-05-13 | 2013-05-30 08:37 | 17 | 2013-03-26 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Rework |  | Complete |  | Completed |  | Plate Bearing Test were carried out on Locations 588C, 592E & 596C which were not cyclical.
| 01CV - Civils | Cxxx-NCR-001024 | NCR | Grout cubes for the west cofferdam not tested |  | Contr |  | CON - Connaught Tunnel (East) |  | 2013-05-31 | 2013-05-28 08:39 | -3 | 2013-03-26 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | The grout cubes produced on the 13-March-2013 for the south vertical wet and dry seals of the west cofferdam (__-IR-2763) was not manufactured in accordance with the specifications by the GPS’ testing subcontractor __. The cubes were discarded and no compressive tests recorded.
| 01CV - Civils | Cxxx-NCR-001029 | NCR | Removal of Contaminated UTX 450mm Water main Pipe Sections |  | Contr |  | CON - Connaught Tunnel (East) |  | 2013-04-26 | 2013-04-30 08:16 | 4 | 2013-04-22 | Civil - Sewage/Water services | 500 |  | Damaged | Rework |  | Complete |  | Completed |  | It was agreed that the four pipes would be removed and re-chlorinated with a mop and spray chlorus.
| 01CV - Civils | Cxxx-NCR-001032 | NCR | BAY 15 East Spongey Ground conditions |  | Contr |  | CON - Connaught Tunnel (East) |  | 2013-05-17 | 2013-04-16 16:59 | -31 | 2013-03-27 | Civil - Civil Engineering General | 500 |  |  | Repair |  | Complete |  | Completed |  | Plate Bearing test on location 588D achieved a maximum 2nd cycle deflection of 2.32mm. Which will generate a Stiffness of 41.4MPa. please see attached result sheet. Please note other Plate Bearing Tests completed passed the criterea set. For area which has suspect spongeness see Extract atttached. Please note that location of Bay is between Downstand beams of Bay15 and adverse weather conditions could have led to water still draining out of area.
| 01CV - Civils | Cxxx-NCR-001033 | NCR | Bay 12 Overdig Crossover Area |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2014-04-27 | 2014-01-17 11:22 | -100 | 2013-03-27 | Civil - Civil Engineering General | 3000 |  | Supervision/Management | Repair | 4 (0.5-3k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | LTP layer protrudes past Concrete slab, please see attached survey, Between Ch 88230 and 88240 on the North side and Ch 88230 and 88250 on the Southside where crossover to be opened. Please note crossover works are underway in these locations. Note; for remainder of Bay 12 outside of crossover seperate NCR to be raised.
| 01CV - Civils | Cxxx-NCR-001034 | NCR | Bay 12 East Overdig |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2014-05-31 | 2014-01-17 11:23 | -134 | 2013-03-27 | Civil - Civil Engineering General | 3000 |  |  | Repair | 4 (0.5-3k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | LTP layer protrudes past Concrete slab, please see attached survey. The crossover area between Ch 88230 and 88240 on the North side and Ch 88230 and 88250 on the Southside is covered in NCR-1033.
| 01CV - Civils | Cxxx-NCR-001045 | NCR | Damage to Bay 11 concrete walls |  | Crossrail | PDP | CON - Connaught Tunnel (East) |  | 2013-07-18 | 2013-07-29 16:03 | 11 | 2013-04-05 | Civil - Tunnelling | 1000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During the breakout of the lower walls for Invert 28, Bay 11 walls have been damaged as shown in attached photos. This was caused when the mechanical breaker took off a localised section of the upper section of the breakout
| 01CV - Civils | Cxxx-NCR-001053 | NCR | Holding Down Bolts - Threaded Bars |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2013-12-06 | 2013-12-10 11:27 | 4 | 2013-04-16 | Civil - Civil Engineering General | 2000 |  | Material | Repair | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | There is evidence of rusting on the cut ends of the threaded bars delivered to site for the Holding Down Bolts. 3 sets of holding down bolts have been cast into the columns (column ref numbers 5, 57a and 57b. No other threaded bars have been cast into concrete but all have been delivered to site. Photos are attached showing the rusting to the cut ends of the threaded bars. No section of the threaded bars is rusting but there is some rust colour staining from the ends
| 01CV - Civils | Cxxx-NCR-001056 | NCR | Bay W4 wall, Steel starter bar laps |  | Contr |  | CON - Connaught Tunnel (East) |  | 2013-06-03 | 2013-05-24 10:30 | -10 | 2013-04-15 | Civil - Civil Engineering General | 500 |  | Design | Rework |  | Complete |  | Completed |  | Drawing states 28 U-bars from edge of pile 9b for the 0.6m high section of wall on the Southern side up to the point where the wall steps to become 0.9m high. U-bars were installed and incoporated into the slab due the the lap lengths required. The actual stepping point for the wall is approximately 1.2m to the East meaning additional starter bars have been cast into the slab into the section of the 0.9m high wall and the starter bars installed will not provide sufficient lap for the required U-bars. Please see attached sketch for details
| 01CV - Civils | Cxxx-NCR-001059 | NCR | Damaged Invert reinforcement couplers in invert 25 |  | Contr |  | CON - Connaught Tunnel (East) |  | 2013-08-24 | 2013-05-07 11:57 | -109 | 2013-04-18 | Civil - Tunnelling | 500 |  | Damaged | Rework |  | Complete |  | Completed |  | While hand breaking around the couplers, __ have damaged the thread in the Front Face B25 couplers as shown on the attachments. The anchor bars have been screwed into the couplers, but there is 1- 3 threads still showing not giving the full anchor strength.
| 01CV - Civils | Cxxx-NCR-001060 | NCR | Additional tie bar chairs in invert 25 |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2013-07-27 | 2013-07-29 15:22 | 2 | 2013-04-16 | Civil - Tunnelling | 1000 |  | Workmanship | Rework | 4 (0.5-3k) | Complete |  | Completed |  | Invert 25 slab reinforcement had been installed as per the design Cxxx-VIN-C-DWG-CR146_ST003-50257 C01. The top cover was out of tolerance and required lifting. Shuttering Tie bars were connected from the horizontal wall props (Design 22) down to the top mat reinforcement and lifted the reinforcement to the require adjustments and then an extra tie bar chair ware installed into the slab. The temporary works has been designed for the wall supports not for any other use. (Not for lifting reinforcement.) The root cause of the cover issue which lead to the lifting of the top mat is the designed chairs, they vary in size (by 10mm) and may have compacted, giving 20mm extra cover in local areas. The extra Tie bar chairs have been adjusted to correct the extra cover, keeping the slab within the allowable tolerance and the pour has bees signed off and concreted
| 01CV - Civils | Cxxx-NCR-001061 | NCR | Bay 9 East LTP Overdig |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2013-07-26 | 2013-07-29 09:23 | 3 | 2013-04-16 | Civil - Civil Engineering General | 3500 |  |  | Repair | 3 (3-6k) | Complete |  | Completed |  | LTP extends past concrete slab/corbel as per the attached survey data sheet. In areas along the southern edge (CH88080-88090) there are 'flapped geotextile' areas where the excess geotextile is flapped outside of the concrete slab as per the attached sketch.
| 01CV - Civils | Cxxx-NCR-001062 | NCR | Cofferdam Works - Epoxy Grout |  | Contr |  | CON - Connaught Tunnel (East) |  | 2013-06-28 | 2013-06-17 12:22 | -11 | 2013-05-22 | Civil - Civil Engineering General | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | Inspection request 2453 was raised as a late request to use Premcrete Epodure HS epoxy grout for prop A1 between face of prop and waler. CRL and Independent inspector were not formally invited to inspect the taking of cubes. Inpection was witnessed by VINCI engineer.
| 01CV - Civils | Cxxx-NCR-001069 | NCR | Bay W3 South, top of concrete wall level |  | Contr |  | CON - Connaught Tunnel (East) |  | 2013-06-21 | 2013-05-24 10:42 | -28 | 2013-04-30 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Rework |  | Complete |  | Completed |  | Finished level of concrete at the Eastern end of the pour are incorrect as per the attached sketch.
| 01CV - Civils | Cxxx-NCR-001072 | NCR | Soffit tie bar sleeves |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2013-08-31 | 2013-09-09 11:37 | 9 | 2013-04-18 | Civil - Tunnelling | 2500 |  | Planning | Repair | 4 (0.5-3k) | Complete |  | Completed |  | When the soffit shutter was erected in bays 1-3 & 9 -11, extra tie bars were added from the soffit face connecting to a wing nut just above the near face reinforcement ( approx 100mm long) to help lift the form work into position then the false work props legs were extended down to the working platform, which took the soffit load. Once the shutter soffit was concreted, the tie bar were removed leaving a 100mm tie bar sleeve in the soffit. The soffit false work design did not show any tie bars in the soffit.
| 01CV - Civils | Cxxx-NCR-001073 | NCR | Bay W6A wall North, Missing chamfer |  | Crossrail | PDP | CON - Connaught Tunnel (East) |  | 2013-07-19 | 2013-07-23 15:48 | 4 | 2013-05-02 | Civil - Civil Engineering General | 1000 |  | Supervision/Management | Repair | 4 (0.5-3k) | Complete |  | Completed |  | Missing chamfer on both sides of wall. As-built levels of wall are incorrect at same location.
| 01CV - Civils | Cxxx-NCR-001079 | NCR | UTX Blinding Concrete Level |  | Contr |  | CON - Connaught Tunnel (East) |  | 2013-05-23 | 2013-05-02 15:04 | -21 | 2013-04-30 | Civil - Civil Engineering General | 500 |  |  | Repair |  | Complete |  | Completed |  | Blinding Levels have been installed opposite of the correct UTX crossing Level as per drawing UTX Blinding Level to be ~99.480 @ Chainage 87965, Level as per drawing UTX Blinding Level to be ~99.443 @ Chainage 87970 Leaving one UTX crossing (CH87965) ~50mm high and the other UTX (CH 87970) ~40mm low.
| 01CV - Civils | Cxxx-NCR-001080 | NCR | Damage to invert 23 Serviseal water proofing |  | Contr |  | CON - Connaught Tunnel (East) |  | 2013-09-30 | 2013-06-25 10:28 | -97 | 2013-05-01 | Civil - Tunnelling | 500 |  | Damaged | Repair |  | Complete |  | Completed |  | During break out of invert 23 lower East wall, the Brokk operator damaged the horizontal water bar which is cast into the upper walls Upper wall bay 9 & 10 see photos. The half which is cast in the upper walls is not damaged but the lower wall half has a number of holes from the Brokk point. The water bar was protected by ply but this was an operator error.
| 01CV - Civils | Cxxx-NCR-001092 | NCR | Invert 26 Slab shear links |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2013-08-31 | 2013-07-12 10:20 | -50 | 2013-05-09 | Civil - Tunnelling | 1500 |  | Design | Rework | 4 (0.5-3k) | Complete |  | Completed |  | The Reinforcement has been installed to approved Drawing Cxxx-VIN-C-DWG-CR146_STOO3-50258 C01- Invert Bay 26, Invert RC details. in invert 26 and has been requested for inspection, during the inspection, Cross rail has spotted an error with the design. Bar Mark 41 shape code 21 is scheduled with the C dimension of 100mm where this should be 160mm.
| 01CV - Civils | Cxxx-NCR-001101 | NCR | Temporary Fire Main Installation |  | Crossrail | PDP | CON - Connaught Tunnel (East) |  | 2013-07-22 | 2013-07-22 12:09 | 0 | 2013-05-17 | Mechanical - Piping | 1000 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Lack of procedure | Completed |  | None adherence to accepted design.
| 01CV - Civils | Cxxx-NCR-001105 | NCR | Bay 10 East Overdig |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2013-07-05 | 2013-07-08 09:14 | 3 | 2013-05-21 | Civil - Civil Engineering General | 1500 |  |  | Repair | 4 (0.5-3k) | Complete |  | Completed |  | LTP extends past slab edge and past the +200mm tolerance established in PTR 964. Please see the attached survey, the overdig in this area is simple overdig as per NCR 949.
| 01CV - Civils | Cxxx-NCR-001106 | NCR | Bay 11 East Overdig |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2013-07-05 | 2013-07-08 09:16 | 3 | 2013-05-21 | Civil - Civil Engineering General | 1500 |  |  | Repair | 4 (0.5-3k) | Complete |  | Completed |  | LTP extends past slab edge and past the +200mm tolerance established in PTR 964. Please see the attached survey, the overdig in this area is simple overdig as per NCR 949.
| 01CV - Civils | Cxxx-NCR-001117 | NCR | Invert Bay 27 Formation |  | Crossrail | PDP | CON - Connaught Tunnel (East) |  | 2013-06-28 | 2013-07-01 08:40 | 3 | 2013-05-24 | Civil - Excavation | 1000 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete |  | Completed |  | On attending IRF 1586 CRL discovered that a layer of ply board topped with 3-4" of sand had been placed on the formation. This detail is not within the specification for the works and should not have been offered to CRL for acceptance.
| 01CV - Civils | Cxxx-NCR-001118 | NCR | Sequencing of Works Associated with Service Tunnel In-Fill |  | Crossrail | PDP | CON - Connaught Tunnel (East) |  | 2013-07-25 | 2013-07-01 08:42 | -24 | 2013-05-24 | Tunnelling - Tunnelling General | 500 |  | Planning | Use As-Is | 4 (0.5-3k) | Complete |  | Completed |  | Access to these tunnels was only gained once the dock passage water was removed. Upon gaining access, a black substance was found. Samples were sent away and whilst waiting for results work continued and the work activity of the filling the service tunnels was overlooked.
| 01CV - Civils | Cxxx-NCR-001120 | NCR | Dock Passage access tower 2 design check |  | Crossrail | XRL | CON - Connaught Tunnel (East) |  | 2013-07-15 | 2013-07-12 10:45 | -3 | 2013-05-25 | Communications and Control Systems | 1500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete |  | Completed |  | Dock passage access tower 2. The original design and associated check certificate was originally sent to the PM prior to works - this was returned Code 4. Due to a change in on site conditions, the work was stopped, the design altered and then erected as per the revised drawing. The change in design was not communicated with the PM.
| 01CV - Civils | Cxxx-NCR-001126 | NCR | Void at underside of Bay 27 upperwall pour - rebar exposed |  | Contr |  | CON - Connaught Tunnel (East) |  | 2013-06-30 | 2013-06-25 12:41 | -5 | 2013-05-30 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | Void found on underside of bay 27 upper wall pour.
| 01CV - Civils | Cxxx-NCR-001127 | NCR | Incorrect position of lacer (bar 229) within U bar (Bar 36) for lower wall shear link Bay 24 |  | Crossrail | PDP | CON - Connaught Tunnel (East) |  | 2013-06-30 | 2013-07-01 08:43 | 1 | 2013-05-30 | Civil - Tunnelling | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete |  | Completed |  | As agreed on site between __, CRL and Cxxx, the bar has been installed below the couplers (see attached photos), however an FCD was not raised prior to inspection.
| 01CV - Civils | Cxxx-NCR-001128 | NCR | Honeycombing and crack at bay 27 waterbar |  | Crossrail | XRL | CON - Connaught Tunnel (East) |  | 2013-06-30 | 2013-07-09 09:27 | 9 | 2013-05-30 | Civil - Civil Engineering General | 1000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | There is a crack on the underside of the upper wall pour (west side) at the waterbar where a brokk has damaged the concrete. Also there is honeycombing along the waterbar in this area.
| 01CV - Civils | Cxxx-NCR-001129 | NCR | Invert 24 excessive cover |  | Crossrail | XRL | CON - Connaught Tunnel (East) |  | 2013-07-30 | 2013-08-07 16:47 | 8 | 2013-05-30 | Civil - Civil Engineering General | 1000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | The cover to the top mat reinforcement on the east side of bay 24 invert is approx. 70mm.
| 01CV - Civils | Cxxx-NCR-001130 | NCR | Displaced couplers Bay 24 West Wall |  | Crossrail | PDP | CON - Connaught Tunnel (East) |  | 2013-07-30 | 2013-07-29 15:25 | -1 | 2013-05-30 | Civil - Tunnelling | 800 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Not Defined | Completed |  | Owing to movement of the coupler during the upper wall pour it was not possible to couple up the l bar (bar 33) owing to a clash with the couplers of bars 229. Therefore the reinforcement is not installed as per the accepted design.
| 01CV - Civils | Cxxx-NCR-001132 | NCR | Geotextile damage Bay 6E |  | Contr |  | CON - Connaught Tunnel (East) |  | 2013-06-27 | 2013-06-21 21:52 | -6 | 2013-05-30 | Civil - Civil Engineering General | 500 |  | Damaged | Repair |  | Complete |  | Completed |  | LTP has been damaged via excavator tracking along the South edge of Bay 6E between CH87982- CH87995 and the North edge between CH87988- CH8797991
| 01CV - Civils | Cxxx-NCR-001137 | NCR | Bay 4 splay. West wall |  | Contr |  | CON - Connaught Tunnel (East) |  | 2013-09-30 | 2013-06-25 12:43 | -97 | 2013-06-03 | Civil - Tunnelling | 500 |  | Design | Use As-Is |  | Complete |  | Completed |  | The reinforcement in bay 4 splay have been installed as attached approved design. Bar mark 136 is detailed incorrectly which has caused the splay thickness to decrease by 65mm. The splay thickness from outside of rebar to outside of rebar, should be 690mm and the actual on site dimension is 625mm. (as shown on attachment). All other bays have been checked and have the correct thickness.
| 01CV - Civils | Cxxx-NCR-001141 | NCR | Bay 8 Soffit Missed Witness Point |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2013-08-31 | 2013-07-19 09:11 | -43 | 2013-06-05 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Personnel Error - Inattention to detail | Completed |  | The __ Inspectors were not invited to this witness point as no Inspection Request was completed.
| 01CV - Civils | Cxxx-NCR-001143 | NCR | Invert 16 upper wall shear key reinforcement exposed |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2013-10-31 | 2013-07-01 09:26 | -122 | 2013-06-05 | Civil - Tunnelling | 1000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete |  | Completed |  | Invert 16, East lower wall has been broken out ready for the installation of reinforcement. While breaking out the shear key, the 55mm concrete spacers and the concrete between the concrete spacers has been broken out exposing the U bars above from the upper walls over a 2m section.
| 01CV - Civils | Cxxx-NCR-001146 | NCR | Invert 1,4,22,23,25,28 Shear links |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2013-12-31 | 2013-10-10 08:28 | -82 | 2013-06-05 | Civil - Tunnelling | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | Invert 1,4,22,23,25,28 have been constructed to the approved detailing reinforcement drawings. Since construction of these invert slabs, it has been made aware the shear links BM 41 has a dimension C of 100mm. This dimension for links should be 160mm as specified in the bending codes. Please find attached statement from Hyten confirming the minimum C dimension is 125mm as this is altered by their computer programme. On site measurements show the actual C dimension is 130mm. Please also see attached statement from Alan Auld Assessing the anchoring length with 60N/mm2 concrete, and the 28 day strengths cube results. Please confirm the existing conditions with the shear links of 130mm dimension and 60N/mm2 concrete is acceptable. 7.8/13 - With regards to the engineering response review, the concrete results provided in attachment (COT-CRL NCR-Cxxx-01146_Att11_Invert Bay 1_ 4.pdf), indicates the concrete cube results from Invert Bay 1 Slab and Invert Bay 4 lower walls, as these pours were completed simultaneouly on the 26/4/13, and as such the cubes have been referenced to both pours.
| 01CV - Civils | Cxxx-NCR-001148 | NCR | Parapet Wall Demolition - Cut Line to Flying Arches |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2013-08-09 | 2013-08-02 17:07 | -7 | 2013-06-07 | Civil - Civil Engineering General | 1500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete |  | Completed |  | During the parapet wall demolition works the existing buttresses were to be completely retained. Therefore a track saw cut was completed around these to retain their structural integrity. Having checked the line of the cut line to the back of arch the as built line is up to 100mm back from the design line as shown in the attached survey and photographs. This means that the new parapet wall can still fly passed the existing buttress however the gap is larger than the 25mm design to allow for the compressor filler to ensure that the new and existing have no structural bond. This will have an impact on the parapet wall reconstruction works.
| 01CV - Civils | Cxxx-NCR-001150 | NCR | Invert 16 Extra bar to lower walls |  | Contr |  | CON - Connaught Tunnel (East) |  | 2013-06-07 | 2013-06-19 16:01 | 12 | 2013-06-06 | Civil - Tunnelling | 500 |  | Workmanship | Rework |  | Complete |  | Completed |  | The correct number of bars have been installed into the invert lower walls, but there is a 200mm gap between the existing cast in reinforcement from the upper walls (bay 6). Extra B32 bars have been added between BM 295 to reduce the centres of the vertical bar. Please confirm this is acceptable
| 01CV - Civils | Cxxx-NCR-001153 | NCR | Water Quality |  | Contr |  | CON - Connaught Tunnel (East) |  | 2013-07-01 | 2013-06-25 12:24 | -6 | 2013-06-06 | Environmental - Ecology | 500 |  | System Defect | Use As-Is |  | Complete |  | Completed |  | Surveillance conducted on frequency, results and tracking against triggers of in-situ and __ testing of Water Quality. Concentrating on DO % volumes. 1) In-situ results not being tracked - risk of __ results indicating breach but arriving 14 days after sample tested e.g. breach of 09 May results only discovered on 06 Jun, almost a month after testing; 2) No in-situ results for 4 weeks in Mat 2013 - results not taken or tracked.
| 01CV - Civils | Cxxx-NCR-001154 | NCR | Bay 4 splay, West wall exposed reinforcement |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2013-09-30 | 2013-07-02 14:18 | -90 | 2013-06-07 | Civil - Tunnelling | 3500 |  | Workmanship | Repair | 3 (3-6k) | Complete |  | Completed |  | Bay 4 West splay was concreted with Bay 5 on Wednesday 5th June. Bay 4 is under the North Dock wall and bay 5 is within the dock. After removing the stop ends along the length of the pour it has become aware the concrete has not filled the whole void in bay 4 under the dock wall, leaving to voids as shown on the attachment drawing and the photos. Void 1 is next to bay 3, with exposed reinforcement. Void 2 is at the edge of the dock wall, No exposed reinforcement but there is a void in the excess cover above the slab against the existing brick tunnel (see photo). The cover varies over the reinforcement but the majority has correct cover. This void id smaller than originally thought, the back is full of concrete, the void is by the stop end. The voids have accrued due to one number concrete port positioned 5m away from bay 3. While concreting the flow did not choke the tunnel and build up against bay 3 but instead flow down into bay 5. The shutter on the face of the dock wall was not high enough to put any back pressure to the flow which left void 2. Bay 4 & 5 East splay will have 2 no ports, 2m and 7m away from bay 3, Viewing ports/ bleed holes will be installed along the length of the pour, the shutter at the dock wall will be higher than the highest point of the pour to ensure back pressure. Remedial of bay 4 West void Void 1- We propose to break out the concrete around the reinforcement in the void area with 25mm gap around the reinforcement, once broken out and inspected, shutter and pump the approved C40 concrete back into the void with bleed hole to prove the void is full. Void 2- While breaking out the brick work for the soffit temporary work beams the surface of the void will be scabbled so when the soffit is concreted/ grouted the concrete will bond to the prepared surface.
| 01CV - Civils | Cxxx-NCR-001156 | NCR | CFA pile 310C - Reinforcement embedment not achieved |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2014-07-31 | 2014-04-03 12:40 | -119 | 2013-06-10 | Civil - Civil Engineering General | 1000 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The CFA pile cage did not reach the full embedment depth as per the design. Note that the pile did achieve toe depth. Achieved pile toe depth: 92mOD Achieved reinforcement toe depth 94.1mOD Achieved reinforcement embedment: 1.92m
| 01CV - Civils | Cxxx-NCR-001158 | NCR | Bay 5 (West) Incorrect position of tie bar |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2013-09-30 | 2013-07-02 09:47 | -90 | 2013-06-12 | Civil - Tunnelling | 1000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Supervision - Insufficient supervision | Completed |  | A formwork tie bar has been cast through the concrete permanent structure, with a small section having no cover in the new reinforced concrete splay.
| 01CV - Civils | Cxxx-NCR-001162 | NCR | Bay 8 west wall- Protruding tie bar |  | Contr |  | CON - Connaught Tunnel (East) |  | 2013-01-11 | 2013-06-17 16:20 | 157 | 2013-06-11 | Civil - Tunnelling | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | A formwork tie bar has been cast through the permanent structure, passing through the mass concrete soffit into splay at bay 8, west wall. (As shown on attached image)
| 01CV - Civils | Cxxx-NCR-001163 | NCR | Bay 8 soffit penetration |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2013-07-30 | 2013-07-02 09:58 | -28 | 2013-06-12 | Civil - Tunnelling | 1000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Supervision - Insufficient supervision | Completed |  | The reinforced concrete splay (east and west) have been drilled into so as to install tie bars to support the stop end of the mass concrete pour to the soffit of bay number 8. The West side has 55mm cover over the reinforcement, the East side has approx 300mm cover over the reinforcement.
| 01CV - Civils | Cxxx-NCR-001164 | NCR | Bay 8 soffit concrete finish |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2013-09-30 | 2013-07-02 10:16 | -90 | 2013-06-12 | Civil - Tunnelling | 1000 |  | Workmanship | Rework | 4 (0.5-3k) | Complete |  | Completed |  | Bay 8 soffit was not finished as specified in KF 10 3232.
| 01CV - Civils | Cxxx-NCR-001165 | NCR | Bay 8 East mass pour concrete without inspection |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2013-07-30 | 2013-07-18 14:23 | -12 | 2013-06-12 | Civil - Tunnelling | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete |  | Completed |  | A concrete pour (pour nr.2 see attached drawing)was required between existing dock bed to the outside edge of the new reinforced concrete tunnel, the reason for this was mainly to reduce flotation properties of the new structure. Bay 8 East pour was completed without prior concrete inspection and approval. Work commenced as this was deemed a non-structural pour. Pour 1 (see attached drawing) was inspected and approved before pouring concrete.
| 01CV - Civils | Cxxx-NCR-001179 | NCR | CFA Pile cut off level should be +0mm and -25mm |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2013-07-31 | 2013-07-29 15:26 | -2 | 2013-06-14 | Civil - Civil Engineering General | 1000 |  | Supervision/Management | Repair | 4 (0.5-3k) | Complete |  | Completed |  | During the trimming down works two piles 63 & 64 were trimmed below the cut off level
| 01CV - Civils | Cxxx-NCR-001180 | NCR | Bay 8 soffit pour started prior to completion of formwork |  | Crossrail | XRL | CON - Connaught Tunnel (East) |  | 2013-07-12 | 2013-06-28 17:45 | -14 | 2013-06-14 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Repair | 4 (0.5-3k) | Complete |  | Completed |  | Bay 8 soffit pour commenced prior to formwork completion. Works continued on the vertical and horizontal formwork in the dock passage end (on the additional part of the pour around the needle beams) as the main section of the pour was concreted.
| 01CV - Civils | Cxxx-NCR-001183 | NCR | Damaged waterbar in invert 17 |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2013-06-28 | 2013-07-01 14:14 | 3 | 2013-06-15 | Tunnelling - Linings - In-situ Concrete | 1000 |  | Damaged | Repair | 4 (0.5-3k) | Complete |  | Completed |  | Serviseal waterproofing strip has been damaged along the invert construction joint between invert 16 and invert 17. (Photo attached). The first rib only has been teared. The waterbar was protected with timber, however was damaged in an operator error.
| 01CV - Civils | Cxxx-NCR-001189 | NCR | 2.2 CMC rows 579-586 out of position |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2013-08-12 | 2013-07-18 14:05 | -25 | 2013-06-24 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | The columns 579E / 580ACEF / 581DE / 582AEF / 583A / 584A / 585E / 586AD have been installed as per the attached spreadsheet This is distance from the designed co-ordinate is stated.
| 01CV - Civils | Cxxx-NCR-001190 | NCR | 2.2 CMC 583E / 584D- multiple issues |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2013-08-12 | 2013-08-13 11:51 | 1 | 2013-06-24 | Civil - Civil Engineering General | 1000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | Cracked Head Column NCR (Applicable to 583E / 584D) The columns 583E and 584D have a crack in the column head which have resulted in a piece of the concrete breaking away at the head and side of the column. Removing these cracked pieces has created a smaller pile head and also a void to the side of the column. The sizes of the cracked concrete and the diameters of the column heads are shown on the attached spreadsheet. (It should be noted that the column has achieved the correct diameter and only the head has a smaller diameter.) Out of Position (Applicable to 583E ) The columns have been installed as per the attached spreadsheet This is distance from the designed co-ordinate is stated.
| 01CV - Civils | Cxxx-NCR-001193 | NCR | Works carried out without CRL acceptance of Method Statement |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2013-08-25 | 2013-08-23 11:44 | -2 | 2013-06-25 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete |  | Completed |  | The removal of the concrete planks spanning between arches 5&6 and 8&9 over the eastern approach ramp was completed prior to CRL acceptance of the Method Statement. The Method Statement had been produced, checked and approved by __ and had gone through an informal review with CRL prior to the works being carried out.
| 01CV - Civils | Cxxx-NCR-001197 | NCR | Bay 8 soffit reinforcement out of position |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2013-08-16 | 2013-08-14 17:18 | -2 | 2013-06-25 | Civil - Tunnelling | 1000 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | Bay 8 Soffit reinforcement protrudes into bay 7 by 200mm, (BM 102 T2). These bars are out of position, they are 40mm lower than designed. Please see FCD 1172 for proposal of rectifying bay 7 reinforcement. We propose to supply concrete cube results, proving the concrete will be approx 60N/mm2 at 28 days and leave as is. Please see attached cover survey sketch. 7.8.13 - This appears to be a duplicate NCR to NCR 1204. Please see attached as built survey of the couplers as requested, see attachment (MX-2700N_20130807_162052.pdf)
| 01CV - Civils | Cxxx-NCR-001200 | NCR | Soffit bay 7 Finish Level differs to answer in RFI 1108 |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2013-07-31 | 2013-07-10 14:50 | -21 | 2013-06-27 12:30 | Civil - Tunnelling | 1000 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | As per RFI 1108, to avoid a step from the level difference between soffit bay 8 and soffit bay 7, a 45 degree fillet was required. This was not completed and the level difference was sloped across the entire slab, as a result of the non conformance bay 7 soffit is now up to 51mm higher than the design. (25mm tolerance) (see attached level survey)
| 01CV - Civils | Cxxx-NCR-001201 | NCR | 2.2 - CMC rows 554-578 out of position |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2013-08-16 | 2013-07-29 09:35 | -18 | 2013-06-28 14:01 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | Out of Position: The columns 554BC / 556AC / 557AF / 558EF / 560E / 561BCD / 562E / 571D / 573CD / 574D / 575B / 576B have been installed as per the attached spreadsheet This is distance from the designed co-ordinate is stated.
| 01CV - Civils | Cxxx-NCR-001202 | NCR | 2.2 - CMC 554F-556F-557E – Trimming level too low |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2013-08-12 | 2013-08-13 16:01 | 1 | 2013-06-28 14:07 | Civil - Civil Engineering General | 1000 |  | Workmanship | Rework | 4 (0.5-3k) | Complete |  | Completed |  | 554 F: Trimming level is 101.031, 68mm below design trimming level 556F: Trimming level is 101.003, 103mm below design trimming level 557E: Trimming level is 101.023, 86mm below design trimming level
| 01CV - Civils | Cxxx-NCR-001203 | NCR | Extra cover on cofferdam soffits Bays 5-8 |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2013-08-16 | 2013-07-10 14:51 | -37 | 2013-07-03 12:17 | Civil - Civil Engineering General | 1500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | Upon carrying out a cover meter survey on the soffit of bays 5-8 prior to the reflooding of the dock passage it was found that there is more than the specified 55-61mm.
| 01CV - Civils | Cxxx-NCR-001204 | NCR | Bay 8 Soffit Top Mat Reinforcement Out of Position |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2013-08-22 | 2013-07-17 16:56 | -36 | 2013-07-03 12:31 | Civil - Civil Engineering General | 1000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | Upon fixing the reinforcemet of the top mat of Bay 7 it was found that the couplers were lower than designed, however bay 8 had already been cast. Consequently this has proved that the Bay 8 reinforcement must be cast in lower than the design level.
| 01CV - Civils | Cxxx-NCR-001205 | NCR | 1.1/2.1 Missing Certification for Material Grading |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2013-07-19 | 2013-07-08 09:28 | -11 | 2013-07-04 10:44 | Civil - Fill | 500 |  | System Defect | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Use of unapproved materials | Completed |  | Missing 6F5 Grading certification During 05/2012 material used for piling platform East and West sites, a grading certification was not undertaken, please see the attached documentation which highlights (in red) specific area. Testing is normally carried out at ~1000T intervals, for the 14185T delivered there has been 20no PSDs carried out (15no. by __, 5no. by the supplier)
| 01CV - Civils | Cxxx-NCR-001206 | NCR | 2.2 CMC Bay 13 – Mechanical damage |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2013-08-18 | 2013-08-14 15:55 | -4 | 2013-07-04 12:01 | Civil - Civil Engineering General | 1000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | Mechanical damage (applicable to 545A / 547B / 553B / 557C) 545A: Trimming level is 100.886, 180mm below design trimming level 547B: Trimming level is 100.944, 130mm below design trimming level 553B: Trimming level is 100.975, 120mm below design trimming level 557C: Trimming level is 100.989, 120mm below design trimming level
| 01CV - Civils | Cxxx-NCR-001207 | NCR | 2.2 - CMC rows 539-553 out of position |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2013-08-18 | 2013-07-25 08:32 | -24 | 2013-07-04 12:00 | Civil - Civil Engineering General | 1000 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | The columns 539CD / 542E / 544B / 545B / 546AC / 547F / 548BF / 550BE / 551A have been installed as per the attached spreadsheet This is distance from the designed co-ordinate is stated.
| 01CV - Civils | Cxxx-NCR-001208 | NCR | Incorrect Effective Depth of Bay 5 Soffit Steelwork |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2013-08-23 | 2013-08-02 11:25 | -21 | 2013-07-04 08:52 | Civil - Civil Engineering General | 1000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | Upon inspection of the Bay 5 Soffit reinforcement, it was found that the cage was out of position. The cage could not be altered as it was predetermined by the location of the coupler on the ends of Bays 4 and 6, and the already cast splays in bay 5
| 01CV - Civils | Cxxx-NCR-001209 | NCR | Failure to follow Permit to Strike of Bay 7 Soffit |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2013-08-03 | 2013-07-11 08:29 | -23 | 2013-07-04 09:09 | Civil - Civil Engineering General | 1000 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Subcontractor Problems - Insufficient surveillance of subcontractors | Completed |  | Permit to Strike issued by __ to __ on 28/6/13 for removal of temp works on Sat 29th June 2013 at 7am detailed the requirement for backpropping. By the time __ went to strike, full 28 day strength had been achieved in the concrete and as such it was assumed that no back propping was required. Back propping was installed following instruction from CRL during an engineering meeting between __/CRL/__/Cxxx on Tues 2/7/13
| 01CV - Civils | Cxxx-NCR-001210 | NCR | Invert 2 lower wall position |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2013-08-25 | 2013-08-20 09:09 | -5 | 2013-07-08 14:35 | Civil - Civil Engineering General | 1500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | Please see attached As-built survey of the lower walls to invert 2. During concreting the lower walls, the shutters moved in the middle section making a 20mm step between the upper walls and the lower walls. The reinforcement did not move as it is cast in the upper walls and the invert slab. We propose to scabble the step between the walls and make good the surface with __ FC. Please see attached additional as built survey (Add as built) to include include the kicker level of invert bay 2.
| 01CV - Civils | Cxxx-NCR-001211 | NCR | 6.1 - Bay 11 Lower Wall West - Couper/Reinforcement Clash and Spacing Issue |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2013-09-19 | 2013-08-09 15:48 | -41 | 2013-07-31 09:16 | Civil - Tunnelling | 1000 |  | Design | Repair | 4 (0.5-3k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | As per KF10.3244 part c) 'All reinforcement shall be securely and accurately fixed in positions shown on the drawings'. In invert bay 11, DWG Cxxx-VIN-C-DWG-CR146_ST003-50243 C02, 2no bars are unable to be fixed in position as per the drawings due to clashing with couplers. Horizontal bars BM359 (see (f)and (g) in attached sketch) clash with the vertical couplers between NF1 and NF3.
| 01CV - Civils | Cxxx-NCR-001213 | NCR | 6.1 Incorrect reinforcement spacing to invert bay 20 |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2013-08-29 | 2013-08-09 15:48 | -20 | 2013-07-10 17:39 | Civil - Tunnelling | 1000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | Location - Invert bay 20 East and West wall, reinforcement spacing to BarMark 33 as per approved drawing (Cxxx-VIN-C-DWG-CR146_ST003-51252) is 150mm. From inspection the spacing between bar nr.6 and nr.7 on the east wall is 215mm, and from west wall bar nr.2 and nr.3 the spacing is 235mm (see attached marked up images). To reduce this spacing we intend to install an additional BarMark33 between these referenced bars.
| 01CV - Civils | Cxxx-NCR-001214 | NCR | 6.1-Low cover on BM33 invert bay 20 east wall |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2013-11-20 | 2013-11-08 17:04 | -12 | 2013-07-12 13:13 | Civil - Tunnelling | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | Invert 20 lower wall vertical reinforcement has one bar out of specification for cover. Specification KF10 institute concrete requires 55mm cover. BM 33 , fifth bar along from invert 21 has 52mm cover. We propose to leave as is
| 01CV - Civils | Cxxx-NCR-001215 | NCR | Wrong specification of steel used |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2013-08-16 | 2013-08-09 16:01 | -7 | 2013-07-11 17:48 | Shafts - Shafts General | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | As an oversight by __ we have ordered and installed the incorrect specification of steel plate in the 600id eye wall FCD COT-CRL FCD-Cxxx-01057 states that the steel plates should be Grade S355JR to BS EN 10025-3 rolled weldable fine grain structual steel Unfortunatly the grade which was installed was S355K2+N to BS EN 10025-2 non alloy structual steel
| 01CV - Civils | Cxxx-NCR-001216 | NCR | 6.1 - Invert 15 - incorrect reinforcement spacing |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2013-07-29 | 2013-07-18 14:26 | -11 | 2013-07-15 13:46 | Civil - Tunnelling | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | Invert bay 15 west wall - reinforcement spacing to bar mark 296 is to be 150mm as per Cxxx-VIN-C-DWG-CR146_ST003-50247. However in two locations between bar no. 3 and no. 4 and between bar no. 16 and no. 17, the spacing is 230mm and 210mm respectively, due to the cast in couplers in the wall bay above (see attached photo). The correct number of bars have been installed.
| 01CV - Civils | Cxxx-NCR-001217 | NCR | Invert 15, CJ 14 coupler reinforcement out of position |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2013-08-14 | 2013-07-25 08:58 | -20 | 2013-07-15 19:37 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | In Invert 15 at the construction joint 14 connecting into Invert 16, the top mat couplers are out of position. Please find attached As built survey showing the Depth between the top mat and bottom mat of reinforcement, the cover to the top mat and the depth of slab. Due to the past results of the concrete gaining approx 60N We propose to use as is
| 01CV - Civils | Cxxx-NCR-001218 | NCR | Invert 15 wall reinforcement out of tollerence |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2013-10-20 | 2013-08-29 13:04 | -52 | 2013-07-17 15:22 | Civil - Civil Engineering General | 800 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | Please find attached As built survey of the reinforcement coupler at invert IJ 14. The couplers have additional cover, up to 7mm extra cover (68mm instead of 61mm) We propose to use as is 7.8/13 - Please see attached pre-pour checks for soffit bay 6, East and West wall.
| 01CV - Civils | Cxxx-NCR-001219 | NCR | Parapet Wall Reconstruction - Post Pour Finishing |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2013-08-05 | 2013-08-12 11:03 | 7 | 2013-07-22 14:24 | Civil - Civil Engineering General | 1500 |  | Material | Repair | 4 (0.5-3k) | Complete | Subcontractor Problems - Insufficient surveillance of subcontractors | Completed |  | Following the concrete pours for the parapet wall works, the tie holes and joints have received further finishing works to fill and smooth any imperfections on the wall. In some locations the render/grout used has been a sand and white cement mix. In these locations the grout has been subject to shrinkage and cracks are visible as shown in the attached document. When the integrity of the render material was tested, the render crumbled away from the wall and exposed that the concrete surface had not been scabbled prior to application, hence there being an insufficient bond.
| 01CV - Civils | Cxxx-NCR-001220 | NCR | 6.1-Incorrect cover to invert 21 reinforcement |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2013-07-26 | 2013-07-30 16:20 | 4 | 2013-07-19 15:52 | Civil - Tunnelling | 500 |  | Planning | Use As-Is | 4 (0.5-3k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | From attached as built survey drawings of invert 21, when constructed there will be excessive cover from the top bar reinforcement (bar mark 43 and 42) to top of invert bay 21 slab, this is due to couplers for bar marks (235,236) being cast in existing invert 20 + 23 pours with additional cover. Please see on attached survey the highlighted areas that are out of the reinforcement cover tolerance, the target cover is 55mm with a tolerance +6mm, -0mm. We propose to leave as is, although for the next invert reinforcement setting out, we will install a grout check along the bay and this will ensure that the couplers will be placed as per design and will reduce any follow on issues to next bay pours. Please confirm the proposal is acceptable.
| 01CV - Civils | Cxxx-NCR-001221 | NCR | 6.1 - Invert bay 25mm couplers damaged |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2013-07-24 | 2013-07-29 16:07 | 5 | 2013-07-22 13:52 | Civil - Tunnelling | 1000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | Invert bay 21 lower walls, Bar Mark 37 25mm couplers have been damaged, this will not allow __ to construct as per the design. The locations for these damaged couplers are indicated on attached images, which are East wall coupler nr. 1 from invert 22 and coupler nr.2 from invert 20. West wall, coupler nr.2 from invert 22 and 20, these are indicated with an asterisk. Please see attached drawing indicating bar mark / locations also for clarity. We propose to cut out the damaged couplers and drill 400mm adjacent to these into the upper wall. This will allow the placement of additional 25mm bars to be cast in with HEP 385 Resin as per NCR 1059, with an increased bar length protruding into the wall.
| 01CV - Civils | Cxxx-NCR-001222 | NCR | 6.1 - Varying Cover on invert bay 21 floor slab |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2013-08-16 | 2013-08-12 10:51 | -4 | 2013-07-22 14:16 | Civil - Tunnelling | 500 |  | Planning | Use As-Is | 4 (0.5-3k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | The reinforcement cover was checked on the top mat of invert 21, bar mark 42 and 43. The measured cover ranged from 50mm to 68mm on various locations throughout the slab. See attached image of measured cover and a drawing showing area of low cover. We propose to leave as is. 7.8/13 - The original drawing was uploaded by mistake,please see attached drawing relevant to this NCR with asssociated cover meter survey as carried out on 7/8/13 (attachment NCR1222 sketch and cover meter survey).
| 01CV - Civils | Cxxx-NCR-001223 | NCR | Parapet wall scaffolding |  | Crossrail | XRL | CON - Connaught Tunnel (East) |  | 2013-09-06 | 2013-08-27 09:55 | -10 | 2013-07-22 12:21 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | During the construction of the reinforcement to the east approach ramp parapet wall portal it was noted that there was an unauthorised amendment to the load bearing scaffolding. A tube and fitting access scaffold was erected on top of the crash deck of the load bearing scaffold and no design had been carried out for its installation.
| 01CV - Civils | Cxxx-NCR-001225 | NCR | Parapet Wall Step in Top of Concrete Level |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2013-08-05 | 2013-08-20 15:56 | 15 | 2013-07-22 16:22 | Civil - Civil Engineering General | 1000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | During the reinforced concrete works for the Parapet Wall Construction the level for the top of concrete was poured 30mm too high on the east bound wall. The location of this is at the corner that links on to the portal wall, between Wall G and Wall H, CH 18329 and extends over an area of approximately 1m. This concrete pour was completed on 17/07/13; the Portal Wall H was poured on 19/07/13 by which point the incorrect level had been observed. The portal has been poured to the correct level to ensure the correct cover on the steel reinforcement is maintained. There is therefore a 30mm step in level at the corner between these two pours as shown in the attached photograph.
| 01CV - Civils | Cxxx-NCR-001226 | NCR | 6.1 - Reinforcement from upper wall protrude into lower wall invert bay 11 |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2013-07-26 | 2013-07-29 16:53 | 3 | 2013-07-23 14:41 | Civil - Tunnelling | 1500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | From breaking out invert bay 11 shear key East and West wall, the u-bars from upper wall protrude into the lower wall of this invert. This may be due to the bars being moved within the concrete pour and as such has moved from the concrete spacer block, please see attached images of the bars. We propose from NCR-001143, to break out 30mm behind the affected bars and install a grout tube tight up to the existing concrete. This will allow us to cast the lower wall and grout invert 11 when complete.
| 01CV - Civils | Cxxx-NCR-001227 | NCR | 6.1 - Incorrect cover to invert bay 11 lower wall B40 couplers |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2013-07-29 | 2013-07-30 16:21 | 1 | 2013-07-25 10:07 | Civil - Tunnelling | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | An as-built survey of the B40, 55mm couplers was completed on the front face of the East and West wall of invert 11 (see attached sketch). This survey concluded that the cover on the reinforcement exceeded the allowable tolerance of 55mm, + 6mm, -0mm in the areas highlighted on as built-survey results. We propose to use as is.
| 01CV - Civils | Cxxx-NCR-001228 | NCR | 6.1 - Incorrect hole diameter drilled invert bay 21 |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2013-07-31 | 2013-08-07 16:52 | 7 | 2013-07-24 13:13 | Civil - Tunnelling | 800 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete |  | Completed |  | This NCR has been raised as a process issue to work carried out for NCR 1221. As agreed for NCR 1221, __ would drill into the upper wall in the areas agreed for the placement of B25 bars with an inspection required to ensure minimum anchorage length is achieved. __ carried out work before a formal response was received from NCR 1221. The hole diameter drilled in first instance was 28mm, this successfully allowed the placement of a B25 bar. Where subsequent drilling took place it was found that the 28mm diameter was not sufficient to place the B25 bars in the other three areas. We propose to carry out the work with a 30mm drill bit to allow the placement of bars.
| 01CV - Civils | Cxxx-NCR-001229 | NCR | Invert 11 reinforcement laser coupler clash |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2013-08-24 | 2013-08-07 17:32 | -17 | 2013-07-25 18:52 | Civil - Civil Engineering General | 1500 |  | Design | Repair | 4 (0.5-3k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | Invert 11 spans between upper wall bays 4 and 5. There is a level difference between the two bays as shown on the attached Invert 11 rebar drawing – CxxxVIN-C-DWG-CR146_ST003-50243 C01. Upper wall bay 5 has BM112 is 32mm dia (3no) which should couple into invert 11 BM 357 but this is scheduled as 25mm dia. 1. We propose to install 2no 32mm bars as BM 357 which splice onto BM359 as shown attached invert 11 drawing. The top coupler as shown on the attached photo is situated between Bay 4 upper wall couplers, not allowing enough room to screw a B32 coupler with the protruding welds on the coupler. 2. We propose to drill and fix a B25 (Same as what is detailed in invert 11 reinforcement drawing) 400mm deep and resin with __385 as previously detailed in NCR 1221
| 01CV - Civils | Cxxx-NCR-001230 | NCR | Invert 8 East wall Water bar position |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2013-08-25 | 2013-08-09 15:48 | -16 | 2013-07-26 07:59 | Civil - Civil Engineering General | 1000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | Invert 8 East wall Serviseal water bar construction joint ‘T’ connection piece has been installed 600mm out of position as shown on attached drawing. We propose to install the reinforcement as approved design but drill the stop end shutters to allow the reinforcement to pass through, and cast the construction joint from water bar to water bar as shown attached.
| 01CV - Civils | Cxxx-NCR-001231 | NCR | 6.1-Damage to waterbar Invert Bay 8 |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2013-08-11 | 2013-08-09 15:49 | -2 | 2013-07-28 11:25 | Civil - Tunnelling | 1000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | The serviseal waterproofing has been damaged on top of blinding level on the West side of construction joint IJ7 as marked on the attached sketch. A similar issue has previously occurred as per NCR-962-Damaged waterproofing system. We propose to carry out a similar repair, placing a metal plate above and below the damaged area in question + 50mm overlap in all directions, with the damaged area and plate sealed using Bituthene LM. (see attached sketches for further explanation)
| 01CV - Civils | Cxxx-NCR-001232 | NCR | Procedural NCR - Works Proceeded in Invert bay 11 without resolution of NCR 1226 |  | Crossrail | XRL | CON - Connaught Tunnel (East) |  | 2013-08-09 | 2013-08-09 15:51 | 0 | 2013-07-26 15:51 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete |  | Completed |  | Despite there being an unresolved NCR (no technical resolution approved) for exposed rebar (NCR 1226) outstanding in invert bay 11, __ workers proceeded to install grout tubes and hydrophonic sealant (per the atttached photograph) which will now need to be removed in order to perform the approved resolution of NCR 1226.
| 01CV - Civils | Cxxx-NCR-001233 | NCR | Procedural NCR - Works Proceeded in Invert bay 08 without resolution of NCR 1230 |  | Crossrail | XRL | CON - Connaught Tunnel (East) |  | 2013-08-09 | 2013-08-09 15:52 | 0 | 2013-07-26 16:45 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete |  | Completed |  | Despite there being an unresolved NCR (no technical resolution approved) for waterbar end points out of alignment (NCR 1230) outstanding in invert bay 08, __ workers proceeded to complete installation of waterbar which may need to be modified in order to comply with the approved resolution of NCR 1230.
| 01CV - Civils | Cxxx-NCR-001234 | NCR | 6.1-Exposed reinforcement from upper wall Invert Bay 8 |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2013-09-18 | 2013-08-09 15:52 | -40 | 2013-07-30 18:07 | Civil - Tunnelling | 1500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | From invert breaking out operations on the East and West wall, the reinforcement from the upper wall has become exposed. The locations and extent of the exposed areas are as marked up on attached sketchs / images. The exposed reinforcement from images are BM127 B12 on west wall and BM01 B12 on the east wall. We propose to further break out 30mm minimum around the exposed reinforcement and scabble back as per NCR1226. We propose to place a grout pipe through the exposed reinforcement thereafter, tight to the existing upper wall concrete.
| 01CV - Civils | Cxxx-NCR-001235 | NCR | 6.1-B25 couplers damaged Invert Bay 8 East Wall |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2013-09-17 | 2013-08-07 17:39 | -41 | 2013-07-29 17:41 | Civil - Tunnelling | 1000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | 2nr. B25mm front face couplers have been damaged on invert bay 8 lower east wall. The locations of these damaged couplers are referenced from invert bay 7 towards invert 9, being coupler nrs are 8 and 10 only. Please see attached drawing and image for clarity. We propose to cut out the damaged couplers, and drill a 32mm diameter hole 400mm deep adjacent to these into the upper wall. This will allow the placement of B25 bars to be cast in with HEP 385 resin as per NCR 1059 / 1221 / 1237, with an increase in bar length protruding into the wall.
| 01CV - Civils | Cxxx-NCR-001236 | NCR | 6.1-Carrying out works without CRL approval invert bay 8-process NCR to NCR 1230 |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2013-08-11 | 2013-08-09 16:49 | -2 | 2013-07-28 13:04 | Civil - Tunnelling | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Other | Completed |  | This NCR has been raised due to __ carryout out works on an NCR (NCR 1230) without Crossrail approval. This included works on the serviseal waterbar on the construction joint WJ3 east wall invert bay 8, before an approved answer was given. Work will halt on areas of where NCR's require completion until approval has been granted.
| 01CV - Civils | Cxxx-NCR-001237 | NCR | 6.1-Damage to B25 couplers Invert Bay 11 West Wall |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2013-08-11 | 2013-08-07 18:21 | -4 | 2013-07-28 14:32 | Civil - Tunnelling | 1500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | 2nr. B25mm front face couplers have been damaged on invert bay 11 lower west wall, upper section of the shear key. The locations of these damaged couplers are referenced from invert bay 10 towards invert 12, being coupler nrs are 14 and 16 only. Please see attached drawing and image for clarity. We propose to cut out the damaged couplers, and drill a 32mm diameter hole 400mm deep adjacent to these into the upper wall. This will allow the placement of B25 bars to be cast in with HEP 385 resin as per NCR 1059 / 1221, with an increase in bar length protruding into the wall.
| 01CV - Civils | Cxxx-NCR-001238 | NCR | Incorrect Drawings onsite - Invert bay 11 |  | Crossrail | XRL | CON - Connaught Tunnel (East) |  | 2013-08-12 | 2013-08-09 15:53 | -3 | 2013-07-29 10:06 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete |  | Completed |  | Surveillance of Drawings onsite indicated that at invert bay 11, workers were using drawing ref: Cxxx-VIN-C-DWG-CR146_ST003-50243 REV C01 however the latest revision of this document is C02, which was returned to contractor 13-May-2013 code 2.
| 01CV - Civils | Cxxx-NCR-001239 | NCR | 6.1-Missing couplers invert bay 11 lower wall west |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2013-09-17 | 2013-08-09 15:56 | -39 | 2013-07-29 15:12 | Civil - Tunnelling | 1000 |  | Design | Repair | 4 (0.5-3k) | Complete | Subcontractor Problems - Insufficient surveillance of subcontractors | Completed |  | Invert bay 11 lower west wall, WJ-04 has been detailed through two separate drawings, one of the invert/lower wall and the other for the upper wall/ splay, where a discrepancy has been observed in the detailing from the designer. In drawing Cxxx-VIN-C-DWG-CR146_ST003-50243, it can be seen that 3nr. Couplers have been detailed on the top in the area as highlighted, with BM357 (25mm) connecting to these couplers. From looking at drawing for bay 5 upper wall and splay reinforcement (Cxxx-VIN-V-DWG-CR146_ST003-50066), as highlighted and detailed, that these couplers have not been detailed and therefore have not been cast into wall pour. We propose a solution similar to NCR 1221. This is to drill a 32mm diameter hole in the positions indicated on the sketch, 400mm deep into WJ-04, resin in place with HEP385 2nr. 25mm diameter bars. This will allow BM36 to be placed around BM357 and tie in accordingly.
| 01CV - Civils | Cxxx-NCR-001240 | NCR | 6.1- Front face concrete damage invert bay 8 west wall |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2013-09-17 | 2013-08-09 15:56 | -39 | 2013-07-29 17:13 | Civil - Tunnelling | 1000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | During break out operations of invert and lower walls to invert bay 11, damage has been caused to the front face concrete finish of the upper wall (see attached photos of damage extent, and sketch to clarify location). We propose to cut out a section around the damaged area, cutting depth 30mm. Scabble the damaged area back to a minimum depth of 30mm. When pouring lower wall shutter, extend the shutter to include this area. Concrete the lower wall and include the damaged area. Once complete, concrete finish to be inspected and made good if further required.
| 01CV - Civils | Cxxx-NCR-001242 | NCR | 5.5 Cfa Pile Reinforcement Height |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2014-07-31 | 2014-07-15 08:41 | -16 | 2013-08-02 09:37 | Civil - Geotechnical Engineering | 2500 |  | Supervision/Management | Repair | 4 (0.5-3k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | East Approach Ramp CFA piles location 227A and 228B - Top of steel installed lower than specified length. 227A Installed 580mm lower at 101.020 instead of 101.600. 228B Installed 528mm lower at 101.072 instead of 101.600. Both piles are Non conformance as the de bonding foam cast below the trim level.
| 01CV - Civils | Cxxx-NCR-001243 | NCR | 6.1-Stop end position, invert bay 11 West wall IJ10 |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2013-09-19 | 2013-08-09 15:56 | -41 | 2013-07-31 16:34 | Civil - Tunnelling | 1000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Subcontractor Problems - Insufficient work planning by the subcontractors | Completed |  | Bars in the upper walls cast out of position invert bay 11, west wall IJ10 B40 coupler to BM33
| 01CV - Civils | Cxxx-NCR-001245 | NCR | 6.1-incorrect cover to invert bay 8 slab reinforcement |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2013-09-19 | 2013-08-09 16:57 | -41 | 2013-07-31 16:27 | Civil - Tunnelling | 1500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | From the attached as built survey drawings of invert bay 8 slab, when invert bay 8 is constructed there will be excessive cover from the top bar reinforcement (bar mark 240 and 239) to top of invert slab, this is due to couplers for bar mark 46 being cast in existing invert 7, IJ7, with additional cover as indicated. Please see on attached as-built survey the highlighted areas that are out of the reinforcement cover tolerance, the target cover is 55mm with a tolerance of +6mm, -0mm. Also see the areas highlighted that are out of tolerance of the difference between design and actual depth, target 670mm with a tolerance of +0mm, -12mm. We propose to leave as is, although for the next invert reinforcement setting out, we will install a grout check along the bay and this will ensure that the couplers will be placed as per design and will reduce any follow on issues to next bay pours.
| 01CV - Civils | Cxxx-NCR-001247 | NCR | Incorrect use of site revision drawings |  | Crossrail | XRL | CON - Connaught Tunnel (East) |  | 2013-08-15 | 2013-08-15 10:37 | 0 | 2013-08-01 13:33 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete |  | Completed |  | Drawing: Cxxx-VIN-C-DWG-CR146_ST003-50286 rEV C02 On site inspection of the parapet wall on the east approach ramp it was observed that the steel fixers were using the incorrect revision for the reinforcement drawings. REV C01 was being used.
| 01CV - Civils | Cxxx-NCR-001248 | NCR | 6.1-Varying cover to reinforcement lower walls invert bay 8 |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2013-09-20 | 2013-08-09 15:57 | -42 | 2013-08-01 15:33 | Civil - Tunnelling | 1000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | There is varying reinforcement cover on the east and west front face lower walls, to invert bay 8. On the east wall cover varies from 52-69, on the west the cover varies from 47-60, this is as highlighted on the attached as built survey drawing of the B55 couplers for BM33 east, BM 33/350 west. For the area of reinforcement with excessive cover (East wall), we propose to use as is providing adequate crack resistance is ok. For the areas with too little cover we propose to offset shutter to allow adequate cover to be achieved, where wall will be cast approx 8mm out of plumb.
| 01CV - Civils | Cxxx-NCR-001249 | NCR | 6.1-Drilling into permanent works, invert bay 11 west wall |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2013-09-21 | 2013-08-09 15:59 | -43 | 2013-08-02 07:56 | Civil - Tunnelling | 800 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Subcontractor Problems - Other | Completed |  | __ have been approved to carry out drilling works to NCR 1229 and NCR 1239. The operatives were required to drill into the permanent works with a 32mm diameter hole, for the placement of 25mm diameter bars. During the operation several attempts to drill to the agreed length of 400mm were unsuccessful due to encountering existing steel reinforcment which obstructed the path of the drill bit. To remove these voids in the permanent works we propose to fill the hole / void with V385 resin. Where the depth is too large to guarantee the resin to completely fill the void, we propose to place V385 resin in addition to a B25 bar cut to full length of the void and cast in place.
| 01CV - Civils | Cxxx-NCR-001251 | NCR | 6.1-Front face concrete damage to invert bay 14 upper wall |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2013-09-25 | 2013-08-15 09:23 | -41 | 2013-08-06 13:03 | Civil - Tunnelling | 1500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | During break out operations of invert and lower walls to invert bay 14, damage has been caused to the front face concrete finish of the upper wall from hand breaking around the front face couplers (see attached photos of damage extent). We propose to cut out a section around the damaged area,(cutting depth 30mm as per NCR 1240), scabble the damaged area back to a minimum depth of 30mm. When pouring lower wall shutter, extend the shutter to include this area. Concrete the lower wall and include the damaged areas. Once complete, concrete finish to be inspected and made good if further required.
| 01CV - Civils | Cxxx-NCR-001252 | NCR | 6.1-Incorrect reinforcement spacing to invert bay 14 |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2013-09-05 | 2013-08-15 09:25 | -21 | 2013-08-06 17:28 | Civil - Tunnelling | 1500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | Invert bay 14 east wall, 2nr. B32 front face couplers (coupler number 13 and 14 from IJ13), which connect to BM296 have been observed to have an excessive c/c spacing, this is as indicated on attached image being measured at 220mm. The approved designed spacing c/c is 150mm. We propose to add in an additional B32 BM296, between the bars to reduce cracking cracking properties of the concrete, and tie to the B25 lacer bars (BM331 and 330) on the East wall.
| 01CV - Civils | Cxxx-NCR-001253 | NCR | 6.1-Exposed u-bars invert bay 14 |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2013-09-06 | 2013-09-03 16:43 | -3 | 2013-08-07 18:15 | Civil - Tunnelling | 1000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | From invert breaking out operations on the East and West wall to invert bay 14, the reinforcement from the upper wall has become exposed. The locations and extent of the exposed areas are as marked up on attached sketchs/ images. The exposed reinforcement from images are BM01 B12 u-bar on West wall and BM97 B12 u-bar on the East wall. We propose as per NCR's (1234 / 1226), to further further break out / scabble back around these exposed areas to a minimum of 30mm. We also propose to place a grout pipe up tight to the exposed reinforcement / or through the exposed bars if required.
| 01CV - Civils | Cxxx-NCR-001254 | NCR | 6.1-Excessive cover to floor slab reinforcement invert bay 14 |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2013-09-07 | 2013-08-09 16:00 | -29 | 2013-08-08 11:52 | Civil - Tunnelling | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | The reinforcement cover was checked on the top mat of invert 14, bar mark 327 and 328 (see attached sketch and as built survey). The measured cover ranged from 55mm to 70mm on various locations throughout the slab. These couplers have been previously cast into invert bay 15 pour. We propose to use as is.
| 01CV - Civils | Cxxx-NCR-001255 | NCR | 6.1-Excessive cover to front face couplers invert bay 14 lower wall |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2013-09-07 | 2013-08-09 16:00 | -29 | 2013-08-08 12:59 | Civil - Tunnelling | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | There is varying reinforcement cover on the east and west front face lower walls, to invert bay 14. On the east wall, cover varies from 55mm to 71mm, on the west wall the cover varies from 55mm to 70mm, this is as highlighted on the attached as built survey drawing of the B32 couplers for BM296 east and west. For the areas of reinforcement with excessive cover, we propose to use as is providing crack resistance is ok.
| 01CV - Civils | Cxxx-NCR-001256 | NCR | 6.1-Incorrect spacing to lacer bars invert bay 14 |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2013-09-08 | 2013-08-13 10:55 | -26 | 2013-08-09 09:51 | Civil - Tunnelling | 800 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | Invert bay 14 west wall backface reinforcement, it has been observed that the B25 lacer bars of BM330 + BM331 have been installed with incorrect vertical spacing. From the attached photo it can be seen that the c/c spacing between bar nr. 3 and 4 from the underside of the upper wall has been installed and measured at 200mm, the designed spacing is to be 150mm c/c. We propose to close this gap by placing and splicing an additional BM330 and BM331, this will be tied to the vertical B32 bars of BM295 to reduce the risk of concrete cracking in this area.
| 01CV - Civils | Cxxx-NCR-001257 | NCR | 6.1-Exposed u-bars invert bay 18 |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2013-09-08 | 2013-08-15 08:28 | -24 | 2013-08-09 15:18 | Civil - Tunnelling | 1500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | From invert breaking out operations on the West wall for invert bay 18, the reinforcement from the upper wall has become exposed. The locations and extent of the exposed areas are as marked up on attached sketchs/ images. The exposed reinforcement from images are BM01 B12 u-bar on West upper wall. We propose as per NCR's (1234 / 1226 / 1253), to further further break out / scabble back around these exposed areas to a minimum of 30mm. We also propose to place a grout pipe up tight to the exposed reinforcement / or through the exposed bars if required.
| 01CV - Civils | Cxxx-NCR-001258 | NCR | 6.1-Front face concrete damage to upper wall invert bay 18 |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2013-09-11 | 2013-08-15 09:26 | -27 | 2013-08-12 08:19 | Civil - Tunnelling | 1500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | During break out operations of invert and lower walls to invert bay 18, damage has been caused to the front face concrete finish of the upper wall East and West (see attached photos of damage extent). We propose to cut out a section around the damaged area, cutting depth 30mm. Scabble the damaged area back to a minimum depth of 30mm. When pouring lower wall shutter, extend the shutter to include this area. Concrete the lower wall and include the damaged area. Once complete, concrete finish to be inspected and made good if further required. Similar NCRs are (NCR1251/1240)
| 01CV - Civils | Cxxx-NCR-001259 | NCR | 6.1-Varying cover to floor slab invert bay 18 |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2013-09-08 | 2013-08-13 10:56 | -26 | 2013-08-09 16:24 | Civil - Tunnelling | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | From the attached as built survey drawing of invert bay 18 floor slab, when invert bay 18 is constructed there will be excessive cover from the top bar reinforcement (bar mark 314 and 315) to top of invert slab, this is due to couplers for bar mark 323 being cast in existing invert 17, IJ6, with additional cover as indicated. Please see on attached as-built survey the highlighted areas that are out of the reinforcement cover tolerance, the target cover is 55mm with a tolerance of +6mm, -0mm. We propose to leave as is, although for the next invert reinforcement setting out, we will install a grout check along the bay and this will ensure that the couplers will be placed as per design and will reduce any follow on issues to next bay pours.
| 01CV - Civils | Cxxx-NCR-001260 | NCR | 6.1 - invert bay 14 slab insufficient cover |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2013-09-27 | 2013-09-20 13:41 | -7 | 2013-08-09 17:40 | Civil - Tunnelling | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | The 1st, 2nd and 3rd BM327 and BM328bars from invert slab 15 to invert 13 in invert slab 14 have 50mm cover as opposed the the requirement of 55mm cover. See attached sketch for location.
| 01CV - Civils | Cxxx-NCR-001261 | NCR | 6.1-Inadequate cover to front face couplers, invert bay 14 lower wall |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2013-11-20 | 2013-11-22 15:25 | 2 | 2013-08-09 18:47 | Civil - Tunnelling | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | This is a reference to NCR 1255- excessive cover to front face couplers invert bay 14 lower wall. Another reinforcement cover check was carried out on the front face couplers from the upper walls, it was observed the couplers highlighted on the attached as built record have inadequate cover, with the recordings marked up. We propose to leave as is, if required during making the good process a cement coating may be appplied to enhance cover locally.
| 01CV - Civils | Cxxx-NCR-001262 | NCR | 6.1 Stop End Position - Invert Bay 14 East |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2013-09-30 | 2013-08-15 08:29 | -46 | 2013-08-11 18:44 | Civil - Tunnelling | 1500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | Bars in the upper walls cast out of position in Invert Bay 14, East Wall IJ12 Coupler to BM296.
| 01CV - Civils | Cxxx-NCR-001263 | NCR | 6.1 Stop End Position - Invert Bay 18 East and West Walls IJ17 |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2013-09-30 | 2013-08-15 08:32 | -46 | 2013-08-11 18:57 | Civil - Tunnelling | 1500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Subcontractor Problems - Insufficient work planning by the subcontractors | Completed |  | Bars in the upper walls cast out of position in Invert Bay 18, East and West walls IJ17 Coupler to BM295 and BM296.
| 01CV - Civils | Cxxx-NCR-001264 | NCR | 6.1-Incorrect cover to couplers from upper wall invert bay 18 |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2013-09-11 | 2013-08-15 15:33 | -27 | 2013-08-12 10:18 | Civil - Tunnelling | 1000 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | There is excessive cover to reinforcement from the front face couplers on the west wall invert bay 18. The areas with excessive cover are as highlighted on the attached as built survey of the B32 couplers for BM296 west wall. For the areas of reinforcement with excessive cover, we propose to use as is providing crack resistance is adequate. 12.8.13 - __ have re-surveyed the area with attached results as per attachment (as built upper wall couplers invert bay 18). East wall results indicate bar nr. 7 having inadequate cover, the remaining bars in this wall have cover within tolerance. West wall results have areas as highlighted with excessive cover. For the area with low cover we propose to leave as is, a cementious coating could be applied around this localised area to give correct cover. For the areas of excessive cover we propose to leave as is, providing crack resistance is adequate.
| 01CV - Civils | Cxxx-NCR-001265 | NCR | Parapet Wall Portal - Corbel Detail |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2014-03-07 | 2014-02-25 16:40 | -10 | 2013-08-12 10:00 | Civil - Civil Engineering General | 1500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Conflicting information on drawings | Completed |  | As Cxxx-EWN-00646 details there is an ambiguity between drawing Cxxx-OVE-S-DDB-CR001_Z-60002 (C03) and Cxxx-OVE-S-DDB-CR001_Z-60003 (C01). Wall H of the parapet wall has been poured without the corbel as detailed in the attached document.
| 01CV - Civils | Cxxx-NCR-001266 | NCR | 6.1-Incorrect spacing to lacer bars invert bay 18 |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2013-09-11 | 2013-08-15 09:27 | -27 | 2013-08-12 12:19 | Civil - Tunnelling | 800 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | Invert bay 18, it has been observed that the B25 lacer bars on the East and West wall front face BM324 have been installed with incorrect vertical spacing. On the East wall, between BM324 nr. 7 and 8 from top of floor slab level, c/c spacing has been measured at 210mm , on the west wall, between BM324 nr. 4 and 5 from top of floor slab level, c/c spacing has been measured at 205mm. The designed spacing is 150mm c/c. We propose to close this gap by placing an additional B25 bar in the area with inadequate spacing; this will be tied to the vertical B32 bars of BM296.
| 01CV - Civils | Cxxx-NCR-001267 | NCR | 6.1-Incorrect cover to invert bay 18 East Wall |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2013-09-11 | 2013-08-15 08:30 | -27 | 2013-08-12 14:58 | Civil - Tunnelling | 800 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | Invert bay 18 east lower wall, it has been observed that there is inadequate cover from BM296 to the kicker shutter, the area as detailed on attached sketch / image. We propose to continue with pour on the floor slab, once complete break out the front face of the kicker in this area and scabble back approximately 15mm as a minimum. When setting up lower wall shutter, we propose to offset shutter at the base 15mm to achieve 55mm cover to this area. Once pour is complete the joints will be sanded back and made good with __ FC. (13.8.13) Revised remedial action - The kicker shutter was adjusted for the slab concrete pour on the 12.8.13, this was offset to allow concrete spacers to be placed between kicker shutter and reinforcement as detailed (see attached conc spacer image 1,2 and 3). Proposed further remedial action will be, leave the slab / kicker pour as is rather than breaking out or scabbling, construct the lower wall shutter from offset kicker level to upper wall pour. Once pour is complete the joints will be sanded back and made good with __ FC.
| 01CV - Civils | Cxxx-NCR-001269 | NCR | 6.1-Incorrect cover to couplers from upper walls invert bay 10 |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2013-09-14 | 2013-08-20 09:03 | -25 | 2013-08-15 14:15 | Civil - Tunnelling | 1000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | There is varying cover to reinforcement from the front face couplers on the east and west wall invert bay 10. The areas of cover out of tolerance are as highlighted on the attached as built survey of the B40 couplers for BM33 on the East wall and BM350 on west wall. For the areas of reinforcement with excessive cover, we propose to use as is providing crack resistance is adequate. For the areas of low cover on the East wall we propose to offset shutter to give adequate cover to reinforcement.
| 01CV - Civils | Cxxx-NCR-001270 | NCR | 6.1-Front face concrete damage upper walls invert bay 10 |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2013-09-15 | 2013-08-20 08:51 | -26 | 2013-08-16 08:35 | Civil - Tunnelling | 1500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | During break out operations of invert and lower walls to invert bay 10, damage has been caused to the front face concrete finish of the upper wall East and West (see attached photos of damage extent). We propose to cut out a section around the damaged area, cutting depth 30mm. Scabble the damaged area back to a minimum depth of 30mm. When pouring lower wall shutter, extend the shutter to include this area. Concrete the lower wall and include the damaged area. Once complete, concrete finish to be inspected and made good if further required. Similar NCRs are (NCR 1258, 1251/1240)
| 01CV - Civils | Cxxx-NCR-001271 | NCR | 6.1-Stop end position invert bay 10 |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2013-09-14 | 2013-08-20 09:05 | -25 | 2013-08-15 15:51 | Civil - Tunnelling | 1500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Subcontractor Problems - Insufficient work planning by the subcontractors | Completed |  | Reinforcement positioning from the upper wall pour clashes with stop end positions at invert joint 8 for invert bay 10. See attached photos, it can be seen that the stop end has been constructed through 1nr. B40 coupler on the East wall to BM350 on the front face and on the west been positioned within 30mm to B25 coupler on the front face to BM37 and to B40 coupler to BM32 on the back face. We propose to "box out" around and directly below the affected couplers, to full length of the stop end with 6"x3" timbers, with the box out on the front face to sit flush with final position of front face concrete pour.
| 01CV - Civils | Cxxx-NCR-001272 | NCR | 6.1-Waterbar kick out into invert bay 10 lower wall |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2013-09-13 | 2013-09-09 11:38 | -4 | 2013-08-14 09:20 | Civil - Tunnelling | 1000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | It can be seen from attached image that the __ Water bar on the east wall of the wall construction joint between bay 4 and invert 10 has been installed where the lower section of water bar protrudes into invert bay 10, with the water bar also not installed flush vertically. We propose to remove a small section of concrete from the rear of the water bar, by hand breaking along the lower side only to the full length of protrusion. We then propose to re-install and fix the water bar on the lower edge, this will allow it to be positioned vertically and give more cover between the water bar and the back face couplers.
| 01CV - Civils | Cxxx-NCR-001273 | NCR | 6.1 Inaccurate Coupler Level Surveys |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2013-10-03 | 2013-10-01 15:03 | -2 | 2013-08-14 09:20 | Civil - Tunnelling | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Personnel Error - Other human error | Completed |  | Inaccurate measurements have been taken of coupler levels in Bays 14 and 18. This has led to additional NCRs being raised (see 1260, 1261 and 1264).
| 01CV - Civils | Cxxx-NCR-001274 | NCR | 150mm Steel Ducting |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2013-10-14 | 2013-09-18 09:20 | -26 | 2013-08-15 18:53 | Civil - Civil Engineering General | 3000 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | The steel ducting installed between CMC 433 & 434 as per PMI 257 and further RFI 805 has not been certified under the relevant standard BS EN 12055 (or BS 1387) defined in RFI 805. The ducts installed are certified to an American Standard ATSM A106. Please note that his does not mean that the ducts installed do not meet the required standard. Please refer to MCR referenced below.
| 01CV - Civils | Cxxx-NCR-001275 | NCR | 6.1-Damaged couplers on invert bay 10 |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2013-09-15 | 2013-09-03 16:46 | -12 | 2013-08-16 15:07 | Civil - Tunnelling | 1000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | Invert bay 10, west wall B25 coupler at front face, nr. 2 from IJ08 has been observed to be damaged, this is preventing BM37 to couple onto this.
| 01CV - Civils | Cxxx-NCR-001276 | NCR | 6.1-Incorrect cover to couplers on floor slab invert bay 10 |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2013-09-15 | 2013-08-19 12:22 | -27 | 2013-08-16 09:29 | Civil - Tunnelling | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | From the attached as built survey drawing of invert bay 10 floor slab, when invert bay 10 is constructed there will be excessive cover from the top bar reinforcement (bar mark 239 and 240) to top of invert slab, this is due to couplers for bar mark 352 being cast in existing invert 11, IJ9, with additional cover as indicated. Please see on attached as-built survey the highlighted areas that are out of the reinforcement cover tolerance, the target cover is 55mm with a tolerance of +6mm, -0mm. We propose to leave as is, although for the next invert reinforcement setting out, we will install a grout check along the bay and this will ensure that the couplers will be placed as per design and will reduce any follow on issues to next bay pours.
| 01CV - Civils | Cxxx-NCR-001278 | NCR | 6.1-Drilling into permanent works invert bay 16 |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2013-09-18 | 2013-09-23 11:10 | 5 | 2013-08-19 17:28 | Civil - Tunnelling | 1000 |  | Supervision/Management | Repair | 4 (0.5-3k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | From observation to invert bay 16 west lower wall, it can be seen that holes have been drilled into the permanent concrete finish (see attached image of damage extent and approximate location on the west wall). We propose to clean out the holes in the concrete and make good as per Cxxx-VIN-C-GMS-CR146_ST003-50125, we will fill holes and make the surface area good with a smooth finish. 20.8.13 - The depth of the holes range approximately from 65mm to 150mm. There appears to be no damage to rebar, see attached photo attachment (NCR 1278 edit pic) this shows the inside of one of the holes. The holes are observed to not be filled with epoxy resin, or have a plastic sheath placed inside. Similar holes have not been observed on the opposing wall.
| 01CV - Civils | Cxxx-NCR-001279 | NCR | 7.1 M&E Building - Pile cap over breaking |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2013-11-14 | 2013-11-11 08:56 | -3 | 2013-08-23 14:01 | Civil - Civil Engineering General | 2000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During breaking down of piles to cut-off levels some overbreaking occured to the sides of the piles. This was caused using hand breakers. The piles with the most damage are 12, 19 and 21. I have attached photos of each one.
| 01CV - Civils | Cxxx-NCR-001280 | NCR | 6.1-Varying cover to front face couplers from upper wall invert bay 13 |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2013-09-23 | 2013-08-28 14:50 | -26 | 2013-08-24 09:49 | Civil - Tunnelling | 1500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | From the attached as-built coupler surveys on the front face of invert bay 13 for the B32 couplers, the highlighted areas indicate the couplers that are placed out of position / tolerance.
| 01CV - Civils | Cxxx-NCR-001281 | NCR | 6.1-Stop end position invert bay 13 |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2013-09-23 | 2013-09-10 11:28 | -13 | 2013-08-24 10:49 | Civil - Tunnelling | 1500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Subcontractor Problems - Insufficient work planning by the subcontractors | Completed |  | The stop end position on the east and West wall with IJ11 with invert bay 12 clashes with the couplers as placed from the upper wall pours. This is a detailed on the attached images.
| 01CV - Civils | Cxxx-NCR-001282 | NCR | 6.1-Varying cover to cast in slab couplers invert bay 13 |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2013-09-23 | 2013-08-28 14:52 | -26 | 2013-08-24 09:59 | Civil - Tunnelling | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | From the attached as built survey the highlighted areas indicate the cast in couplers on the floor slab that are out of cover tolerance. These areas all have excessive cover.
| 01CV - Civils | Cxxx-NCR-001283 | NCR | 6.1-Front face concrete damage invert bay 13 |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2013-09-23 | 2013-09-10 11:35 | -13 | 2013-08-24 09:41 | Civil - Tunnelling | 1000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | During break out operations of invert and lower walls to invert bay 13, damage has been caused to the front face concrete finish of the upper wall East and West (see attached photos of damage extent). We propose to cut out a section around the damaged area, cutting depth 30mm. Scabble the damaged area back to a minimum depth of 30mm. When pouring lower wall shutter, extend the shutter to include this area. Concrete the lower wall and include the damaged area. Once complete, concrete finish to be inspected and made good if further required. Similar NCRs are (NCR 1258, 1251,1240,1270)
| 01CV - Civils | Cxxx-NCR-001284 | NCR | Invert 19 reinforcement cover |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2013-09-23 | 2013-08-28 14:54 | -26 | 2013-08-24 15:05 | Civil - Civil Engineering General | 1000 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | Please find cover survey of the couplers to invert 19. KF10 Concrete Specification details cover to be 55mm +6, -0. There are a number of bars which are out of tolerance Please confirm this is acceptable to concrete
| 01CV - Civils | Cxxx-NCR-001285 | NCR | Parapet Wall - Concrete low at end of pour |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2013-09-24 | 2013-09-23 14:53 | -1 | 2013-08-27 16:26 | Civil - Civil Engineering General | 1500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Supervision - Insufficient supervision | Completed |  | Following the concrete pour on 23/08/13 of Parapet Wall B CH 18573 – 18561 it has been observed that the very end of the pour has been left low. The attached survey identifies that the end point is 20mm lower than the design level and there is a visible fall down to this point which covers a distance of 400mm; from which all previous levels are correct.
| 01CV - Civils | Cxxx-NCR-001286 | NCR | 6.1-Front face concrete damage to upper wall invert bay 19 |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2013-09-26 | 2013-09-10 11:29 | -16 | 2013-08-27 17:10 | Civil - Tunnelling | 1500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | During break out operations of invert and lower walls to invert bay 19, damage has been caused to the front face concrete finish of the upper wall East and West (see attached photos of damage extent). We propose to cut out a section around the damaged area, cutting depth 30mm. Scabble the damaged area back to a minimum depth of 30mm. When pouring lower wall shutter, extend the shutter to include this area. Concrete the lower wall and include the damaged area. Once complete, concrete finish to be inspected and made good if further required. Similar recent NCRs are (NCR 1270/1283)
| 01CV - Civils | Cxxx-NCR-001288 | NCR | Invert 19 B25 coupler damage West wall |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2013-09-27 | 2013-09-10 11:33 | -17 | 2013-08-28 13:59 | Civil - Civil Engineering General | 1500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | While breaking out the couplers (by hand) in Invert 19 West wall, 2 no B25 couplers were damaged as shown on the attached photos. As previously agreed in NCR 1275 We propose to drill 400mm deep into the upper wall and resin additional bar adjacent to the damaged coupler
| 01CV - Civils | Cxxx-NCR-001289 | NCR | Use of unapproved material |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2014-01-31 | 2014-01-24 16:59 | -7 | 2013-08-28 16:02 | Civil - Civil Engineering General | 2500 |  | Planning | Repair | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | A product (__) was used without an approved MCR. This product was used to repair the galvanising of the threaded bars as detailed on NCR 1053.
| 01CV - Civils | Cxxx-NCR-001290 | NCR | 6.1-Damaged waterbar invert bay 9 |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2013-10-01 | 2013-09-10 11:37 | -21 | 2013-09-01 09:48 | Civil - Tunnelling | 2500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | The previously installed serviseal waterbar has been damage in the locations as detailed on attached sketch, with attached images indicating extent of damage. We propose as per NCR962 and NCR1231 to repair the waterbar via placement of a thin metal plate above and below + 50mm overlap in all directions where possible with the damaged area and plate sealed using Bituthene LM. (see attached sketches for further explanation) . __ construction have been contacted regarding the damage and been asked to advise on the most appropriate method of repair.
| 01CV - Civils | Cxxx-NCR-001292 | NCR | 6.1-Front face concrete damage to upper wall invert bay 9 |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2013-10-01 | 2013-09-10 11:38 | -21 | 2013-09-01 12:46 | Civil - Tunnelling | 1500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | During break out operations of invert and lower walls to invert bay 9, damage has been caused to the front face concrete finish of the upper wall East (see attached photos of damage extent). We propose to cut out a section around the damaged area, cutting depth 30mm. Scabble the damaged area back to a minimum depth of 30mm. When pouring lower wall shutter, extend the shutter to include this area. Concrete the lower wall and include the damaged area. Once complete, concrete finish to be inspected and made good if further required. Similar recent NCRs are (NCR 1283/1286)
| 01CV - Civils | Cxxx-NCR-001294 | NCR | 6.1-Excessive cover to front face couplers from upper walls invert bay 9 |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2013-10-04 | 2013-09-09 12:46 | -25 | 2013-09-04 15:40 | Civil - Tunnelling | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | From the attached as-built coupler surveys on the front face of invert bay 9 for the B32 coupler from upper walls, the highlighted areas indicate the couplers that are placed out of position / tolerance.
| 01CV - Civils | Cxxx-NCR-001295 | NCR | 6.1-Excessive cover to reinforcement on floor slab invert bay 9 |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2013-10-05 | 2013-09-12 09:21 | -23 | 2013-09-05 11:47 | Civil - Tunnelling | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | From the attached as built survey drawings of IJ08 / WJ03, the highlighted areas indicate the cast in couplers on the floor slab that are out of cover tolerance. These areas all have excessive cover. Similar recent NCR is 1276.
| 01CV - Civils | Cxxx-NCR-001296 | NCR | 6.1-Damaged B25 couplers at front face invert bay 9 |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2013-10-04 | 2013-09-10 11:38 | -24 | 2013-09-04 14:33 | Civil - Tunnelling | 1000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | Invert bay 9, east wall B25 coupler at front face, nr. 5 from IJ08 has been observed to be damaged, West wall B25 coupler at front face, nr. 4 from IJ08has also been observed to be damaged. This is preventing BM37 to couple onto this.
| 01CV - Civils | Cxxx-NCR-001297 | NCR | Invert 9 West wall IJ-08 anchor barsCentral tunnel invert 9 |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2013-10-05 | 2013-10-01 15:07 | -4 | 2013-09-05 18:20 | Civil - Civil Engineering General | 1000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Subcontractor Problems - Insufficient work planning by the subcontractors | Completed |  | Invert 9 Lower West wall IJ-08 has differences in bar size couplers to the bay adjacent. This is due to a higher shear key step in the lower walls in bay 4, and that the lower walls are Type 3 reinforcement compared to the upper walls which are type 1. Please see attached proposal to use the B32 couplers which will splice into the B25 laser bars (BM340) with a 1300mm splice as highlighted in pink We propose to Drill a 32mm dia hole 400mm deep and resin as previously agreed in Cxxx –FCD – 001205 We also propose to use the B25 which is out of position highlighted in yellow and splice it with a B25 1300mm splice which is on the other side of the vertical B24 (BM 37) as shown on the attachment. With this in place invert 9 will have the correct numbers Please confirm this is acceptable
| 01CV - Civils | Cxxx-NCR-001298 | NCR | 6.1 Invert Bay 12 - Damaged waterbar |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2013-09-23 | 2013-09-17 16:53 | -6 | 2013-09-09 12:34 | Civil - Tunnelling | 1000 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The waterbar between the upper and lower walls in Invert Bay 12 West wall was found to kick out at the bottom and reduce the cover to the far face wall reinforcement (BM295) to 20mm minimum. The kick out is due to the concrete and steel arch rings behind the waterbar. We propose to break out the remaining concrete further and burn the steel arch rings further to give the correct 55mm cover between the waterbar and far face reinforcement.
| 01CV - Civils | Cxxx-NCR-001299 | NCR | Invert 12 West Upper wall waterbar heat damage |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2013-10-10 | 2013-09-18 08:43 | -22 | 2013-09-10 11:43 | Civil - Civil Engineering General | 1000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | Please see attached photos of the Serviseal in Invert 12 West Upper wall construction joint. Photo 1 shows slight heating to the back of the serviseal in the upper wall CJ, There is no sign of damage to the front face. As discussed with __ from __ water proofing and __ the back will be coated with __ Bituthene LM to guarantee that there is no water path through the serviseal. Please see email from __ confirming the site visit and that the repair is acceptable Photo 2 show heat damage to the edge of the Serviseal, this has not damaged to 1st rib so as a belt and braces measure this also has been coated with Bithuthene LM. Please confirm this is acceptable
| 01CV - Civils | Cxxx-NCR-001300 | NCR | Invert 12 Upper wall concrete damage |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2013-10-10 | 2013-09-18 08:43 | -22 | 2013-09-10 12:20 | Civil - Civil Engineering General | 1000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | While breaking out the lower wall to invert 12, there are areas of damage to the permanent upper walls as shown on the attached photos. As previously agreed in NCR 1240, __ propose to cut around the damaged area and break out 30mm deep recess, so that the damaged area will be concreted with the lower wall pours. Please confirm this is acceptable
| 01CV - Civils | Cxxx-NCR-001301 | NCR | Invert 12 cover survey to the couplers |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2013-10-10 | 2013-09-19 16:51 | -21 | 2013-09-10 12:58 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | Please find attached invert 12 couplers survey. The cover is out of tolerance as specified in KF10 insitu Concrete specification __ Propose to use as is Please confirm this is acceptable
| 01CV - Civils | Cxxx-NCR-001302 | NCR | 7.3 Shaft Ringbeam - Cover to ringbeam slab |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2013-09-18 | 2013-09-19 16:51 | 1 | 2013-09-11 16:25 | Civil - Civil Engineering General | 500 |  | System Defect | Use As-Is | 4 (0.5-3k) | Complete | Subcontractor Problems - Other | Completed |  | Cover on the design intent drawing Cxxx-OVE-S-DDL-CR001_1-22165 shows the cover to the bottom of the reinforcement should be 75mm. However on detailed drawing which was submitted it showed 50mm cover. Actual cover of installed reinforcement is 55mm.
| 01CV - Civils | Cxxx-NCR-001303 | NCR | Invert 16 Sump water bar damage |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2013-10-16 | 2013-09-25 09:18 | -21 | 2013-09-11 18:13 | Civil - Civil Engineering General | 1500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | Please see attached photos of invert 16 damaged water bar. While hand breaking invert 16 to construct the sump, the serviseal water bars has been damaged as attached. __ inspector (Steve Tomlinson) came to site on Tuesday 10th September and has confirmed the attached repair. This consists of cutting off the damaged area and installing Serviseal Pile cap profile which has a Bituthene LM backing, metal plate on the front and is bolted back to the concrete to form a gasket to stop the water path behind the water bar as shown attached At the two end of the damage area the Serviseal pile cap profile will be lapped with the existing serviseal by 300mm, which will be plated on both sides and Bituthene LM sandwiched between to make sure a water tight connection. Additional Grout tube to be added above the repair as shown on attached sketch Rev 2 Please confirm this is acceptable
| 01CV - Civils | Cxxx-NCR-001304 | NCR | Invert Bay 12 - Bent Shear Links |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2013-10-12 | 2013-10-08 17:41 | -4 | 2013-09-12 11:46 | Civil - Tunnelling | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Personnel Error - Violation of requirement or procedure | Completed |  | The reinforcement in Invert Bay 12 uses 10mm shear links (BM360) in the slab. Some of the shear links used were found to have a bent lower leg caused by operatives bending the shear link to aid installation. The bent shear links were subsequently replaced during the reinforcement inspection.
| 01CV - Civils | Cxxx-NCR-001305 | NCR | Invert 12 East and West lower wall kicker |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2013-09-30 | 2013-09-25 09:18 | -5 | 2013-09-16 16:42 | Civil - Civil Engineering General | 1500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | Please see attached photos showing the kicker to Invert 12 East and west wall. While striking the kicker the front face was removed, as Discussed with __ and __, the concrete was broken back to the reinforcement so once the lower wall was shuttered the concrete could bond to the slab and kicker. Please confirm this is acceptable
| 01CV - Civils | Cxxx-NCR-001307 | NCR | Missing Concrete Test Cube Results for LOS Monitoring |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2013-10-27 | 2013-10-08 17:48 | -19 | 2013-09-13 16:07 | Civil - Utilities Engineering | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | It has been noted by our sub contractor that a small number of test cube results can not be submitted with the iTP for the Sub Construction Certificate 8.9. Summary of Results Missing: UTM01 - 7 & 14 day results TM01 - 7 & 14 day results TM02 - 7 day results All 28 day results will be submitted with the ITP
| 01CV - Civils | Cxxx-NCR-001309 | NCR | 6.1- Protruding tie bars from soffit bay 11 end elevation |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2013-10-18 | 2013-10-18 16:27 | 0 | 2013-09-18 08:44 | Civil - Tunnelling | 1000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | Protruding tie bars have been observed to protrude on the end elevation of Bay 11, East and West wall as marked up on attached sketch. There appears to be 1 protruding bar on the West wall, also there appears to be 3 nr. protruding tie bars on the east wall.
| 01CV - Civils | Cxxx-NCR-001310 | NCR | 6.1- Temporary works bracket fixings protrude upper wall soffit bay 11 |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2013-12-06 | 2013-10-25 14:55 | -42 | 2013-10-17 13:24 | Civil - Tunnelling | 1000 |  | Planning | Repair | 4 (0.5-3k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | Stainless steel bolts to fix the temporary works brackets to the RC concrete walls have been observed to be permanently cast into the structure, these cannot be removed. The locations of these remaining bolts are as indicated on the attached sketch, being upper/ lower prop nr. 2 west wall, lower prop nr.3 west wall and upper / lower prop east wall.
| 01CV - Civils | Cxxx-NCR-001311 | NCR | 6.1- Temporary works bracket fixings protrude upper wall soffit bay 10 |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2013-10-18 | 2013-10-08 08:16 | -10 | 2013-09-18 10:06 | Civil - Tunnelling | 1000 |  | Planning | Repair | 4 (0.5-3k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | Stainless steel bolts to fix the temporary works brackets to the RC concrete walls have been observed to be permanently cast into the structure, these cannot be removed / unscrewed. The locations of these remaining bolts are as indicated on the attached sketch, being upper prop nr. 6 on the West wall, upper / lower prop nr. 9 on the East wall, upper / lower prop nr. 10 on the West wall.
| 01CV - Civils | Cxxx-NCR-001312 | NCR | 6.1-Exposed aggregate soffit bay 10 |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2013-10-31 | 2013-10-25 16:50 | -6 | 2013-10-01 09:31 | Civil - Tunnelling | 1000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | From post pour inspection it has been observed there is small section of exposed aggregate soffit bay 10 East, between the joint with the upper wall / splay and the soffit as detailed on the attached sketch, also see image DSCN8216 for clarity.
| 01CV - Civils | Cxxx-NCR-001313 | NCR | 6.1- Temporary works bracket fixings protrude upper wall soffit bay 9 |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2013-11-06 | 2013-10-25 16:43 | -12 | 2013-10-07 09:39 | Civil - Tunnelling | 1000 |  | Planning | Repair | 4 (0.5-3k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | Stainless steel bolts to fix the temporary works brackets to the RC concrete walls have been observed to be permanently cast into the structure, these cannot be removed / unscrewed. The locations of these remaining bolts are as indicated on the attached sketch.
| 01CV - Civils | Cxxx-NCR-001314 | NCR | WJ 10 Drip channel |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2013-10-19 | 2013-10-07 09:33 | -12 | 2013-09-19 08:34 | Civil - Civil Engineering General | 1000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | Drawing Cxxx-OVE-C4-DDD-CR001_Z-22722 - C01 shown a 20mm wide drip channel, WJ10 was chased 27mm wide as shown on attachment. As specified in FCD 1212, __ propose to install a 30mm backing rod which is cut down to allow for the 10mm thick mastic and 5mm gap above for the water to track down, as shown on attachment
| 01CV - Civils | Cxxx-NCR-001315 | NCR | 6.1 WJ 9 Drip channel |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2013-11-14 | 2013-10-07 09:34 | -38 | 2013-09-20 16:17 | Civil - Civil Engineering General | 1000 |  | Equipment Breakdown | Repair | 4 (0.5-3k) | Complete | Subcontractor Problems - Insufficient work planning by the subcontractors | Completed |  | Please see attached drawing Cxxx-OVE-C4-DDD-CR001_Z-22722 waterproofing detail. The Drip channel is shown 20mm wide. While chasing WJ9 with the blades set up at 20mm wide the drip channel is cut 24mm wide due to blades rubbing on the sides. __ propose to leave the drip channel 24mm wide but use a 30mm wide backing foam which will be cut down to allow 5mm gap for the water to track along and 10mm of mastic as previously agreed in NCR 1314
| 01CV - Civils | Cxxx-NCR-001316 | NCR | 6.1 Invert 16 sump reinforcement changes |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2013-10-19 | 2013-10-14 16:24 | -5 | 2013-09-19 12:06 | Civil - Civil Engineering General | 1000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | Please see attached changes to the reinforcement in Invert 16 sump due to the 600mm dia pipe being out of position Please confirm this is acceptable
| 01CV - Civils | Cxxx-NCR-001317 | NCR | Bay W7 - __ UTX - South Chamber |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2013-10-25 | 2013-10-24 15:41 | -1 | 2013-09-23 11:00 | Civil - Utilities Engineering | 2500 |  | Material | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | The South chamber of the __ UTX in bay W7 has been delivered to site with the ducts exiting the chamber at high level 280mm lower than the level that they are specified to pass through cores in the DLR wall. Drawing Cxxx-OVE-Cxxx-SITE-SK-00142 Rev 01 (provided under RFI 1066, PMI 497) states that the ducts are to enter the DLR wall with the bottom invert at 101.430, however the actual ivert level is 101.150m. The drawing states the chamber is to be 3000mm max from invert to cover, the chamber delivered to site is 2820mm from invert to cover level.
| 01CV - Civils | Cxxx-NCR-001318 | NCR | 6.1-Bay 8 upper wall East concrete finish (exposed aggregate appearance) |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2013-12-20 | 2013-10-25 16:38 | -56 | 2013-10-21 12:53 | Civil - Tunnelling | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | In the area as indicated on attached sketch with image for clarity (DSCN 9098), during the making good process this area has been rubbed back and left an exposed aggregate appearance to the final finish on the concrete face.
| 01CV - Civils | Cxxx-NCR-001319 | NCR | 6.1-Bay 1-11 - Grout box screw rusting |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2013-12-28 | 2013-11-12 17:06 | -46 | 2013-10-29 09:39 | Civil - Tunnelling | 2000 |  | Supervision/Management | Repair | 4 (0.5-3k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | On the front finish to the concrete suround of the __ __ grout boxes, there has been observed an area of rusting which is consistent throughout Bays 1-11. See attached image of example area with proposal to rectify.
| 01CV - Civils | Cxxx-NCR-001320 | NCR | 6.1-Poor concrete finsh Soffit Bay 9 Lower Wall |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2013-11-06 | 2013-10-25 14:52 | -12 | 2013-10-07 10:15 | Civil - Tunnelling | 800 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | The concrete finish has been observed to have a poor finish on invert 22 west lower wall (as detailed on attached sketch with images for clarity). This area is approximately 700mm x 700mm square.
| 01CV - Civils | Cxxx-NCR-001321 | NCR | 6.1-Invert 16 slab reinforcement u-bars |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2013-10-24 | 2013-10-16 10:32 | -8 | 2013-09-24 15:57 | Civil - Tunnelling | 1000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | From on site measurements the leg length of bar mark 284 has been measured at 1650. From RC drawing / schedule this should have been 1800.
| 01CV - Civils | Cxxx-NCR-001322 | NCR | 1.5 - West Attenuation Tank Weir Wall reinforcement |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2013-12-05 | 2013-12-02 13:51 | -3 | 2013-09-23 14:39 | Civil - Civil Engineering General | 1500 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | The contractor has observed that 2No extra horizontal reinforcement starter bars have been cast into the perimeter wall of the Attenuation Tank where the wall joins to one of the weir walls. This detail has been mistakenly left on the reinforcement drawing following revision due to changes in the general arrangement of the tank. The result being that the 2No starter bars are above the revised level of the weir wall at that location.
| 01CV - Civils | Cxxx-NCR-001323 | NCR | 6.1-Reinforcement cover to invert bay 16 slab |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2013-10-24 | 2013-10-09 08:30 | -15 | 2013-09-24 15:24 | Civil - Tunnelling | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | The reinforcement cover on invert bay 16 slab has been checked, with recordings as per attached as built cover survey. From the survey it can be seen that the cover ranges from one area of 50mm, to 95mm.
| 01CV - Civils | Cxxx-NCR-001324 | NCR | West Attenuation Tank Weir Wall - Missing reinforcement |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2013-11-09 | 2013-10-29 08:14 | -11 | 2013-09-25 09:20 | Civil - Civil Engineering General | 1500 |  | Design | Repair | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | 4No vertical reinforcing bars have been omitted from the weir walls due to confusion between reinforcement drawings.
| 01CV - Civils | Cxxx-NCR-001325 | NCR | 6.1-Hydrotite fixing / exposured to water invert 16 slab |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2013-10-24 | 2013-10-08 08:17 | -16 | 2013-09-24 18:56 | Civil - Tunnelling | 1000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | From site inspection on 24.9.13 the hydrotite waterbar on invert bay 16 slab, construction joint between invert slab / top slab of sump (as detailed on attached sketch), this was observed to have been exposed to water coming in from top of invert 16 slab. The hydrotite also appeared to strip away from the CJ on the areas as shown on sketch, possibly due to water exposure / poor fixing with sika swell glue. The hydrotite was placed on saturday 21.9.13.
| 01CV - Civils | Cxxx-NCR-001326 | NCR | 6.1-Invert bay 16 sump walls, BM 259 cut |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2013-10-24 | 2013-10-09 09:21 | -15 | 2013-09-24 19:31 | Civil - Tunnelling | 800 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | BM259 on the east and West wall (as detailed on attached sketch), have been observed to be cut before placement on site. This has reduced the lap length with BM 260. The approximate distance between slab and top of a cut BM 259 is 1.060m (worst case scenario).
| 01CV - Civils | Cxxx-NCR-001327 | NCR | 6.1-Invert bay 16 slab, top mat beam bar require modification |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2013-10-25 | 2013-10-09 09:23 | -16 | 2013-09-25 08:37 | Civil - Tunnelling | 1000 |  | Design | Repair | 4 (0.5-3k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | Bar Mark 286 B25 has been detailed 3000mm long, top and bottom mat of invert bay 16 slab. During construction, these bars could not be placed in position due to being too long, this was an oversight from __ not to raise an associated FCD in advance. This would have allowed __ to propose a solution with a remedial agreed for construction to continue on site.
| 01CV - Civils | Cxxx-NCR-001328 | NCR | 6.1-Invert bay 16 slab, spacing between lapped bars |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2013-10-25 | 2013-10-09 09:24 | -16 | 2013-09-25 13:57 | Civil - Tunnelling | 800 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Invert bay 16 slab, BM 284 has been observed on the East wall, nr.9 from IJ15 towards IJ14 as detailed on sketch, to not directly lap with BM278 due to clashing with BM259 and 260 (see attached image for clarity). This has left a gap in excess of 50mm.
| 01CV - Civils | Cxxx-NCR-001329 | NCR | 6.1 WJ 8 Soffit Drainage Channel Dimensions |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2013-11-14 | 2013-10-16 16:17 | -29 | 2013-09-25 08:38 | Civil - Tunnelling | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | Please see attached drawing Cxxx-OVE-C4-DDD-CR001_Z-22722 waterproofing detail. The Drip channel is shown 20mm wide. While chasing WJ8 with the blades set up at 20mm wide the drip channel is cut 24mm wide due to blades rubbing on the sides. __ propose to leave the drip channel 24mm wide but use a 30mm wide backing foam which will be cut down to allow 5mm gap for the water to track along and 10mm of mastic as previously agreed in NCR 1314, 1315 and FCD1219.
| 01CV - Civils | Cxxx-NCR-001330 | NCR | 6.1-Invert bay 16 exposed reinforcement bar |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2013-10-25 | 2013-10-09 09:22 | -16 | 2013-09-25 13:33 | Civil - Tunnelling | 1000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | From hydrodemolition operations of the invert 16 temporary slab for the construction of the sump, reinforcement has been exposed and left an inadequte face on the concrete to pour the sump walls / slab to, this is as detailed on attached sketch on IJ 14 to the East side.
| 01CV - Civils | Cxxx-NCR-001331 | NCR | SFA Pile 345F Out of Position |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2013-11-07 | 2013-10-22 09:25 | -16 | 2013-09-26 09:50 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | The pile reference 345F has been installed at the following coordinates: 345F: (92352.991 ; 34582.645) ; Vector 0.270 The distance from the designed co-ordinate is stated at platform level.
| 01CV - Civils | Cxxx-NCR-001337 | NCR | concrete testing |  | Crossrail | XRL | CON - Connaught Tunnel (East) |  | 2014-01-19 | 2014-01-23 14:42 | 4 | 2013-09-26 14:16 | Civil - Civil Engineering General | 2000 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Concrete cube test does not conform to British Standards. Laborarty tank limits deviates from BS/EN limits.
| 01CV - Civils | Cxxx-NCR-001338 | NCR | 6.1-Invert 16 sump,inlet to 600 concrete pipe pour cast out of tolerance |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2013-12-20 | 2013-11-04 11:48 | -46 | 2013-10-21 13:55 | Civil - Tunnelling | 2000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | It has been observed during inspection of the concrete finish of invert 16 sump area that concrete placed around the inlet to the 600 concrete pipe has been cast out of position, leaving a 950mm x 200mm area with concrete finish out of position / tolerance (see attached image and sketch). This area of concrete protrudes out of position by approximately 75mm.
| 01CV - Civils | Cxxx-NCR-001339 | NCR | 6.1-Protruding bolts Bay 1-8 |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2013-12-21 | 2013-11-06 08:39 | -45 | 2013-10-22 16:09 | Civil - Tunnelling | 3500 |  | Planning | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Other | Completed |  | Stainless steel bolts to fix the temporary works brackets to the RC concrete walls have been observed to be permanently cast into the structure, these cannot be removed / unscrewed. The locations of these remaining bolts are as indicated on the attached sketches of Bays 1 to 8.
| 01CV - Civils | Cxxx-NCR-001340 | NCR | 6.1-Bay 1-8-Protruding tie bars |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2013-12-23 | 2013-11-06 08:42 | -47 | 2013-10-24 13:03 | Civil - Tunnelling | 2500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Formwork tie bars have been observed to be permanently cast into the structure, these cannot be removed. The locations of these remaining tie bars are as indicated on the attached sketches indicating approximate locations.
| 01CV - Civils | Cxxx-NCR-001341 | NCR | 6.1-Concrete face damage from removal of temporary works, Bay 1-8 |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2013-12-22 | 2013-11-12 17:08 | -40 | 2013-10-23 17:16 | Civil - Tunnelling | 4000 |  | Damaged | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Other | Completed |  | The temporary works brackets bolted to the upper walls are as labelled on attached sketch from prop nr. 1 to 57 (upper and lower). During the temporary works removal, it has been observed in the areas as detailed that an area of the permanent concrete face has been removed with the bracket, these areas range in size from small (40mm-75mm), medium (75mm-150mm) and large (150mm+) and are as indicated on the attached sketch, maximum depth not exceeding 40mm. A sketch has been uploaded to detail the upper and lower prop locations affected separately with images to detail typical damage.
| 01CV - Civils | Cxxx-NCR-001342 | NCR | 6.1-Exposed aggregate Bay 1-8 |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2013-12-27 | 2013-11-12 17:05 | -45 | 2013-10-28 10:03 | Civil - Tunnelling | 3500 |  | Workmanship | Repair | 3 (3-6k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | See attached sketches detailing the approximate locations of exposed aggregate encountered from bays 1-8. The affected bays include Bay 1 (IJ01), Bay 4, Bay 5, Bay 6, Bay 7 and invert 16 sump.
| 01CV - Civils | Cxxx-NCR-001344 | NCR | Cores for __ Ducts - West Approach Ramp North Buttress |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2013-11-15 | 2013-10-16 16:19 | -30 | 2013-10-01 13:03 | Civil - Utilities Engineering | 1500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | 1 No. of the 6 No. 178mm ID cores drilled in the North buttress of the West approach ramp for the __ diversion ducts has been cored off line from the direction of the ducts exiting the North __ UTX chamber. 5 No. of the cores drilled are within approximately 50mm of the line of the ducts exiting the North __ UTX chamber, however 1 No. core is approximately 150mm out of line with the duct. See attached sketch showing position of holes relative to each other on each side of the buttress wall.
| 01CV - Civils | Cxxx-NCR-001345 | NCR | 6.1- Bay 11 Exposed aggregate upper wall / splay joint |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2013-11-01 | 2013-10-25 16:54 | -7 | 2013-10-02 10:11 | Civil - Tunnelling | 1000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | From post pour inspection it was observed that on the East wall, joint with upper wall / splay (as detailed on sketch and with image attached), there is an area of exposed aggregate.
| 01CV - Civils | Cxxx-NCR-001350 | NCR | 6.1-Invert 16 sump base slab 28 day cube results |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2014-01-04 | 2013-11-07 13:48 | -58 | 2013-11-05 16:59 | Civil - Tunnelling | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | Specification K10 Insitu Concrete request 2no 28day cubes every 50m3. Due to communication break down between __ and __, the pour listed below does not have the correct number of 28 day cube results. Invert 16 sump base slab (8m3). This was a __ mistake, although the 1nr. 28 day requested cube result is as attached (strength at 28days exceeds minimum strength required at 28 days)
| 01CV - Civils | Cxxx-NCR-001351 | NCR | Rust Staining Surface Rail East & West |  | Crossrail | PDP | CON - Connaught Tunnel (East) |  | 2014-01-31 | 2014-02-03 13:51 | 3 | 2013-10-07 12:13 | Civil - Civil Engineering General | 5500 |  | Material | Use As-Is | 3 (3-6k) | Complete | Discipline/Workmanship - Other | Completed |  | Rust Staining has been observed on the surface rail walls both on the East surface rail and west surface rail. Rust staining is sporadic but consistent accross the walls. See attached photos of a sampling of what is observed.
| 01CV - Civils | Cxxx-NCR-001353 | NCR | 2.4 - E6 wall, damaged from striking shutter |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2014-01-17 | 2013-12-04 09:15 | -44 | 2013-10-10 13:47 | Civil - Civil Engineering General | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | While striking shutter for E6b north wall, top right inside corner was damaged. The shutter was struck from the bottom, causing it to knock the top wall corner. When damaged no reinforcement was showing. No photo was taken before the attempted repair.
| 01CV - Civils | Cxxx-NCR-001354 | NCR | 2.4 - Repairing E6b North wall without inspection |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2013-11-11 | 2013-11-05 11:55 | -6 | 2013-10-10 15:58 | Civil - Civil Engineering General | 500 |  | System Defect | Rework | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | Repairing E6b north wall without an inspection.
| 01CV - Civils | Cxxx-NCR-001355 | NCR | 2.4 - No chamfer on E6 north wall |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2013-11-28 | 2013-11-11 08:22 | -17 | 2013-10-10 16:03 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | No vertical chamfer on E6b north wall, inside face, Ch. 87961. The NCR is on the section of bay 6 north wall that increases in thickness, near the start of bay 5. Please refer to pictures provided.
| 01CV - Civils | Cxxx-NCR-001356 | NCR | 1.4 - Vehicle struck W6 north wall |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2014-02-20 | 2014-02-26 08:17 | 6 | 2013-10-10 16:11 | Civil - Civil Engineering General | 1000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | Vehicle on site to collect tracked excavator from West compound, struck W6 north wall while exiting the compound. Please refer to attached photo for extent of the damage. Repair using Weber Five Star Repair Concrete CP The perimeter of the prepared area shall be well defined by a saw cut. All concrete shall be removed to give a minimum clear dimension of 20 mm to all exposed rebar reinforcement. No priming of the reinforcement is required, Five Star repair concrete CP forms a good cementitious bond to clean exposed reinforcement. Grout-tight formwork is essential. Use a light, uniform application of release agent and good quality sealed ply formwork. The parent concrete shall be thoroughly saturated with potable water prior to the application of the repair concrete. For optimum flow use 3.7 litres of water. Mix for 3 minutes. Winter working Five Star repair concrete CP can be used down to 5°C provided cold weather working precautions are carried out. At low temperatures the strength development of repair concrete is greatly reduced with strengths similar to that expressed by the Sadgrove method. Striking times of formwork will be effected. The concrete shall be cured with wet hessian, polythene or frost blankets for at least 48 hours to prevent rapid loss of water. The formwork shall not be removed until the repair can support the dead and imposed loads, normally 48 hours at temperatures above 15°C and 72 hours at lower temperatures
| 01CV - Civils | Cxxx-NCR-001358 | NCR | 6.1 28day cube results in the tunnel |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2013-12-16 | 2013-10-25 23:51 | -52 | 2013-10-17 14:11 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | Specification K10 Insitu Concrete request 2no 28day cubes every 50m3. Due to communication break down between __ and __, the pours listed below do not have the correct number of 28 day cube results. Bay 1-3 East splay (80m3) 3no 28 day results because __ used the 28day result instead of the 56 day result for an extra 7 day result ( As shown attached). Bay 4-5 East splay (80m3) 3 No. 28 day results because __ used the 28day result for a 4 day result instead of the 56 day result ( as shown attached) Invert bay 2 & 5 lower walls (36m3) 1no 28 day cube result because __ used the 28 day result for an extra 6 day result ( as shown attached) Bay 6 soffit and splay- The structure measures 90m3 so only 4 no 28day results have been allowed for, but with the extra concrete used to fill the void along the structure against the brick work, the total pour was 140m3. (All result attached) Bay 7 soffit and splay- The structure measures 90m3 so only 4 no 28day results have been allowed for, but with the extra concrete used to fill the void along the structure against the brick work, the total pour was 140m3. (All result attached) Bay 10 & 11 (96m3) 2no 28day results because __ used the miss 2 cubs for early strength ( results attached) Invert 12 lower walls (20m3)- 1no 28 day result, __ mistake, 32 day result was the closest result once the mistake was identified. All the results have gained the required 40N/mm2 earlier than 28 days and all pours have results after 28 days.
| 01CV - Civils | Cxxx-NCR-001359 | NCR | 5.4 - Improper storage of __ TS Grout |  | Crossrail | XRL | CON - Connaught Tunnel (East) |  | 2013-11-06 | 2013-11-07 10:02 | 1 | 2013-10-23 09:23 | Civil - Civil Engineering General | 1000 |  | Material | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Improper storage of material | Completed |  | As observed at insepction IRF#3330 it was observed that the __ TS grout was being stored in wet conditions in the tunnel - which in turn resulted in the hardening of the grout inside the bags. This is a failure to comply with the manufacturer's instructions for the storage of these materials. IRF #3330 was failed by PM and Contractor's independent insepctor due to this hardening
| 01CV - Civils | Cxxx-NCR-001360 | NCR | Head house shaft connection between exting brick and new segments |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2014-03-31 | 2014-03-18 11:55 | -13 | 2013-10-23 13:29 | Civil - Civil Engineering General | 2000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Please see attached drawing Cxxx-OVE-C4-DDD-CR001_Z-23206 C01 Pump house construction details. Detail 1 shows the connection detail between the existing brick work shaft and the new concrete segments. Due to the brick work over break, the dry packing has been installed at an angle as shown in the attached photos and diagram. To make the tunnel look uniform __ propose install B12 anchors at 450mm centres with a laser and shutter and grout the connection. Please note where the brick work is removed at a high level as shown on photo 2, the shutter will require extending up to cover this area. Please confirm this is acceptable
| 01CV - Civils | Cxxx-NCR-001361 | NCR | 2.2 CMC Rows 339-361 – Mechanical damage |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2014-01-17 | 2014-01-15 16:35 | -2 | 2013-11-11 08:35 | Civil - Civil Engineering General | 3000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Mechanical damage (applicable to 339F / 340A / 342B / 344A / 357D / 359A / 360A,D,E / 361D) Trimming levels are as per the attached spreadsheet.
| 01CV - Civils | Cxxx-NCR-001362 | NCR | 2.2 CMC Rows 339-361- out of position |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2013-12-23 | 2013-11-28 17:36 | -25 | 2013-11-11 08:34 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Out of Position (Applicable to 339E / 340B, E / 342D, E / 345F / 346B, C /356F / 357C / 358D / 361B, E) The columns have been installed at per the attached spreadsheet. The distance from the designed co-ordinate is stated.
| 01CV - Civils | Cxxx-NCR-001363 | NCR | 2.2 CMC rows 339–361 - multiple issues |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2014-01-17 | 2014-01-15 16:36 | -2 | 2013-11-11 08:36 | Civil - Civil Engineering General | 3000 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Mechanical damage (Applicable to 339A / 357F / 361C, F) Trimming levels are as per the attached spreadsheet. Out of Position (Applicable to 339A / 357F / 361C, F) The columns have been installed as per the attached spreadsheet This is distance from the designed co-ordinate is stated.
| 01CV - Civils | Cxxx-NCR-001364 | NCR | 6.1 - Concrete Testing Lab Temperatures |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2013-12-28 | 2013-11-29 15:51 | -29 | 2013-10-29 16:16 | Civil - Tunnelling | 1500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Description of non conformance: Concrete cube testing does not conform with British Standards. Laboratory Air/Tank Temps exceeded BS/EN limits (22 deg C) from 6 July to 11 August. Attached is a list of cube results taken from the tunnel, with * indicating cubes which were affected by these high temperatures. Why this happened: Air temperature reached over 30 Deg C during extreme summer weather. __ are required to record the Minimum and Maximum readings, it’s likely that the Maximum temperature was reached and sustained for as little as just two hours in 24 hours. How we can assure that the results are OK: Attached is a trend analysis of all __ cube results for this year. How we can prevent happening this in the future: This is a common and continuing problem during summer. __ are continuing discussions with UKAS, their QA department and senior Management for the possible implantation of air conditioning. Further details: EN Standard 12390-2 2009 requires deviations from making and curing requirements to be reported and in this respect the laboratory is compliant. It is worth stating that this is an area that is always examined by UKAS during assessment visits and therefore closely monitored.
| 01CV - Civils | Cxxx-NCR-001365 | NCR | 5.4 IR Bay E2 - Width exceeds 2.8m constraint |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2013-12-10 | 2013-11-15 17:54 | -25 | 2013-11-11 09:16 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | The invert replacement bays are required to be a maximum of 2.8m wide as shown on drawing *23205 (referenced). Bay E2 is currently 2.95m wide as broken out with a maximum of 3.2m locally. The designer has confirmed that the temporary works can resist the design loads of a 3.2m bay (attached).
| 01CV - Civils | Cxxx-NCR-001366 | NCR | 5.4 IR Bay E1 - Protection of Formation |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2013-11-25 | 2013-11-22 17:52 | -3 | 2013-11-11 11:46 | Civil - Excavation | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Bay E1 was broken out and excavated to formation approximately 48hrs before blinding. The formation then softened due to water in the excavation causing additional excavation and blinding concrete to be required. Bay E1 has now been blinded. If the formation had been left open to raise/close the NCR it would only have softened further.
| 01CV - Civils | Cxxx-NCR-001367 | NCR | Elasticity and Thermal co-efficient testing of concrete |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2013-12-26 | 2013-12-17 12:36 | -9 | 2013-11-08 16:29 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | KF10.2205 clause g) requires the testing of concrete to check the modulus of elasticity and the co-efficient of thermal expansion for surface rail and tunnel refurbishment works. No testing to check these parameters has been done on the project to date.
| 01CV - Civils | Cxxx-NCR-001368 | NCR | 5.4 IR Bay E2 - Reduced edge distance on anchors |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2013-11-25 | 2013-12-10 11:50 | 15 | 2013-11-11 09:31 | Civil - Civil Engineering General | 3000 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | Bay E2 breakout exceeded 2.8m (NCR 1366) and this caused the edge distance on the vertical support anchors to be reduced. The temporary works design *52601 (referenced) requires 150mm edge distance to the vertical support anchors. The temporary works designer has checked the anchors with the reduced edge distance and confirmed they are acceptable (attached)
| 01CV - Civils | Cxxx-NCR-001369 | NCR | 6.1-Protruding tie bars end elevation Bay 1 (IJ-01) and 11 (IJ-25) |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2014-01-10 | 2013-11-28 11:36 | -43 | 2013-11-11 11:29 | Civil - Tunnelling | 1000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Protruding tie bars have been observed to protrude on the end elevation of Bay 1 and Bay 11 at floor slab level, as marked up on attached sketch. These were observed during breaking out operations of the next section of tunnelling invert replacement. The tie bars located on slab level have inadequate cover, having approximately 40mm cover to top of floor slab.
| 01CV - Civils | Cxxx-NCR-001370 | NCR | 5.4 IR Bay E1 - Level of Blinding |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2013-11-25 | 2013-11-12 17:44 | -13 | 2013-11-11 12:03 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The first blinding pour in bay E1 was between 28mm to 80mm below required level. The blinding was topped up during the final pour to achieve the required blinding level. (Normally blinding would be in 1 pour however due to the formation issues 3 pours were completed)
| 01CV - Civils | Cxxx-NCR-001371 | NCR | 5.4 IR Control of Water in Excavations |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2014-01-17 | 2014-01-13 16:59 | -4 | 2013-11-11 12:24 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | KE10.3217 requires that the contractor takes measures to maintall all excavations as dry as practicable. The pumps setup in invert replacement excavations E1, E2 and E3 have either not been working and/or are not sufficient to maintain a dry excavation. Additionally water has been pumped from one bay to another bay which unneccessarily introduces more water into a bay. Additional pumps and pipe system to transfer the water directly to the main tunnel drainage is being setup.
| 01CV - Civils | Cxxx-NCR-001372 | NCR | 6.1-Protruding tie bars in soffit Bay 11 end elevation |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2014-05-16 | 2014-05-16 14:03 | 0 | 2013-11-15 13:40 | Civil - Tunnelling | 800 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Protruding tie bars have been observed on the soffit of Bay 11 end elevation as detailed on attached sketch, these are additional to NCR's 1309 and 1369. These were not identified on NCR1309 as cast in as there was no access to the area to investigate if bar was cast in or set in freely to hold service cables in place. They were not identified on NCR 1369, as this required closing out to allow invert replacement contractor to proceed and there still remains no access for __ to carry out these repairs until invert contractor completes first section of works and the NCR 1369 required closing out.
| 01CV - Civils | Cxxx-NCR-001373 | NCR | 6.1-Varying cover to couplers on floor slab, invert bay 1 (IJ-01), Invert bay 11 (IJ-25) and trial bay 1 (Invert replacement scheme) |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2014-01-12 | 2013-11-19 11:20 | -54 | 2013-11-13 17:45 | Civil - Tunnelling | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | See attached cover surveys for the invert bay 1 (IJ-01), invert bay 28 (IJ-25) and trial bay 1 west (east side CJ). Highlighted are the areas out of tolerance.
| 01CV - Civils | Cxxx-NCR-001374 | NCR | 5.4 IR Bay W1 - Shear Key Overbroken |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2013-12-20 | 2013-12-11 15:47 | -9 | 2013-11-12 16:36 | Civil - Tunnelling | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Bay W1 East and West wall – Shear key incorrectly broken out. Vertical face of shear key should be 225mm. Measurements after breakout show vertical face to be between 150mm - 190mm.
| 01CV - Civils | Cxxx-NCR-001375 | NCR | 6.1 Bay 6 Mean concrete strength |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2013-12-10 | 2013-12-05 09:05 | -5 | 2013-11-12 16:20 | Civil - Tunnelling | 800 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Specification Cxxx-OVE-Z4-RSP-CR001-00002 Clause 10.2205 C) states that 'The mean strength of a set of two cubes shall be taken as the test result. When the difference between the two cube strengths divided by their mean exceeds 15%, the test result shall be deemed invalid'. For Bay 6 soffit cube results (poured 22/6/13), the variation exceeded 15%. Further analysis indicates that: (1) The average variation in the mix to date is 3%. (2) The average variation in the cubes taken from the previous pour (19/6/13) is 4%, and the following pour (25/6/13) is 2%. (3) The lab technicians did not note any discrepancies on their worksheets on that day. The lab cannot offer any reason for the strength difference between the samples.
| 01CV - Civils | Cxxx-NCR-001376 | NCR | 5.4 IR Bay W1 - Bent bolts/straps |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2014-01-17 | 2014-01-13 17:21 | -4 | 2013-11-14 11:30 | Civil - Tunnelling | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | During breakout of the walls in bay W1, the straps above the excavation and the bolts securing them to the wall have been bent.
| 01CV - Civils | Cxxx-NCR-001377 | NCR | 5.4 IR Trial Bay 1 - Concrete Damage |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2013-12-12 | 2013-12-10 13:49 | -2 | 2013-11-14 17:14 | Civil - Tunnelling | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | During excavation of bay W1, the edge of structural slab level of Trial Bay 1 slab has been damaged at the joint of W1/Trial Bay 1. Refer to Attachment 1 for details of damage, max depth 20mm.
| 01CV - Civils | Cxxx-NCR-001378 | NCR | 5.4 IR Bay E1 - Shear key breaking inside corner |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2014-01-17 | 2014-01-13 16:55 | -4 | 2013-11-14 16:11 | Civil - Tunnelling | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | The inside corner of a 100mm width of shear key in Bay E1 West wall was underbroken, with the vertical face of the shear key measuring 215mm, as opposed to the required 225mm. The remaining shear key areas in Bay E1 are correctly formed.
| 01CV - Civils | Cxxx-NCR-001379 | NCR | 6.1-Bay 1 end elevation, slab+kicker / lower wall concrete finish offset |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2014-05-16 | 2014-05-16 14:13 | 0 | 2013-11-15 10:42 | Civil - Tunnelling | 1000 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Management Problem - Not Defined | Completed |  | From attached image / sketch it can be seen that the CJ between the kicker and lower wall on Bay 1 (IJ01) West wall, end elevation has been offset by approximately 20mm.
| 01CV - Civils | Cxxx-NCR-001380 | NCR | 5.4 IR Bay W3 Props not Parallel to Bay |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2013-12-13 | 2013-11-15 17:56 | -28 | 2013-11-15 09:27 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | The temporary works drawings for the invert replacement shows the temporary works props parallel to the bay being broken out. On bay W3 the excavated bay is not parallel with the props due to the curvature of the tunnel. Bay W2 breakout is suspended until this NCR is resolved. The design has confirmed that the slight offset is acceptable. The additional calcs attached show that the prop load is actually spread more evenly than the standard design case and therefore this loading arrangement is acceptable.
| 01CV - Civils | Cxxx-NCR-001381 | NCR | 2.2 CMC rows 313-338 - cracked heads |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2014-01-26 | 2014-01-15 14:37 | -11 | 2013-11-27 08:26 | Civil - Civil Engineering General | 3500 |  | Workmanship | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Other | Completed |  | The columns references 314D,E / 317F / 320C / 322D,E / 323C / 324C / 325B,F / 327B / 328C,F / 329B,C,D / 330B,C,F / 331B,C,D,E,F / 332B,F the column has achieved the correct diameter and only the head has a smaller diameter.)
| 01CV - Civils | Cxxx-NCR-001382 | NCR | 2.2 CMC rows 313-338 - reduced diameter |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2014-01-26 | 2013-12-03 17:43 | -54 | 2013-11-27 08:28 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Reduced diameter (Applicable to 314C / 315E / 316B,C / 318B) Reduced diameters are as per the attached spreadsheet.
| 01CV - Civils | Cxxx-NCR-001383 | NCR | 2.2 CMC rows 313-338 - Mechanical damage |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2014-01-26 | 2014-01-15 14:38 | -11 | 2013-11-27 08:36 | Civil - Civil Engineering General | 1500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Mechanical damage (applicable to 326A / 334E / 336B / 337B,E / 338A,C,D) Trimming levels are as per the attached spreadsheet.
| 01CV - Civils | Cxxx-NCR-001384 | NCR | 2.2 CMC rows 313-338 - out of position |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2014-01-26 | 2013-12-03 17:45 | -54 | 2013-11-27 08:39 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Out of Position (Applicable to 313A,B / 316E / 324A,B / 325A / 326E,F / 328B / 329A,F / 333C,D,F / 335A / 336A,E) The columns have been installed at per the attached spreadsheet. The distance from the designed co-ordinate is stated.
| 01CV - Civils | Cxxx-NCR-001385 | NCR | 2.2 CMC rows 313-338 - multiple issues |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2014-01-26 | 2014-01-15 14:44 | -11 | 2013-11-27 08:45 | Civil - Civil Engineering General | 4000 |  | Workmanship | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Other | Completed |  | Mechanical damage (Applicable to 317B,C / 318C / 319C / 320F / 321B / 334A,F / 336B,F / 337C) Trimming levels are as per the attached spreadsheet. Out of Position (Applicable to 315C,D,F / 317E / 318D,E / 319C,D,E / 320B,D,E / 321D,F / 322C,F / 323B,E / 324F / 326C / 327E / 328D,E / 329E / 330D,E / 334A,F / 336B,F / 337C) The columns have been installed as per the attached spreadsheet This is distance from the designed co-ordinate is stated. Reduced Diameter (Applicable to 315B,C / 317B,C,E / 318C,D,F / 319B,C,E,F / 320B,F / 321B,F / 322F / 323F / 324D,F / 325C / 326B / 328D,E) Reduced diameters are as per the attached spreadsheet. Cracked Heads (Applicable to 315B,D / 316F / 317E / 318E,F / 319B,D,E,F / 320D,E / 321D,F / 322C,F / 323B,E,F / 324D / 325C / 326B,C / 327E / 328E / 329E / 330D,E) The columns referenced above have a crack in the column head which have resulted in a piece of the concrete breaking away at the head and side of the column. Removing these cracked pieces has created a smaller pile head and also a void to the side of the column. The sizes of the cracked concrete and the diameters of the column heads are shown on the attached spreadsheet. (It should be noted that the column has achieved the correct diameter and only the head has a smaller diameter.)
| 01CV - Civils | Cxxx-NCR-001386 | NCR | 5.4 IR Bay W1 - Missing couplers |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2013-12-20 | 2013-11-22 17:57 | -28 | 2013-11-16 14:17 | Civil - Tunnelling | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | 5no. couplers are missing on Trial Bay 1 West and East walls. See Attachment 1 for details of locations. We propose to drill a 25mm diameter hole 400mm deep at the missing coupler locations. This will allow placement of B20 bars (1200mm minimum bar length) to be cast in with __ HIT-HY 150 resin spliced a minimum of 800mm onto BM8. Please see attached HIT HY-150 technical data sheet, for the hole diameter recommendation and embedded depth.
| 01CV - Civils | Cxxx-NCR-001387 | NCR | 6.1-Excessive cover to couplers trail bay 2 west (west CJ) |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2014-01-19 | 2013-11-21 16:45 | -59 | 2013-11-20 08:15 | Civil - Tunnelling | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | See attached cover survey to couplers on Trial Bay 2 on the west tunnel (West CJ). It can be seen that there is excessive cover to couplers as highlighted.
| 01CV - Civils | Cxxx-NCR-001388 | NCR | 6.1-Bay 1 end elevation damage to concrete face |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2014-02-18 | 2013-11-28 08:27 | -82 | 2013-11-20 08:50 | Civil - Tunnelling | 800 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The lower wall of Bay 1 end face (IJ-01) East and West wall, appears to have concrete damage (in the form of chips no greater than 10mm deep). See attached images with general areas highlighted.
| 01CV - Civils | Cxxx-NCR-001389 | NCR | 5.4 IR Site Adjustment to Bay E1 Shear Links |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2013-12-12 | 2013-11-26 11:37 | -16 | 2013-11-21 10:48 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The shear links within the Invert Replacement bays are meant to have a slight bend on the bottom leg. The operatives on site bent the bottom leg back slightly to return it to a 90degree bend. This was to enable them to fix the steel on site. FCD 1249 has been raised to revised the reinforcement detailing to remove the slightly bend. This work should not have been completed on site without the FCD being agreed.
| 01CV - Civils | Cxxx-NCR-001390 | NCR | 5.4 IR Bay E1 Trimming of Wall U Bars without FCD |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2014-01-08 | 2014-01-07 15:37 | -1 | 2013-11-21 11:04 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The Bay E1 wall U-bars are too long for the available space. Reinforcement drawing *50302 shows the U-bars stopping before the slab T1 steel. On site this was not the case and the site operatives trimmed some of the U-bars to avoid them clashing with the T1 steel. This was not agreed in an FCD before the trimming works were done. FCD 1247 has now been submitted and notes that the 1300mm minimum lap is being maintained to ensure the design is not compromised.
| 01CV - Civils | Cxxx-NCR-001391 | NCR | 5.4 IR E1 Hydrotite incorrectly installed |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2013-12-20 | 2013-12-11 15:47 | -9 | 2013-11-21 13:39 | Civil - Civil Engineering General | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The Hydrotite in bay E1 had come loose along the Bay E1/Central tunnel construction joint. During cleaning of the bay the hydrotite was knocked out of position. New hydrotite was installed on the wall using the agreed method.
| 01CV - Civils | Cxxx-NCR-001392 | NCR | 5.4 IR Bay E3 - Shear Key Incorrectly Broken |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2014-01-04 | 2013-12-03 17:59 | -32 | 2013-11-23 11:34 | Civil - Tunnelling | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Bay E3 West and East wall - shear key incorrectly broken out. East side shear key vertical face should be 225mm tall but measures approx 160mm. See Attachment 1 for details. West side shear key vertical face is not vertical, being approx 235mm deep at top increasing to approx 360mm deep at bottom. The shear key is approx 250mm deep. See Attachment 2 for details
| 01CV - Civils | Cxxx-NCR-001393 | NCR | 5.4 IR Failure to follow ITP for Shear Keys |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2014-01-04 | 2013-12-03 18:03 | -32 | 2013-11-23 12:11 | Civil - Tunnelling | 500 |  | Planning | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | ITP number Cxxx-VIN-C-ITP-CR146_ST003-50086 shows the shear key inspection taking place the stage before or the stage after blinding. The next stage after both of these inspections is reinforcement. Currently, after a bay is blinded, the reinforcement is installed and then the shear key is broken out. This is not following the order of the ITP and is causing much more work to correctly breakout the shear key with the wall reinforcement in place.
| 01CV - Civils | Cxxx-NCR-001394 | NCR | 5.4 IR Bay E2 and W2 - Shear Key Overbroken |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2014-01-06 | 2013-12-10 11:49 | -27 | 2013-11-25 16:04 | Civil - Tunnelling | 1000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Worker not trained for the work being performed | Completed |  | Bay E2 and W2 - shear keys incorrectly broken out. The shear keys achieve the 225mm height, but are not vertical. The shear keys should be 225mm deep. Bay E2: West - 225mm deep at top, 430mm deep at bottom. East - 225mm deep at top, 310mm deep at bottom Bay W2: West - Ok. East - 225mm deep at top, 300mm deep at bottom Refer to Attachment 1, 2 and 3 for details
| 01CV - Civils | Cxxx-NCR-001395 | NCR | 5.4 IR E4 Bay Width Exceeds 2.8m |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2013-12-11 | 2013-12-10 13:47 | -1 | 2013-11-27 13:37 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The excavation for bay E4 has exceeded 2.8m. The bay is 3.1m wide as measured by the furthest North and South points. The average bay width is ~2.95m. We propose using as-is based on the NCR 1365 which confirmed that a 3.2m bay was acceptable for a similar issue of bay E2. Bay breakout is completed (due to the overbreak) except for an small area next to each vertical prop where approximately 100mm of breakout remains. This bay is 2.6m at this location and the additional breakout does cause any constraints to be exceeded.
| 01CV - Civils | Cxxx-NCR-001396 | NCR | 5.4 IR - W1 wall cover |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2014-01-13 | 2014-01-07 08:46 | -6 | 2013-12-02 10:43 | Civil - Tunnelling | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | See attached cover survey to the front face reinforcement on bay W1. It can be seen that there is insufficient cover to some bars along the top of the north wall.
| 01CV - Civils | Cxxx-NCR-001397 | NCR | 5.4 IR - Bay W3 key |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2014-01-13 | 2013-12-10 11:42 | -34 | 2013-12-02 19:27 | Civil - Tunnelling | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Worker not trained for the work being performed | Completed |  | The shear key along the east wall of Bay W3/W6 is incorrectly broken out. The shear key is approximately 170mm minimum deep over a length of 280mm in Bay W3 and a 220mm length in Bay W6. The correct height of the shear key should be 225mm. Refer to attachment 1 for details. Please note that this shear key was broken out prior to the introduction of the shear key template. The west side of Bay W3 and both sides of Bay E4 were broken out afterwards using the template meeting the criteria.
| 01CV - Civils | Cxxx-NCR-001398 | NCR | Missing documentation |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2014-01-31 | 2014-01-16 15:14 | -15 | 2013-12-03 14:10 | Civil - Civil Engineering General | 500 |  | System Defect | Use As-Is | 4 (0.5-3k) | Complete | Personnel Error - Not Defined | Completed |  | Formation level survey documentation for West Surface Rail Bays 1, 2, 4 & 5 were misplaced and lost from __ records.
| 01CV - Civils | Cxxx-NCR-001399 | NCR | Missing documentation |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2014-01-31 | 2014-01-16 12:18 | -15 | 2013-12-03 15:45 | Civil - Civil Engineering General | 500 |  | System Defect | Use As-Is | 4 (0.5-3k) | Complete | Personnel Error - Other human error | Completed |  | Survey documentation for final levels of top of LTP for West Surface Rail Bays 5 & 6 were misplaced and lost from __ records.
| 01CV - Civils | Cxxx-NCR-001400 | NCR | 6.1 - Missing Outside Face Coordinates |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2014-01-29 | 2014-01-17 14:05 | -12 | 2013-12-10 17:21 | Civil - Tunnelling | 500 |  | Planning | Use As-Is | 4 (0.5-3k) | Complete | Personnel Error - Not Defined | Completed |  | We refer you to Drawing Ref: Cxxx-OVE-C4-DDB-CR146_Z-00001 and Cxxx-OVE-C4-DDB-CR146_Z-00010. These drawings give proposed coordinates and levels for the inside face and outside face of the tunnel at each invert and wall joint. A complete set of as built coordinates and levels of the outside face have not been recorded.
| 01CV - Civils | Cxxx-NCR-001401 | NCR | 1.4 - Attenuation Tank Corner Damage |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2014-01-20 | 2013-12-11 15:48 | -40 | 2013-12-06 17:12 | Civil - Civil Engineering General | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Attenuation Tank North-East corner was damaged by a mechanical excavator. Refer to attached photos.
| 01CV - Civils | Cxxx-NCR-001402 | NCR | 5.4 IR Gap at top of walls |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2014-03-31 | 2014-03-10 09:06 | -21 | 2013-12-09 14:56 | Civil - Tunnelling | 1000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Upon striking of the wall shutters in bays E2, E4, W3 it was found that there was a gap between the top of the concrete wall and the brickwork. Refer to Attachment 1 for details. The maximum gap is approximately 20mm. The shear key joint TAM pipes have been grouted and it was noted that there was no water or grout loss through the gap when pumped through at a pressure of 4 bar. We propose to construct a timber 'letterbox' shutter along the top of the wall and fill the gap with Tamcrete MFC (the same product used to grout the shearkey). Refer to Attachment 2 for details.
| 01CV - Civils | Cxxx-NCR-001403 | NCR | Missing documentation |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2014-01-31 | 2014-01-16 15:16 | -15 | 2013-12-10 16:26 | Civil - Civil Engineering General | 500 |  | System Defect | Use As-Is | 4 (0.5-3k) | Complete | Personnel Error - Not Defined | Completed |  | Survey documentation for final levels of top of Engineering Fill for West Surface Rail Bays 1 & 2 were misplaced and lost from __ records.
| 01CV - Civils | Cxxx-NCR-001404 | NCR | 6.1 Excessive cover to couplers Trial Bay 1 (west CJ) |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2014-03-07 | 2014-02-20 08:28 | -15 | 2013-12-18 11:23 | Civil - Tunnelling | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Please see attached the cover survey to couplers on Trial Bay 1 (west CJ). It can be seen that there is excessive cover to couplers as highlighted. Please note that this cover survey is measured to the centre of the 20mm diameter lacer couplers exposed when the CJ is scabbled. The calculated cover to the 40mm diameter T1 reinforcement is based on subtracting the bar diameters away from the measurements. As the T1 reinforcement sits on the lacers, the cover to the T1 reinforcement will be governed by the raised couplers, not the odd dropped coupler.
| 01CV - Civils | Cxxx-NCR-001405 | NCR | 6.1 Central Tunnel Remedials |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2014-07-31 | 2014-07-31 08:16 | 0 | 2013-12-19 11:47 | Civil - Tunnelling | 1500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Remedials to the concrete in the central tunnel have 'popped' out in some areas. See attached photo of Bay 1 West Upper Wall.
| 01CV - Civils | Cxxx-NCR-001406 | NCR | 5.4 - Improper Concrete Placement |  | Crossrail | XRL | CON - Connaught Tunnel (East) |  | 2014-01-30 | 2014-01-17 14:02 | -13 | 2013-12-20 15:12 | Civil - Concrete Pavement | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | Concrete being poured into a single location (i.e. into the corner of a wall) and the poker vibrator being used to shift the concrete, through the vibration action. This is unnecessarily increasing the risk of concrete segregation and is not the correct way to place concrete and This is a failure to comply with BS 8000 2.2 Concrete being poured in the wrong direction relative to the shear links. The links are only tied on the top, and therefore the direction of concrete flow must be pushing the links onto the lacers.
| 01CV - Civils | Cxxx-NCR-001407 | NCR | 5.4 IR Bay E5, W4 - shear key lacers |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2014-01-30 | 2014-01-10 16:53 | -20 | 2014-01-02 12:40 | Civil - Tunnelling | 1500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | When installing the wall reinforcement on bays E5 and W4, there was diffuculty in fitting the BM09 shear key lacers into the couplers in the neighbouring existing bays. This was mainly due to clashing with reinforcement. (For example, FCD1238 allowed the placement of the front L-bars on the B3 layer. The position of the BM09 couplers on the trial bays would clash with the now moved up L-bars.) The other reason seems to be the tight tolerance on the couplers preventing the bars coupling easily and hampered by the main wall reinforcement being installed giving little room to move. We propose to drill a 16mm hole 400mm deep at the shear key lacer locations. This will allow placement of B12 bars (1200mm minimum bar length) to be cast in with __ HIT-HY 150 resin spliced a minimum of 800mm onto BM09. Please see attached HIT HY-150 technical data sheet for the hole recommendation and embedded depths.
| 01CV - Civils | Cxxx-NCR-001408 | NCR | 5.4 IR - E5, E6, W4 wall cover |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2014-02-13 | 2014-01-07 08:54 | -37 | 2014-01-02 17:46 | Civil - Tunnelling | 1000 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | See attached cover surveys to the front face reinforcement on bays E5, E6 and W4. It can be seen that there is insufficient cover to some bars on the North and South walls.
| 01CV - Civils | Cxxx-NCR-001409 | NCR | 5.4 Incorrect Drawing Revisions on SIte |  | Crossrail | PDP | CON - Connaught Tunnel (East) |  | 2014-01-31 | 2014-02-02 15:45 | 2 | 2014-01-03 11:32 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | During random check of drawings on site, it was noted that: 1) Incorrect drawing and revision was available on site (Cxxx-VIN-C-DWG-CR146_ST003-50314 Rev 3.0 was on site where 4.0 is on eB) 2) Drawings had been duly updated with RFI and FCD information (red-line) for appropriate use on site (though the wrong revision)
| 01CV - Civils | Cxxx-NCR-001410 | NCR | 7.1 Support Building Slab Recess - and Finishes |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2014-02-21 | 2014-02-18 12:37 | -3 | 2014-01-03 16:18 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The recesses within the support building all have imperfections, caused by trapped water/air from the conrete pour. Please see photographs attached. They are approximatly upto 5mm deep and vary in size from a few mm's to 30mm. Cover survey attached
| 01CV - Civils | Cxxx-NCR-001411 | NCR | 7.1 Support Building cover issues |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2014-02-22 | 2014-02-10 17:45 | -12 | 2014-01-08 16:10 | Civil - Civil Engineering General | 1000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The cover to the 16mm diameter starter bars for the 700mm upstand on the outside of the Support building slab is currently out of tolerance in a number of locations. Following the post pour inspection of the M&E building slab the cover at slab level of each of the starter bars on the East, South and West sides of the slab have been measured (see attached spreadsheet). This survey shows that the starter bar cover is out of the +6mm/-0mm tolerance specified, with up to +11mm and -10mm deviation from the design cover of 55mm.
| 01CV - Civils | Cxxx-NCR-001412 | NCR | 5.4 IR Bay W5 Shear key overbroken |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2014-02-17 | 2014-01-16 16:40 | -32 | 2014-01-06 17:29 | Civil - Tunnelling | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Bay W5 South wall – Shear key incorrectly broken out. Vertical face of shear key should be 225mm. Measurements after breakout show : 1) an area 650mm width where the vertical face is between 190mm-200mm, and an area of 200mm width where the vertical face is between 135mm-190mm. 2) Another area of 800mm width and 70mm high, 30mm maximum depth has broken away from the front face brickwork.
| 01CV - Civils | Cxxx-NCR-001413 | NCR | 5.4 IR Gap at top of W4 South wall |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2014-02-19 | 2014-01-17 08:22 | -33 | 2014-01-08 15:01 | Civil - Tunnelling | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Upon striking of the wall shutters in bay W4 it was found that there was a gap between the top of the concrete wall and the brickwork. Refer to Attachment 1 for details. The maximum gap is approximately 10mm. The shear key joint TAM pipes have been grouted and it was noted that there was no water or grout loss through the gap when pumped through at a pressure of 4 bar. We propose to construct a timber 'letterbox' shutter along the top of the wall and fill the gap with Tamcrete MFC (the same product used to grout the shearkey). Refer to NCR 1402 for details of proposed remedial.
| 01CV - Civils | Cxxx-NCR-001414 | NCR | 5.4 IR Bay E7 Slab - Low cover |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2014-05-16 | 2014-05-13 16:35 | -3 | 2014-01-09 12:02 | Civil - Tunnelling | 1000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The first approx. 6no BM02 and BM03 bars from bay E3 in bay E7 have varying cover - min. 40mm - as opposed to the required 55 mm cover. See attached survey for details.
| 01CV - Civils | Cxxx-NCR-001415 | NCR | 5.4 IR Bay W6 Shear key overbroken |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2014-02-20 | 2014-02-05 13:36 | -15 | 2014-01-09 19:03 | Civil - Tunnelling | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | During the break out the shear key on bay W6 North wall the bottom of the vertical face fall away from the shear key, potentially due to localised weak brick work. Refer to the Attachment 1 for photos of the affected area and a close up of section of loose brick work before and after it was tapped gently with a hammer. The vertical face of the remaining shear key in the affected area is between 160mm and 200mm, the total depth of the shear key is in excess of required 225mm. Please note that the two brick high area of the shear key from bay W3 has been addressed in completed NCR 1397.
| 01CV - Civils | Cxxx-NCR-001416 | NCR | 7.3 Shaft Baffle - RFI 00494 |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2014-12-28 | 2014-10-16 15:07 | -73 | 2014-01-10 09:38 | Shafts - Shafts General | 1000 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | RFI 494 and the corresponding sketch Cxxx-OVE-Cxxx-SK-0043. 200mm wide expoband H45 expansion joint membrane to be bonded over expansion joint using supastik E10 adhesive. The H45 membrane is peeling off the baffle wall.
| 01CV - Civils | Cxxx-NCR-001417 | NCR | 5.4 IR Prodecural - Poor quality supervision |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2014-02-24 | 2014-02-24 10:14 | 0 | 2014-01-13 10:55 | Civil - Tunnelling | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Subcontractor Problems - Insufficient surveillance of subcontractors | Completed |  | An inspection of the shear key breakout on bays W6 and E8 was booked on 10/01/2014 at 10:30am. Upon arrival it became evident that the shear keys required additional trimming (approximately 10mm in places) to achieve the 225mm required depth. The additional breakout required was carried out after the inspection. This NCR has been raised to highlight the poor quality supervision for the invert replacement works. We propose to hold a briefing session between __ Site engineers and __s Site engineers/supervisors to ensure that quality checks are thoroughly carried out prior to inspections.
| 01CV - Civils | Cxxx-NCR-001418 | NCR | 5.4 IR Exposed reinforcement at CJ E4/E8 |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2014-02-24 | 2014-02-05 13:38 | -19 | 2014-01-13 10:39 | Civil - Tunnelling | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Upon striking the shutter of E4 slab it has been discovered approx. 600mm length of exposed BM01/BM11 spliced bars. 1) We propose to break out a 100mm wide x 30mm deep along the length of exposed bar with the aid of a saw cut and replaced with concrete cast during the remainder of the bay E8 slab concrete pour. Please note that as BM01/BM11 are spliced side by side, we envisage that breaking 30mm around the reinforcement (as per previous similar NCRs) would require extensive break out and not guarantee the fact that the concrete will fill the void. - Please note that the exposed bar was falsely identified as a B40 bar (BM01/BM11). Upon a breaking out it was evident that this exposed reinforcement was in fact a loose B12 bar. As discussed with J.Sammon, this B12 bar was removed and the break out to 30mm depth was completed. 2) For other areas of grout lose near the exposed reinforcement we propose to scabble back to sound concrete.
| 01CV - Civils | Cxxx-NCR-001419 | NCR | 5.4 IR Bay W5 Low cover |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2014-05-09 | 2014-05-06 17:49 | -3 | 2014-01-13 11:37 | Civil - Tunnelling | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The first approx. 5no BM02 and BM03 bars from bay W2 in bay W5 have varying cover - min. 45mm - as opposed to the required 55 mm cover. Refer to attached 'NCR 1419 Cover survey' for details.
| 01CV - Civils | Cxxx-NCR-001420 | NCR | 5.4 IR Bay E8 Shear key overbroken |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2014-02-24 | 2014-01-16 15:32 | -39 | 2014-01-13 11:29 | Civil - Tunnelling | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Bay E8 South wall - shear key incorrectly broken out. The shear keys achieve the 225mm height, but a 400mm wide section is not vertical at the lower layer of bricks. Refer to Attachment 1 for details.
| 01CV - Civils | Cxxx-NCR-001421 | NCR | 5.4 IR Bay E8 Damaged coupler |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2014-02-24 | 2014-02-05 13:39 | -19 | 2014-01-13 15:49 | Civil - Tunnelling | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | 1no. of BM20 coupler was damaged on CJ E4-E8, North wall. Refer to Attachment 1 for detail of location. As per similar NCRs (i.e. NCR1386), we propose to drill a 25mm diameter hole 400mm deep near the damage coupler location. This will allow placement of B20 bars (1200mm minimum bar length) to be cast in with __ HIT-HY 150 resin, spliced a minimum of 800mm onto BM8. Refer to Attachment 1 for reinforcement detail. Please see attached HIT HY-150 technical data sheet, for the hole diameter recommendation and embedded depth.
| 01CV - Civils | Cxxx-NCR-001422 | NCR | 5.4 IR Failure to follow specifications for concrete |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2014-03-31 | 2014-03-27 13:53 | -4 | 2014-01-13 17:18 | Civil - Tunnelling | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | During an inspection in the bay W5 it was noticed poor scabbling in the slab at CJ W2-W5. At this point, the bottom mat and partly the top mat reinforcement had been installed. The operatives were immediately told to stop installing reinforcement and the affected areas were scabbled. The specification 'KF10-Insitu concrete' clause KF10.3207 f) : 'At construction joints, the removal of laitance shall be achieved by the use of air/ water jets while the concrete is still green, the use of sandblasting or mechanically operated tools after the concrete has hardened should be avoided if possible.'
| 01CV - Civils | Cxxx-NCR-001423 | NCR | 7.3 Leaking Joint within Microtunnel |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2014-09-30 | 2014-08-28 11:27 | -33 | 2014-01-17 08:47 | Civil - Drainage | 4000 |  | Workmanship | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Other | Completed |  | Following review of the Microtunnel CCTV survey (from the central box sump to the pump shaft), there is evidence that the 7th joint from the end (approximately 15m from the shaft) is leaking.
| 01CV - Civils | Cxxx-NCR-001424 | NCR | 5.4 IR Gap at top of W6 South wall |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2014-03-03 | 2014-02-24 10:53 | -7 | 2014-01-20 15:25 | Civil - Tunnelling | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Upon striking of the wall shutters in bay W6 it was found that there was a gap between the top of the concrete wall and the brickwork. Refer to Attachment 1 for details. The maximum gap is approximately 10mm. The shear key joint TAM pipes have been grouted and it was noted that there was no water or grout loss through the gap when pumped through at a pressure of 4 bar. We propose to construct a timber 'letterbox' shutter along the top of the wall and fill the gap with Tamcrete MFC (the same product used to grout the shear-key). Refer to NCR 1413 for details of proposed remedial.
| 01CV - Civils | Cxxx-NCR-001425 | NCR | 5.4 IR Bay E21 Shear key overbroken |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2014-03-04 | 2014-02-18 12:39 | -14 | 2014-01-21 11:48 | Civil - Tunnelling | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | 1) During breaking out of the shear-key on Bay E21 South wall the operatives discovered several weak points in brickwork, at the bottom edge of the shear-key. Refer to Attachment 1 (page 1 and 2) for details. As per NCR 1412, operatives stopped the works and informed their supervisor. The loose brickwork has been carefully removed by a chipping hammer. 2) During breaking out shear-key on Bay E21 South wall, the small area of max. depth 10mm has been over broken. Refer to Attachment 1 (Page 3).
| 01CV - Civils | Cxxx-NCR-001426 | NCR | 7.1 Support Building - North End Wall |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2014-02-04 | 2014-02-05 14:43 | 1 | 2014-01-21 12:19 | Civil - Civil Engineering General | 1000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The north east end wall of the support building had not been detailed or constructed as construction drawings Cxxx-OVE-Cxxx-SITE-SK-0180 or Cxxx-OVE-S-DDL-CR001_1-22150 a subsequent RFI 1392 was raised requested further detail for the end of the wall to enable construction.
| 01CV - Civils | Cxxx-NCR-001427 | NCR | 5.4 IR Bay W7 Missing couplers |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2014-03-05 | 2014-02-06 17:35 | -27 | 2014-01-22 11:53 | Civil - Tunnelling | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | 2 no. lacers without a coupler at CJ W4-W7 have been installed into Bay W4 Slab. See Attachment 1 for details of locations. We propose to drill a 25mm diameter hole 400mm deep at the missing coupler locations. This will allow placement of B20 bars (1200mm minimum bar length) to be cast in with __ HIT-HY 150 resin spliced a minimum of 800mm onto BM8. Please see attached HIT HY-150 technical data sheet, for the hole diameter recommendation and embedded depth.
| 01CV - Civils | Cxxx-NCR-001428 | NCR | 7.1 Support Building - Beam 1 starter bars |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2014-02-07 | 2014-02-05 14:45 | -2 | 2014-01-24 16:15 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | 4no started bars for the upstand walls are missing from the ends of beam 1 (as shown on the attached photos). These are required as per the intent drawings at 150mm centres and were in the detailed design drawings Cxxx-VIN-C-DWG-CR146_ST003-50079 and Cxxx-VIN-C-DWG-CR146_ST003-50080. The detailed design drawing were used at the pre-pour inspection.
| 01CV - Civils | Cxxx-NCR-001429 | NCR | 5.4 IR Bay W7 South wall Lacers |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2014-03-10 | 2014-02-19 16:07 | -19 | 2014-01-27 09:18 | Civil - Tunnelling | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The 2no. of top lacers BM10 in the CJ W4-W7 Bay W7 South wall shear-key, are installed too low. Refer to Attachment 1 for details. Please note that the position of these lacers has been correctly installed at CJ W7-W10. We propose to drill 2no. 16mm diameter holes 400mm deep at CJ W4-W7. This will allow placement of additional lacers (2400mm minimum bar length) to be cast in with __ HIT-HY 150 resin. Please see attached HIT HY-150 technical data sheet, for the hole diameter recommendation and embedded depth. Please note that where reinforcement is encountered during drilling of the holes preventing the full depth 400mm, we propose to resin in a short piece of reinforcement to prevent voids in the concrete.
| 01CV - Civils | Cxxx-NCR-001430 | NCR | 5.4 IR Bay E9 Slab - Low cover |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2014-05-09 | 2014-05-08 17:12 | -1 | 2014-01-27 17:26 | Civil - Tunnelling | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The first 2no. BM02 and BM03 bars from bay E5 in bay E9 have varying cover - min. 50mm - as opposed to the required 55 mm cover. Refer to attached 'NCR 1430 Cover survey' for details.
| 01CV - Civils | Cxxx-NCR-001431 | NCR | 5.4 - Improper storage of reinforcement |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2014-03-11 | 2014-02-24 10:58 | -15 | 2014-01-28 11:26 | Civil - Tunnelling | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | It has been observed that the reinforcement in the tunnel is stored improperly. KF. 10.3243 requirements (avoid contamination, steel must be kept clean & free from earth, paints, oil, grease etc, Reinforcement shall not be stacked in positions where water running off will cause staining to any of the permanent works). It has been repeatedly observed that the reinforcement stored in between bays is laid in the mud without any timber packings beneath. We propose to re-stack the reinforcement that is currently incorrectly stored on timber packs, clear of the mud and debris, jet-wash to remove contamination and cover with plastic sheeting.
| 01CV - Civils | Cxxx-NCR-001432 | NCR | 5.4 IR East Additional 26m Wall U-bar Clearance |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2014-02-11 | 2014-02-05 13:23 | -6 | 2014-01-28 14:51 | Civil - Civil Engineering General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The reinforcement for the east invert replacement additional 26m bays E20 to E30 and bay E16 wall U-bars do not fit within the wall pour. The bars cannot be trimmed to fit as the required lap length would not be achieved. The U-bars will instead extend through the top mat of the slab reinforcement. At the point where the wall reinforcement meets the slab reinforcement it will not be possible to achieve the require gap of maximum aggregate size plus 5mm required in EC2.
| 01CV - Civils | Cxxx-NCR-001433 | NCR | 5.4 IR Control of Water in Excavations |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2014-03-11 | 2014-02-25 16:53 | -14 | 2014-01-28 12:02 | Civil - Tunnelling | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | KE10.3217 requires that the contractor takes measures to maintain all excavations as dry as practicable. The pumps setup in invert replacement excavation E21 has been pumping water into invert replacement excavation E22 which unnecessarily introduces more water into a bay. Additional pump and pipe system to transfer the water directly to the main tunnel will be setup.
| 01CV - Civils | Cxxx-NCR-001434 | NCR | 2.4 Rust Staining on surface rail Walls |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2015-03-26 | 2015-02-25 13:46 | -29 | 2014-01-28 11:17 | Civil - Civil Engineering General | 500 |  | Material | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Rust Staining as been observed on the surface of the walls in Surface Rail East as detailed in NCR 1351.
| 01CV - Civils | Cxxx-NCR-001435 | NCR | 1.4, 2.4, 3.3 & 5.5 Rust Staining on F2 Walls |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2015-01-28 | 2014-02-06 17:24 | -356 | 2014-01-28 11:24 | Civil - Civil Engineering General | 3000 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Rust Staining as been observed on the surface of the F2 walls in Surface Rail East & West as detailed in NCR 1351.
| 01CV - Civils | Cxxx-NCR-001436 | NCR | 5.4 IR Bay E9 Wall lacers |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2014-03-19 | 2014-02-18 12:47 | -29 | 2014-02-05 12:22 | Civil - Tunnelling | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Lacers in Bay E9 North and South wall has been installed horizontally when these should follow a gradient of the tunnel. This caused to an increasing gap between top lacer and U-bar reinforcement. Refer to Attachment 1 for details. We propose to drill a 25mm diameter hole 400mm deep into CJ E5-E9. This will allow placement of B20 bars (1200mm minimum bar length) to be cast in with __ HIT-HY 150 resin spliced a minimum of 800mm onto BM8. Please see attached HIT HY-150 technical data sheet, for the hole diameter recommendation and embedded depth.
| 01CV - Civils | Cxxx-NCR-001437 | NCR | 5.4 IR Improper storage of reinforcement |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2014-03-12 | 2014-02-24 11:00 | -16 | 2014-01-29 18:10 | Civil - Tunnelling | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | As per 'NCR 1431 5.4 - Improper storage of reinforcement', it has been observed that the reinforcement in the tunnel is stored improperly. The remedial actions should have been taken within 24 hours, however, these actions have not been taken completely and improperly stored reinforcement has been found in the tunnel. Refer to Attachment 1 for details. We propose to re-stack the reinforcement that is currently incorrectly stored on timber packs, clear of the mud and debris, jet-wash to remove contamination and cover with plastic sheeting.
| 01CV - Civils | Cxxx-NCR-001438 | NCR | 5.4 IR Bay W7 Walls Concrete undercompaction |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2014-04-18 | 2014-04-08 13:17 | -10 | 2014-02-05 12:53 | Civil - Tunnelling | 750 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | During post-pour (pre-repair) inspection it has been noticed that on the walls there are small areas of under-compacted concrete. Refer to Attachment 1 for detail of locations. 1) We propose to mark up a square/rectangular area with duct tape (to protect unaffected areas of walls) scabble back the affected areas to remove any loose/weak material, then make good as per agreed MSRA Cxxx-VIN-C-GMS-CR146_ST003-50236. 2) We propose to use the same remedial action for other concrete undercompaction uncovered in the walls of future bays.
| 01CV - Civils | Cxxx-NCR-001439 | NCR | 5.4 IR Bay W4 Concrete Shrinkage |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2014-04-04 | 2014-04-08 13:18 | 4 | 2014-02-05 16:11 | Civil - Tunnelling | 750 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | During post-pour (pre-repair) inspection a small concrete shrinkage has been noticed on the north wall, right top corner. Refer to Attachment 1 for details. We propose to carefully clear the shrinkage opening of any loose/weak material and install a timber 'letterbox' shutter and fill the shrinkage with Tamcrete MFC (the same product used to grout the shear-key). Then make good as per agreed MSRA Cxxx-VIN-C-GMS-CR146_ST003-50236.
| 01CV - Civils | Cxxx-NCR-001440 | NCR | 5.4 IR Bay W8 Shear-key overbroken |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2014-03-18 | 2014-02-12 17:15 | -34 | 2014-02-04 11:22 | Civil - Tunnelling | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | 1) The back faces of shear-keys in Bay W8 North and South wall have been slightly over-broken. Refer to Attachment 1 for details. We propose to use as is. 2) The grout curtain drill hole at top of the shear-key caused a weak point in brick work on front face of shear-key in North wall and this small part of weak bricks felt out during the breaking-out operation. We propose to saw cut around the damaged area, cutting depth min.100mm. Break back the damaged area to a minimum depth of min.100mm by saw cutting underneath. Pour wall ensuring this area is incorporated. Once complete, concrete finish to be inspected and made good further if required.
| 01CV - Civils | Cxxx-NCR-001441 | NCR | 5.4 IR Bay W9 Damaged couplers |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2014-03-19 | 2014-02-19 16:09 | -28 | 2014-02-05 13:34 | Civil - Tunnelling | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | 5no. of BM20 coupler was damaged on CJ W6-W9, Slab. Refer to Attachment 1 for detail of locations. We propose to drill 25mm diameter holes 400mm deep near the damage coupler locations. This will allow placement of B20 bars (1200mm minimum bar length) to be cast in with __ HIT-HY 150 resin, spliced a minimum of 800mm onto BM2. Refer to Attachment 1 for reinforcement detail. Please see attached HIT HY-150 technical data sheet, for the hole diameter recommendation and embedded depth.
| 01CV - Civils | Cxxx-NCR-001442 | NCR | 7.1 - M&E Building Drainage |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2014-06-30 | 2014-06-25 15:49 | -5 | 2014-02-05 15:23 | Civil - Civil Engineering General | 3000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | Following a post pour inspection of the M&E building slab, review of the full tranche of design drawings and discussions with Cxxx it has become apparent that a 110mm dia. PVC-U drainage pipe c/w air admittance valve was required to be cast into the M&E building slab and this pipe has not been installed. The Support Building - Public Health Service Detail (Ground and Roof Level) drawing Cxxx-OVE-P-DDD-CR001_Z-30255 C01 shows roof drainage, a water main and a foul drainage pipe to be installed from the M&E building in the central compound. Section B shown on drawing Cxxx-OVE-P-DDD-CR001_Z-30200 C01 shows the 110mm dia. PVC-U drainage pipe is to pass through the concrete slab at 600mm depth.
| 01CV - Civils | Cxxx-NCR-001443 | NCR | 6.1- Soffit Drainage drip Channel Defects |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2014-07-31 | 2014-07-31 08:22 | 0 | 2014-02-06 16:21 | Civil - Tunnelling | 5000 |  | Workmanship | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Other | Completed |  | See attached image, it can be observed that the drainage drip channel mastic has fallen out from the channel itself, and has been observed to be affected from possible water ingress from the construction joint.
| 01CV - Civils | Cxxx-NCR-001444 | NCR | 2.4 Bay E13 Holding Down Bolt No.62 Out of Position |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2014-03-14 | 2014-02-20 16:50 | -22 | 2014-02-07 11:34 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Upon completion of the as built survey of bay E13 holding down bolt No.62 it has been identified as out of position; +20mmE & -24mmN (+10mmE &-14mmN out of tolerance) See attached sketch Cxxx-SK-677 showing the design position of the bolts and the as built position of the bolts including the centre point. See attached "E13 Bolt No. 62 Position.pdf" given the record as built coordinates for the bolts and centre points.
| 01CV - Civils | Cxxx-NCR-001445 | NCR | 5.4 IR Bay E12 Width Exceeds 2.8m |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2014-03-24 | 2014-03-20 10:34 | -4 | 2014-02-10 17:59 | Civil - Tunnelling | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The excavation for bay E12 has exceeded design width 2.8m in area of 1.2m length. The bay is max. 2.9m wide at this over-broken area. Refer to Attachment 1 for details. Please note that the timber guide has been used and that the setting-out engineer has marked the breaking line for excavation. We propose using as-is based on the NCR 1365 which confirmed that a 3.2m bay was acceptable for a similar issue of bay E2. To avoid the over-breaking in future excavations, we propose to saw cut approx. 100mm deep at the breaking line/lines. This will provide a clean cut edge and prevent any loose-jointed brickwork falling away.
| 01CV - Civils | Cxxx-NCR-001446 | NCR | 2.4 Bay E8 Holding Down Bolt No.52a Out of Position |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2014-08-29 | 2014-08-15 11:30 | -14 | 2014-02-07 14:21 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Upon completion of the as built survey of bay E8 holding down bolt No.52a the bolt group has spread and are out of position See attached sketch Cxxx-SK-678 showing the design position of the bolts and the as built position of the bolts See attached "Bay E8 Bolt No.52a Survey.pdf " provides the coordinates for each bolt and identifies the difference in easting and northing out of position
| 01CV - Civils | Cxxx-NCR-001447 | NCR | 7.5 - Shaft Pad Stone Pour Duration |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2014-05-30 | 2014-03-19 13:29 | -72 | 2014-02-11 13:33 | Civil - Civil Engineering General | 4000 |  | Workmanship | Rework | 3 (3-6k) | Complete | Management Problem - Inadequate supervision | Completed |  | Following a surveillance carried out on the pad stone concrete pour that took place on 07/02/14 it has become apparent that a number of pad stones were cast more than 2 hours after the concrete had been batched. KF10.3221 b) states that 'concrete shall be compacted in its final position within two hours of the introduction of cement to the aggregate, unless a longer time has been agreed by the Project Manager'. On 07/02/14 2m^3 of C32/40 concrete (c/w fibres) was batched at 08:17:33 and arrived on site at 08:35hrs. This concrete was discharged into 8 No. 0.25m^3 tubs and the wagon left site at 08:50hrs. By 10:17hrs 3 No. pad stones had been completed: pad stone numbers 5 and 6 (SW face of shaft) on level -4.5 and number 6 (west face) on level -1. Concrete placement continued and 5 No. pad stones were completed between 10:17hrs and 14:00hrs: pad stone numbers 7, 8, 1, 3 and 5 on level -1. Concrete cubes were cast by __ for this pour at 09:00hrs.
| 01CV - Civils | Cxxx-NCR-001448 | NCR | 5.4 IR Bay W10 Slab - low cover |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2014-05-09 | 2014-05-06 17:47 | -3 | 2014-02-12 09:38 | Civil - Tunnelling | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The first 3no. BM02 and BM03 bars from bay W7 in bay W10 have varying cover - min. 50mm - as opposed to the required 55 mm cover. Refer to attached 'NCR 1448 Cover survey' for details. As a full cover survey was undertaken during the reinforcement inspection Bay W7 and found to be within allowable tolerances, this lack of cover is probably caused due the fact that an odd numbers of lacers in affected area are protruding into the bay W10 slightly more then others and therefore the first 2no. of BM02 and BM03 are 'sitting' on the couplers instead on the lacers.
| 01CV - Civils | Cxxx-NCR-001449 | NCR | 5.4IR - E12 Damaged coupler |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2014-03-26 | 2014-03-20 10:35 | -6 | 2014-02-12 16:56 | Civil - Tunnelling | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | 1no. BM20 coupler was damaged on CJ E8-E12, Slab. Refer to Attachment 1 for detail of location. We propose to drill 25mm diameter holes 400mm deep near the damage coupler location. This will allow placement of a B20 bar (1200mm minimum bar length) to be cast in with __ HIT-HY 150 resin, spliced a minimum of 800mm onto BM2. Refer to Attachment 1 for location. Please see attached HIT HY-150 technical data sheet, for the hole diameter recommendation and embedded depth.
| 01CV - Civils | Cxxx-NCR-001450 | NCR | 5.4 IR Bay E13 Shear-key overbroken |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2014-03-28 | 2014-03-24 13:37 | -4 | 2014-02-14 14:49 | Civil - Tunnelling | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | A small part of weak brick at top of the shear-key in North and South wall felt out during the breaking out operation, probably because of weak point in brick work on the edge of the shear-key. Refer to 'Attachment 1' for details. We propose to saw cut around the damaged area, cutting depth min.100mm. Break back the damaged area to a minimum depth of 100mm by saw cutting underneath. Pour wall ensuring this area is incorporated. Once complete, concrete finish to be inspected and made good further if required.
| 01CV - Civils | Cxxx-NCR-001451 | NCR | 5.4 IR Calibration Torque Wrenches |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2014-04-01 | 2014-03-20 11:51 | -12 | 2014-02-18 15:30 | Civil - Tunnelling | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Subcontractor Problems - Other | Completed |  | Upon routine surveillance in the tunnel, the calibration certificates for the 2no. torque wrenches were requested. It was discovered that both of these certificates were not on the __ Instrumentation Register and only 1no. was immediately available. The other certificate was found soon after, after some searching in the __s cabins. Both of the certificates have now been added to the __ Instrumentation Register and have been laminated and tied onto the torque wrenches themselves (see attached photograph). We propose to carry out a review of __s instruments and upload the relevant calibration certificates onto the __ Instrumentation Register.
| 01CV - Civils | Cxxx-NCR-001452 | NCR | 5.4 IR Bay E23 South wall - Low cover |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2014-04-02 | 2014-03-24 13:47 | -9 | 2014-02-19 12:31 | Civil - Tunnelling | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | There is insufficient cover to the first 3no. of BM07 and BM05 from CJ E23-E21. Minimum cover is 45mm. Refer to Attachment 1 for details.
| 01CV - Civils | Cxxx-NCR-001453 | NCR | 5.4 IR Bay E14 SLab - Low cover |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2014-05-16 | 2014-05-13 16:33 | -3 | 2014-02-20 10:44 | Civil - Tunnelling | 750 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The first 1no. BM02 and BM03 bars from bay E10 in bay E14 has varying cover - min. 50mm - as opposed to the required 55 mm cover. Refer to attached 'NCR 1453 Cover survey' for details.
| 01CV - Civils | Cxxx-NCR-001454 | NCR | 5.4IR Procedural - No permit in place |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2014-04-04 | 2014-03-06 15:35 | -29 | 2014-02-21 18:22 | Civil - Tunnelling | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Bay W10 temporary works were removed on the night shift of 20/02/14. The permit to strike the temporary works had not been issued at the time of striking. The __s supervisor had assumed the permit was in place due to the following: - They had seen the cube results for the walls on W10 on 19/02/14 (46.7N/mm2) and observed to be above the required 40N/mm2. To date, as the walls are poured at least 1 day after the slab, the strength of the slab has been higher than the walls and this was also assumed by the supervior. In this instance, however, the permit was not issued due to waiting for a satisfactory recent slab cube result. - Bay W9 walls were poured the same day as W10 walls and the permit to strike the temporary works was issued 19/02/14. Please find attached cube results for the walls and slab showing excess of 40N/mm2 at time of striking.
| 01CV - Civils | Cxxx-NCR-001455 | NCR | 5.1 IR Bay E14 Concrete damage |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2014-04-04 | 2014-03-20 11:52 | -15 | 2014-02-21 18:31 | Civil - Tunnelling | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Upon the scabbling of construction joint E14-E10 north and South wall, it has been noticed that the small damage to the concrete has been done along the edge. Refer to Attachment 1 for details.
| 01CV - Civils | Cxxx-NCR-001456 | NCR | 2.4 Damage to Corbel Bay E13 |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2014-07-23 | 2014-05-19 15:46 | -65 | 2014-02-24 11:23 | Civil - Civil Engineering General | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Please see attached pictures taken of reinforced concrete corbel on bay E13 Factory Road side (at expansion joint E13/14) Damage to the corbel was discovered during kerb reinstatement works along Factory Road Damage has occur to the corbel on bay E13 at the bottom of the corbel below ground level There is damage to the mastic joint on the corbel
| 01CV - Civils | Cxxx-NCR-001457 | NCR | 5.4IR - W12 vertical anchor distance |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2014-04-09 | 2014-03-20 11:57 | -20 | 2014-02-26 10:27 | Civil - Tunnelling | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The edge distance for the anchors installed to the bottom of the vertical props into the concrete of slab of bay W9 for the temporary works in Bay W12 are 70mm. The required edge distance stated on drawing L12757-701 is 150mm. The temporary works designer has been been contacted and has confirmed that this edge distance into the concrete is ok (refer to attached calculations).
| 01CV - Civils | Cxxx-NCR-001458 | NCR | 5.4IR - Failure to follow ITP for post-pour repairs |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2014-04-08 | 2014-03-21 17:02 | -18 | 2014-02-25 12:32 | Civil - Tunnelling | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | Work has begun in the tunnel making good to the invert replacement walls. The south wall of Bay E5 has been made good, however it has not had a post-pour (pre-repair) inspection (item 4.12 of ITP Cxxx-VIN-C-ITP-CR146_ST003-50086). Upon inspection of the making good repairs carried on E5 south wall, no major works seem to have been undertaken. This problem has occured because in the beginning stages of carrying out post-pour (pre-repairs) inspections, bays E1 and E5 north walls were inspected separately due to obstructions due to scaffolding, storage of spoil etc. Every bay since then has been inspected as a whole bay including the slab. The inspection tracker that serves as a checklist for ITP items per bay has been updated to split the item of post-pour (pre-repair) into north wall, south wall and slab separately to ensure no confusion over upcoming bays (see Attachment 1). This has been sent out to J __s and __ staff to keep track of which bays are ok to make good to.
| 01CV - Civils | Cxxx-NCR-001459 | NCR | 5.4 IR Bay W12 Damage couplers |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2014-04-09 | 2014-03-21 17:06 | -19 | 2014-02-26 14:00 | Civil - Tunnelling | 700 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Approx. 7no of B20 couplers have been damaged on CJ W9-W12, during the breaking out operation in Bay W12. Refer to Attachment 1 for details. We propose to drill 25mm diameter holes 400mm deep near the damage couplers location. This will allow placement of a B20 bar (1200mm minimum bar length) to be cast in with __ HIT-HY 150 resin, spliced a minimum of 800mm onto BM2. Please see attached HIT HY-150 technical data sheet, for the hole diameter recommendation and embedded depth.
| 01CV - Civils | Cxxx-NCR-001460 | NCR | Benching Concrete/ channel East attenuation tank |  | Crossrail | XRL | CON - Connaught Tunnel (East) |  | 2014-08-29 | 2014-08-28 20:05 | -1 | 2014-02-26 17:12 | Civil - Drainage | 8000 |  | Incorrect Installation | Use As-Is | 2 (6-60k) | Complete | Discipline/Workmanship - Other | Completed |  | The benching concrete has not been poured to the correct levels (refer sketch Cxxx-OVE-c315-SITE-SK-00168). This has resulted in a reduced capacity of the attenuation tank. Outstanding RFI 1432 has yet to be responded to. This is to clarify size of channels and benching concrete levels.
| 01CV - Civils | Cxxx-NCR-001461 | NCR | 5.4IR - Trial Bay 2 lacer couplers |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2014-04-11 | 2014-03-24 14:09 | -18 | 2014-02-28 19:06 | Civil - Tunnelling | 750 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | With reference to FCD1296, 9no, couplers were found to be missing or filled with concrete at CJ Trial Bay 2 - W13. Refer to attachment 1 for details. As per FCD1296, additional reinforcement bars are to be fixed into the concrete in place of these couplers. Proposal from FCD1296: 'We propose to drill 25mm diameter holes 400mm deep near the damage couplers location. This will allow placement of a B20 bar (1200mm minimum bar length) to be cast in with __ HIT-HY 150 resin, spliced a minimum of 800mm onto BM2. Please note that where reinforcement is encountered during drilling of the holes preventing the full depth 400mm, we propose to resin in a short piece of reinforcement to prevent voids in the concrete.'
| 01CV - Civils | Cxxx-NCR-001462 | NCR | 5.4IR - W13 excessive cover |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2014-04-11 | 2014-04-11 09:18 | 0 | 2014-02-28 20:01 | Civil - Tunnelling | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The couplers for the slab and South wall lacers from Trial Bay 2 in Bay W13 cause the cover to Bay W13 BM02 and BM03 to have excessive cover. The maximum cover found in the slab is 80mm and the south wall is 75mm, refer to attached 'NCR 1462 Attachment 1' for details. We propose to pour the slab ensuring that the cover to the reinforcement at the CJ with Trial Bay 2 is no more than 70mm. An area of the Trial Bay 2 slab will then be locally scabbled down a maximum of 10mm to remove the stepped joint and create a smooth transition. For the localised area of 75mm cover on the South Wall we propose to use as-is.
| 01CV - Civils | Cxxx-NCR-001463 | NCR | 5.4IR - Trial Bay 2 concrete damage |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2014-04-11 | 2014-03-20 11:58 | -22 | 2014-02-28 19:21 | Civil - Tunnelling | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The edge of structural slab level of Trial Bay 2 slab has been damaged at the joint of W13/Trial Bay 2. Refer to Attachment 1 for details of damage. Max depth approx 40mm, max width approx 40mm.
| 01CV - Civils | Cxxx-NCR-001464 | NCR | 5.4IR - Incorrect resin used |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2014-04-11 | 2014-03-20 15:03 | -22 | 2014-02-28 20:27 | Civil - Tunnelling | 800 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | During an inspection of Bay W13 and to close out FCD1292 - W13 lacer couplers, it was noticed that 1no. of the bars was fixed into the Trial Bay 2 with __ HIT 70 resin instead of the __ HIT 150 resin that was included in the FCD. __ HIT 70 does not give the same capacity as __ HIT 150 and is suited to brickwork instead of concrete. After this was found, a full check was done of the cast-in bars (see Attachment 1 - The darker resin indicates __ HIT 150 resin) and all other fixed reinforcement bars found to be fixed correctly. Another length of reinforcement was then fixed into Trial Bay 2 next to the bar in question (see Attachment 1).
| 01CV - Civils | Cxxx-NCR-001465 | NCR | 7.5 - Head House Shaft Breakout in wrong location |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2014-04-07 | 2014-03-28 08:31 | -10 | 2014-03-01 14:57 | Civil - Civil Engineering General | 1000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Please refer to the attached photo Padstone breakout has occured in an incorrect location, not joining onto any other correct padstones. This breakout is on level -4 North face of the shaft. The breakout is currently 200mm depth approx. and edges are saw cut as per usual.
| 01CV - Civils | Cxxx-NCR-001466 | NCR | 5.4 Bay W13 Exposed reinforcement |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2014-04-14 | 2014-03-20 12:00 | -25 | 2014-03-03 09:48 | Civil - Tunnelling | 750 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Upon striking the shutter from the kicker in Bay W13 an area of concrete under-compaction has been discovered. 4no of BM06 and BM10 have been partly exposed. Refer to Attachment 1 for details. We propose to saw cut around the area of exposed reinforcement, break back min. 30mm behind the reinforcement as far as the void goes, and pour wall ensuring this area is incorporated. Once complete, concrete finish to be inspected and made good further if required. We will ensure that a limpet poker is located at kicker level, to ensure the wall pour sufficiently fills the void.
| 01CV - Civils | Cxxx-NCR-001467 | NCR | 5.4 IR Bay W13 Concrete damage |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2014-04-14 | 2014-03-20 15:04 | -25 | 2014-03-03 12:17 | Civil - Tunnelling | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | It has been noticed that the small damage to the concrete has been done along the edge of Trial Bay2 North and South walls. Refer to Attachment 1 for details. We propose to saw cut around the damaged area, cutting depth min.30mm and the cutting inclining by 5mm over the 30mm such that the remedial concrete is wedged in place. Break back the damaged area to a minimum depth of 30mm and pour wall ensuring this area is incorporated. Once complete, concrete finish to be inspected and made good further if required.
| 01CV - Civils | Cxxx-NCR-001468 | NCR | 5.4 IR Bay E24 Concrete damage |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2014-04-14 | 2014-03-20 15:05 | -25 | 2014-03-03 14:04 | Civil - Tunnelling | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | It has been noticed that the small damage to the concrete has been done along the edge of Bay E22 North and South walls. Refer to Attachment 1 for details. We propose to saw cut around the damaged area, cutting depth min.30mm and the cutting inclining by 5mm over the 30mm such that the remedial concrete is wedged in place. Break back the damaged area to a minimum depth of 30mm and pour wall ensuring this area is incorporated. Once complete, concrete finish to be inspected and made good further if required.
| 01CV - Civils | Cxxx-NCR-001469 | NCR | 7.1 - M&E Building Backfill |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2014-05-30 | 2014-04-03 08:37 | -57 | 2014-03-05 11:35 | Civil - Civil Engineering General | 1000 |  | System Defect | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Backfilling commenced around the M&E Building without an Inspection Request being raised to Crossrail. The excavation and filling ITP (Cxxx-VIN-C-ITP-CR146_ST003-50053 Rev 1.0) requires the compaction of material (item 10) is to be offered to Crossrail as a witness point, this was not raised via an IRF. The M&E building upstand walls were backfilled with 6F5 on Saturday 01/03/14. There was a __ engineer supervising the Saturday works who recorded the number of layers, depth of layers and number of passes. Although the works were witnessed by the __ engineer the information was not recorded on the check sheet until Monday 03/03/14. The backfill that was carried out to the slab level on 16/01/14 was also not notified by IRF and compaction testing was not carried out in this location at this stage in the backfill process.
| 01CV - Civils | Cxxx-NCR-001472 | NCR | 7.5 - Head House Shaft padstones grout loss level -1 numbers 1 & 3 |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2014-04-09 | 2014-03-27 14:51 | -13 | 2014-03-04 15:05 | Civil - Civil Engineering General | 750 |  | System Defect | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Please refer to attached photographs. During the concreting of the padstones there was a small amount of grout loss at the bottom right hand corners of the shutters which has left a small amount of exposed aggregate in the padstone.
| 01CV - Civils | Cxxx-NCR-001473 | NCR | 5.4 IR Bay E15 Gap at top of walls |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2014-04-16 | 2014-03-20 15:06 | -27 | 2014-03-05 09:49 | Civil - Tunnelling | 800 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Upon striking of the wall shutters in bay E15 it was found that there was a gap between the top of the concrete wall and the brickwork. The maximum gap is approximately 20mm, the depth approximately 160mm. Refer to Attachment 1 for details. We propose to construct a timber 'letterbox' shutter along the top of the wall and then grout the shear-key through the TAM pipe at a pressure of 4 bar. If the void depth reaches TAM pipe, then the void should be filled completely during the grouting. If the depth of void does not reach TAM pipe, then we propose pour Tamcrete MFC (the same product used to grout the shear-key) from top into the letterbox shutter, ensuring that the void is filled completely and that air can escape.
| 01CV - Civils | Cxxx-NCR-001474 | NCR | 5.4 IR Bay E16 Slab - Damage couplers |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2014-04-16 | 2014-03-21 08:34 | -26 | 2014-03-05 09:47 | Civil - Tunnelling | 750 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | 3no of B20 couplers have been damaged on CJ E12-E16, during the breaking out operation in Bay E16. Refer to 'Attachment 1 (updated)' for details. We propose to drill 25mm diameter holes 400mm deep near the damage couplers location. This will allow placement of a B20 bar (1200mm minimum bar length) to be cast in with __ HIT-HY 150 resin, spliced a minimum of 800mm (bottom of slab)/1250mm (top of slab) onto BM2. For drilled holes where we could not reach min depth 400mm, we propose cast in B20 bar of sufficient length with __ HIT-HY 150 resin to seal these redundant holes. Please see attached HIT HY-150 technical data sheet, for the hole diameter recommendation and embedded depth.
| 01CV - Civils | Cxxx-NCR-001475 | NCR | 2.2 Bay E3 CFA Below Cut Off Level |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2014-03-19 | 2014-03-14 15:40 | -5 | 2014-03-05 09:40 | Civil - Civil Engineering General | 600 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | During pile breakdown Bay E3 CFA Piles 311A, 311B & 311D have been broken down below design cut off level Design Cut Off: 311A&D - 99.656 & 311B - 99.206 As Built Cut Off Level: 311A - 99.606 (-50mm) 311B - 99.165 (-41mm) 311D - 99.519 (-137mm)
| 01CV - Civils | Cxxx-NCR-001477 | NCR | 5.4 Bay E17 Slab - Exposed reinforcement |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2014-04-16 | 2014-03-20 15:06 | -27 | 2014-03-05 15:42 | Civil - Tunnelling | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Upon scabbling of construction joint E13-E17 it has been discovered approx. 800mm length of exposed BM02 Hook-bar (top mat 1). Refer to Attachment 1 for details. We propose to include an additional hook-bar in E17 slab adjacent to the exposed hook-bar with a maximum 50mm gap between the bars.
| 01CV - Civils | Cxxx-NCR-001480 | NCR | 5.4 IR Bay E17 Damaged couplers |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2014-04-17 | 2014-03-21 08:35 | -27 | 2014-03-06 13:27 | Civil - Tunnelling | 600 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Approximately 8no of B20 couplers have been damaged on CJ E13-E17 and CJ E17-E2, during the breaking out operation in Bay E17. Refer to Attachment 1 for details. We propose to drill 25mm diameter holes 400mm deep near the damage couplers location. This will allow placement of a B20 bar (1200mm minimum bar length) to be cast in with __ HIT-HY 150 resin, spliced a minimum of 800mm onto BM2. For drilled holes where we could not reach min depth 400mm, we propose cast in B20 bar of sufficient length with __ HIT-HY 150 resin to seal these redundant holes. Please see attached HIT HY-150 technical data sheet, for the hole diameter recommendation and embedded depth.
| 01CV - Civils | Cxxx-NCR-001481 | NCR | 5.4 IR Bay W14 - Damaged couplers |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2014-04-18 | 2014-03-26 08:25 | -23 | 2014-03-07 15:35 | Civil - Tunnelling | 600 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Approximately 4no of B20 couplers have been damaged on CJ W11-W14 and CJ W14-W3, during the breaking out operation in Bay W14. Refer to Attachment 1 for details. We propose to drill 25mm diameter holes 400mm deep near the damage couplers location. This will allow placement of a B20 bar (1200mm minimum bar length for bottom of slab, 1650mm minimum bar length for top of slab) to be cast in with __ HIT-HY 150 resin, spliced a minimum of 800mm (for bottom of slab) respective 1200mm (for top of slab). For drilled holes where we could not reach min depth 400mm, we propose cast in B20 bar of sufficient length with __ HIT-HY 150 resin to seal these redundant holes. Please see attached HIT HY-150 technical data sheet, for the hole diameter recommendation and embedded depth.
| 01CV - Civils | Cxxx-NCR-001482 | NCR | 5.4 IR Bay E17 Slab - Low cover |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2014-05-16 | 2014-05-13 17:04 | -3 | 2014-03-07 16:56 | Civil - Tunnelling | 750 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Upon a cover survey in Bay E17 it has been discovered, that there is an area of low cover to the top-mat reinforcement. The minimum cover in this area is 50mm - as opposed to required 55mm. We propose to pour the slab ensuring that the cover to the reinforcement is min.55mm (by installing screed-rails). The slab will then be locally scabbled down to remove the stepped joint and prepare the surface to accept a minimum thickness of 12mm of __ Patchroc GP or similar approved in accordance with the manufacturer’s instructions and primed using __ Nitobond EP or similar approved.
| 01CV - Civils | Cxxx-NCR-001483 | NCR | 5.4 IR Bay W14 Concrete damage |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2014-04-21 | 2014-03-21 17:07 | -31 | 2014-03-10 10:26 | Civil - Tunnelling | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | It has been noticed that the damage to the concrete has been done along the edges of Bay W14 South wall. Refer to Attachment 1 for details. We propose to saw cut around the damaged area, cutting depth min.30mm and the cutting inclining by 5mm over the 30mm such that the remedial concrete is wedged in place. Break back the damaged area to a minimum depth of 30mm and pour wall ensuring this area is incorporated. Once complete, concrete finish to be inspected and made good further if required.
| 01CV - Civils | Cxxx-NCR-001484 | NCR | 5.4 IR Bay W14 South Wall - Exposed reinforcement |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2014-04-21 | 2014-03-26 08:31 | -26 | 2014-03-10 13:15 | Civil - Tunnelling | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Upon scabbling of CJ W14-W3 South wall in Bay W14 it has been noticed, that 1no of BM 05 (shear-key U-bar) has been partly exposed. Refer to Attachment 1 for details. We propose to include an additional BM05 U-bar in W14 South wall adjacent to the exposed U-bar with a 30mm gap between the bars. Refer to Attachment 1 for sketch.
| 01CV - Civils | Cxxx-NCR-001485 | NCR | 5.4 IR Bay E16 Gap at top of wall |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2014-04-21 | 2014-03-21 17:09 | -31 | 2014-03-10 16:13 | Civil - Tunnelling | 750 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Upon striking of the wall shutters in bay E16 it was found that there was a gap between the top of the concrete wall and the brickwork. The maximum gap is approximately max.30mm, the depth approximately 50mm. There seems to be a small area of exposed grout pipe. Refer to Attachment 1 for details. We propose to construct a timber 'letterbox' shutter along the top of the wall and then grout the shear-key through the TAM pipe at a pressure of 4 bar. If the void depth reaches TAM pipe, then the void should be filled completely during the grouting. If the depth of void does not reach the TAM pipe, then we propose to pour Tamcrete MFC (the same product used to grout the shear-key) from the top into the letterbox shutter, ensuring that the void is filled completely and that air can escape.
| 01CV - Civils | Cxxx-NCR-001486 | NCR | 2.5 - Damage to Existing Silvertown Footbridge |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2014-08-29 | 2014-08-29 17:25 | 0 | 2014-03-11 08:25 | Civil - Civil Engineering General | 1000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Damage has been seen to underside of the existing Silvertown footbridge (August 2013). It is believed that an excavator came into contact with the pedestrian footbridge above bay E4. A joint inspection was carried out with Jonathan Wheeler (__) and Mike Simms (Crossrail) who determined that only surface damaged had been caused and no reinforcement exposed.
| 01CV - Civils | Cxxx-NCR-001487 | NCR | 5.4 IR Bay E17 Walls - Concrete damage |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2014-04-22 | 2014-03-21 17:10 | -32 | 2014-03-11 09:43 | Civil - Tunnelling | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | It has been noticed that the damage to the concrete has been done along the edges of Bay E17 North and South wall. Refer to Attachment 1 for details. We propose to saw cut around the damaged area, cutting depth min.30mm and the cutting inclining by 5mm over the 30mm such that the remedial concrete is wedged in place. Break back the damaged area to a minimum depth of 30mm and pour wall ensuring this area is incorporated. Once complete, concrete finish to be inspected and made good further if required.
| 01CV - Civils | Cxxx-NCR-001488 | NCR | 2.2 Damage to CFA 310B Reinforcement |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2014-04-30 | 2014-04-07 13:15 | -23 | 2014-03-11 10:30 | Civil - Civil Engineering General | 750 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | During Pile Breakdown of CFA 310B in bay E3, 3No. 16mm Starter Bars were damaged approximately 250mm above cut off level (see attached photo of damaged bars)
| 01CV - Civils | Cxxx-NCR-001489 | NCR | 2.2 Damage to Bay E3 CMC Rows 307-312 |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2014-04-30 | 2014-04-30 14:56 | 0 | 2014-03-11 13:04 | Civil - Civil Engineering General | 8000 |  | Incorrect Installation | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Other | Completed |  | CMC row 307-309 & 312 have been identified as defective piles. The reinforcement is protruding from the side of the piles in 15No. CMC The reinforcement is not cast into the concrete and can be seen down the side of the concrete in 4No. CMC Total 19No. CMC piles defective on rows 307-309 & 312 CMC Piles without defects in rows 307-309 & 312: CMC 307B, 307F, 309B, 312B & 312E It must be noted that CMC rows 307-309 & 312 where carried out on 12th & 13th June 2013 All other CMC rows within bay E3 where drilled on 12th July 2012 & 25th September 2012 During bulk excavation & CMC pile break down in bay E3, we have not identified this defect in the other CMC rows Integrity tests have now been completed for all CMC within bay E3 Within CMC rows 307-309 & 312 a number of CMC piles required breaking down up to and over 1m to remove cracked head of the CMC
| 01CV - Civils | Cxxx-NCR-001490 | NCR | 5.4 IR Bay E18 Damaged couplers |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2014-04-22 | 2014-03-24 14:13 | -29 | 2014-03-11 15:20 | Civil - Tunnelling | 750 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Approximately 9no of B20 couplers have been damaged on CJ E18-E14 and CJ E18-E3, during the breaking out operation in Bay E18. Refer to Attachment 1 for details. We propose to drill 25mm diameter holes 400mm deep near the damage couplers location. This will allow placement of a B20 bar (1200mm minimum bar length) to be cast in with __ HIT-HY 150 resin, spliced a minimum of 800mm onto BM2. For drilled holes where we could not reach min depth 400mm, we propose cast in B20 bar of sufficient length with __ HIT-HY 150 resin to seal these redundant holes. Please see attached HIT HY-150 technical data sheet, for the hole diameter recommendation and embedded depth.
| 01CV - Civils | Cxxx-NCR-001491 | NCR | 2.2 CMC rows 304D / 308ABC - reduced diameter |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2014-05-30 | 2014-04-07 15:05 | -53 | 2014-03-14 14:10 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Reduced diameter (Applicable to 304D / 308ABC) - 304D : average diameter 310mm - 308A : average diameter 300mm - 308B : average diameter 240mm - 308C : average diameter 300mm
| 01CV - Civils | Cxxx-NCR-001492 | NCR | 5.4 IR Bay E17 Gap at top of wall |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2014-04-25 | 2014-03-27 14:52 | -29 | 2014-03-14 11:52 | Civil - Tunnelling | 750 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Upon striking of the wall shutters in bay E17 it was found that there was a gap between the top of the concrete south wall and the brickwork. The maximum gap is approximately 40mm, the depth approximately 30mm. Please note that there is no sign of exposed grout pipe. Refer to attachment 1 for details. We propose to construct a timber 'letterbox' shutter along the top of the wall and then grout the shear-key through the TAM pipe at a pressure of 4 bar. If the void depth reaches TAM pipe, then the void should be filled completely during the grouting. If the depth of void does not reach the TAM pipe, then we propose to pour Tamcrete MFC (the same product used to grout the shear-key) from the top into the letterbox shutter, ensuring that the void is filled completely and that air can escape.
| 01CV - Civils | Cxxx-NCR-001493 | NCR | Columns trimmed too low (Applicable to 300A, 302B, 303F & 305A) |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2014-05-13 | 2014-05-15 16:04 | 2 | 2014-03-14 16:05 | Civil - Civil Engineering General | 1000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Columns too low (Applicable to 300A, 302B, 303F & 305A) 300A: Trimming level is 99.120, 34mm below design trimming level 302B: Trimming level is 99.111, 113mm below design trimming level 303F: Trimming level is 99.163, 95mm below design trimming level 305A: Trimming level is 99.241, 82mm below design trimming level
| 01CV - Civils | Cxxx-NCR-001494 | NCR | 2.2 CMC Rows 300-306 multiple issues |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2014-05-14 | 2014-05-16 14:22 | 2 | 2014-03-15 18:23 | Civil - Civil Engineering General | 3000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Reduced (Cracked) head diameter at trim level (Applicable to CMC 306E) The size of the cracked concrete and the diameter of the column head is shown on the attached spreadsheet. Reduced pile diameter (Applicable to CMCs 300BEF/301ABCE/302ADEF/303ABC/304ABE/305BC/306B) The installed columns have diameters as stated in the attached spreadsheet Out of position piles (Applicable to CMCs 300EF/301CDEF/302CD/303CDE/304BCEF/305BCD/306ABE) The columns have been installed as per the attached spreadsheet.The distance from the designed co-ordinate is stated. Trim level too low (Applicable to CMCs 300BEF/301ABCDEF/302ACDEF/303ABCDE/304ABCEF/305BCD/306AB) The difference between the trim level and designed trim level for each CMC is stated on the attached spreadsheet. Reinforcement too high (Applicable to CMC 304B) The level of the top of rebar and the difference to the highest rebar trimming level is stated in the attached schedule. Mechanical damage (Applicable to CMC 306B) The depth of mechanical damage is stated in the attached schedule.
| 01CV - Civils | Cxxx-NCR-001495 | NCR | 2.2 Out of position piles (Applicable to CMCs 305EF/306CD) |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2014-05-30 | 2014-05-19 16:02 | -11 | 2014-03-17 09:21 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Out of position piles (Applicable to CMCs 305EF/306CD) The columns have been installed as per the attached spreadsheet. The distance from the designed co-ordinate is stated.
| 01CV - Civils | Cxxx-NCR-001496 | NCR | Reduced pile diameter (Applicable to CMC 300C, average diameter is 300 mm) |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2014-05-16 | 2014-03-28 08:58 | -49 | 2014-03-17 10:22 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Reduced pile diameter (Applicable to CMC 300C, average diameter is 300 mm as stated in the attached spreadsheet)
| 01CV - Civils | Cxxx-NCR-001497 | NCR | 5.4 IR Bay E18 Concrete damage |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2014-04-29 | 2014-03-27 15:30 | -33 | 2014-03-18 08:18 | Civil - Tunnelling | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | It has been noticed that the damage to the concrete has been done along the edges of Bay E18 North and South wall. Refer to Attachment 1 for details. We propose to saw cut around the damaged area, cutting depth min.30mm and the cutting inclining by 5mm over the 30mm such that the remedial concrete is wedged in place. Break back the damaged area to a minimum depth of 30mm and pour wall ensuring this area is incorporated. Once complete, concrete finish to be inspected and made good further if required.
| 01CV - Civils | Cxxx-NCR-001498 | NCR | 5.4 IR Bay E25 Gap at top of the wall |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2014-04-29 | 2014-03-27 15:31 | -33 | 2014-03-18 08:48 | Civil - Tunnelling | 1000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Upon striking of the wall shutters in bay E25 it was found that there was a gap between the top of the concrete south wall and the brickwork. The maximum gap is approximately 30mm, the maximum depth approximately 110mm. Refer to attachment 1 for details. We propose to construct a timber 'letterbox' shutter along the top of the wall and then grout the shear-key through the TAM pipe at a pressure of 4 bar. If the void depth reaches TAM pipe, then the void should be filled completely during the grouting. If the depth of void does not reach the TAM pipe, then we propose to pour Tamcrete MFC (the same product used to grout the shear-key) from the top into the letterbox shutter, ensuring that the void is filled completely and that air from the void can escape.
| 01CV - Civils | Cxxx-NCR-001499 | NCR | 5.4 IR Bay E19 Damaged couplers |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2014-04-29 | 2014-03-27 16:27 | -33 | 2014-03-18 09:42 | Civil - Tunnelling | 850 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Approximately 10no of B20 couplers have been damaged on CJ E15-E19 and CJ E19-E4, during the breaking out operation in Bay E19. Refer to Attachment 1 for details. We propose to drill 25mm diameter holes 400mm deep near the damage couplers location. This will allow placement of a B20 bar (1200mm minimum bar length) to be cast in with __ HIT-HY 150 resin, spliced a minimum of 800mm onto BM2. For drilled holes where we could not reach min depth 400mm, we propose cast in B20 bar of sufficient length with __ HIT-HY 150 resin to seal these redundant holes. Please see attached HIT HY-150 technical data sheet, for the hole diameter recommendation and embedded depth.
| 01CV - Civils | Cxxx-NCR-001500 | NCR | 5.4 IR Bay E19 Concrete damage |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2014-04-30 | 2014-03-27 16:29 | -34 | 2014-03-19 09:39 | Civil - Tunnelling | 800 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | It has been noticed that the damage to the concrete has been done along the edges of Bay E19 North and South wall and Slab. It also has been noticed two small areas of exposed reinforcement in the slab, CJ E4-E19. Refer to Attachment 1 for details. 1) For concrete damage on walls we propose to saw cut around the damaged area, cutting depth min.30mm and the cutting inclining by 5mm over the 30mm such that the remedial concrete is wedged in place. Break back the damaged area to a minimum depth of 30mm and pour wall ensuring this area is incorporated. Once complete, concrete finish to be inspected and made good further if required. 2) For concrete damage on slab edge (marked as Damaged area 1) we propose to saw cut around the damaged area, cutting depth min.30mm. Break back the damaged area to a minimum depth of 30mm and scabble down another 10mm to achieve breaking depth 40mm without exposing the reinforcement. Then pour the slab ensuring this area is incorporated. Once complete, concrete finish to be inspected and made good further if required. 3) For concrete damage on slab edge (marked as Damaged area 2) we propose to saw cut around the damaged area, cutting depth min.30mm. Break back the damaged area to a minimum depth of 30mm and scabble down another 10mm to achieve breaking depth 40mm without exposing the reinforcement. Break back min30mm around the exposed bar and pour slab ensuring this area is incorporated. Once complete, concrete finish to be inspected and made good further if required. 4) For exposed hook-bar in CJ E4-E19 we propose to include an additional BM03 hook-bar adjacent to the exposed bar with a 50mm gap between the bars.
| 01CV - Civils | Cxxx-NCR-001501 | NCR | 5.4 IR Procedural - Failure to follow ITP procedure |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2014-04-29 | 2014-03-21 08:37 | -39 | 2014-03-18 18:24 | Civil - Tunnelling | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | ITP number Cxxx-VIN-C-ITP-CR146_ST003-50086 shows the reinforcement installation follows the formation, shear-key and scabbling inspections. During the scabbling inspection in Bay E19 it has been noticed, that the bottom-mat reinforcement has started to be installed.
| 01CV - Civils | Cxxx-NCR-001502 | NCR | 5.4 IR Bay W15 Gap at top of the wall |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2014-05-02 | 2014-03-28 15:00 | -35 | 2014-03-21 09:35 | Civil - Tunnelling | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Upon striking of the wall shutters in bay W15 it was found that there was a gap between the top of the concrete south and north wall and the brickwork. The maximum gap is approximately 10mm, the maximum depth approximately 60mm. Refer to attachment 1 for details. We propose to construct a timber 'letterbox' shutter along the top of the wall and then grout the shear-key through the TAM pipe at a pressure of 4 bar. If the void depth reaches TAM pipe, then the void should be filled completely during the grouting. If the depth of void does not reach the TAM pipe, then we propose to pour Tamcrete MFC (the same product used to grout the shear-key) from the top into the letterbox shutter, ensuring that the void is filled completely and that air from the void can escape.
| 01CV - Civils | Cxxx-NCR-001503 | NCR | 5.4 IR Bay E26 Concrete damage |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2014-05-05 | 2014-03-31 13:43 | -35 | 2014-03-24 08:25 | Civil - Tunnelling | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | It has been noticed that the damage to the concrete has been done along the edge of Bay E26 North wall. Refer to Attachment 1 for details. We propose to saw cut around the damaged area, cutting depth min.30mm and the cutting inclining by 5mm over the 30mm such that the remedial concrete is wedged in place. Break back the damaged area to a minimum depth of 30mm and pour wall ensuring this area is incorporated. Once complete, concrete finish to be inspected and made good further if required.
| 01CV - Civils | Cxxx-NCR-001504 | NCR | 5.4 IR Bay E20 Concrete damage |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2014-05-05 | 2014-03-31 15:59 | -35 | 2014-03-24 08:47 | Civil - Tunnelling | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | It has been noticed that the damage to the concrete has been done along the edge of Bay E20 South wall. Refer to Attachment 1 for details. We propose to saw cut around the damaged area, cutting depth min.30mm and the cutting inclining by 5mm over the 30mm such that the remedial concrete is wedged in place. Break back the damaged area to a minimum depth of 30mm and pour wall ensuring this area is incorporated. Once complete, concrete finish to be inspected and made good further if required.
| 01CV - Civils | Cxxx-NCR-001505 | NCR | 5.4 IR Bay E19 Gap at top of the wall |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2014-05-05 | 2014-03-31 16:01 | -35 | 2014-03-24 09:03 | Civil - Tunnelling | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Upon striking of the wall shutters in bay E19 it was found that there was a gap between the top of the concrete south wall and the brickwork. The maximum gap is approximately 20mm, the maximum depth approximately 50mm. Refer to attachment 1 for details. We propose to construct a timber 'letterbox' shutter along the top of the wall and then grout the shear-key through the TAM pipe at a pressure of 4 bar. If the void depth reaches TAM pipe, then the void should be filled completely during the grouting. If the depth of void does not reach the TAM pipe, then we propose to pour Tamcrete MFC (the same product used to grout the shear-key) from the top into the letterbox shutter, ensuring that the void is filled completely and that air from the void can escape.
| 01CV - Civils | Cxxx-NCR-001506 | NCR | 5.4 IR West tunnel - Concrete shrinkage and under-compaction |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2014-05-07 | 2014-05-08 17:10 | 1 | 2014-03-26 14:24 | Civil - Tunnelling | 3000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | During post-pour (pre-repair) inspections in the West tunnel it has been noticed that on the walls there are small areas of under-compacted concrete and concrete shrinkages. Refer to Attachment 1 for details. We propose to scabble back the affected areas to remove any loose/weak material, then carry out the investigation to see how deep these defects are and how much concrete has to be removed to achieve a sound surface. Crossrail will be shown the investigative works to approve remedial actions prior to making good. We propose to make good in accordance with the agreed method statement using __ __ S for these affected areas, where the investigation had proved that the defects do not extend beyond 20mm.
| 01CV - Civils | Cxxx-NCR-001507 | NCR | 5.4 IR Bay E27 Gap at top of the wall |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2014-05-12 | 2014-05-12 09:31 | 0 | 2014-03-31 15:03 | Civil - Tunnelling | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Upon striking of the wall shutters in bay E27 it was found that there was a gap at top of the concrete South and North wall. The maximum gap is approximately 20mm, the maximum depth approximately 40mm. Refer to Attachment 1 for details. We propose to construct a timber 'letterbox' shutter along the top of the wall and then grout the shear-key through the TAM pipe at a pressure of 4 bar. If the void depth reaches TAM pipe, then the void should be filled completely during the grouting. If the depth of void does not reach the TAM pipe, then we propose to pour Tamcrete MFC (the same product used to grout the shear-key) from the top into the letterbox shutter, ensuring that the void is filled completely and that air from the void can escape. The residual grout in the letter box will be removed and the surface made good in accordance with the approved method statement.
| 01CV - Civils | Cxxx-NCR-001508 | NCR | 5.4 IR Bay E20 Gap at top of the wall |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2014-05-12 | 2014-05-09 14:00 | -3 | 2014-03-31 15:11 | Civil - Tunnelling | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Upon striking of the wall shutters in bay E20 it was found that there was a gap at top of the concrete South and North wall. The maximum gap is approximately 20mm, the maximum depth approximately 50mm. Refer to Attachment 1 for details. We propose to construct a timber 'letterbox' shutter along the top of the wall and then grout the shear-key through the TAM pipe at a pressure of 4 bar. If the void depth reaches TAM pipe, then the void should be filled completely during the grouting. If the depth of void does not reach the TAM pipe, then we propose to pour Tamcrete MFC (the same product used to grout the shear-key) from the top into the letterbox shutter, ensuring that the void is filled completely and that air from the void can escape. The residual grout in the letter box will be removed and the surface made good in accordance with the approved method statement.
| 01CV - Civils | Cxxx-NCR-001509 | NCR | 5.4 IR 28day cube results in the West tunnel |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2014-05-16 | 2014-04-24 18:42 | -22 | 2014-04-04 09:42 | Civil - Tunnelling | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | Single Tunnel Invert Replacement ITP Cxxx-VIN-C-ITP-CR146_ST003-50086 requests 2no 28day cubes every 50m3 (or 2no 28day cubes each pour if less then 50m3). Due to communication break down between J__s and __, the pours listed below do not have the correct number of 28 day cube results. Bay W1 Walls (7m3) 0no 28 day results due to miscommunication between J__ and __. The results have gained the required 40N/mm2 earlier than 28 days, as shown in attached 5,6 and 7 day results. Bay W5 Walls (8m3) 1no 28 day result because J__ used the 28 day cube for an extra 4 day result. The result have gained the required 40N/mm2 as shown in attached 28 day result. Bay W6 Walls (8m3) 1no 28 days results because J__ used 28 day cube for an extra 7 day result. The results have gained the required 40N/mm2 earlier than 28 days, as shown in attached 7 day results.
| 01CV - Civils | Cxxx-NCR-001510 | NCR | 1.6 - CMC Rows 155 to 165 - diameter too small |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2014-07-18 | 2014-07-01 08:33 | -17 | 2014-06-20 16:17 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Reduced Diameter (Applicable to 156C / 157BF / 158ABC / 159B / 164AB) The installed columns have average diameters as per the attached schedule.
| 01CV - Civils | Cxxx-NCR-001511 | NCR | 1.6 - CMC Rows 155 to 165 – cracked heads |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2014-07-04 | 2014-07-02 13:46 | -2 | 2014-06-20 15:45 | Civil - Civil Engineering General | 2000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The columns references 155F / 159C / 162A /§ 163D / 164D, have a crack in the column head which have resulted in a piece of the concrete breaking away at the head and side of the column. Removing these cracked pieces has created a smaller pile head and also a void to the side of the column. The sizes of the cracked concrete and the diameters of the column heads are shown on the attached spreadsheet. (It should be noted that the column has achieved the correct diameter and only the head has a smaller diameter.)
| 01CV - Civils | Cxxx-NCR-001512 | NCR | 1.2 - CMC Rows 155 to 165 - out of position |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2014-07-04 | 2014-06-27 18:03 | -7 | 2014-06-20 15:47 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The columns 1551 / 156D / 157CE / 158DE / 159DF / 160F / 161CDF / 163BF / 164F / 165BE have been installed as per the attached schedule. This is distance from the designed co-ordinate is stated.
| 01CV - Civils | Cxxx-NCR-001513 | NCR | 1.2 - CMC Rows 155 to 165 - multiple issues |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2014-07-04 | 2014-07-02 13:46 | -2 | 2014-06-20 16:14 | Civil - Civil Engineering General | 2000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Cracked Head Column NCR (Applicable to 155E / 156E / 157AD / 158F / 159AE / 160BCE / 161AB / 162BEF / 163E / 164E / 165DF) The columns from row 155 to 165 have a crack in the column head which have resulted in a piece of the concrete breaking away at the head and side of the column. Removing these cracked pieces has created a smaller pile head and also a void to the side of the column. The sizes of the cracked concrete and the diameters of the column heads are shown on the attached spreadsheet. (It should be noted that the column has achieved the correct diameter and only the head has a smaller diameter.) Out of Position (Applicable to 155BE / 156BE / 157D / 159E / 160CDE / 161AB / 162BEF / 163E / 164E / 165DF) The columns have been installed as per the attached spreadsheet. This is distance from the designed co-ordinate is stated. Reduced Diameter (Applicable to 155BD / 156AB / 157A / 158F / 159A / 160D / 165DF) The installed columns have diameters as stated in the attached spreadsheet. Columns too low (Applicable to 155BD / 156A) The trimming levels are as per the attached spreadsheet.
| 01CV - Civils | Cxxx-NCR-001514 | NCR | 1.6 OHLE 16 & 17 Bay W7 Trimming Below Cut off Level |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2014-05-29 | 2014-05-19 16:06 | -10 | 2014-04-03 10:39 | Civil - Civil Engineering General | 800 |  | Damaged | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Due to an error on site, OHLE CFA piles No. 16 & 17 were saw cut at formation level; approximately 450mm below design cut off level. An angle grinder was used to created a saw cut at formation level (please see attached photos)
| 01CV - Civils | Cxxx-NCR-001515 | NCR | 5.4 IR Bay E28 Concrete damage |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2014-05-15 | 2014-05-12 08:58 | -3 | 2014-04-03 16:33 | Civil - Tunnelling | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | It has been noticed that the damage to the concrete has been done along the edge of Bay E28 Slab and Walls. Refer to Attachment 1 for details. 1) For concrete damage on walls, we propose to saw cut around the damaged area, cutting depth min.30mm and the cutting inclining by 5mm over the 30mm such that the remedial concrete is wedged in place. Break back the damaged area to a minimum depth of 30mm and pour wall ensuring this area is incorporated. Once complete, concrete finish to be inspected and made good further if required. 2) For concrete damage on slab edge we propose to saw cut around the damaged area, cutting depth min.30mm. Break back the damaged area to a minimum depth of 30mm and scabble down another 10mm to achieve breaking depth 40mm without exposing the reinforcement. Then pour the slab ensuring this area is incorporated. Once complete, concrete finish to be inspected and made good further if required. 3) A small piece of ply-wood has been discovered in the North wall during the breaking out the damaged area at CJ E26-E28 (refer to page 2 and 3, Attachment 2). This piece of plywood has been carefully and completely removed from the concrete wall without exposing the reinforcement. Refer to Attachment 2. As discussed with Crossrail and __ on site, the saw cut around the damaged area has been done, inclining approx. 5mm over the approx. 40mm depth to ensure that remedial concrete is wedged in place. The wall has been poured ensuring the damaged area has ben incorporated. Additional shutter vibrator has been placed near to damaged area to provide sufficient compaction. Once complete, concrete finish to be inspected and made good further if required.
| 01CV - Civils | Cxxx-NCR-001516 | NCR | 5.4 IR Bay E28 Damage couplers |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2014-05-15 | 2014-04-16 11:03 | -29 | 2014-04-03 17:12 | Civil - Tunnelling | 800 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Approx. 3no of B20 couplers have been damaged on CJ E26-E28 during the breaking out operation in Bay E28. Refer to Attachment 1 for details. We propose to drill 25mm diameter holes 400mm deep near the damage couplers location. This will allow placement of a B20 bar (1650mm minimum bar length for top mat and 1200mm minimum bar length for bottom mat) to be cast in with __ HIT-HY 150 resin, spliced a minimum of 1250mm (top mat) respective 800mm (bottom mat). Please see attached HIT HY-150 technical data sheet, for the hole diameter recommendation and embedded depth.
| 01CV - Civils | Cxxx-NCR-001517 | NCR | 5.4 IR West tunnel - Protruding tie bars |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2014-05-19 | 2014-05-07 11:12 | -12 | 2014-04-07 10:55 | Civil - Tunnelling | 600 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Formwork tie bars have been observed to be permanently cast into the structure, these cannot be removed. Refer to Attachment 1 for details. Based on the response to Cxxx-NCR-001313 and Cxxx-NCR-001340 (see attached) for similar problems, we propose to saw cut (square 100mmx100mm centred on the tie bar) around the cast-in tie bar, break back approximately 50mm and cut back the bar. We propose to then make good to this area with __ S as per approved method statement Cxxx-VIN-C-GMS-CR146_ST003-50236. To ensure that the remedial material is wedged in place, we propose to incline the cut edge 5mm-10mm over the 50mm depth.
| 01CV - Civils | Cxxx-NCR-001518 | NCR | 5.4 IR Bay E29 Damaged couplers |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2014-05-19 | 2014-04-11 13:45 | -38 | 2014-04-07 11:41 | Civil - Tunnelling | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Approx. 2no of B20 couplers have been damaged on CJ E20-E29 during the breaking out operation in Bay E29. Refer to Attachment 1 for details. We propose to drill 25mm diameter holes 400mm deep near the damage couplers location. This will allow placement of a B20 bar (1650mm minimum bar length for top mat and 1200mm minimum bar length for bottom mat) to be cast in with __ HIT-HY 150 resin, spliced a minimum of 1250mm (top mat) respective 800mm (bottom mat). Please see attached HIT HY-150 technical data sheet, for the hole diameter recommendation and embedded depth. Please note that during the steel fixing operation more couplers with damaged threads may be discovered. The final position of damaged couplers will be marked up in the Attachment 2.
| 01CV - Civils | Cxxx-NCR-001519 | NCR | 5.4 IR Bay E29 Concrete damage |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2014-05-19 | 2014-05-09 14:02 | -10 | 2014-04-07 18:13 | Civil - Tunnelling | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | It has been noticed that the damage to the concrete has been done along the edge of Bay E29 Slab and Walls. Refer to Attachment 1 for details. 1) For concrete damage on walls, we propose to saw cut around the damaged area, cutting depth min.30mm and the cutting inclining by 5mm over the 30mm such that the remedial concrete is wedged in place. Break back the damaged area to a minimum depth of 30mm and pour wall ensuring this area is incorporated. Once complete, concrete finish to be inspected and made good further if required. 2) For concrete damage on slab edge we propose to saw cut around the damaged area, cutting depth min.30mm. Break back the damaged area to a minimum depth of 30mm and scabble down another 10mm to achieve breaking depth 40mm without exposing the reinforcement. Then pour the slab ensuring this area is incorporated. Once complete, concrete finish to be inspected and made good further if required.
| 01CV - Civils | Cxxx-NCR-001520 | NCR | 7.1 Post pour defects Upstand Wall Support Building |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2014-04-24 | 2014-04-22 11:25 | -2 | 2014-04-10 12:00 | Civil - Civil Engineering General | 600 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | During the post pour inspection of the support building upstand walls (IR 3356) 2 No. areas of grout loss and 2 No. areas of damage were highlighted as requiring repair.
| 01CV - Civils | Cxxx-NCR-001521 | NCR | 5.4 IR Bay E30 Gap at top of the wall |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2014-05-27 | 2014-05-12 09:27 | -15 | 2014-04-15 17:08 | Civil - Tunnelling | 600 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Upon striking of the wall shutters in bay E30 it was found that there was a gap at top of the concrete South wall. The maximum gap is approximately 10mm, the maximum depth approximately 220mm. Refer to Attachment 1 for details. We propose to construct a timber 'letterbox' shutter along the top of the wall and then grout the shear-key through the TAM pipe at a pressure of 4 bar. If the void depth reaches TAM pipe, then the void should be filled completely during the grouting. If the depth of void does not reach the TAM pipe, then we propose to pour Tamcrete MFC (the same product used to grout the shear-key) from the top into the letterbox shutter, ensuring that the void is filled completely and that air from the void can escape. The residual grout in the letter box will be removed and the surface made good in accordance with the approved method statement.
| 01CV - Civils | Cxxx-NCR-001522 | NCR | 5.4 IR Bay W14 North wall - excessive cover |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2014-06-04 | 2014-05-08 14:35 | -27 | 2014-04-23 09:33 | Civil - Tunnelling | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Specification 'KF10 Insitu concrete, KF10.3244 f)' (document number Cxxx-OVE-Z4-RSP-CR001-00023) states : 'The concrete cover to steel reinforcement shown on the Drawings is the clear cover to the outside of the reinforcement, including stirrups, and shall be adhered to during construction to within tolerances of +3mm-0mm for cover up to 40mm and +6mm-0mm for cover over 40mm.' As-built survey of Bay W14 North wall shows area of excessive cover to steel reinforcement. Refer to Attachment 1 for details. We propose use as is, based on the following : 1) The close inspection has been carried out by J.__ engineer and there are no signs of fissures in the concrete face. 2) The attached 28d cube results shows strength 58.0 N/mm2 and 56.4 N/mm2. The results have gained the required 40N/mm2 earlier than 28 days, as shown in attached 7 day results. 3) The position of the wall is within tolerance as per ITP Cxxx-VIN-C-ITP-CR146_ST003-50086 (refer to survey, Attachment 1, page2).
| 01CV - Civils | Cxxx-NCR-001523 | NCR | 5.4 IR East tunnel - Concrete shrinkage and grout loss |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2014-06-11 | 2014-05-09 14:05 | -33 | 2014-04-30 10:55 | Civil - Tunnelling | 2000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | During post-pour (pre-repair) inspections in the East tunnel it has been noticed that on the walls there are small areas of grout loss and concrete shrinkages. Refer to Attachment 1 for details. Based on the response to Cxxx-NCR-001506 for the same problem in the West tunnel, we propose : Grout loss - We propose to scabble back the affected areas to remove any loose/weak material, then carry out the investigation to see how deep these defects are and how much concrete has to be removed to achieve a sound surface. The results are to be agreed with the Project Manager’s representative. Concrete shrinkages - We propose to construct a timber 'letterbox' shutter along the top of the wall and then grout the shear-key through the TAM pipe at a pressure of 4 bar. If the void depth reaches TAM pipe, then the void should be filled completely during the grouting. If the depth of void does not reach the TAM pipe, then pour Tamcrete MFC (the same product used to grout the shear-key) from the top into the letterbox shutter, ensuring that the void is filled completely and that air from the void can escape. The residual grout in the letter box is to be removed and the surface made good in accordance with the approved method statement. We propose to make good in accordance with the agreed method statement using __ __ S for these affected areas, where the investigation had proved that the defects do not extend beyond 20mm.
| 01CV - Civils | Cxxx-NCR-001524 | NCR | 5.3 Invert Reprofiling East SIngle Tunnel |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2014-05-19 | 2014-05-15 16:07 | -4 | 2014-04-28 17:18 | Civil - Civil Engineering General | 1000 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Between Chainage 18205 and 18225 the invert reprofiling has been over dug by between 33mm and 77mm, please see attached spreadsheet for details at various chainages.
| 01CV - Civils | Cxxx-NCR-001525 | NCR | 6.1 Staining Bay 7 West Upper Wall |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2014-08-30 | 2014-07-29 15:44 | -32 | 2014-04-29 09:16 | Civil - Tunnelling | 750 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | As per the attached image, there is some staining evident on the Upper Wall of Bay 7 West. Further investigation is required to determine the cause of this staining.
| 01CV - Civils | Cxxx-NCR-001526 | NCR | 5.4 IR Surface scratches to tunnel crown |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2014-06-11 | 2014-05-08 17:25 | -34 | 2014-04-30 08:24 | Civil - Tunnelling | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | It was observed that number of face blemishes/scratches occurred on the crown of the tunnel during the works, probably caused by the knuckle of the excavator scratching the tunnel crown. Refer to the 'Attachment 1' for photos. Please note J.__ acknowledge the majority of blemishes are due to J.__ excavators, however it must be noted that another contractor carried out works in the tunnel in advance of J.__ works package. As discussed on the engineering meeting on 08/04/2014, we propose no remedial action and use as is.
| 01CV - Civils | Cxxx-NCR-001527 | NCR | 7.5 - Head House Shaft Repairs, R26 concrete pour level below top of breakout |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2014-05-31 | 2014-05-29 10:12 | -2 | 2014-05-01 08:44 | Civil - Civil Engineering General | 700 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Please refer to the attached report Cxxx-OVE-C4-RGN-CR146_WS158-50012 & attached repair location sketch. The concrete in Repair breakouts R26.11 & R26.33 were not poured fully in the breakout void. The top of concrete finishes is approx. 10mm from top of breakout. The roof of the breakout is sloped, therefore the void is only at the face with varying depths, up to 30mm. Please refer to attached sketch for the extent and further information.
| 01CV - Civils | Cxxx-NCR-001528 | NCR | 5.4 IR East tunnel - Protruding tie bars |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2014-06-11 | 2014-05-09 14:08 | -33 | 2014-04-30 09:33 | Civil - Tunnelling | 600 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Formwork tie bars have been observed to be permanently cast into the structure, these cannot be removed. Refer to Attachment 1 for details. Based on the response to Cxxx-NCR-001517 for the same problem in the West tunnel, we propose to saw cut (square 100mmx100mm centred on the tie bar) around the cast-in tie bar, break back approximately 50mm and cut back the bar. We propose to then make good to this area with __ S as per approved method statement Cxxx-VIN-C-GMS-CR146_ST003-50236. To ensure that the remedial material is wedged in place, we propose to incline the cut edge 5mm-10mm over the 50mm depth.
| 01CV - Civils | Cxxx-NCR-001529 | NCR | 5.4 IR Additional 26m East Tunnel - Concrete shrinkage and Grout loss |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2014-06-17 | 2014-05-16 14:24 | -32 | 2014-05-06 10:14 | Civil - Tunnelling | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | During post-pour (pre-repair) inspections in the Additional 26m East tunnel it has been noticed that on the walls there are small areas of grout loss and concrete shrinkages. Based on the response to Cxxx-NCR-001506 for the same problem in the West tunnel : The affected areas have been scabbled back and any loose/weak material has been removed and the sound surface has been achieved. The investigation to see how deep these defects are has been carried out. Refer to 'NCR 1529 Attachment 1' for photos of investigative works and signed IR 5609. The investigation has proved that the depth of the defects does not extend beyond 20mm. We propose to make good in accordance with the agreed method statement using __ __ S for these affected areas, as the investigation had proved that the defects do not extend beyond 20mm.
| 01CV - Civils | Cxxx-NCR-001530 | NCR | 5.4 IR Additional 26m East tunnel - Protruding tie bars |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2014-06-11 | 2014-05-12 09:29 | -30 | 2014-04-30 14:48 | Civil - Tunnelling | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Formwork tie bars have been observed to be permanently cast into the structure, these cannot be removed. Refer to Attachment 1 for details. Based on the response to Cxxx-NCR-001517 for the same problem in the West tunnel, we propose to saw cut (square 100mmx100mm centred on the tie bar) around the cast-in tie bar, break back approximately 50mm and cut back the bar. We propose to then make good to this area with __ S as per approved method statement Cxxx-VIN-C-GMS-CR146_ST003-50236. To ensure that the remedial material is wedged in place, we propose to incline the cut edge 5mm-10mm over the 50mm depth.
| 01CV - Civils | Cxxx-NCR-001531 | NCR | Crack Repair Trials-No curing agent used |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2014-06-26 | 2014-06-26 15:52 | 0 | 2014-05-01 14:58 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | A number of the trial repairs (D358, D361, D365, D369, D380, D391 & D392) have been finished with the Weber HB40 without using a curing agent.
| 01CV - Civils | Cxxx-NCR-001532 | NCR | 5.3 Invert Reprofiling missed witness point and method statement ommision |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2014-05-31 | 2014-05-15 17:12 | -16 | 2014-05-01 16:10 | Civil - Civil Engineering General | 1000 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | Following a review of the method statement for invert reprofiling to improve the methodology and include breaking, the decision was made to revert to the original method. In making this decision, the addition of the requirement to control the line of the removal (distance from track centreline to 'critical step') was missed. The original method statement detailed level control but not line as the line was to be installed by saw cutting further into the step. When the work commenced in line with this method statement it was also done so without the required IRF being submitted for the witness point of reprofiling.
| 01CV - Civils | Cxxx-NCR-001533 | NCR | 5.2 Procedural NCR |  | Contr | TWC | CON - Connaught Tunnel (East) |  | 2014-07-03 | 2014-07-09 15:02 | 6 | 2014-05-12 16:54 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | During the crack repair trials, all repairs were meant to have been booked with IR's at each step of the ITP. A number of the repairs were undertaken without booking inspections or inviting ICI or CRL inspectors to witness the repair.
| 01CV - Civils | Cxxx-NCR-001534 | NCR | 3.3 & 2.4 F3 Wall Finish |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2015-01-15 | 2015-01-16 16:06 | 1 | 2014-05-13 15:14 | Civil - Civil Engineering General | 3000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Post Pour inspection IR5472 (please see attached) Inspection of F3 wall finish bay E7-E11 & E13-E15 failed due to non compliance with KF10.3229 g) & h) It has been observed that an F3 finish has not been achieved due to the following issues: 1. Blemishes present throughout 2. Staining on a number of panels 3. Panel marks in a number of locations 4. Cover blocks grinning through concrete 5. Tie holes not equally spaced NOTE: FCD 868 - Change of finish from F3 to F4 finish
| 01CV - Civils | Cxxx-NCR-001535 | NCR | 2.2 Failure to follow process |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2014-06-06 | 2014-05-30 15:09 | -7 | 2014-05-16 09:24 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | In the engineering meeting held on 08/04/14 between CRL, designers and __, it was discussed and agreed that mas concrete is acceptable for remedial works of pile numbers 306 A, 306 B and 306E. This has not been formalised afterwards through FCD/RFI. The remedial works are completed for these piles with mass concrete based on the agreement in the engineering meeting. Approximate dimensions of the concrete surround around each pile is about 800 mm X 800mm (detailed measurements to follow for each of the three piles).
| 01CV - Civils | Cxxx-NCR-001536 | NCR | 5.3 Breaking-out within the critical step |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2014-07-10 | 2014-06-16 11:06 | -24 | 2014-05-29 12:13 | Civil - Tunnelling | 1000 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | ITP Cxxx-VIN-C-ITP-CR146_ST003-50111 requires to control the line of the removal (distance from track centreline to 'critical step'). During the installation of brackets for the track saw in West single tunnel -Westbound wall, the 'critical step' has been partly broken-out in 7 places. Refer to the Attachment 1 for details and photos. The dimension of break-outs varries from 50mmx150mm to 150mmx200mm. Location of the break-outs : 1 - westbound chainage 17977 m 2 - westbound chainage 17979 m 3 - westbound chainage 17981 m 4 - westbound chainage 17983 m 5 - westbound chainage 17985 m 6 - westbound chainage 17987 m 7 - westbound chainage 17989 m We propose to use as is.
| 01CV - Civils | Cxxx-NCR-001537 | NCR | Cover Bay 12 slab |  | Crossrail | XRL | CON - Connaught Tunnel (East) |  | 2015-01-15 | 2015-01-15 10:52 | 0 | 2014-06-09 11:11 | Civil - Civil Engineering General | 700 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | During the removal of the black top on bay 12 slab with a road plainer, there is evidence that the concrete layer has been plained away leaving potential low cover to the reinforcement in numerous areas of the concrete slab
| 01CV - Civils | Cxxx-NCR-001538 | NCR | 2.4 East Approach Ramp CFA pile reinforcement trim level |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2014-07-31 | 2014-07-23 09:01 | -8 | 2014-06-11 16:47 | Civil - Civil Engineering General | 1500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | 4No rows of CFA piles in the East Approach Ramp have been broken down previously to allow for access into the tunnel. The 20mm steel reinforcement for these piles was also cut off to a similar level meaning that there is currently insufficient length to lap into the slab of bay E1 as per the design drawings (Cxxx-OVE-C4-DDA-CR001_Z-31128). Please see attached pictures for clarity
| 01CV - Civils | Cxxx-NCR-001539 | NCR | 5.2 Missed 4.5 post repair inspection (Trials) |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2014-07-31 | 2014-07-31 08:26 | 0 | 2014-06-12 09:44 | Civil - Civil Engineering General | 500 |  | Testing and Commissioning | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | Due to misinterpretation of ITP the post repair inspection was missed for the trial repairs but sprayed concrete continued on other repairs outside of the trial.
| 01CV - Civils | Cxxx-NCR-001541 | NCR | 5.3 Saw-cutting within the critical step |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2014-07-31 | 2014-07-01 08:57 | -30 | 2014-06-14 13:17 | Civil - Tunnelling | 1000 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | During the post-sawcut survey of ‘Cut line 2’ (top face of the critical step) in the West and East single tunnel has been discovered to be re-profiled out of the tolerance. Refer to attachment 'NCR 1541 - Cutline 2 - Survey' for details. The setting-out of 'Cut line 2' has been checked by __ engineers during the Setting-out inspection prior the saw-cutting, as per Cxxx-VIN-C-ITP-CR146_ST003-50111. All marks have been found within the tolerance. Refer to attachment 'NCR 1541 - Cutline 2 - Setting-out' for details. These defects have been recorded in attached 'Record of intrusions into critical invert corner'. We propose use as is.
| 01CV - Civils | Cxxx-NCR-001542 | NCR | 2.3 Temporary works submission |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2014-10-05 | 2014-09-02 14:43 | -33 | 2014-06-19 14:48 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Other management problem | Completed |  | Temporary works design 118 for mobile crane stability check (Cxxx-VIN-C-DWG-CR146_ST003-50380) was not submitted for acceptance prior to commencement of works on site.
| 01CV - Civils | Cxxx-NCR-001543 | NCR | 2.3 Approach Ramp excavation (temporary works) |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2014-08-18 | 2014-07-21 11:46 | -28 | 2014-06-19 16:40 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | During excavation of bay E1, the formation was excavated excessively beyond the subsequent prop location prior to the prop being installed contrary to the temporary works sequence. This meant that an excessive area was left unsupported.
| 01CV - Civils | Cxxx-NCR-001546 | NCR | 7.5 Repairs to defects not in the scope of works |  | Contr | TWC | CON - Connaught Tunnel (East) |  | 2014-10-12 | 2014-10-08 15:28 | -4 | 2014-06-20 11:33 | Civil - Civil Engineering General | 1000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | A number of Defects in the Head House Shaft have been Prepared (Saw cut and broken back) for repair which weren’t on their revised scope of works to do. These include; Defect 1 - 200mm x 200mm Damaged render Defect 8-11 - 50mm Damp spot Defect 15 - 100mm x 100mm Damaged render
| 01CV - Civils | Cxxx-NCR-001547 | NCR | 7.5 - Breakout of Padstone concrete |  | Contr | TWC | CON - Connaught Tunnel (East) |  | 2014-08-31 | 2014-08-08 11:20 | -23 | 2014-06-23 16:34 | Civil - Civil Engineering General | 600 |  | Damaged | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The removal of the ladder rungs in the Head House Shaft has been done by breaking using hand-mechanical means, as per MS 50296. During this 2 padstones have been damaged. Please see the attached photographs fo the extend of the damage. Padstones level -2, No. 6 & 7 are damaged.
| 01CV - Civils | Cxxx-NCR-001549 | NCR | 1.8 - Bay W7A slab out of tolerance |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2014-08-06 | 2014-07-18 15:12 | -19 | 2014-06-26 16:08 | Civil - Civil Engineering General | 6000 |  | Incorrect Installation | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Other | Completed |  | During a post pour survey, it has been found that the end of surface rail slab W7a on the Western approach ramp is out of tolerance (approximately 3-4m long section at the east end of the bay up to a maximum of 68mm from design level). The design tolerance is 25mm. In addition, the bay W8 blinding has been tied into the end of W7a and is out of tolerance by a similar amount.
| 01CV - Civils | Cxxx-NCR-001550 | NCR | 5.2 Repairs to defects not in the scope of works |  | Contr | TWC | CON - Connaught Tunnel (East) |  | 2014-08-28 | 2014-08-29 16:40 | 1 | 2014-08-14 15:54 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | A number of Defects on the Approach ramps have been prepared (Saw cut and broken back) for repair which weren’t on their revised scope of works to do. These include: D1401 – crack on East ramp, South wall D270 – East ramp, South wall – Void near tunnel entrance defective concrete removed (Unsure on how much was removed or what the size of the void was before) D494 – Saw cut larger area than was provided in the schedule (West ramp, North wall) D510 – Saw cut vegetation area instead of jet washing (West ramp, North wall)
| 01CV - Civils | Cxxx-NCR-001551 | NCR | Failure to follow the IR procedure |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2014-07-15 | 2014-07-03 15:28 | -12 | 2014-07-01 13:20 | Civil - Tunnelling | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | 5no of 'Notification of Inspection Request' have been issued to Crossrail. However, only 3no of these have been signed by CRL prior the inspections. This fact has not been spotted by __ engineer responsible for these IRs, therefore technically CRL has been not invited for inspections. This failure to follow IR procedure caused to failed inspections.
| 01CV - Civils | Cxxx-NCR-001552 | NCR | 7.4 - Incorrect size bars used in draw pit DP01 wall |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2014-08-01 | 2014-08-01 13:23 | 0 | 2014-07-01 14:31 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The base of draw pit DP01 has been cast with a number of B10 starter bars in wall 4 where B12 bars are specified. Wall 4 has been cast with 17 No. B10 bars on the outside face of the wall (including 2 No. bars that are part of the adjoining wall), and 11 No. B10 & 6 No. B12 bars on the inside face of the wall (including 2 No. bars that are part of the adjoining wall).
| 01CV - Civils | Cxxx-NCR-001553 | NCR | 7.4 - Incorrect Spacing of Draw Pit Starter Bars |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2014-08-01 | 2014-08-01 13:23 | 0 | 2014-07-01 14:41 | Civil - Civil Engineering General | 750 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The bases of draw pits DP01 and DP02 have been poured with the starter bars at 150mm spacing on all 4 No. walls. The base of draw pit DP04 has been also been fixed with starter bars at 150mm spacing on all 4 No. walls, however this base has not yet been poured. On walls with ducts in the reinforcement should be spaced at 300mm centres with each bar between the ducts doubled up in order to maintain the required volume of steel. As per reinforcement detailing referenced below.
| 01CV - Civils | Cxxx-NCR-001555 | NCR | 3.3 - E12 Wall Shutter Failure |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2014-09-26 | 2014-09-02 15:47 | -24 | 2014-07-03 13:36 | Civil - Civil Engineering General | 2000 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | On striking the shutters to the North Wall A on Bay E12 it was found that the bottom of the shutter had move at one end of the wall causing the outside face of the wall to be 30mm out of alignment (30mm wider). It was decided by __ that the remedial action was to break out this section of the wall, this decision was made without consultation with Crossrail.
| 01CV - Civils | Cxxx-NCR-001556 | NCR | 1.8 Blinding levels in East Approach Ramp |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2014-10-02 | 2014-09-02 15:53 | -30 | 2014-07-04 15:50 | Civil - Civil Engineering General | 1000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Several areas of bay E1 have been identified as having blinding levels out of tolerance (± 25mm). One area has been identified as being 35mm high, several areas have been found to be around 40mm low.
| 01CV - Civils | Cxxx-NCR-001557 | NCR | 2.7 East approach ramp CFA pile reinforcement damage |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2014-08-27 | 2014-07-23 08:56 | -35 | 2014-07-09 17:33 | Civil - Civil Engineering General | 600 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Following pile breakdown in the East Approach Ramp, several reinforcing bars for the CFA piles have been damaged during the pile cropping operation (i.e snapped below cut level/ excessively kinked). It will therefore not be possible to crank these bars into the slab as per design. There are approximately 7No reinforcing bars that have sheared off too low or have been bent to a degree that may make cranking the bars impossible. Please see attached photos for clarity
| 01CV - Civils | Cxxx-NCR-001558 | NCR | 5.4 - 28 Day Cube Result For E7 Slab |  | Contr | TWC | CON - Connaught Tunnel (East) |  | 2014-08-20 | 2014-07-21 11:16 | -30 | 2014-07-09 18:34 | Civil - Civil Engineering General | 500 |  | Testing and Commissioning | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | In KF10 - Insitu Concrete (Cxxx- OVE-Z4-RSP-CR001-00023) Section KF10.2205a it states 'One set of test specimens shall be prepared from the sample and shall be cured for 28 days. A set of samples shall comprise at least two cubes for testing at 28 days.' The Single Tunnel Invert Replacement ITP Cxxx-VIN-C-ITP-CR146_ST003-50086 Inspection Number 3.14 also communicates this as it requests 2no 28day cubes every 50m3 (or 2no 28day cubes each pour if less then 50m3). Due to communication break down between J__s and __, E7 Slab Pour only has one 28 day cube result This incedent happened at the same time as W1 Walls, W5 Walls and W6 walls in the west single tunnel (NCR1509) but it has only been highlighted now that E7 Slab is missing a 28 cube result Bay E7 Slab (18.5m3) only has 1 28 day results due to miscommunication between J__ and __. The results have gained the required 40N/mm2 earlier than 28 days, as shown in attached Concrete test cube results. The 11 day cube reached 40.2N/mm2 The one 28 day cube result we have reached 51.2N/mm2 The 56 day cube reached 62.6N/mm2
| 01CV - Civils | Cxxx-NCR-001559 | NCR | 5.3 Re-profiling - Trimming below design SEL |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2014-10-19 | 2014-09-11 10:29 | -38 | 2014-07-11 11:48 | Civil - Tunnelling | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The last stage of wall re-profiling requires trimming to the design SEL by using a small hand held breaker such a __ TE80 or similar as per method statement Cxxx-VIN-C-GMS-CR146_ST003-50292. Operatives are briefed on daily basis on scope of the works, methods and tools to be used. These instructions are followed. However, the breaker __ TE3000 has been used to trim the final stage in approx. 10m long section in the East single tunnel and West approach ramp. This breaker produce lower hand-arm vibration magnitude then smaller __ TE80, but it is more difficult to control the depth of trimming/breaking. This caused to localize over broken areas. Please note that offset line to control the depth of trimming has been clearly marked. Please note that only small local areas have been over broken under the design SEL and that none of these areas are within the 'critical step'. The depth of over breaking varies from -2mm to -96mm. Refer to attachment 'NCR 1559 - Survey 2' for details. Please note that the original survey (NCR 1559 - Survey) has been superseded due to typos.
| 01CV - Civils | Cxxx-NCR-001560 | NCR | 1.8 Bay W8 slab levels |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2014-10-13 | 2014-09-02 15:54 | -41 | 2014-07-15 08:32 | Civil - Civil Engineering General | 1000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | During checks carried out on W7A slab it was discovered that the finished level of W8 slab too low and out of tolerance (± 25mm). This error exists over the width of the slab and approx. 1m length from the movement joint, please see survey attached. A cover survey has been carried out and shows that insufficient cover has been achieved in this area.
| 01CV - Civils | Cxxx-NCR-001561 | NCR | 2.4 Bay E3 South wall post pour inspection |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2014-08-29 | 2014-07-23 08:57 | -37 | 2014-07-17 09:23 | Civil - Civil Engineering General | 500 |  | Planning | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | Waterproofing has been applied to the outside face of the South wall in bay E3 prior to the post pour inspection being carried out. The inspection point has therefore been missed.
| 01CV - Civils | Cxxx-NCR-001562 | NCR | 5.4 - Not enough cylinders taken for Bay E2 |  | Contr | TWC | CON - Connaught Tunnel (East) |  | 2014-10-30 | 2014-09-04 09:26 | -56 | 2014-07-24 17:12 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | In KF10.2205 clause g) it requires the testing of concrete to check the modulus of elasticity and the co-efficient of thermal expansion. This is also communicated in NCR 1367 to take 3 cylinders from 3 different batches each time the structural concrete is changed for both the Determination of Thermal Expansion Coefficient and the Determination of Static Modulus Elasticity. Due to a comunication breakdown within __ on 1 of the batches for E2 walls on 3rd December only 1 cylinder for both tests ware taken but cylinders were also taken for the 2nd of December for E3 Walls and the 4th December for E4 Slab which each had 3 cylinders for both tests The structural concrete changed once again after this in March which again was to take 3 cylinders from 3 batches which was achieved. These bays were W13 Walls, E24 Walls and E16 Slab. Please see attached __ and Technology center results and table of results for comparison
| 01CV - Civils | Cxxx-NCR-001563 | NCR | 5.4 Missing Documentation |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2014-10-05 | 2014-08-27 12:03 | -39 | 2014-07-30 09:40 | Civil - Tunnelling | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | Inspection and Test Plan Cxxx-VIN-O4-RGN-CR146_ST003-50203 (Invert Replacement Trail Bays 1 & 2) requires Excavation and Concrete Inspection Check Sheets (CICS), Concrete Pour Record Sheets (CPRS) and Concrete Delivery Tickets (C__) to be completed and presented as deliverable items for this work. A number of these checksheets have been misplaced, and a number of delivery tickets are not clearly legible. The following is a summary of the missing documents: - CICS and CPRS for Blinding - CICS for Invert Slabs and Walls The following concrete delivery tickets are also not clearly legible: - C__ 7030933 & 7030948 for Walls - C__ 7030740, 7030750, 7030760 & 7030770 for Invert Slabs The supplier of this concrete has gone into receivership since the original tickets were issued. Several attemps have been made to locate better, more legible copies of the tickets from this supplier, but with no success. Copies of these documents are attached to this NCR for your review.
| 01CV - Civils | Cxxx-NCR-001564 | NCR | 7.4 - Draw Pit DP02 North Wall Duct Centres |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2014-10-30 | 2014-09-04 09:28 | -56 | 2014-08-07 08:43 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The ducts passing through the North wall of draw pit DP02 towards DP01 have been cast in out of position. Attached is a sketch showing the as-built positions of the ducts in Wall 1 of DP02 with as-built duct centres shown. The middle row of ducts are up to 90mm lower than the design meaning the duct centres below are reduced and above are increased.
| 01CV - Civils | Cxxx-NCR-001565 | NCR | 1.4 W7 wall height |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2014-11-19 | 2014-09-04 16:30 | -76 | 2014-08-12 14:36 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | In the West surface rail it has been discovered that a section of the wall has been cast with a step of approx. 10mm where the chamfer of one wall section wall fixed at the incorrect level. The section of wall adjacent to it was cast to the correct level hence leaving a step between the pours. This deviation is within the tolerance for wall levels however a visible step is present.
| 01CV - Civils | Cxxx-NCR-001566 | NCR | 7.5 - Damage to dismantling joint |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2014-10-31 | 2014-10-08 14:21 | -23 | 2014-08-15 15:00 | Civil - Civil Engineering General | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Please refer to the attached photos, email and RFI 912. The viking johnson dismantling joint, which will be used at the micro tunnel eye in the shaft, has been damaged before installation. The black rislan protective coating has been scratched off in 1 location.
| 01CV - Civils | Cxxx-NCR-001567 | NCR | 1.4 & 2.4 - Mastic Joint Leakage |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2015-01-15 | 2015-01-15 09:09 | 0 | 2014-08-15 16:10 | Civil - Civil Engineering General | 800 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Mastic joints installed in the surface rail wall joints have been found to be leaking in a number of isolated locations. A white paste appears to be leaking out of cracks in the mastic. Following a survey carried out with Fastglobe, approximately 10 No. locations of white paste leaking from the mastic joints have been found. Attached are photos of examples of the white material leaking and an area where a sample was cut out of the mastic joint.
| 01CV - Civils | Cxxx-NCR-001568 | NCR | 1.4 & 2.4 - Mastic Joints Cracking |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2014-12-12 | 2014-12-10 11:52 | -2 | 2014-08-15 16:35 | Civil - Civil Engineering General | 500 |  | Design | Repair | 4 (0.5-3k) | Complete | External Phenomenon - Other | Completed |  | Mastic joints installed in the surface rail wall joints have been found to be cracking in many locations. In the majority of locations the mastic is firm and appears to have been installed correctly. Attached are photos of examples of the cracks seen in the mastic joints .
| 01CV - Civils | Cxxx-NCR-001569 | NCR | Integrity Tests were not carried out on four piles in OHLE mast 41 |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2014-11-19 | 2014-09-15 16:22 | -65 | 2014-08-20 11:29 | Civil - Civil Engineering General | 500 |  | System Defect | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | Integrity Tests were not carried out on four piles in OHLE mast 41
| 01CV - Civils | Cxxx-NCR-001570 | NCR | 5.3 Re-profiling - Cutting out of tolerance |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2014-10-28 | 2014-09-18 15:33 | -40 | 2014-09-16 09:29 | Civil - Tunnelling | 0 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The tolerance for vertical cut line 1 (Dimension A) is +/- 25mm. There are sections in East approach ramp (both Eastbound and Westbound wall), where the post saw-cut survey shown localized areas out of tolerance. Refer to attached survey. We propose to use as is.
| 01CV - Civils | Cxxx-NCR-001571 | NCR | 5.3 Re-profiling - West tunnel - Cutting above the design level |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2014-11-19 | 2014-09-11 10:34 | -69 | 2014-08-27 17:56 | Civil - Tunnelling | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Refer to attached copy of the as built level survey of "cut line 2" which is the horizontal cut line on the top of the 'critical step'. Points in purple are outside of the +25mm tolerance (too high). Given that the cut line is so close to tolerance, there is not enough to get a saw back in, any remaining work would have to be hand broken which would have a greater chance of getting over broken the 'critical step'. We propose use as is.
| 01CV - Civils | Cxxx-NCR-001572 | NCR | 5.3 Re-profiling - West tunnel - Cutting below the design level |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2014-11-26 | 2014-09-04 09:32 | -83 | 2014-08-27 17:55 | Civil - Tunnelling | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Refer to attached copy of the as built level survey of "cut line 2" which is the horizontal cut line on the top of the 'critical step'. Points in red are outside of the -0mm tolerance (too low). We propose use as is.
| 01CV - Civils | Cxxx-NCR-001573 | NCR | 2.4 Damage to slab movement joint E3/ E4 |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2014-12-01 | 2014-12-02 09:00 | 1 | 2014-09-02 09:40 | Civil - Civil Engineering General | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Following completion of the E3 and E4 slabs, it has been found that a corner of concrete at the movement joint has cracked off. Please see pictures attached for details. It is noted that no reinforcement has been exposed within the damaged section.
| 01CV - Civils | Cxxx-NCR-001574 | NCR | 6.1 - Leakage in RC central box above the axis (ref. Cxxx-PWK-00019) |  | Crossrail | XRL | CON - Connaught Tunnel (East) |  | 2015-06-20 | 2016-11-18 12:51 | 517 | 2014-09-03 10:06 | Civil - Civil Engineering General | 20000 |  | Incomplete Works | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Other | Completed |  | KT10.1301 states: i) For tunnels containing track, the area above axis shall be free from all leakage seepage and damp patches and shall comply with the requirements of BS 8102 Table 1; grade 3. A survey has been carried out and recorded in Cxxx-VIN-C-RGN-CR146_ST003-53601 which shows the the constructed works do not comply with this cluase.
| 01CV - Civils | Cxxx-NCR-001575 | NCR | Leaking in-tunnel wellpoints |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2015-02-28 | 2015-03-03 13:46 | 3 | 2014-09-15 08:10 | Civil - Tunnelling | 2000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | During wall re-profiling in the East and West single tunnel has been discovered 4no of leaking core holes. This is due to insufficient grouting. We propose to repair these leakages as per approved method statement number Cxxx-VIN-C-GMS-CR146_ST003-50089, point '9.5 PROCEDURE FOR REPAIR OF LEAKING CORE HOLES (PREVIOUSLY GROUTED)' : • A 152 mm core hole will be drilled over the existing 90 mm grouted hole to a depth of 250 mm below the existing brick level (covered under previous RAMS for coring works) • The core will be broken out. Any existing pipework within the cored hole will be broken out to a depth of 250 mm. • A 150 mm mechanical packer (drain stopper) will be placed to the base of the cored hole. The packer will be expanded using a socket and ratchet until the core is sealed. • A 50 mm layer of bentonite pellets will be placed over the packer and allowed to hydrate for at least 1 hour. This will form a non-shrinking seal and protect the rubber packer from direct contact with cement grout. • Any standing water within the removed cored hole will be removed and a check carried out to ensure no accumulation of water. • Several 10 mm angled key holes will be drilled into the brick to a depth of up 25 mm in the remaining cored hole using a SDS cordless hand drill. This will provide a mechanical key for the final grout plug. • A grout will be mixed using OPC cement with a __-4a admixture as per the manufactures instructions. This will be placed in the remainder of the cored hole and finished flush with existing surface with a minimum depth of 100 mm.
| 01CV - Civils | Cxxx-NCR-001576 | NCR | 6.1 - Leakage in RC central box below the axis (ref. Cxxx-PWK-00018) |  | Crossrail | XRL | CON - Connaught Tunnel (East) |  | 2015-03-31 | 2015-02-25 13:27 | -34 | 2014-09-23 17:32 | Civil - Civil Engineering General | 4000 |  | Incomplete Works | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Other | Completed |  | KT10.1301 states: ii) For tunnels containing track, leakage from the area below axis shall be limited to damp patches and minor weeping of joints. The average level of water ingress in any drainage section shall be less than 0.12 litres/ day/m², except that within any 10m length, ingress of 0.24litres/ day/ m² shall be permitted from any separate square metre. A survey has been carried out and recorded in Cxxx-VIN-C-RGN-CR146_ST003-53636 which shows that 4 no. locations produce leakage which is above the specified allowance.
| 01CV - Civils | Cxxx-NCR-001577 | NCR | 5.3 Re-profiling - Cut line 1 out of tolerance |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2014-11-07 | 2014-10-09 15:54 | -29 | 2014-09-26 12:25 | Civil - Tunnelling | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Post saw-cut survey of Eastbound wall Cut line 1 in East approach ramp shows small (approx. 3.0m x 0.5m) area out of the tolerance +25mm/-25mm. Refer to attached survey for details. We propose to trim this are to achieve design position within tolerance +25mm/-25mm.
| 01CV - Civils | Cxxx-NCR-001579 | NCR | 1.8 Covers over weep holes |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2014-11-03 | 2014-10-27 12:21 | -7 | 2014-10-17 15:10 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Comment to IR 6907 from 02/10/2014 states that the weep hole is to be covered straight after the installation. See attached. On 09/10/2014 has been highlighted by CRL that the covers are placed over weep holes but not fixed to the slab and therefore likely to be knocked from their position by passing operatives or plant. This could cause to trip&slip hazard as the diameter of weep hole is approx. 250mm and depth approx. 400mm. The defect has been rectified the same day, all covers have been fixed to the slab, task briefing sheet has been updated and operatives briefed. See attached IR 6913 and task briefing sheet. Location of weepholes : West approach ramp Number of weepholes : approx. 20 (please note that weepholes have been covered as mentioned in IR, but not screwed down to the slab) Condition of the weep holes : two numbers weep holes have been found with a small amount of debris. All these would have been cleared as a part of ITP requirements prior to grouting. These two holes have been cleared immediately on 09/10/2014 prior to fixing covers. Please note that weep holes installation has been completed. Grouting works will be carried out as per ITP.
| 01CV - Civils | Cxxx-NCR-001580 | NCR | 1.4 Damage to Buttress 14b - West Surface Rail |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2014-12-22 | 2014-12-05 08:25 | -17 | 2014-10-23 08:29 | Civil - Civil Engineering General | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | External Phenomenon - Other | Completed |  | It has been observed that a buttress on the West Surface Rail (buttress 14b) has been damaged. Concrete has chipped off one of the vertical edges but no reinforcement has been exposed. Please see attached pictures for clarity.
| 01CV - Civils | Cxxx-NCR-001581 | NCR | 2.4 & 3.3 - Cover to Factory Road Wall |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2014-12-01 | 2014-11-12 08:18 | -19 | 2014-10-24 09:13 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Following a cover meter survey of Factory Road "F3" wall the maximum and minimum cover has been found to be outside the design requirement of 55mm +6mm/-0mm. The cover meter survey was carried out at 10m c/c along the top and middle of the wall (staggered to provide a reading every 5m), as requested. The attached results show the maximum cover to be 68mm and the minimum cover to be 50mm. Giving a maximum of +13mm and -5mm.
| 01CV - Civils | Cxxx-NCR-001582 | NCR | 1.8 Weep holes - Deviation from design |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2015-01-15 | 2014-12-05 14:41 | -41 | 2014-10-27 11:59 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Cxxx-FCD-001360 and ITP Cxxx-VIN-C-ITP-CR146_ST003-50131 stays that the glued double socket is to remain open ended and temporarily plugged with plywood. Instead of glued double socket an extension with thread connection has bee used, remain open ended and temporarily plugged with a plastic cap. Refer to attached Cxxx-NCR-001582 Sketch and Photos. This change of design has been carried out without an FCD in place. We propose use as is.
| 01CV - Civils | Cxxx-NCR-001585 | NCR | 1.4 - West Surface Rail holding down bolts (No.7) position |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2015-02-28 | 2015-01-29 08:13 | -30 | 2014-11-10 12:21 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Following receipt of as-built information for OLE assembly No.7 in bay W3, it has been identified that the bolt assembly is out of position by approx. 40mm. The bolt assembly is in-line with the track centre line as per design however the assembly along with buttress has been constructed approx. 40mm Eastwards. Please see attached sketch showing as-built details for clarity.
| 01CV - Civils | Cxxx-NCR-001586 | NCR | 1.4 - Track slab cover to reinforcement |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2014-12-19 | 2014-11-17 12:11 | -32 | 2014-11-10 12:39 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Further to the cover surveys carried out on the West Surface Rail it has been observed that cover is between 53 and 62mm therefore Max. 2mm outside of the tolerance (55 - 61mm). Please see attached surveys for bays W4 - W7 for clarity.
| 01CV - Civils | Cxxx-NCR-001587 | NCR | 1.5 - Incorrect Alignment of Interclamp Fence on East Wall |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2014-12-18 | 2014-12-19 13:32 | 1 | 2014-11-13 15:04 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | As per the attached sketch, approximately 2/3 the length of interclamp handrail on the East Ramp (bays E3-E5) on the south wall has been installed centrally. It cannot be installed with the centre of the handrail offset 170mm from the inside of the wall (as per dwg. Cxxx-OVE-R4-DDB-CR001_Z-72779) due to a clash with steel when drilling for the hold down bolts.
| 01CV - Civils | Cxxx-NCR-001589 | NCR | 7.4 Bellmouth Chamber |  | Contr | TWC | CON - Connaught Tunnel (East) |  | 2015-02-28 | 2015-02-24 10:34 | -4 | 2014-11-27 16:52 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Personnel Error - Inattention to detail | Completed |  | In Drawing Cxxx-OVE-D-DDD-CR001_Z-53220 entering the Bellmouth chamber is a drainage pipe 110mm wide, detailed further by Sketch Cxxx-SK-0176. The walls of the Bellmouth Chamber were poured without the box out for this 110 drainage pipe so there is no opening for it.
| 01CV - Civils | Cxxx-NCR-001590 | NCR | 5.2 Use of a non approved product for Arch Waterproofing |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2014-12-03 | 2014-12-03 10:14 | 0 | 2014-12-01 18:10 | Civil - Civil Engineering General | 0 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Lack or improper material identification and traceability | Completed |  | Metaset Rapid hardening repair mortar was accidently omitted from MCR Cxxx-VIN-C-RSP-CR146_ST003-50388. As it was included in the ITP and Method Statement, the product was used by the sub-contractor to repair arch 11 on the Eastern Approach Ramp.
| 01CV - Civils | Cxxx-NCR-001591 | NCR | De-bonding of mastic on concrete movement joints |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2015-02-28 | 2015-01-21 16:58 | -38 | 2014-12-01 17:35 | Civil - Civil Engineering General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | De-bonding has been observed between the mastic sealant and the concrete on a number of concrete movement joints.
| 01CV - Civils | Cxxx-NCR-001592 | NCR | Water ingress into surface rail UTXs |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2015-03-31 | 2015-04-02 15:23 | 2 | 2014-12-02 14:24 | Civil - Civil Engineering General | 10000 |  | Incorrect Installation | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Other | Completed |  | During a joint site visit with Crossrail and Cxxx, it was noticed that there was water ingress in one of the under track crossings (UTX) on the East surface rail.
| 01CV - Civils | Cxxx-NCR-001593 | NCR | 3.3 Bay E15 slab cracks |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2015-02-28 | 2015-01-16 16:12 | -43 | 2014-12-04 14:53 | Civil - Civil Engineering General | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Following a site walkthrough with Crossrail, a number of cracks have been identified on the track slab of bay E15.
| 01CV - Civils | Cxxx-NCR-001594 | NCR | 5.2 Process Failure on Arch Waterproofing |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2015-01-08 | 2015-01-07 10:40 | -1 | 2014-12-09 11:20 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Upon conducting an inspection (IR7204) of an Adhesion test of the arch substrate, the sub-contractor (Metrail) could not provide the calibration certificate at the time. Metrail continued to proceed with work at risk, knowing that the IR was to be verified by this certificate. Further testing had also been carried out with a Holiday (Spark) Test still with no certificates being readily available.
| 01CV - Civils | Cxxx-NCR-001595 | NCR | 1.5 - MH6A caisson construction - depth |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2015-01-15 | 2015-01-12 12:38 | -3 | 2014-12-14 12:30 | Civil - Civil Engineering General | 650 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The caisson being installed for the construction of MH6A has been sunk deeper than the design level provided. The bottom of the caisson rings was to be installed to around 99.1m ATD to suit the base slab level of 99.125m ATS (as per FCD 1356), however the caisson rings were sunk to a depth of 98.35m ATD. This has put the caisson rings into the gravel layer, causing significant water ingress. This means that the rings can no longer be undermined to form the base slab as per drawing Cxxx-OVE-R4-DDB-CR001_Z-72777 C03.
| 01CV - Civils | Cxxx-NCR-001596 | NCR | 2.4, 3.3 - Coping Stones - Mortar strenght not reached |  | Contr | TWC | CON - Connaught Tunnel (East) |  | 2015-02-26 | 2015-01-28 14:09 | -29 | 2015-01-22 16:06 | Civil - Civil Engineering General | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Regarding the mortar agreed in MCR Cxxx-VIN-C-RSP-CR146_ST003-50452 and alternate installation in FCD 1352. The agreed M12 __ mortar was to reach a compressive strength of 12N/mm2 after 28 days. After cube testing it was found that the 28 day cubes had a compressive strength of 11.25N/mm2 and 11.1N/mm2 giving an average Compressive strength of 11.175N/mm2 which is below the agreed allowable strength. The 56 day cube has been crushed and the compressive strength is 12.2N/mm2 which is over the 12N/mm
| 01CV - Civils | Cxxx-NCR-001597 | NCR | 5.3 Wall Re-profiling - Insufficient number of cubes |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2015-02-19 | 2015-02-20 08:34 | 1 | 2015-02-05 11:46 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The ITP 'Wall re-profiling' Cxxx-VIN-C-ITP-CR146_ST003-50111 states in section 12 'Testing TamCrete 40HB' that 1 set of 4 cubes is to be taken for testing purposes. Due to communication break down, only 2no cubes have been taken and tested. The average strength of 28 day cubes has exceeded characteristic strength 40N/mm. Please refer to attached test report. We propose use as is due to facts that : 1) This material has been use for making good to fix/core holes. This scope of works is not a critical structural work. 2) KF 10.2205 states that minimum 1 set of 2no 28 days cubes has to be taken for testing purposes. 3) The average strength of 28 day cubes has exceeded characteristic strength 40N/mm.
| 01CV - Civils | Cxxx-NCR-001598 | NCR | 7.4 Drawpits - 1 Concrete Cube made |  | Contr | TWC | CON - Connaught Tunnel (East) |  | 2015-03-03 | 2015-02-27 09:05 | -4 | 2015-02-17 15:35 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Refer to drawing Cxxx-OVE-S-DDL-CR001_1-22175 in the north Central on the Drawpit 3 Soffit Pour only 1 28 day cube was made In KF10.2205 a it states that a set of samples shall comprise of at least two cubes for testing at 28 days.
| 01CV - Civils | Cxxx-NCR-001599 | NCR | 7.4 Drawpit 4 - Base Slab Test Results |  | Contr | TWC | CON - Connaught Tunnel (East) |  | 2015-03-04 | 2015-02-27 09:03 | -5 | 2015-02-18 09:39 | Civil - Base Course | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Refer to Drawing Cxxx-OVE-S-DDL-CR001_1-22175 Drawpit 4 slab pour on 02/07/2014 has had no strength testing done on it.
| 01CV - Civils | Cxxx-NCR-001600 | NCR | 2.4 - Long Term Strength Testing |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2015-04-03 | 2015-03-24 11:56 | -10 | 2015-03-20 11:22 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Following completion of the Surface Rail concrete works, the long term strength gain report for concrete cubes has been compiled. It has been found that, although a greater number of long term results have been obtained, they have not provided at the frequency specified in KF10. Please see attached draft version of the report highlighting the results obtained and the intervals at which long term results should have been provided. It can be seen from the report that there are 284 concrete pours which therefore requires 29 sets of long term results however a total of 69 complete sets of long term results have been provided. The Yellow highlighted boxes indicate where long term results are missing or a full set of results has not been obtained. It should also be noted that none of the results provided are below specification.
| 01CV - Civils | Cxxx-NCR-001601 | NCR | 5.2 Process Failure of Drainage Pipework MCR |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2015-04-01 | 2015-03-26 19:20 | -6 | 2015-03-25 15:16 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Procedure Problem - Other | Completed |  | The pipework for the Vent Shaft and Bomb Damage Drainage System was installed prior to an approved MCR.
| 01CV - Civils | Cxxx-NCR-001602 | NCR | 2.5 Below Strength Cube Results |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2015-04-29 | 2015-04-02 10:41 | -27 | 2015-04-01 08:05 | Civil - Civil Engineering General | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The 28 Day Cube Strength for Pour W2 on The East Surface Rail Weldmesh Fencing Works (Post Installation) have achieved a compressive strength of 21.1 N/mm2 & 19.1 N/mm2 and not the 25 N/mm2 required
| 01CV - Civils | Cxxx-NCR-001603 | NCR | 1.5 west Weldmesh fence, cube reports |  | Contr | TWC | CON - Connaught Tunnel (East) |  | 2015-04-30 | 2015-04-20 13:02 | -10 | 2015-04-09 11:23 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The fence posts for the Weldmesh Fence are to have a 75mm thick concrete layer of C20/25 to support the base of the post. For the fence posts between the chainages of 17175 - 17250 concrete ticket - 7041691 Concrete Cubes were taken for testing and passed with a Compressive Strength. See attached Cube results For the fence posts between 17250 - 17330 cubes were not taken.
| 01CV - Civils | Cxxx-NCR-001604 | NCR | 1.5 Failure to take cubes for Palisade Fencing |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2015-04-23 | 2015-04-10 22:42 | -13 | 2015-04-09 13:50 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The engineer involved with the Palisade fencing failed to take concrete test cubes for two days, the 06/01/15 and 26/01/15. The concrete (C20/25) was used for the fence post foundations. Please see below for the related areas for which the cubes were not taken: West Approach Ramp North Side - Buried Ledge, EB CH 17477 to EB CH 17503. North Side - West Compound Portal, EB CH 17754 to Portal. South Side - Side Fixed, EB Ch 17506 to EB Ch 17539. South Side - West Portal Compound, EB Ch 17754 - to Portal. Attached are the Pour Records, along with the delivery ticket attached to it, verifying that the correct type of concrete was used.
| 01CV - Civils | Cxxx-NCR-001605 | NCR | 1.5 West Attenuation Tank, Mislaid Compaction Records & Failure of NDM's |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2015-04-28 | 2015-04-20 13:20 | -8 | 2015-04-14 11:30 | Civil - Fill | 500 |  | System Defect | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Compaction Records for the backfilling of the West Attenuation Tanks have been mislaid, however NDM Compaction Tests for the back filling of the tank are available. The tests require 95% end product compaction and from the results it can be seen that only 1/5 of the tests pass the lowest being 92.1%
| 01CV - Civils | Cxxx-NCR-001606 | NCR | 2.5 Mislaid Compaction Records for East Attenuation Tank |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2015-04-28 | 2015-04-20 13:19 | -8 | 2015-04-14 11:43 | Civil - Fill | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Compaction Records for the backfilling of the East Attenuation Tank have been mislaid, however NDM Compaction Tests for the back filling of the tank are available
| 01CV - Civils | Cxxx-NCR-001607 | NCR | 1.5 Compound Capping - Partial Missing Compaction Records |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2015-05-04 | 2015-04-23 17:12 | -11 | 2015-04-20 14:56 | Civil - Fill | 500 |  | Testing and Commissioning | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | The Compaction Records for the 2nd Layer of Capping laid on 12th February 2014 in the Western Compound in Area C-F (See Location 3) cannot be found. Compaction Records for Layer 1 Area C-J & Layer 2 G-J (Locations 1 & 2) are available and have passed the NDM Tests
| 01CV - Civils | Cxxx-NCR-001608 | NCR | 7.4 Separation Tank - Cube testing |  | Contr | TWC | CON - Connaught Tunnel (East) |  | 2015-05-04 | 2015-04-22 18:51 | -12 | 2015-04-20 11:03 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | Please refer to Drawing Cxxx-OVE-D-DDD-CR001_Z-53220 relating to North Central Water drainage system. Seven C20/25 concrete pours equating to 38m3 of concrete Which surround the Separation Tank and the Pre-cast Chamber didn't have concrete cubes for testing taken. Three C20/25 concrete pours equating to 22.5m3 of concrete did have cubes taken. The C20/25 concrete mix was agreed for the works in RFI 1441 Please see attached cube reports that were taken on pours around the Separation Tank and the Pre-cast Chamber. S1557994 - 28 day - Average of 47.95N/mm2 S1399276 - 28 day - Average of 45.45N/mm2 S1557409 - 28 day - Average of 35.85N/mm2 - 56 day - 40.5N/mm2 - 90 day - 45.4N/mm2
| 01CV - Civils | Cxxx-NCR-001609 | NCR | 2.5 Missing Compaction Records & Testing |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2015-05-05 | 2015-04-23 16:43 | -12 | 2015-04-21 14:42 | Civil - Fill | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | Compaction Records for the Backfilling of Bay W7 on the South & Manhole 6A - MH 6 have been mislaid. There also have not been any compaction tests carried out
| 01CV - Civils | Cxxx-NCR-001610 | NCR | 5.2 Rusting Pipework - Bomb Damage and Vent Shafts |  | Contr | VIN | CON - Connaught Tunnel (East) |  | 2015-07-13 | 2015-06-24 09:27 | -19 | 2015-04-24 12:42 | Civil - Civil Engineering General | 1000 |  | Damaged | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Attached are some pictures of the East and West Vent shaft pipework along with the bomb damage pipework. After installation, some rusting has appeared on the pipework. It seems the rust is prevalent only in certain areas, rather than the whole system.
| 01CV - Civils | Cxxx-NCR-000038 | NCR | Late submission of monitoring report |  | Contr |  | ROP - Royal Oak Portal (West) |  | 2010-11-11 | 2010-11-04 11:33 | -7 | 2010-10-11 | Surveying - Instrumentation and Monitoring | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | After the night shift of 09-07-2010 the monitoring report was not submitted to the PM within 24 hrs.
| 01CV - Civils | Cxxx-NCR-000039 | NCR | Asset Protection Barrier Position |  | Contr |  | ROP - Royal Oak Portal (West) |  | 2010-11-11 | 2010-11-02 15:13 | -9 | 2010-10-11 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | The APB at Chainage 410 has been installed 100 mm out of position in plan. This is 25 mm outside of the specified tolerance.
| 01CV - Civils | Cxxx-NCR-000040 | NCR | Commencement of guide-wall construction |  | Contr |  | ROP - Royal Oak Portal (West) |  | 2010-11-11 | 2010-11-02 15:58 | -9 | 2010-10-11 | Structural Engineering - Diaphragm Walls | 500 |  | System Defect | Use As-Is |  | Complete |  | Completed |  | The guide wall construction began without an approved ITP being in place.
| 01CV - Civils | Cxxx-NCR-000041 | NCR | Diaphragm wall panel N38 reinforcement |  | Contr |  | ROP - Royal Oak Portal (West) |  | 2010-11-11 | 2010-11-04 11:01 | -7 | 2010-10-11 | Structural Engineering - Diaphragm Walls | 500 |  | System Defect | Use As-Is |  | Complete |  | Completed |  | Whilst pouring the third load the reinforcement floated upwards 115 mm.
| 01CV - Civils | Cxxx-NCR-000042 | NCR | Reinforcement cage problem 1 |  | Contr |  | ROP - Royal Oak Portal (West) |  | 2010-11-11 | 2010-11-04 11:07 | -7 | 2010-10-11 | Structural Engineering - Diaphragm Walls | 500 |  | Planning | Repair |  | Complete |  | Completed |  | 13 number cage sections were delivered to site with shear links configured such that minor local adjustments had to be made on site.
| 01CV - Civils | Cxxx-NCR-000043 | NCR | Reinforcing cage problem 2 |  | Contr |  | ROP - Royal Oak Portal (West) |  | 2010-11-11 | 2010-11-04 11:17 | -7 | 2010-10-11 | Structural Engineering - Diaphragm Walls | 500 |  | Supervision/Management | Repair |  | Complete |  | Completed |  | Whilst undertaking the minor local adjustments described in NCR 042 the operative removed more reinforcement than was required.
| 01CV - Civils | Cxxx-NCR-000044 | NCR | Pumping chamber waling beam |  | Contr |  | ROP - Royal Oak Portal (West) |  | 2010-11-11 | 2010-11-04 11:59 | -7 | 2010-10-11 | Structural Engineering - Concrete Member | 500 |  | Supervision/Management | Rework |  | Complete |  | Completed |  | planned to use rapid early strength gain concrete to facilitate commencing excavation of the chamber on a specific date. On receipt of the 5 day compressive strength test result realised that normal early strength gain concrete had been used by mistake.
| 01CV - Civils | Cxxx-NCR-000045 | NCR | Diaphragm wall cover to reinforcement |  | Contr |  | ROP - Royal Oak Portal (West) |  | 2010-11-11 | 2010-11-04 12:16 | -7 | 2010-10-11 | Structural Engineering - Diaphragm Walls | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | An inspection of the reinforcing cage to panel N24 identified that the spacers had been fixed to the inner reinforcement rather than the outer reinforcement resulting in potential cover of 55mm.
| 01CV - Civils | Cxxx-NCR-000046 | NCR | Reinforcing cages problem 3 |  | Contr |  | ROP - Royal Oak Portal (West) |  | 2010-11-11 | 2010-11-04 12:30 | -7 | 2010-10-11 | Structural Engineering - Diaphragm Walls | 500 |  |  | Rework |  | Complete |  | Completed |  | Three cages were delivered to site with a total of 54 missing links.
| 01CV - Civils | Cxxx-NCR-000047 | NCR | Concrete compressive strength test failure 1 |  | Contr |  | ROP - Royal Oak Portal (West) |  | 2010-11-12 | 2011-01-18 15:29 | 67 | 2010-10-12 | Structural Engineering - Diaphragm Walls | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | An identity test for compressive strength undertaken on cubes made from sample reference Q977119 from panel N39 cast on 03.09.2010 failed to satisfy the acceptance criteria.
| 01CV - Civils | Cxxx-NCR-000048 | NCR | Concrete Compressive strength failure 2 |  | Contr |  | ROP - Royal Oak Portal (West) |  | 2010-11-12 | 2011-02-07 09:45 | 87 | 2010-10-12 | Structural Engineering - Diaphragm Walls | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | An identity test for compressive strength undertaken on sample reference Q977120 taken from panel N39 cast on 03.09.2010 failed to satisfy the acceptance criteria in accordance with BS EN 206 - 1 Annex B - Acceptance criteria.
| 01CV - Civils | Cxxx-NCR-000049 | NCR | Concrete Compressive Strength failure 3 |  | Contr |  | ROP - Royal Oak Portal (West) |  | 2010-11-12 | 2011-01-17 13:24 | 66 | 2010-10-12 | Structural Engineering - Diaphragm Walls | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | An identity test for compressive strength undertaken on sample reference Q991081 taken from panel N24 cast on 07.09.2010 failed to satisfy the acceptance criteria in BS EN 206 - 1 Annex B - Acceptance criteria.
| 01CV - Civils | Cxxx-NCR-000050 | NCR | Concrete Compressive Strength Failure 4 |  | Contr |  | ROP - Royal Oak Portal (West) |  | 2010-11-12 | 2011-01-17 13:28 | 66 | 2010-10-12 | Structural Engineering - Diaphragm Walls | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | An identity test for compressive strength undertaken on sample reference ZC29810A taken from panel N46 cast on 08.09.2010 failed to satisfy the acceptance criteria in BS EN 206 - 1 Annex B - Acceptance criteria.
| 01CV - Civils | Cxxx-NCR-000051 | NCR | Concrete Compressive strength failure 5 |  | Contr |  | ROP - Royal Oak Portal (West) |  | 2010-11-12 | 2011-01-17 13:34 | 66 | 2010-10-12 | Structural Engineering - Diaphragm Walls | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | An identity rest for compressive strength undertaken on sample reference ZC29810B taken from panel N46 cast on 08.09.2010 failed to satisfy the acceptance criteria in BS EN 206 - 1 Annex B - Acceptance criteria.
| 01CV - Civils | Cxxx-NCR-000052 | NCR | Concrete compressive strength failure 6 |  | Contr |  | ROP - Royal Oak Portal (West) |  | 2010-11-12 | 2011-01-17 13:35 | 66 | 2010-10-12 | Structural Engineering - Diaphragm Walls | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | An identity test for compressive strength undertaken on sample reference Q977122 taken from panel N40 cast on 09.09.2010 failed to comply with the acceptance criteria in BS EN 206 - 1 Annex B - Acceptance criteria.
| 01CV - Civils | Cxxx-NCR-000053 | NCR | Concrete compressive strength failure 7 |  | Contr |  | ROP - Royal Oak Portal (West) |  | 2010-11-13 | 2011-02-10 11:26 | 89 | 2010-10-13 08:32 | Structural Engineering - Diaphragm Walls | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | An identity test for compressive strength undertaken on sample reference Q977123 taken from panel N40 cast on 09.09.2010 failed to satisfy the requirements of BS EN 206 - 1 Annex B / Acceptance Criteria.
| 01CV - Civils | Cxxx-NCR-000060 | NCR | Portal Sheet Pile Wall / Pile 29 |  | Contr |  | ROP - Royal Oak Portal (West) |  | 2010-11-09 | 2011-02-16 21:49 | 99 | 2010-11-03 | Structural Engineering - Steel Member | 500 |  |  | Repair |  | Complete |  | Completed |  | Pile 29 has reached refusal at a toe level of 111.500 m.
| 01CV - Civils | Cxxx-NCR-000061 | NCR | Compressive Strength Testing Regime |  | Contr |  | ROP - Royal Oak Portal (West) |  | 2010-12-07 | 2011-01-07 17:53 | 31 | 2010-11-03 | Structural Engineering - Concrete Member | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | Cubes produced from samples taken from diaphragm wall panels S6 and N43 were not removed from their moulds and stored in water within 72 hrs of being cast.
| 01CV - Civils | Cxxx-NCR-000062 | NCR | Panel S45 / Inspection by CC |  | Contr |  | ROP - Royal Oak Portal (West) |  | 2010-12-07 | 2010-12-17 17:01 | 10 | 2010-11-03 | Structural Engineering - Diaphragm Walls | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | The cage for panel S45 was installed without an inspection by CC.
| 01CV - Civils | Cxxx-NCR-000063 | NCR | Reinforcement tying wire |  | Contr |  | ROP - Royal Oak Portal (West) |  | 2010-12-07 | 2011-01-19 08:23 | 43 | 2010-11-03 | Structural Engineering - Diaphragm Walls | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | A small amount of 1.6mm annealed steel tire wire has been used.
| 01CV - Civils | Cxxx-NCR-000072 | NCR | Diaphragm Wall / Reinforcement Detailing Drawings |  | Contr |  | ROP - Royal Oak Portal (West) |  | 2010-12-23 | 2011-03-02 09:24 | 69 | 2010-11-23 08:01 | Structural Engineering - Reinforcement | 500 |  | Workmanship | Rework |  | Complete |  | Completed |  | 24 drawing ammendments have not been highlighted and referenced.
| 01CV - Civils | Cxxx-NCR-000075 | NCR | APB [POST & RAIL] 1 |  | Contr |  | ROP - Royal Oak Portal (West) |  | 2011-01-03 | 2011-01-10 17:32 | 7 | 2010-12-01 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Rework |  | Complete |  | Completed |  | Excavations for posts not at the spacing detailed on the construction drawing. 6 of the first 11 excavations to the west of the sheet pile APB.
| 01CV - Civils | Cxxx-NCR-000076 | NCR | APB [POST & RAIL] 2 |  | Contr |  | ROP - Royal Oak Portal (West) |  | 2011-01-03 | 2011-01-18 15:01 | 15 | 2010-12-01 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | Certain posts have been installed with an embedment length of 1600 mm.
| 01CV - Civils | Cxxx-NCR-000077 | NCR | APB [POST & RAIL] 3 |  | Contr |  | ROP - Royal Oak Portal (West) |  | 2011-01-03 | 2011-01-10 18:12 | 7 | 2010-12-01 | Civil - Civil Engineering General | 500 |  | Workmanship | Rework |  | Complete |  | Completed |  | Several post sockets between E55 and E63 were formed innacurately such that the respective posts could not be installed correctly.
| 01CV - Civils | Cxxx-NCR-000078 | NCR | Sheet Pile Portal Wall |  | Contr |  | ROP - Royal Oak Portal (West) |  | 2011-01-03 | 2011-01-18 15:10 | 15 | 2010-12-01 | Structural Engineering - Steel Member | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | Pile 143 in the south wall and piles 2, 6, 28, 51 & 53 in the north wall deviate more than 75mm from the plan design position. The attached excell spread sheet lists the as-built postion of all the sheet piles.
| 01CV - Civils | Cxxx-NCR-000079 | NCR | Sheet Pile Portal Wall Capping Beam |  | Contr |  | ROP - Royal Oak Portal (West) |  | 2011-01-03 | 2011-01-18 15:21 | 15 | 2010-12-01 | Structural Engineering - Concrete Member | 500 |  | Design | Use As-Is |  | Complete |  | Completed |  | The sheet piles have a permissable installation tolerance of +/- 75mm. The reinforcement detail does not have the flexibility to accommodate this variation. The cover to reinforcement varies from 0 [zero] mm to 120mm. Sketch attached indicating the key measurements/dimensions.
| 01CV - Civils | Cxxx-NCR-000080 | NCR | Sheet pile wall shear stud connection |  | Contr |  | ROP - Royal Oak Portal (West) |  | 2011-01-03 | 2011-01-17 14:28 | 14 | 2010-12-01 | Structural Engineering - Concrete Member | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | One stud on pile 54 in the north wall failed to comply with the testing requirements.
| 01CV - Civils | Cxxx-NCR-000081 | NCR | Sheet pile wall lining wall / Shear studs |  | Contr |  | ROP - Royal Oak Portal (West) |  | 2011-01-03 | 2011-01-17 14:19 | 14 | 2010-12-01 | Structural Engineering - Concrete Member | 500 |  | Supervision/Management | Repair |  | Complete |  | Completed |  | During the pre-pour inspection for capping beam K it was observed that only half the required shear studs had been provided.
| 01CV - Civils | Cxxx-NCR-000082 | NCR | Capping Beam K / Concreting Interuption |  | Contr |  | ROP - Royal Oak Portal (West) |  | 2011-01-03 | 2011-03-07 11:16 | 63 | 2010-12-01 | Structural Engineering - Concrete Member | 500 |  | Material | Repair |  | Complete |  | Completed |  | Fresh concrete was placed against in-situ concrete that had been in position for more than 30 minutes.
| 01CV - Civils | Cxxx-NCR-000088 | NCR | Eaething and Bonding 3 |  | Contr |  | ROP - Royal Oak Portal (West) |  | 2011-01-21 | 2011-03-31 10:14 | 69 | 2010-12-15 08:30 | Civil - Civil Engineering General | 500 |  | Design | Repair |  | Complete |  | Completed |  | The 5 diaphragm wall panels were constructed without electrical testing of the cages. await clarification of the testing requirements.
| 01CV - Civils | Cxxx-NCR-000093 | NCR | Diaphragm Wall Panel N32 / Base slab connection |  | Contr |  | ROP - Royal Oak Portal (West) |  | 2011-02-04 | 2011-03-02 08:51 | 26 | 2011-01-05 | Structural Engineering - Diaphragm Walls | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | For panel N32 couplers were not fixed in the correct location by the manufacturer. The error was not observed by the site team. The reinforcing cage was installed and the panel was cast.
| 01CV - Civils | Cxxx-NCR-000094 | NCR | Diaphragm Wall Cut-Off Level |  | Contr |  | ROP - Royal Oak Portal (West) |  | 2011-01-14 | 2011-03-02 09:06 | 47 | 2011-01-10 | Structural Engineering - Concrete Member | 500 |  | Supervision/Management | Repair |  | Complete |  | Completed |  | Diaphragm Wall concrete will be broken down to a level of 121.500 m AOD.
| 01CV - Civils | Cxxx-NCR-000100 | NCR | Diaphragm Wall Reinforcement |  | Contr |  | ROP - Royal Oak Portal (West) |  | 2011-01-20 | 2011-03-02 09:04 | 41 | 2011-01-14 13:09 | Structural Engineering - Concrete Member | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | In approx. 3% of the couplers exposed to date concrete grout has entered the couplers and set within the internal threads.
| 01CV - Civils | Cxxx-NCR-000103 | NCR | DIAPHRAGM WALL CAPPING BEAM WATERBAR |  | Contr |  | ROP - Royal Oak Portal (West) |  | 2011-01-24 | 2011-03-02 09:03 | 37 | 2011-01-18 15:12 | Structural Engineering - Concrete Member | 500 |  | Supervision/Management | Rework |  | Complete |  | Completed |  | At the capping beam joint between N CB 16 and N CB 17 the waterbar has been terminated incorrectly.
| 01CV - Civils | Cxxx-NCR-000104 | NCR | Diaphragm Wall Break down 2 |  | Contr |  | ROP - Royal Oak Portal (West) |  | 2011-01-26 | 2011-03-02 16:21 | 35 | 2011-01-20 08:13 | Structural Engineering - Concrete Member | 500 |  | Damaged | Repair |  | Complete |  | Completed |  | It certain locations the break down has extended locally below the design cut-off level.
| 01CV - Civils | Cxxx-NCR-000105 | NCR | REFERENCE NCR 094 |  | Contr |  | ROP - Royal Oak Portal (West) |  | 2011-01-26 | 2011-03-22 11:32 | 55 | 2011-01-20 09:02 | Structural Engineering - Concrete Member | 500 |  | Supervision/Management | Repair |  | Complete |  | Completed |  | Diaphragm wall cut-off level has been formed 100mmm lower than designed level at void former locations. Please consider attached sketch as clarification to NCR 094.
| 01CV - Civils | Cxxx-NCR-000107 | NCR | Capping Beam Reinforcement 2 |  | Contr |  | ROP - Royal Oak Portal (West) |  | 2011-01-31 | 2011-03-02 09:09 | 30 | 2011-01-24 11:19 | Structural Engineering - Concrete Member | 500 |  | Material | Repair |  | Complete |  | Completed |  | The hooks' projection length (P) of the fabricated links below are equal to 150mm which is less than the design requirement of 210mm -Beam M bar mark 09 (drawing ref. C150-CSY-S-DDL-CR076_PT001-02072 rev. C01) -Beam N bar mark 09 (drawing ref. C150-CSY-S-DDL-CR076_PT001-02072 rev. C01) -Beam B bar mark 56 (drawing ref. C150-CSY-S-DDL-CR076_PT001-02051 rev. C01) -Beam C bar mark 11 (drawing ref. C150-CSY-S-DDL-CR076_PT001-02052 rev. C01)
| 01CV - Civils | Cxxx-NCR-000108 | NCR | Capping beam Reinforcement 3 |  | Contr |  | ROP - Royal Oak Portal (West) |  | 2011-01-31 | 2011-03-02 09:10 | 30 | 2011-01-24 11:24 | Structural Engineering - Concrete Member | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | The hooks' projection length (P) of the fabricated links below are equal to 150mm which is less than the design requirement of 210mm -Beam M bar mark 10 (drawing ref. C150-CSY-S-DDL-CR076_PT001-02072 rev. C01) -Beam N drawing ref. C150-CSY-S-DDL-CR076_PT001-02072 rev. C01)
| 01CV - Civils | Cxxx-NCR-000109 | NCR | Diaphragm Wall Damage below cut-off line |  | Contr |  | ROP - Royal Oak Portal (West) |  | 2011-01-31 | 2011-03-02 09:12 | 30 | 2011-01-25 18:24 | Structural Engineering - Concrete Member | 500 |  | Damaged | Repair |  | Complete |  | Completed |  | In the following locations: NCB-16 to NCB-9 & SCB-16 to SCB-9] the concrete break down process has resulted in fractures and spalling extending beneath the cut-off level.
| 01CV - Civils | Cxxx-NCR-000113 | NCR | Diaphragm Wall / Vertical Reinforcement |  | Contr |  | ROP - Royal Oak Portal (West) |  | 2011-03-01 | 2011-04-04 13:02 | 34 | 2011-02-01 | Structural Engineering - Concrete Member | 500 |  | Damaged | Repair |  | Complete |  | Completed |  | Certain couplers within diaphragm wall panels beneath capping beams N CB 7 to N CB 17 have been damaged such that the correct connection cannot be made.
| 01CV - Civils | Cxxx-NCR-000116 | NCR | APB Post Concrete Surround |  | Contr |  | ROP - Royal Oak Portal (West) |  | 2011-02-07 | 2011-03-02 09:14 | 23 | 2011-02-01 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | ST5 concrete was used with a consistence of S1.
| 01CV - Civils | Cxxx-NCR-000122 | NCR | Diaphragm Wall Concrete Failure Panel N39 |  | Contr |  | ROP - Royal Oak Portal (West) |  | 2011-03-01 | 2011-03-02 09:18 | 1 | 2011-02-16 18:52 | Structural Engineering - Concrete Member | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | An identity test for compressive strength undertaken on sample reference Q977120 taken from panel N39 cast on 03.09.2010 failed to satisfy the acceptance criteria in accordance with BS EN 206 - 1 Annex B - Acceptance criteria. We attach the delivery ticket, the 28 day test certificate, the 56 day test certificate and a spread sheet listing the producers test results.
| 01CV - Civils | Cxxx-NCR-000123 | NCR | Diaphragm Wall Concrete Failure Panel N24 |  | Contr |  | ROP - Royal Oak Portal (West) |  | 2011-03-02 | 2011-03-02 09:17 | 0 | 2011-02-17 16:33 | Structural Engineering - Concrete Member | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | An identity test for compressive strength undertaken on sample reference Q991081 taken from panel N24 cast on 07.09.2010 failed to satisfy the acceptance criteria in BS EN 206-1 Annex B - Acceptance criteria. We attach the delivery ticket, the 28 dy test certificate and the 56 dy test certificate.
| 01CV - Civils | Cxxx-NCR-000124 | NCR | Diaphragm Wall Concrete Failure Panel N46 |  | Contr |  | ROP - Royal Oak Portal (West) |  | 2011-03-04 | 2011-03-03 08:38 | -1 | 2011-02-21 10:40 | Structural Engineering - Concrete Member | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | An identity test for compressive strength undertaken on sample reference ZC29810B taken from panel N46 cast on 09.09.2010 failed to satisfy the acceptance criteria in BS EN 206-1 Annex B - Acceptance criteria. A further test undertaken 56 days after casting gave a result of 42.5N/mm2.
| 01CV - Civils | Cxxx-NCR-000125 | NCR | Diaphragm Wall Concrete Failure Panel N40 |  | Contr |  | ROP - Royal Oak Portal (West) |  | 2011-03-04 | 2011-03-02 09:57 | -2 | 2011-02-21 11:07 | Structural Engineering - Concrete Member | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | Two identity tests for compressive strength undertaken on sample references Q977122 and Q977123 taken from panel N40 on 09.09.2010 failed to satisfy the requirements of BS EN 206-1 Annex B - Acceptance criteria.
| 01CV - Civils | Cxxx-NCR-000126 | NCR | Diaphragm Walls Inclinometers |  | Contr |  | ROP - Royal Oak Portal (West) |  | 2011-03-07 | 2011-03-02 09:20 | -5 | 2011-02-22 16:10 | Structural Engineering - Diaphragm Walls | 500 |  | Planning | Use As-Is |  | Complete |  | Completed |  | Inclinometer I1 has been installed in panel N2 and inclinometer I4 has been installed in panel S2. These variant positions were selected to avoid the gantry crane substructure installation.
| 01CV - Civils | Cxxx-NCR-000127 | NCR | Diaphragm Wall Capping Beam K |  | Contr |  | ROP - Royal Oak Portal (West) |  | 2011-03-07 | 2011-03-03 08:31 | -4 | 2011-02-22 16:20 | Structural Engineering - Concrete Member | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | Water was added to a part load of concrete subsequently incorporated into capping beam K. The added volume was in accordance with the producers direction and was compliant with the specification.
| 01CV - Civils | Cxxx-NCR-000137 | NCR | Diaphragm Wall Panel N13 Cover to reinforcement |  | Contr |  | ROP - Royal Oak Portal (West) |  | 2011-03-28 | 2011-04-04 13:00 | 7 | 2011-03-15 20:52 | Structural Engineering - Concrete Member | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | For panel N13 the cover to the inner face is 20mm and the cover to the outer face is 120mm. We attach 3 photos to clarify the details.
| 01CV - Civils | Cxxx-NCR-000138 | NCR | Asset Protection Barrier / Construction detail |  | Contr |  | ROP - Royal Oak Portal (West) |  | 2011-04-15 | 2011-04-04 12:59 | -11 | 2011-03-15 21:46 | Civil - Civil Engineering General | 500 |  | Material | Repair |  | Complete |  | Completed |  | The plywood sheets have been connected with 45mm nails at 300mm c/c.
| 01CV - Civils | Cxxx-NCR-000139 | NCR | Asset Protection Barrier / Constructed Verticallity & Height |  | Contr |  | ROP - Royal Oak Portal (West) |  | 2011-04-18 | 2011-04-04 12:55 | -14 | 2011-03-16 12:40 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | The constructed verticallity varies from vertical to 1/120. The level of the top of the barrier varies as the corresponding ground level varies such that the height remains as near constant as possible.
| 01CV - Civils | Cxxx-NCR-000143 | NCR | Capping Beam N CB-14 / Reinforcement |  | Contr |  | ROP - Royal Oak Portal (West) |  | 2011-04-22 | 2011-03-28 11:34 | -25 | 2011-03-23 13:06 | Structural Engineering - Reinforcement | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | In capping beam reference N CB-14 four of these bars have been provided as M42 studding in grade 4.8 steel to BS EN ISO 898-1.
| 01CV - Civils | Cxxx-NCR-000164 | NCR | Diaphragm Wall Panel N32 / Connection to base slab |  | Contr |  | ROP - Royal Oak Portal (West) |  | 2011-05-19 | 2011-05-18 15:58 | -1 | 2011-05-13 08:22 | Structural Engineering - Concrete Member | 500 |  | Workmanship | Rework |  | Complete |  | Completed |  | For Diaphragm wall panel N32 the couplers have been fixed 829mm lower than designed. This NCR was first raised as NCR 093 on 05.01.2011. See attached sketch.
| 01CV - Civils | Cxxx-NCR-000166 | NCR | HSFB Piers 1 & 2 HD Bolts |  | Contr |  | ROP - Royal Oak Portal (West) |  | 2011-05-20 | 2011-05-18 15:46 | -2 | 2011-05-17 19:01 | Structural Engineering - Bolted Connections | 500 |  | Material | Rework |  | Complete |  | Completed |  | The existing bolts and nuts were severely corroded such that the nuts could not be removed and the threads were unserviceable. It is possible that the corrosion extends to the pier concrete reinforcement.
| 01CV - Civils | Cxxx-NCR-000167 | NCR | HSFB Bearing Pin Joints |  | Contr |  | ROP - Royal Oak Portal (West) |  | 2011-05-20 | 2011-05-18 15:59 | -2 | 2011-05-17 19:27 | Structural Engineering - Steel Member | 500 |  | Material | Rework |  | Complete |  | Completed |  | It has been determined that the existing pin is 50mm diam. and stainless steel and that the hole in the existing lower bearing section is 60mm. The proposed design deviates from the existing condition to such an extent that the contractor has concerens regarding the structural stability of the proposed design.
| 01CV - Civils | Cxxx-NCR-000168 | NCR | HSFB Horizontal movement during realignment |  | Contr |  | ROP - Royal Oak Portal (West) |  | 2011-05-20 | 2011-05-18 16:01 | -2 | 2011-05-17 19:45 | Structural Engineering - Steel Member | 500 |  | Design | Rework |  | Complete |  | Completed |  | The technical requirements described above were complied with and a consequential horizontal movement of the upper bearing sections was observed above piers 1 and 2. This introduced a vertical misalignment between upper and lower bearing sections above each pier. This issue had been raised in advance by the contractor via RFI 155. Additional consequential horizontal movement [not envisaged by the contractor] was observed at the same positions.
| 01CV - Civils | Cxxx-NCR-000170 | NCR | Head wall Diaphragm Wall capping beam voids |  | Contr |  | ROP - Royal Oak Portal (West) |  | 2011-05-24 | 2011-06-17 08:51 | 24 | 2011-05-24 12:27 | Civil - Structural Engineering | 500 |  | Design | Rework |  | Complete |  | Completed |  | Starter bars from Panels H1 and H3 are clashing with the existing voids present in head wall capping beam shown in drawing number C150-CSY-S-DDL-CR076_PT001-02425.
| 01CV - Civils | Cxxx-NCR-000173 | NCR | Beam R - 2 no's sheet piles out of tolerance |  | Contr |  | ROP - Royal Oak Portal (West) |  | 2011-06-06 | 2011-06-17 08:50 | 11 | 2011-06-03 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | 2 No's sheet piles in beam R are out of tolerance by 100 mm. This will affect the construction of the capping beam R.
| 01CV - Civils | Cxxx-NCR-000176 | NCR | Steel Props reference U1 end plates |  | Contr |  | ROP - Royal Oak Portal (West) |  | 2011-06-29 | 2011-06-21 13:06 | -8 | 2011-06-16 08:07 | Structural Engineering - Steel Member | 500 |  | Material | Rework |  | Complete |  | Completed |  | The U1 prop end plates that connect to the portal headwall have been incorrectly fabricated. The end plate width and height dimensions are larger than detailed. The bolt holes are incorrectly positioned.
| 01CV - Civils | Cxxx-NCR-000178 | NCR | Working Without Accepted ITPs |  | Contr |  | ROP - Royal Oak Portal (West) |  | 2011-07-08 | 2011-07-06 15:14 | -2 | 2011-07-01 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Rework |  | Complete |  | Completed |  | Construction of shafts has commenced before Crossrail acceptance of ITPs.
| 01CV - Civils | Cxxx-NCR-000183 | NCR | No Design or Specification of Shaft Segments and Associated Components |  | Contr |  | ROP - Royal Oak Portal (West) |  | 2011-07-27 | 2011-11-30 14:55 | 126 | 2011-07-13 15:44 | Shafts - Linings | 500 |  | Supervision/Management | Rework |  | Complete |  | Completed |  | The contractor, , has no design details of the precast concrete segment linings. All but one ring of the shaft have been installed.
| 01CV - Civils | Cxxx-NCR-000184 | NCR | Records to Show Compliance of Shaft Segments and Associated Components |  | Contr |  | ROP - Royal Oak Portal (West) |  | 2011-08-03 | 2011-11-30 14:51 | 119 | 2011-07-13 16:06 | Shafts - Linings | 500 |  | Supervision/Management | Rework |  | Complete |  | Completed |  | could not produce evidence that shaft ring segments and associated components comply with specified requirements. All but one of the segment rings of the pump shaft have been installed.
| 01CV - Civils | Cxxx-NCR-000185 | NCR | Setting out - Base Slab step B4/B5 |  | Contr |  | ROP - Royal Oak Portal (West) |  | 2011-07-26 | 2011-08-03 15:44 | 8 | 2011-07-26 12:41 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Rework |  | Complete |  | Completed |  | Step location in the blinding section between B4 and B5 (launch Slab) is 500mm out of position
| 01CV - Civils | Cxxx-NCR-000186 | NCR | Setting out- Base Slab step CH420 -CH440 |  | Contr |  | ROP - Royal Oak Portal (West) |  | 2011-07-26 | 2011-08-03 15:48 | 8 | 2011-07-26 12:54 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Rework |  | Complete |  | Completed |  | Step location in the blinding section between CH420 and CH440 is approximately 800mm out of position
| 01CV - Civils | Cxxx-NCR-000201 | NCR | Strain Gauges / Diagonal Props |  | Contr |  | ROP - Royal Oak Portal (West) |  | 2011-08-17 | 2011-08-22 08:44 | 5 | 2011-08-04 | Surveying - Instrumentation and Monitoring | 500 |  | Equipment Breakdown | Use As-Is |  | Complete |  | Completed |  | Strain gauges 91037N-D, 91038N-A and 91038S-C have failed to record measurements at 15 minute intervals.
| 01CV - Civils | Cxxx-NCR-000202 | NCR | H & C Trough North Wall Monitoring |  | Contr |  | ROP - Royal Oak Portal (West) |  | 2011-08-17 | 2011-08-26 08:58 | 9 | 2011-08-04 | Surveying - Instrumentation and Monitoring | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | The H & C trough north wall monitoring has not taken place at monthly intervals.
| 01CV - Civils | Cxxx-NCR-000203 | NCR | Sitewide settlement manual survey |  | Contr |  | ROP - Royal Oak Portal (West) |  | 2011-08-17 | 2011-08-15 09:32 | -2 | 2011-08-04 | Surveying - Instrumentation and Monitoring | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | The sitewide settlement manual survey has not taken place twice per week during the excavation.
| 01CV - Civils | Cxxx-NCR-000204 | NCR | D Wall Capping Beam Manual Survey |  | Contr |  | ROP - Royal Oak Portal (West) |  | 2011-08-17 | 2011-08-26 08:45 | 9 | 2011-08-04 | Surveying - Instrumentation and Monitoring | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | The D wall capping beam targets have not been surveyed manually twice per week.
| 01CV - Civils | Cxxx-NCR-000205 | NCR | Harrow Rd Pavement & A40 column bases |  | Contr |  | ROP - Royal Oak Portal (West) |  | 2011-08-17 | 2011-08-26 08:44 | 9 | 2011-08-04 | Surveying - Instrumentation and Monitoring | 500 |  |  | Use As-Is |  | Complete |  | Completed |  | Settlement monitoring for Harrow Rd pavement and the A40 column bases has not been undertaken at weekly intervals during excavation.
| 01CV - Civils | Cxxx-NCR-000206 | NCR | Harrow Road Retaining Wall |  | Contr |  | ROP - Royal Oak Portal (West) |  | 2011-08-17 | 2011-08-26 08:43 | 9 | 2011-08-04 | Surveying - Instrumentation and Monitoring | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | The Harrow Rd Retaining Wall prisms have not been monitored 4 times per day.
| 01CV - Civils | Cxxx-NCR-000207 | NCR | Base slab construction joints |  | Contr |  | ROP - Royal Oak Portal (West) |  | 2011-09-01 | 2011-08-26 08:42 | -6 | 2011-08-04 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | Base slabs 11, 12 &13 cast on the 2nd of August in one operation without the construction joints. There was no evidence made available to demonstrate that this is acceptable to the Designer
| 01CV - Civils | Cxxx-NCR-000208 | NCR | Piezometer PV70001 |  | Contr |  | ROP - Royal Oak Portal (West) |  | 2011-08-17 | 2011-08-26 08:38 | 9 | 2011-08-04 | Surveying - Instrumentation and Monitoring | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | The automated piezometer PV70001 has not been monitored daily between 11.01.2011 and 14.06.2011.
| 01CV - Civils | Cxxx-NCR-000209 | NCR | Denso tape wrappings to reinforcement steel |  | Contr |  | ROP - Royal Oak Portal (West) |  | 2011-09-01 | 2011-08-15 13:03 | -17 | 2011-08-04 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | An outer layer of Denso tape wrapping to the clamps and reinforcement steel was seen to be in place for approximately 25 number connections. Evidence was not made available to demonstrate that the Denso tape wrapping to the reinforcement steel was acceptable to the Designer
| 01CV - Civils | Cxxx-NCR-000210 | NCR | Inclinometer IE70113 |  | Contr |  | ROP - Royal Oak Portal (West) |  | 2011-08-17 | 2011-08-15 13:01 | -2 | 2011-08-04 | Surveying - Instrumentation and Monitoring | 500 |  | Damaged | Use As-Is |  | Complete |  | Completed |  | Manual inclinometer IE70113 has not been monitored since 02.07.2011.
| 01CV - Civils | Cxxx-NCR-000211 | NCR | Placing concrete with measured slump that exceeds the specified limits |  | Contr |  | ROP - Royal Oak Portal (West) |  | 2011-09-01 | 2011-08-26 08:33 | -6 | 2011-08-04 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | The surveillance and pour records document that one concrete delivery with a measured slump of 220mm and a second delivery with a slump of 200mm were placed in the base slab pour.
| 01CV - Civils | Cxxx-NCR-000212 | NCR | C230 Monitoring |  | Contr |  | ROP - Royal Oak Portal (West) |  | 2011-08-17 | 2011-08-26 08:22 | 9 | 2011-08-04 | Surveying - Instrumentation and Monitoring | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | To date, whilst the monitoring began on 06.07.2011, the reporting has not begun.
| 01CV - Civils | Cxxx-NCR-000213 | NCR | TfL Action Plan |  | Contr |  | ROP - Royal Oak Portal (West) |  | 2011-08-17 | 2011-08-26 08:21 | 9 | 2011-08-04 | Surveying - Instrumentation and Monitoring | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | To date these ammendments have not been made.
| 01CV - Civils | Cxxx-NCR-000214 | NCR | Data Transmission to UCIMS |  | Contr |  | ROP - Royal Oak Portal (West) |  | 2011-08-17 | 2011-08-26 08:20 | 9 | 2011-08-04 | Surveying - Instrumentation and Monitoring | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | To date the data has not been transmitted.
| 01CV - Civils | Cxxx-NCR-000247 | NCR | Damaged park bench at Hampden Steet Footbridge |  | Contr |  | ROP - Royal Oak Portal (West) |  | 2012-09-28 | 2013-02-19 08:59 | 144 | 2012-08-23 11:37 | Civil - Landscaping | 500 |  | Damaged | Repair |  | Complete |  | Completed |  | Park bench damaged during HSFB jacking operations
| 03SR - Stations (RfL) | Cxxx-NCR-000003 | NCR | Temporary Works Procedure |  | Contr | SKC | PNY - Paddington New Yard (West) |  | 2014-03-27 | 2014-03-24 09:31 | -3 | 2014-03-13 17:14 | Civil - Concrete Pavement | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Procedure Problem - Lack of procedure | Completed |  | Temporary works design and checking has commenced prior to acceptance of the Cxxx temporary works procedure.
| 03SR - Stations (RfL) | Cxxx-NCR-000004 | NCR | Procedural - Checking of formation for pile mat construction |  | Crossrail | XRL | PNY - Paddington New Yard (West) |  | 2014-05-13 | 2014-05-12 15:49 | -1 | 2014-04-29 10:39 | Civil - Fill | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Defective or inadequate procedure | Completed |  | CRL was invited to attend a planned witness point intervention for the placing and compaction of 6F2 material for the piling platform in the AD-1 West area South side that will eventually be used for the test pile construction. Inspection held at 0945 on 29 April 2014. Upon reviewing the contractor’s records for this inspection, it was observed that the check sheet had not been correctly completed prior to the CRL inspection. Notably, IN 6 (for the removal of soft spots in the formation) and IN 7 (for the testing of the formation prior to backfilling) had not been completed and were left blank on the check sheet. This provides a lack of confidence that these checks were correctly completed on the formation with the pile platform backfilling now on-going. This NCR has been raised by CRL upon attending a planned witness point inspection and finding a procedural failure by the Contractor.
| 03SR - Stations (RfL) | Cxxx-NCR-000005 | NCR | Lesson Learned |  | Contr | VIN | PNY - Paddington New Yard (West) |  | 2014-05-15 | 2014-05-14 09:31 | -1 | 2014-05-01 09:50 | Structural Engineering - Structural Engineering - General | 500 |  | System Defect | Rework | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | __ is not participated in and contributed to CRL’s lessons learned procedures within 12 weeks of the starting date of the Contract as stated within the CQP 14.8
| 03SR - Stations (RfL) | Cxxx-NCR-000006 | NCR | Delivery of Pile Cages without approved documentation |  | Contr | VIN | PNY - Paddington New Yard (West) |  | 2014-05-28 | 2014-05-30 16:02 | 2 | 2014-05-08 12:25 | Structural Engineering - Reinforcement | 3000 |  | Documentation and Records | Reject | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | Delivery of 8 piles to site by __ without an approved ITP, MCR for welding and signed checksheets
| 03SR - Stations (RfL) | Cxxx-NCR-000007 | NCR | Quality Management Plan |  | Contr | VIN | PNY - Paddington New Yard (West) |  | 2014-06-20 | 2014-06-24 10:37 | 4 | 2014-05-14 09:59 | Systems - Systems Engineering General | 500 |  | System Defect | Reject | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | The project has not produced a Competency Matrix for the project to identified personnel competencies as stated within section 6.3 of Rev 02 Cxxx-COS-O4_STP-CR076-SD006-50006 Competency Management Plan.
| 03SR - Stations (RfL) | Cxxx-NCR-000008 | NCR | Quality Management Plan |  | Contr | VIN | PNY - Paddington New Yard (West) |  | 2014-06-13 | 2014-06-17 09:18 | 4 | 2014-05-14 10:08 | Systems - Systems Engineering General | 500 |  | Documentation and Records | Reject | 4 (0.5-3k) | Complete | Management Problem - Inadequate resources | Completed |  | One of the key deliverable required on the project by CRL is for __ to maintain a Contract Master Deliverables List (CMDL) to use as the basis for the project filing system as per the requirement stated within the Works Information 2B Part 13.3. Revision 2.0 Cxxx-COS-O4-MDL-CR076_SD006-50001 (CMDL) was verified on eB at the audit. However, it was noted during this review that this document is not being updated or reviewed regularly to include all the deliverables for the project and in line with the Project Programme. Also, the owner of this document is not identified.
| 03SR - Stations (RfL) | Cxxx-NCR-000009 | NCR | Quality Management Plan -Internal __ Audit |  | Contr | VIN | PNY - Paddington New Yard (West) |  | 2014-06-08 | 2014-06-09 10:40 | 1 | 2014-05-14 10:27 | Systems - Systems Engineering General | 500 |  | Documentation and Records | Reject | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | __ is employed by __ to manage material sampling. The calibration certificates for these materials are produced by __. This document not yet submitted to __ by __. It was also noted during review that __ has not maintained the full Schedule of Calibration and Test Equipment. The full schedule of test and calibration equipment is to be submitted periodically to the PM for information only.
| 03SR - Stations (RfL) | Cxxx-NCR-000010 | NCR | __ Quality Management Audit |  | Contr | VIN | PNY - Paddington New Yard (West) |  | 2014-06-02 | 2014-06-02 09:47 | 0 | 2014-05-19 13:33 | Systems - Systems Engineering General | 500 |  | Design | Reject | 4 (0.5-3k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | __ project specific Organisational Chart enclosed within the section 4 of the Quality Plan is not effectively implemented. The names of some of the key project members, such as the Quality Manager, RAMs Manager, those within the external offices such as India were not identified within the chart. Loads of boxes are left incomplete and to be TBA.
| 03SR - Stations (RfL) | Cxxx-NCR-000011 | NCR | Bus Deck - LDA Piles - Rejected Pile Cage |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2014-06-25 | 2014-06-11 16:59 | -14 | 2014-06-11 10:43 | Structural Engineering - Reinforcement | 1000 |  | Manufacturing Defect | Reject | 4 (0.5-3k) | Complete | Personnel Error - Inattention to detail | Completed |  | Pile Ref. Type 2 -No. 7 Pile Deliveried on the 21/05/14 The debonding foam length was 200mm short (600mm opposed to the required 800mm) and the length of straight bar above the helical was 200mm too short (800mm opposed to the required 1m).
| 03SR - Stations (RfL) | Cxxx-NCR-000012 | NCR | Drawing Revisions |  | Crossrail | PDP | PNY - Paddington New Yard (West) |  | 2014-06-06 | 2014-06-09 15:48 | 3 | 2014-05-29 11:55 | Geotechnical Engineering - Concrete - Bored Pile | 500 |  | Documentation and Records | Reject | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | __ Subcontractor __ Limited site operatives are currently not using the latest revision of drawings. CRL on attendance at site noticed __ foreman had for use, the wrong revision of CRL drawing with number Cxxx-CSY-S-DDA-CR076_MS005-01051. Current drawing issued on latest RIR 05 is at revision C02. However, Rev C01 is bring used.
| 03SR - Stations (RfL) | Cxxx-NCR-000013 | NCR | WPP for AD1 Pile Installation Works |  | Contr | VIN | PNY - Paddington New Yard (West) |  | 2014-07-07 | 2014-06-27 14:47 | -10 | 2014-06-02 14:42 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Reject | 4 (0.5-3k) | Complete | Management Problem - Misunderstand the definition of the requirement | Completed |  | WPP for AD1 Pile Installation Works Cxxx-COS-C-STP-CR076_SD006-50002 Rev 1 was given a DRN Category Code 2 by NR accepted with Amendments after the document had been Code 2 by CRL. __ started works based on this. __ amended the document to Rev 2 addressing the NR comments however CRL added further comments to this and returned the document as CODE 3. __ addressed the outstanding comments and revised the document to Rev 3 but only altered the document and not the comment sheet. Cxxx continued to work under a CRL DECAL CODE 3 but a NR CODE 2. Upon investigation the comments were seen as minor and that a NCR should be raised for a procedural reason.
| 03SR - Stations (RfL) | Cxxx-NCR-000014 | NCR | Bored Piles - Plastic Wheel Spacers |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2014-06-23 | 2014-06-12 17:30 | -11 | 2014-06-09 18:05 | Geotechnical Engineering - Concrete - Bored Pile | 500 |  | Manufacturing Defect | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | No MCR for Plastic Wheel Spacers
| 03SR - Stations (RfL) | Cxxx-NCR-000015 | NCR | Piling - Tracking over pile |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2014-06-26 | 2014-06-13 13:23 | -13 | 2014-06-12 08:02 | Geotechnical Engineering - Concrete - Bored Pile | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | BG18 Tracking over Piles 147 - 152
| 03SR - Stations (RfL) | Cxxx-NCR-000016 | NCR | Piling - Verticality 1:150 AD1 Bus Deck |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2014-06-26 | 2014-06-23 08:56 | -3 | 2014-06-12 10:08 | Geotechnical Engineering - Concrete - Bored Pile | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Misunderstand the definition of the requirement | Completed |  | Pile Records sheets being completed to a 1:150 verticality check when the ITP states 1:75. 1:75 Verticality - __e __ spec 1:75 Verticality - 1700 series of the Highways Spec for Conventional and Solthread piles 1:150 Verticality - Appendix Cxxx Spec for Secant piles
| 03SR - Stations (RfL) | Cxxx-NCR-000017 | NCR | __ Quality Audit |  | Contr | VIN | PNY - Paddington New Yard (West) |  | 2014-07-13 | 2014-06-20 16:31 | -23 | 2014-06-12 16:06 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Reject | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | The overall Competency Management of the project specific staff were not clearly identified within the __'s QA Plan. Also there was no evidence found during the audit that the Competency Matrix submitted within the Appendix 3 of the QA plan is effectively managed in order to give __ / CRL the confidence that operatives were selected based on the set minimum requirements.
| 03SR - Stations (RfL) | Cxxx-NCR-000018 | NCR | __'s Quality Audit |  | Contr | VIN | PNY - Paddington New Yard (West) |  | 2014-06-26 | 2014-06-20 16:44 | -6 | 2014-06-12 17:04 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Reject | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | IN17 form and Reinforcement Cage Records were verified at the audit. It was noted that the relevant Check Sheets were not completed to meet the set quality requirements of the project. It was also evident that some sections of these documents were left incomplete and blank.
| 03SR - Stations (RfL) | Cxxx-NCR-000019 | NCR | Piling - Pile 285 & 286 incorrect toe level |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2014-07-18 | 2014-07-16 09:01 | -2 | 2014-06-13 17:54 | Geotechnical Engineering - Concrete - Bored Pile | 2000 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | Piles 285 & 286 have been found to be installed to the incorrect toe level - the cage has been installed to the correct level however the toe of the pile has been installed to 96.5m ATD rather than 95.5ATD, 1m high.
| 03SR - Stations (RfL) | Cxxx-NCR-000020 | NCR | New __ Batching Plant Piling - Bowed Casing |  | Contr | SKC | PNY - Paddington New Yard (West) |  | 2014-07-02 | 2014-06-30 14:30 | -2 | 2014-06-18 12:38 | Geotechnical Engineering - Concrete - Bored Pile | 500 |  | Damaged | Reject | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | The top of the casing used on the __ Batching Plant P5 was found to be bowed by approximately 20mm in plan. This may have had an affect on the pile position, which will be checked once the pile has gained sufficient strength to be excavated around.
| 03SR - Stations (RfL) | Cxxx-NCR-000021 | NCR | Missed CRL Hold Points - start of hard secant piles for BDU |  | Crossrail | XRL | PNY - Paddington New Yard (West) |  | 2014-07-04 | 2014-06-24 16:00 | -10 | 2014-06-20 11:46 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Reject | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | Upon review of the pre-construction check sheet for hard secant piles for the BDU, CRL observed that two hold points for this activity had not been signed off by Crossrail prior to commencement of the activity. This applied to confirmation that a permit to load was in place and that all applicable MCRs were at code-2 or higher.
| 03SR - Stations (RfL) | Cxxx-NCR-000022 | NCR | New __ Batching Plant Piling - Discharging concrete before slump results confirmed |  | Contr | SKC | PNY - Paddington New Yard (West) |  | 2014-07-17 | 2014-07-07 13:40 | -10 | 2014-07-03 08:49 | Civil - Geotechnical Engineering | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Worker not correctly instructed | Completed |  | On 03/07/14 __ Ltd were seen to be discharging concrete into P65 of the Aggregate Bin piles before the slump test results were confirmed by __. The slump results were within tolerance, but not waiting for the results first does not comply with quality procedures.
| 03SR - Stations (RfL) | Cxxx-NCR-000023 | NCR | Cxxx Temporary Works Quality Audit |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2014-07-31 | 2014-07-28 15:29 | -3 | 2014-07-03 10:30 | Systems - Systems Engineering General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | The Temporary works Design Brief has been produced by TWC for the significant items. It was noted that this document does not have a revision number or document control number. The document was issued for construction on the 07th of March 2014. However, there was no evidence found of this document or the associated records submitted on eB. In addition, the Lever Arch Folders containing the hard copies of the relevant temporary works documentations and records were presented at the audit. These documents were also not submitted to the Cxxx Document Controller for uploading onto the eB system and ICosNet by the TWC. It was evident at the audit that there are general document control issues regarding the management and control of documents as the majority of these documents are maintained within the Lever Arch Files rather than submission on eB and ICosNet.
| 03SR - Stations (RfL) | Cxxx-NCR-000024 | NCR | Temporary Works Quality Audit |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2014-07-31 | 2014-07-29 12:32 | -2 | 2014-07-03 10:35 | Systems - Systems Engineering General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | The WI and Temporary Work procedures stated that the project will produce and submit a Design Statement. However, it was noted during the audit that this has not been produced or submitted on the project as requested within the contract and procurement procedure.
| 03SR - Stations (RfL) | Cxxx-NCR-000025 | NCR | Temporary Works Quality Audit |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2014-07-31 | 2014-07-31 15:43 | 0 | 2014-07-03 10:40 | Structural Engineering - Structural Engineering - General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | The following listed temporary works Design Check Certificates were verified at the audit • Derailment Walls – Cert No: C1431/17/CHK001 • Weighbridge – Cert No: C1431-07-Chk001 • Pile Cap Bases A-C – Cert No: C1431/15/CHK001 It was noted that the drawings numbers stated within these certificates were not consistent with the numbers within the actual drawings attached to the certs.
| 03SR - Stations (RfL) | Cxxx-NCR-000026 | NCR | Piling - Test Piles - Incorrect level of Solthread Pile |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2014-07-17 | 2014-07-04 13:24 | -13 | 2014-07-03 16:29 | Geotechnical Engineering - Geotechnical Engineering - General | 5000 |  | Incorrect Installation | Use As-Is | 3 (3-6k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | Test Pile STP1 (Solthread Pile) was installed to the incorrect depth, 21m rather than 16m
| 03SR - Stations (RfL) | Cxxx-NCR-000027 | NCR | Secant Piles - BDU - Pile Cages - Coupler Location incorrect |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2014-07-18 | 2014-07-09 14:00 | -9 | 2014-07-04 08:06 | Structural Engineering - Reinforcement | 2000 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Personnel Error - Inattention to detail | Completed |  | During the inspection of the pile cages for the secant wall the couplers and box-outs in piles 52 and 53 were incorrectly positioned on the reinforcing cage.
| 03SR - Stations (RfL) | Cxxx-NCR-000028 | NCR | No records of calibration for piling rig |  | Crossrail | PDP | PNY - Paddington New Yard (West) |  | 2014-07-24 | 2014-08-12 09:56 | 19 | 2014-07-10 07:46 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Verification Problems - Other | Completed |  | No records of calibration for Piling rig number BG18
| 03SR - Stations (RfL) | Cxxx-NCR-000029 | NCR | Recycled capping material chemical tests not undertaken to specified requirements |  | Crossrail | PDP | PNY - Paddington New Yard (West) |  | 2014-08-28 | 2014-08-28 08:27 | 0 | 2014-07-10 08:04 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | Recycled capping material chemical tests not undertaken to specified requirements as stated in Works Information v 2B part 20.8 & SHW series 601/15
| 03SR - Stations (RfL) | Cxxx-NCR-000030 | NCR | AD1 - BDU - Secant Piles - Male 31 Pile Lost Rig Data |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2014-07-24 | 2014-07-14 16:15 | -10 | 2014-07-10 10:57 | Geotechnical Engineering - Concrete - Bored Pile | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Personnel Error - Inattention to detail | Completed |  | Electronic pile log for secant male pile M31 was lost due to operator error, Operator accidently hit delete instead of save
| 03SR - Stations (RfL) | Cxxx-NCR-000031 | NCR | New __ Batching Plant Aggregate Bin Pile P5 Out of Positional Tolerance |  | Contr | SKC | PNY - Paddington New Yard (West) |  | 2014-07-29 | 2014-07-21 11:22 | -8 | 2014-07-15 09:20 | Geotechnical Engineering - Concrete - Bored Pile | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | (Please note: this NCR has been reworked to provide the correct as-built co-ordinate of P5). With reference to Cxxx-NCR-000020, after excavation around the first row of aggregate bin piles, P5 was found to be out of positional tolerance at 104mm from it design position. This exceeds the 75mm tolerance. The as-built co-ordinate of the centre of the pile is 75623.884, 36596.300.
| 03SR - Stations (RfL) | Cxxx-NCR-000032 | NCR | New __ Batching Plant Pile P9 Reinforcement Level Out of Tolerance |  | Contr | SKC | PNY - Paddington New Yard (West) |  | 2014-07-30 | 2014-07-24 09:34 | -6 | 2014-07-16 17:49 | Geotechnical Engineering - Concrete - Bored Pile | 750 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Pile P9 of the New __ Batching Plant Aggregate Bin piles, has a top of reinforcement level of 121.304m, 221mm lower than design. The tolerance is +150mm/-50mm. The projection of the bars is still within tolerance, but the cut-off level will have to be reduced to remove the debonding foam.
| 03SR - Stations (RfL) | Cxxx-NCR-000033 | NCR | Bus Deck - Secant Piles - Male 66 |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2014-08-07 | 2014-07-28 09:29 | -10 | 2014-07-24 14:12 | Geotechnical Engineering - Concrete - Bored Pile | 500 |  | Incomplete Works | Use As-Is | 4 (0.5-3k) | Complete | Verification Problems - Unavailability or inadequate M&TE | Completed |  | No concrete cubes taken for male pile number 66, on 10-7-2014. M66 was the next pile to be sampled based on the requirement for samples every 24m3, as per item 6.11 of the approved ITP Cxxx-COS-C-ITP-CR076_SD006-50009
| 03SR - Stations (RfL) | Cxxx-NCR-000034 | NCR | New __ Batching Plant Piles P32, P42 and P43 Top of Steel Level |  | Contr | SKC | PNY - Paddington New Yard (West) |  | 2014-08-05 | 2014-08-04 13:31 | -1 | 2014-07-29 16:19 | Geotechnical Engineering - Concrete - Bored Pile | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The top of steel level in piles P32, P42 and P43 in the New __ Batching Plant Aggregate Bin area is out of the +150/-50mm tolerance at -163mm, -69mm and -67mm respectively. The overall projection lengths of these bars is: P32=737mm P42=831mm P43=833mm which exceeds the minimum projection required as detailed in Cxxx-NCR-00032. This is the same non-conformance type as Cxxx-NCR-00032which was raised on P9.
| 03SR - Stations (RfL) | Cxxx-NCR-000035 | NCR | New __ Batching Plant - Aggregate Bins Ground Beams 4&5 |  | Contr | SKC | PNY - Paddington New Yard (West) |  | 2014-08-20 | 2014-08-13 08:13 | -7 | 2014-08-06 10:46 | Civil - Structural Engineering | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | The concrete tickets for Ground Beams on Gridlines 4 and 5 were not checked prior to the concrete being placed. This resulted in a mix being discarged which was not approved for this structure. The batching plant did send the wrong mix, but this was not picked up on. The approved mix was a C40/50 CIIIA, and a C40/50 CIIIA+SR mix was placed. This will not affect the structural integrity of the beams, but the process of checking tickets was not adhered to.
| 03SR - Stations (RfL) | Cxxx-NCR-000036 | NCR | New __ Batching Plant - Aggregate Bin Pile P72 Top of Steel Level |  | Contr | SKC | PNY - Paddington New Yard (West) |  | 2014-08-28 | 2014-08-27 16:33 | -1 | 2014-08-07 11:07 | Geotechnical Engineering - Concrete - Bored Pile | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Personnel Error - Inattention to detail | Completed |  | The top of steel in Pile P72 in the Aggregate Bins area has been found to be out of tolerance. The steel is 233mm high and there is a +150/-50mm tolerance on steel level. The lifting bands from the pile will be cut off. Care will be taken to ensure the projection bars are not damaged during the cutting operation.
| 03SR - Stations (RfL) | Cxxx-NCR-000037 | NCR | Bus Deck - Concrete - Reinforcement Clashes (__) |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2014-08-21 | 2014-08-19 11:52 | -2 | 2014-08-07 13:36 | Structural Engineering - Reinforcement | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | As per Cxxx-RFI-000201 Projection bars from piles clash with other longitudinal bars of the derailment wall when installed as per the Cxxx intent. The photo attached shows a bar which has been cranked in a controlled manner to allow installation of the derailment wall cage. We intend to place concrete Saturday 9-8-14. Please confirm this is acceptable.
| 03SR - Stations (RfL) | Cxxx-NCR-000038 | NCR | Cxxx Procurement Quality Audit |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2014-09-06 | 2014-09-03 09:49 | -3 | 2014-08-07 16:56 | Systems - Systems Engineering General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | Section 5.3 of Cxxx-COS-VS-GPD-CR076_SD006-50001 Procedure for Procurement of Subcontractors & Suppliers stated that the Squad review will be undertaken with the relevant design consultants, planning, commercial, project management, engineering and HSQE team in all pre-qualification, tender, mid-tender interview, post tender interviews on the project. It was evident at the audit that the Squad review is not regularly undertaken. The initial Squad review record dated 07/01/2014 was presented at the audit. It was noted during the review of this document that some member of the Squad team were not invited to attend the initial review. .
| 03SR - Stations (RfL) | Cxxx-NCR-000039 | NCR | New __ Batch Plant - Aggregate Bin Beam 3 Concrete Pour |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2014-08-23 | 2014-08-22 14:41 | -1 | 2014-08-09 13:25 | Structural Engineering - Concrete Member | 500 |  | Equipment Breakdown | Use As-Is | 4 (0.5-3k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | While pouring the concrete for ground beam 3 of the __ aggregate bins, a total time of 90 minutes elapsed between the time of completion of discharge of the 1st load of concrete and the start of discharge of the 2nd load of concrete. The concrete batch plant had a mechanical break down and could not batch the following loads in the time frame requested.
| 03SR - Stations (RfL) | Cxxx-NCR-000040 | NCR | Procurement Quality Audit |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2014-09-10 | 2014-09-08 14:59 | -2 | 2014-08-11 09:25 | Systems - Systems Engineering General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | Section 5.3 of the Rev 3.0 Cxxx-COS-V3-GDP-CR076_SD006-50001 Procedure for Procurement of subcontractors and suppliers required that the procurement team is to implement the Tender Query Schedule to capture and record all tender queries. However, it was noted during this audit that the procurement team has not produced this document therefore it was unclear how the Tender Queries are managed and monitored.
| 03SR - Stations (RfL) | Cxxx-NCR-000041 | NCR | Procedures for Calibration of Measuring and Test Equipment and Monitoring against Method Statements are not in place |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2014-09-26 | 2014-09-22 11:00 | -4 | 2014-08-12 16:46 | Systems - Systems Engineering General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | Cxxx have not produce or implement the following listed procedures on the project as requested within section 20.4 of the Work Information. The WI has stated that Contractor is to submit these QSPs for acceptance. 1) Control and Calibration of Measuring and Test Equipment Procedure 2) Monitoring against Method Statements Procedure
| 03SR - Stations (RfL) | Cxxx-NCR-000042 | NCR | __ - failure to complete slump test prior to concrete discharge |  | Crossrail | XRL | PNY - Paddington New Yard (West) |  | 2014-08-27 | 2014-08-19 15:53 | -8 | 2014-08-13 11:48 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | ITP for the installation of reinforced concrete to the __ batching plant (Cxxx-COS-C-ITP-CR076_SD006-50006 Rev. 4) item 13 requires a slump test to be undertaken prior to the discharge of a concrete load into the permenatn works. During the concrete pour for the aggregate bins ground slab undertaken on the 13th of August 2014, it was observed that the 5th concrete wagon was discharged prior to a slump test being performed on the delivery. The slump test for this load, once completed , confirmed that the concrete delivered was of compilant workability for an S4 slump required for the mix design. Contractor to implemnt steps to ensure that all site team are clear on the processes required for checking of slump pror to discharging concrete into the permenant works.
| 03SR - Stations (RfL) | Cxxx-NCR-000043 | NCR | New __ Batch Plant - Aggregate Bin Slab GL13-7 - Delays During Concrete Pour |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2014-11-28 | 2014-12-16 08:27 | 18 | 2014-08-14 19:02 | Structural Engineering - Concrete Member | 2000 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | During the concrete pour for the aggregate bin ground slab between GLs 13-7, the concrete was not supplied at the intervals requested and on three separate occasions there was over 1hr elapsing between the completion of discharge between one wagon and the start of discharge of the following wagon. This has resulted in possible cold joints in the slab. The full extent of the cold joints will not be known until all the shutters are struck (scheduled for Friday 15/8/14).
| 03SR - Stations (RfL) | Cxxx-NCR-000044 | NCR | New __ Batching Plant Aggregate Bins Ground Floor Slab - Hairline Cracks |  | Contr | SKC | PNY - Paddington New Yard (West) |  | 2014-11-07 | 2015-01-08 13:54 | 62 | 2014-08-19 16:11 | Structural Engineering - Concrete Member | 1000 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Improper handling of material | Completed |  | Hairline cracks have been identified in the north and south walls of the ground floor slab in the aggregate bins structure, poured on 13th August. A photo has been attached and the NCR has been passed to __ Formwork to try and ascertain why the cracks have appeared.
| 03SR - Stations (RfL) | Cxxx-NCR-000045 | NCR | AD-1 Bus deck piles - positional tollerance |  | Crossrail | XRL | PNY - Paddington New Yard (West) |  | 2014-09-11 | 2014-09-08 12:38 | -3 | 2014-08-21 11:08 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | During the Field engineering meeting on 07 August 2014 (see Cxxx-XRL-Z-MRC-CR076_SD006-50022), __ advised that several piles for the AD-1 bus deck works had been found to have been constructed out of positional tolerance in plan. To date (21 August 2014), __ have failed to raise an NCR on this observation within 24hrs and hence this NCR is being raised by CRL in light of __'s failure to follow their own non-conformance procedure (see Cxxx-COS-O4-GPD-CR076_SD006-50007 Rev 2, Cl 4).
| 03SR - Stations (RfL) | Cxxx-NCR-000046 | NCR | Bus Deck - Lightning protection - Works Commencing early |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2014-09-04 | 2014-09-08 12:37 | 4 | 2014-08-21 11:12 | Utilities Engineering - Utilities General | 500 |  | Documentation and Records | Reject | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | Contractor performed preliminary earthing checks on the piles prior to documentation been approved by CRL.
| 03SR - Stations (RfL) | Cxxx-NCR-000047 | NCR | New __ Batching Plant - Aggregate Bins GL13 Wall Finish |  | Contr | SKC | PNY - Paddington New Yard (West) |  | 2014-11-28 | 2015-03-05 11:42 | 97 | 2014-08-22 08:59 | Structural Engineering - Finishes | 1000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Worker not correctly instructed | Completed |  | The lower wall on GL13 of the Aggregate Bins should have an F3 finish with ties. A photo has been attached of the actual finish which shows that the joints are not uniform.
| 03SR - Stations (RfL) | Cxxx-NCR-000048 | NCR | Bus Deck - BDU - Secant Piles - Female Piles, No. 28 and 33 |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2014-10-10 | 2014-10-22 08:38 | 12 | 2014-08-29 17:02 | Civil - Civil Engineering General | 1000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Management Problem - Improper resource allocation | Completed |  | Female Piles Number 28 and 33 have been broken down below cut off level and out of tolerance. Pile F28 is 150mm below cut off level = 120.075m ATD Pile F33 is 420mm below cut off level = 119.805m ATD
| 03SR - Stations (RfL) | Cxxx-NCR-000049 | NCR | Concrete Constituent Testing |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2014-10-24 | 2014-10-13 11:09 | -11 | 2014-08-30 13:31 | Structural Engineering - Testing | 1000 |  | Testing and Commissioning | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | Series 1700 of specification appendix 5/1 requires the cement and aggregates for ready mix concrete to be tested at regular intervals (nominally on a monthly basis). __ has not undertaken this testing or received test results/ certificates from the concrete supplier (__) as it not deemed necessary as the supplier is a ISO9001 multinational supplier of concrete.
| 03SR - Stations (RfL) | Cxxx-NCR-000050 | NCR | New __ Batch Plant - Cofferdam Sheet Pile Steel Grade |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2014-09-13 | 2014-09-02 12:20 | -11 | 2014-08-30 13:36 | Geotechnical Engineering - Steel - Driven Pile | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | The temporary works design for the __ sheet pile cofferdams specifies a steel grade of 355GP for the sheet piles for the skip elevator and elevator hopper pits. The sheet piles delivered to site to be installed have a steel grade of 390GP which is a high grade of steel.
| 03SR - Stations (RfL) | Cxxx-NCR-000051 | NCR | New __ Batch Plant - Aggregate Bin North Wall (1A) Finish Discolouration |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2014-11-28 | 2015-02-06 15:56 | 70 | 2014-08-30 14:26 | Structural Engineering - Concrete Member | 2000 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | When pouring the concrete for wall 1A on the aggregate bin walls in the new __ batch plant, there was 1hr between the finish of discharge for the first concrete wagon and the start of discharge for the second concrete wagon. This has resulted in a discolouration along the pour line between the two loads of concrete. refer to the attached photos.
| 03SR - Stations (RfL) | Cxxx-NCR-000052 | NCR | __'s Yard Retaining Wall Damage |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2015-03-13 | 2015-03-24 09:43 | 11 | 2014-08-30 14:33 | Architectural - Brickworks/Blockworks | 2000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | During the construction/ use of the ramp for the Alfred Road upper piling platform, a section of the blockwork to the __’s Yard retaining wall has been damaged. Refer to the attached photos.
| 03SR - Stations (RfL) | Cxxx-NCR-000053 | NCR | Bus Deck - Secant Piles - Concrete Strength Failures in Female Piles at 56 days |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2014-09-16 | 2014-09-08 14:34 | -8 | 2014-09-02 09:43 | Geotechnical Engineering - Concrete - Bored Pile | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | Concrete Strength Failure in female piles below the 56 day Characteristic design requirement as per appendix 17/1 of C12/15. Piles and strength at 56 days: F37 - 11.4N/mm2 poured on the 25 June 14 F42 - 12.6N/mm2 poured on the 27 June 14 There are 3 others which have failed at 28 days - still waiting on 56 day results: F52 - 12.5N/mm2 F60 - 13.1N/mm2 F77 - 12.6N/mm2 56day results are due later this week for these.
| 03SR - Stations (RfL) | Cxxx-NCR-000054 | NCR | Bus Deck - LDA Piles - P288 Slump Failure |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2014-09-17 | 2014-09-08 14:52 | -9 | 2014-09-03 10:45 | Geotechnical Engineering - Concrete - Bored Pile | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | Slump test result for Pile P288 was 200mm, which exceeds the 180mm limit for S3 target slump as per the MCR Cxxx-COS-C-LRC-CR076_SD006-50008. Even though the slump failed, the concrete was used anyway.
| 03SR - Stations (RfL) | Cxxx-NCR-000055 | NCR | Bus Deck - Columns - F4 Finish WCC approval |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2014-10-22 | 2014-10-14 09:15 | -8 | 2014-09-06 12:37 | Structural Engineering - Finishes | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | Column Construction Commenced before Westminster City Council has given approval as per the requirement of Works Information Part 2A - Clause 3.3.1
| 03SR - Stations (RfL) | Cxxx-NCR-000056 | NCR | Bus Deck Alfred Rd Sheet Piles - Larger Sheet Pile Section Sizes Delivered To Site |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2014-10-16 | 2014-09-29 13:36 | -17 | 2014-09-25 17:00 | Geotechnical Engineering - Steel - Driven Pile | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Use of unapproved materials | Completed |  | Upon inspection of the sheet piles delievered to site, it was discovered that the pile sections SPUK had delievered a mix of 2607, 2707 and 2807 piles sections. The MCR only has approval for the 2607 sections and not the 2707 and 2807. The sheet pile sections are of the same grade of steel (355MPa) just with a greater wall thickness. The 2707 and 2807 are 12.7mm and 13.1mm respectively which is thicker than the 12mm on the 2607 piles. These sheet piles are of the same grade of steel just with a stronger section modulus.
| 03SR - Stations (RfL) | Cxxx-NCR-000057 | NCR | New __ Batch Plant - Skip Elevator Sheet Piling - Pile Refusal |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2014-09-25 | 2014-09-22 08:26 | -3 | 2014-09-09 18:21 | Geotechnical Engineering - Steel - Driven Pile | 1000 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | During the installation of the skip elevator pit sheet piles, three sheet piles hit refusal and could not be driven to the design toe level. Attached is a marked up drawing showing the as-built pile toe levels and the location of the sheet piles.
| 03SR - Stations (RfL) | Cxxx-NCR-000058 | NCR | ITP Cxxx-COS-C-ITP-CR076_SD006-50012 Rev 4.0 Needs to be amended |  | Crossrail | PDP | PNY - Paddington New Yard (West) |  | 2014-10-01 | 2014-09-25 14:18 | -6 | 2014-09-10 13:19 | Civil - Civil Engineering General | 500 |  | Planning | Rework | 4 (0.5-3k) | Complete | Personnel Error - Inattention to detail | Completed |  | Surveillance QS 335-03 found the ITP requires amendment to items 3, 6, 7 and 24. Please refer to the surveillance report for details
| 03SR - Stations (RfL) | Cxxx-NCR-000059 | NCR | Bus Deck - Alfred Road Sheet Piles - Preconstruction CRL Hold point not signed off |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2014-09-30 | 2014-09-19 12:13 | -11 | 2014-09-11 18:59 | Geotechnical Engineering - Steel - Driven Pile | 500 |  | Supervision/Management | Reject | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | Sheet Piling Commenced Without CRL signing their hold point on the preconstruction check sheet as per the ITP Cxxx-COS-C-ITP-CR076_SD006-50005
| 03SR - Stations (RfL) | Cxxx-NCR-000060 | NCR | Scanned images of signature is used on various Environmental documentation not wet signature as requested within Cxxx Document Control Procedure and the Contract |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2014-09-29 | 2014-09-26 09:57 | -3 | 2014-09-15 12:25 | Environmental - Environmental General | 500 |  | Documentation and Records | Reject | 4 (0.5-3k) | Complete | Personnel Error - Violation of requirement or procedure | Completed |  | The various environmental documents were found on eB with scanned images of signatures not wet signatures has required by Cxxx Document Control procedure and the contract requirement.
| 03SR - Stations (RfL) | Cxxx-NCR-000061 | NCR | Bus Deck - Concrete Finish - Column Z1a Blow holes |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2014-10-22 | 2014-10-21 16:58 | -1 | 2014-09-16 17:19 | Structural Engineering - Finishes | 1000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Blow holes on column Z1a do not meet the standard of the approved column sample provided for westminster city council, as per table 17/3 of the HA 1700 series appendices.
| 03SR - Stations (RfL) | Cxxx-NCR-000062 | NCR | New __ Batch Plant - Aggregate Bin Wall Pour 3A - Possible Cold Joint |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2015-01-30 | 2015-01-16 10:59 | -14 | 2014-09-17 07:41 | Structural Engineering - Concrete Member | 1000 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | Upon striking the shutters for the aggregate bin lower wall pour 3A, it was discovered that there may be a possible cold joint at the door opening. Refer to the attached photos.
| 03SR - Stations (RfL) | Cxxx-NCR-000063 | NCR | New __ Batch Plant - Aggregate Bin Wall Pour 3A - Concrete Finish to Walls 2A, 2B, 3A & 3B |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2014-11-28 | 2015-04-02 08:33 | 125 | 2014-09-17 07:38 | Structural Engineering - Concrete Member | 1500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Upon striking the shutters for the aggregate bin lower wall pours 2A, 2B, 3A and 3B, it was discovered that generally the overall finish to the walls is not as per the specified F3 finish. Refer to the attached photos. The quality issues relating to the walls are as follows: • Cover spacer blocks protruding from finished surface • Areas of the wall surface that are rough, blemished and do have a uniform, smooth finish. • Excessive and large blow holes present • Blue staining on the surface • Rust marks running down the walls • Hair line cracks in the wall surface at various locations • Nails being used to secure pieces of timbers to the side of the base slab finished surface for supporting the wall formwork
| 03SR - Stations (RfL) | Cxxx-NCR-000064 | NCR | New __ Batch Plant - Elevator Hopper Pit Cofferdam - Sheet Piles Hitting Refusal |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2014-10-13 | 2014-09-24 09:35 | -19 | 2014-09-18 08:22 | Geotechnical Engineering - Steel - Driven Pile | 1000 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | External Phenomenon - Other | Completed |  | During the installation of the sheet piles for the elevator loader hopper pit, 5 no. sheet piles reached refusal and could not be driven to the required design toe level. Refer to the attached marked up drawing showing the as-built toe levels and location of the sheet piles.
| 03SR - Stations (RfL) | Cxxx-NCR-000065 | NCR | Bus Deck - LDA Piles - AD1 - Pile 48 low top of steel |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2014-10-01 | 2014-09-23 17:40 | -8 | 2014-09-17 12:57 | Geotechnical Engineering - Concrete - Bored Pile | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Pile 48 reinforcement steel is at 121.369 ATD. Design is 121.485 (therefore steel is 116mm low). As per the accepted ITP the tolerance is +150m/ -50mm. (Cxxx-COS-C-ITP-CR076_SD006-50007) Current projection length is 784mm from pile cut off level. Location of of pile is in derailment wall on GL-1 which is a C32/40 concrete. Minimumn design projection is 830mm.
| 03SR - Stations (RfL) | Cxxx-NCR-000066 | NCR | Bus Deck - LDA Piles - Piles 153, 154, 155 projection rebar bent |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2014-10-17 | 2014-10-03 12:36 | -14 | 2014-09-19 11:07 | Structural Engineering - Reinforcement | 1000 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Piles 153, 154 & 155 projection rebar was bent by the excavator when excavating pile mat.
| 03SR - Stations (RfL) | Cxxx-NCR-000067 | NCR | Bus Deck - BDU Capping Beam Pour #2 Concrete from Battersea Plant |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2014-10-14 | 2014-09-29 13:38 | -15 | 2014-09-23 12:25 | Structural Engineering - Concrete Member | 500 |  | Equipment Breakdown | Use As-Is | 4 (0.5-3k) | Complete | External Phenomenon - Power failure or transient | Completed |  | Concrete supply for the BDU capping beam #2 (located approximately between gridlines X2-3 and Y2-3) was pre-arranged to come from the Park Royal plant. This was because the mix has changed now to a 10mm aggregate which __ brought in especially to Park Royal for the pour. On the day of the pour (22/9) the Park Royal plant unexpectedly went down after we had poured 6 waggons from the 17 ordered. The only other plant that had 10mm aggregate available to provide concrete volume required was the Battersea plant. Our current MCR for the BDU capping beam is only accepted using the: Paddington, Park Royal and Kings Cross plants. In order to keep the concrete alive, supply was brought in from Battersea as it was unknown when Park Royal supply would be available again. A single wagon ended up providing 7.7m3 from the Battersea plant in the pour as Park Royal was back online in the afternoon. 5No. cubes samples were taken on the single truck from Battersea as this coincided with the normal testing regiment. The exact same mix design (C32/40 A4_10mm) was used for the production of the concrete from Battersea as shown by the attached concrete ticket.
| 03SR - Stations (RfL) | Cxxx-NCR-000068 | NCR | On site concrete testing by __ not carried out in accordance with national standards for BDU capping beam pour |  | Crossrail | XRL | PNY - Paddington New Yard (West) |  | 2014-10-16 | 2014-10-20 10:58 | 4 | 2014-09-25 09:49 | Civil - Civil Engineering General | 1000 |  | Testing and Commissioning | Rework | 4 (0.5-3k) | Complete | Personnel Error - Inattention to detail | Completed |  | During Crossrail quality surveillance (QS336-04) dated 11th September 2014 slump testing for the capping beam pour was witnessed being carried out by __. Whilst witnessing the test, the __ technician did not use a remixing tray and square mouthed shovel to remix the sample before carrying out the slump test. BS EN 12350-2:2009 Testing Fresh Concrete Part 2: Slump Test clause 5 states “The sample shall be re-mixed using the remixing container and the square mouthed shovel before carrying out the test”. Additionally, it was noted that the base plate in which the test was being carried out on was placed on un-even ground made up of un-compacted 6F2, subsequently causing the base plate to tilt in various directions when compacting the concrete into the mould. This also caused the slump to fall ‘to one side’ when the cone was lifted, similar to a shear slump. BS EN 12350-2:2009 clause 4.5 states “Base plate/surface … rigid, flat, plate or surface on which to place the mould” and clause 6 “Dampen the mould and base plate and place the mould on the horizontal base plate/surface”.
| 03SR - Stations (RfL) | Cxxx-NCR-000069 | NCR | No temperature monitoring was carried out on the BDU capping beam pour to verify that the internal temperature of the concrete did not exceed 70oC |  | Crossrail | XRL | PNY - Paddington New Yard (West) |  | 2014-10-30 | 2014-10-17 14:29 | -13 | 2014-09-25 09:53 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | During Crossrail quality surveillance (QS336-04) dated 11th September 2014 it was noted that the dimensions for the BDU capping beam concrete pour was approximately 1m (height) x 2.5m (width) x 10m (length). During the site visit it was identified that no measures were in place to monitor the core temperature and temperature differential within the capping beam section which is typically monitored through the use of embedded thermocouples. SHW 1700 series structural concrete clause 1710.5 (ii) c states “The concrete temperature shall at no time exceed 70oC”. As no monitoring was in place, the internal temperature could not be verified as being below clause 1710.5. Additionally temperature differential is of importance; see CIRIA report Cxxx and comments under Finding 2 QS336-04.
| 03SR - Stations (RfL) | Cxxx-NCR-000070 | NCR | Temporary works design and drawings for the formwork installation of the BDU capping beam pour was not issued on eB prior to the BDU capping beam pour as required by ITP Inspection No. 2 as a (H) point |  | Crossrail | XRL | PNY - Paddington New Yard (West) |  | 2014-10-30 | 2014-10-20 10:50 | -10 | 2014-09-25 10:01 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | During Crossrail quality surveillance (QS336-04) dated 11th September 2014 temporary works design check certificate was provided and on post surveillance review it was identified that the temporary works design for the capping beam pour was submitted on eB for Crossrail approval on the 15th September 2014, four days after the capping beam pour; Cxxx-COS-S-CER-CR076_SD006-50009 Rev 1 refers. ITP Reinforced Concrete Works, Cxxx-COS-C-ITP-CR076_SD006-50012 Rev 4 Code 1, Inspection Number 2 states that the temporary works design and drawings should be issued on iCosNet and eB with confirmation of approval prior to the start of works; this is a Hold Point (H) for __ and __. This NCR has been raised by Crossrail in light of the Contractor’s failure to raise the NCR within 24hrs of the observation as required by Cl. 4.0 of the Cxxx non-conformance procedure (Cxxx-COS-O4-GPD-CR076_SD006-50007 Rev.2).
| 03SR - Stations (RfL) | Cxxx-NCR-000071 | NCR | New __ Batching Plant - P92 Low top of steel |  | Contr | SKC | PNY - Paddington New Yard (West) |  | 2014-11-07 | 2014-10-27 08:37 | -11 | 2014-09-25 14:45 | Geotechnical Engineering - Concrete - Bored Pile | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The deisgn pile cut off level for P92 in the GTU base is 120.775. The cut off level had to be broken down to 120.345 in order to remove the de-bonding foam on the projection bars. The pile was installed low.
| 03SR - Stations (RfL) | Cxxx-NCR-000072 | NCR | Bus Deck - Alfred Rd Retaining Wall Sheet Pile Refusal |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2014-12-12 | 2014-12-05 08:33 | -7 | 2014-09-25 15:51 | Civil - Geotechnical Engineering | 10000 |  | Design | Use As-Is | 2 (6-60k) | Complete | Management Problem - Other | Completed |  | A number of the sheet piles situated at the base of the Alfred Rd retaining wall were unable to be installed to the required toe depth. A very stiff clay layer was observed to be present at appoximately 115mATD. To date the following piles have not reached their design toe depth. The piles are numbered from East to West. No. 02, Toe Level = 114.850mATD, Difference = 2.850m High No. 03, Toe Level = 114.340mATD, Difference = 2.340m High No. 05, Toe Level = 112.780mATD, Difference = 0.780m High No. 06, Toe Level = 112.235mATD, Difference = 0.235m High No. 07, Toe Level = 112.990mATD, Difference = 0.990m High No. 08, Toe Level = 115.370mATD, Difference = 3.370m High No. 28, Toe Level = 113.860mATD, Difference = 1.860m High
| 03SR - Stations (RfL) | Cxxx-NCR-000073 | NCR | New __ Batching Plant - Low Compressive Strength Concrete Results for Aggregate Bin Structures |  | Contr | SKC | PNY - Paddington New Yard (West) |  | 2014-12-12 | 2014-12-01 11:53 | -11 | 2014-09-25 17:34 | Geotechnical Engineering - Concrete - Bored Pile | 1500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | The 28 day compressive strength results for Columns 10A and 10B in the Aggregate Bins, was lower than the specifiec 50N/mm2. The results achieved 41.2 and 42.1N/mm2.
| 03SR - Stations (RfL) | Cxxx-NCR-000074 | NCR | Surveying - Delayed incorporation of monitoring data into the CRL UCIMS monitoring database |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2015-01-31 | 2015-02-19 13:29 | 19 | 2014-09-26 13:02 | Geotechnical Engineering - Geotechnical Monitoring | 500 |  | Software | Reject | 4 (0.5-3k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | No monitoring data is currently being incorporated into the Crossrail UCIMS database due to delay in the set up of Geoscope 7 online database as required by Cl. 13 of the Cxxx earthworks specification (Cxxx-CSY-C2-RSP-CR076_MS005-50001 Rev.3).
| 03SR - Stations (RfL) | Cxxx-NCR-000075 | NCR | New __ Batching Plant - Chamfer left on corner of Wall 1A Aggregate Bins |  | Contr | SKC | PNY - Paddington New Yard (West) |  | 2014-12-05 | 2014-12-09 10:21 | 4 | 2014-10-01 15:30 | Structural Engineering - Concrete Member | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | A chamfer in the south east corner of upper wall 1A in the aggregate bins came away from the shutter and is partially embeded in the corner of the wall.
| 03SR - Stations (RfL) | Cxxx-NCR-000076 | NCR | New __ Batching Plant - Core A1 & A2 General Finishes (GL13-9). |  | Contr | SKC | PNY - Paddington New Yard (West) |  | 2014-12-05 | 2015-03-31 16:18 | 116 | 2014-10-01 18:31 | Structural Engineering - Concrete Member | 1500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The first lift of upper walls in Core A1 & A2 in the aggregate bins have general finishes that require remedial work. This area includes the internal walls avove the intermediate slaba and the external walls GL13-9. Remedial works include: - Deviation of ply has created gaps between joints - The lower kicker needs making good - Tie holes, notably one on the outer eastern A1 wall needs making good - The areas between wall pours needs making good Photos attached.
| 03SR - Stations (RfL) | Cxxx-NCR-000077 | NCR | Bus Deck - MEP - Bus Depot - Existing Water pressure monitoring |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2014-12-12 | 2014-12-02 13:07 | -10 | 2014-10-03 09:56 | Mechanical - Hot & Cold Water Supplies | 1000 |  | Manufacturing Defect | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | The data logger that was measuring the water pressure for the existing bus garage did not record any data over the period that it was installed. We requested from the hire company that we required logging at one hour intervals, and were informed that the pressure gauge that the supplied would do that job. Upon inspection of the device the hire company have found that the logger will only log to a maximum of 59 mins 59 secs. Data logger has now been installed and data is being read please refer to attached
| 03SR - Stations (RfL) | Cxxx-NCR-000078 | NCR | Bus deck - Derailment Wall 2 - Reinforcement Schedule, drawing and fixing incorrect (50013) |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2014-10-20 | 2014-10-14 09:08 | -6 | 2014-10-06 10:25 | Structural Engineering - Reinforcement | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | Upon fixing reinforcement to COS-S-DWG-CR076_MS005-50013 __ formwork noticed that the scheduled rebar did not match the length of the derailment wall. The schedule COS-S-TSC-CR076_MS005-50013 had the following lengths of bar. Bar Mark 72 = 1760 mm Bar Mark 205 = 11025 mm Bar Mark 14 = 12000 mm Bar Mark 70 = 7720 mm Total effective rebar length minus cover using designed lap length of 1240mm = 28915mm Derailment wall as per to GA drawing is 29404mm Difference = 490mm short on rebar length. __'s difference split over two lap locations meaning there was only 1000mm lap in two locations. Please see attached email sent to __ regarding the works __ undertook, and the confirmation from the __ that the remedial work to be done to mitigate is satisfactory.
| 03SR - Stations (RfL) | Cxxx-NCR-000079 | NCR | Bus Deck - Derailment Wall 2 - Pour 2 Concrete Slump failure |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2014-10-20 | 2014-10-20 16:00 | 0 | 2014-10-06 14:22 | Structural Engineering - Concrete Member | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | On Saturday 04-10-14 the second pour of Derailment Wall on GL2 was completed, 24m3 (4 loads). Pour was scheduled for 10:30am. The 2nd wagon to site failed its first slump test, but passed when restested after the 4th truck was poured first.
| 03SR - Stations (RfL) | Cxxx-NCR-000080 | NCR | Chamber procured prior to MCR sign off |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2014-10-28 | 2014-10-14 17:17 | -14 | 2014-10-06 15:58 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | Utility chamber materials were ordered prior to the MCR being signed off Code 1. The sign off the MCR is subject to an associated FCD that for the inspection chamber lids. The ITP calls for an MCR sign off "prior to delivery/use in works" __ request the PFE Code 3’s the associated MCR and we will resubmit the MCR with only the elements that are not constrained by the FCD in order to maintain programme.
| 03SR - Stations (RfL) | Cxxx-NCR-000082 | NCR | __ - Permit to Load Props 2 and 3 in the Elevator Loading Hopper |  | Crossrail | XRL | PNY - Paddington New Yard (West) |  | 2014-10-29 | 2014-10-22 16:36 | -7 | 2014-10-08 17:03 | Civil - Excavation | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Personnel Error - Inattention to detail | Completed |  | In accordance with ITP Cxxx-COS-C-ITP-CR076_SD006-50002 Rev. 5 - IN 11, CRL were invited to attend the hold point intervention for the permit to load frames at level 2 & 3 for the elevator loading hopper temporary works. On review, it was established that: 1) 2 hanging chains had not been installed between props 1-2 and 2-3 as required by drawing 37054/MH/101 Revision C03. 2) ITP check sheet had not been updated to indicate that there were two props to be installed at the low level following a revision to the temporary works design. Therefore details of only one of the low level props had been installed. 3) Contractors Permit to load (PTL) had been signed by the TWS and TWC, however no document revisions were included on the PTL. This was seen as an important omission based on the fact that a revision to the temporary works design had occurred. 4) Review of the ITP check sheet found that the top prop had been installed outside of the tolerance specified on the ITP (installed -70mm from design against a tolerance of +/- 20mm).
| 03SR - Stations (RfL) | Cxxx-NCR-000083 | NCR | Bus Deck - BDU - Eastern Approach slab - Rail U-Bolts Omitted |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2015-01-30 | 2014-11-20 11:17 | -71 | 2014-10-27 09:57 | Structural Engineering - Inserts | 750 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Subcontractor Problems - Interfacing problems | Completed |  | The U-Bolts for the rail shown on drawing Cxxx-CSY-S-DDD-CR076_MS005-01255 were omitted.
| 03SR - Stations (RfL) | Cxxx-NCR-000084 | NCR | New __ Batching Plant P78 Out of Positional Tolerance |  | Contr | SKC | PNY - Paddington New Yard (West) |  | 2014-11-12 | 2014-10-24 13:49 | -19 | 2014-10-22 16:56 | Geotechnical Engineering - Concrete - Bored Pile | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Pile P78 in the __ Batching Plant has as-built coordinates of 75588.041, 36620.994 which is 99mm out of position. The poistional tolerance is +/- 75mm.
| 03SR - Stations (RfL) | Cxxx-NCR-000085 | NCR | New __ Batching Plant - Ground Floor Slab Levels |  | Contr | SKC | PNY - Paddington New Yard (West) |  | 2015-06-30 | 2015-06-19 17:14 | -11 | 2014-10-24 18:03 | Structural Engineering - Concrete Member | 55000 |  | Workmanship | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The ground floor slab of the aggregate bins has shown signs of ponding. __ Formwork to carry out level survey and to propose any remedial action to be undertaken.
| 03SR - Stations (RfL) | Cxxx-NCR-000086 | NCR | Bus Deck - BDU Capping Beam Pour #3 Limestone 10mm Aggregate |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2014-11-28 | 2014-11-04 14:46 | -24 | 2014-10-27 11:06 | Structural Engineering - Concrete Member | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Use of unapproved materials | Completed |  | The BDU capping beam pour #3 located on the north eastern site of the BDU, running 23m east, required the use of 10mm aggregate. Due to high concrete demands last week, Larfarge tarmac were able to supply the 10mm mix using limestone aggregate. Upon later checking the MCR, it was found the approved MCR only contained reference to 10mm gravel mix, not limestone that was used in the BDU capping beam. Hence, an unapproved material was used in the capping beam pour#3. The __ delivery ticket states that the concrete has been supplied in accordance with BS 8500. The 7 Day cube results for the 10mm limestone aggregate are in the same order of magnitue as the cube results for capping beam pours #1 and #2 that used 10mm gravel. These are: 33.7 MPa, 35.8 MPa and 32.4 MPa. Capping beam pours #1 and #2 (using 10mm gravel) have had mean cube crush results to date of: 7 Day - 34.6 MPa (8No. Samples) 28 Day - 50.1 MPa (16 No. Samples)
| 03SR - Stations (RfL) | Cxxx-NCR-000087 | NCR | New __ Batch Plant - Water Main - Valve MCR |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2014-11-19 | 2014-11-14 16:35 | -5 | 2014-10-29 07:15 | Utilities Engineering - Water | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | The valves for the water main in the new __ batch plant were installed prior to the MCR being apporved code 1.
| 03SR - Stations (RfL) | Cxxx-NCR-000088 | NCR | New __ Batch Plant - Concrete Remedials Starting without Code1 RAMS |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2014-11-12 | 2014-11-11 12:49 | -1 | 2014-10-29 07:21 | Structural Engineering - Concrete Member | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Procedure Problem - Defective or inadequate procedure | Completed |  | The concrete remedial works to the __ aggregate bins commenced prior to CRL approving the RAMS code 1.
| 03SR - Stations (RfL) | Cxxx-NCR-000089 | NCR | Bus Deck: GUC inclinometer - Unapproved grout mix |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2014-11-27 | 2015-02-19 13:37 | 84 | 2014-10-30 14:55 | Geotechnical Engineering - Grouting Instrumentation | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | With reference to drawings Cxxx-CSY-C2-DDD-CR076_MS005-1028 and RFI 306. 3 no. inclinometer tubes were encased in a grout mix that had no approved MCR (Materials compliance Record). The grout used had a mix proportion of 1:2:7 (Bentonite: Cement: Water) which the subcontractor believes has the same stifness as that of the surrounding clay.
| 03SR - Stations (RfL) | Cxxx-NCR-000090 | NCR | Bus Deck - Integrity Tesing - Pile 42 |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2014-11-17 | 2014-11-05 10:54 | -12 | 2014-10-30 16:31 | Geotechnical Engineering - Concrete - Bored Pile | 500 |  | Equipment Breakdown | Use As-Is | 4 (0.5-3k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | Pile 42 was integrity tested when it was not completely broken down to cut off level due to plant break down. Top of pile was approximately 1m higher than cut off. Technican was booked in for Monday when pile cropper had breakdown on Saturday.
| 03SR - Stations (RfL) | Cxxx-NCR-000091 | NCR | Bus Deck - AD1 Derailment Wall GL1 - Low Concrete Cover south side of the wall around GL.W |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2015-01-30 | 2015-01-19 15:00 | -11 | 2014-11-18 09:18 | Structural Engineering - Reinforcement | 1000 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During a prepour inspection performed by __s Site Engineers on 31/10/14 it was noticed that the top half of the starter bars from the previous pour were within the design cover zone on the south side of derailment wall 1 near GL-W. The bars that were then lapped onto these were also in the cover zone. Cover in this area was noticed to be approximately 40mm as against the design 65mm, the bars were realigned to the correct cover along the length of the pour
| 03SR - Stations (RfL) | Cxxx-NCR-000092 | NCR | Bus Deck -BDU - North side Capping beam increased reinforcment cover |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2014-11-17 | 2014-11-05 10:55 | -12 | 2014-10-31 15:56 | Structural Engineering - Reinforcement | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | Bar Mark 05 on schedule Cxxx-COS-S-TSC-CR076_MS005-50050 detailed incorrectly, increasing the cover on the northern capping beam of the BDU.
| 03SR - Stations (RfL) | Cxxx-NCR-000093 | NCR | Bus Deck Piling: P220 - No Concrete cube samples taken |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2014-12-05 | 2014-11-25 11:02 | -10 | 2014-11-11 19:28 | Civil - Structural Engineering | 500 |  | Testing and Commissioning | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | During piling works on Monday 10/11/13,the first load (8m3)of concrete was used to complete pile P220 (solthread pile) . Cube samples for the concrete batch were to be taken from subsequent loads intended to complete the rest of the piles scheduled for the day, however, due to the late cancellation of concrete we missed the opportunity to take samples as required by the ITP- Cxxx-COS-C-ITP-CR076_SD006-5007 (1set of cubes in 24m3 of concrete) .
| 03SR - Stations (RfL) | Cxxx-NCR-000094 | NCR | New __ Batch Plant - Possible Defects with Piles 74 & 77 |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2015-08-31 | 2015-09-01 11:29 | 1 | 2014-11-17 12:15 | Geotechnical Engineering - Concrete - Bored Pile | 5000 |  | Workmanship | Use As-Is | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The integrity testing on piles 74 and 77 in the new __ Batch Plant have revealed annomolies/ possible defects in the concrete. The pile designer has reviewed the test results and construction records and has advised that the piles are fit for purpose. The piling subcontractor have provided a statement to this effect.
| 03SR - Stations (RfL) | Cxxx-NCR-000095 | NCR | Bus Deck - BDU - Western BDU Upstands - __s held in place with steel chairs |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2014-12-12 | 2015-03-19 14:11 | 97 | 2014-11-25 12:12 | Structural Engineering - Concrete Member | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | The galvinised halfens were held in place with steel chairs meaning there was reinforcement inside the cover zone in these isoloated areas.
| 03SR - Stations (RfL) | Cxxx-NCR-000097 | NCR | __ Plant:- Temporary Works Clash with Loader Hopper Pile Cap (Ground Obstruction) |  | Contr | SKC | PNY - Paddington New Yard (West) |  | 2014-12-18 | 2014-12-18 15:47 | 0 | 2014-11-27 12:42 | Civil - Civil Engineering General | 2000 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | We attach our as built survey of the temporary works sheet piles in the __ Loader Hopper Pile Cap. The survey indicates a clash with the temporary works steel sheet piles and the permanent works pile cap ( P98) of 86mm. We believe this temporary steel pile has deviated from its true line due to a ground obstruction or some other cause beyond our control.
| 03SR - Stations (RfL) | Cxxx-NCR-000098 | NCR | Bus Deck - BDU - Western Approach Slab - Cold Joint / Formwork movement |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2015-01-30 | 2015-01-12 10:18 | -18 | 2014-11-26 11:43 | Structural Engineering - Concrete Member | 2000 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The south western corner of western BDU approach slab appears to have a cold joint or movement in the formwork.
| 03SR - Stations (RfL) | Cxxx-NCR-000099 | NCR | Bus Deck - Columns - Mechanical Damage AD1 GL-4 Columns |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2015-03-20 | 2015-01-22 07:59 | -57 | 2014-11-26 16:49 | Architectural - Finishes | 1000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Improper preservation of material after installation | Completed |  | It has been noticed that there are some small mechanical damage on the columns on GL-1 in AD1
| 03SR - Stations (RfL) | Cxxx-NCR-000100 | NCR | New __ Batching Plant - Skip Elevator Wall Finish |  | Contr | SKC | PNY - Paddington New Yard (West) |  | 2014-01-24 | 2015-02-19 13:13 | 391 | 2014-11-27 10:41 | Structural Engineering - Finishes | 5000 |  | Incorrect Installation | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | On striking the shutter on the south west wall in the skip elevator, it can be seen that the concrete has segregated on the lower half of the wall and there are signs of exposed aggregate.
| 03SR - Stations (RfL) | Cxxx-NCR-000101 | NCR | Mess room slab missing nib |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2015-01-16 | 2015-01-28 08:45 | 12 | 2014-11-27 10:43 | Civil - Civil Engineering General | 1000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | Cxxx-RFI-000300 stipulates a change to the mess room slab alignment. This change (eastern nib section of mess room slab) was not poured by our sub-contractor. See attached "Mess room slab NCR" Note the corresponding paving slab to the east was cast prior to the mess room. Please see proposed corrective action
| 03SR - Stations (RfL) | Cxxx-NCR-000102 | NCR | __ Utilities: DP7 level |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2015-05-20 | 2015-04-15 11:15 | -35 | 2014-11-27 11:16 | Civil - Civil Engineering General | 1000 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Draw pit 7 and surrounding pavement slabs have been cast. There is a lip in the levels of the top of the pavement slab and the top of the chamber lid (chamber lower). Please see attached as-built survey "Cxxx-COS-CIV-SKT-000146_DP7_PAVEMENT AS-BUILT SURVEY-006" The largest step is 14mm.
| 03SR - Stations (RfL) | Cxxx-NCR-000103 | NCR | Temporary works sheet piles in the __ Loader Hopper Pile Cap. |  | Contr | SKC | PNY - Paddington New Yard (West) |  | 2014-12-18 | 2014-12-18 16:32 | 0 | 2014-11-27 12:45 | Civil - Civil Engineering General | 500 |  | Material | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | Our survey indicates a clash with the temporary works steel sheet piles to the west wall with the permanent works of approx 60mm We believe this temporary steel pile has deviated from its true line due to a ground obstruction or some other cause beyond our control.
| 03SR - Stations (RfL) | Cxxx-NCR-000104 | NCR | Bus Deck - Derailment Wall GL2 Column Starter Bob Bar |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2014-12-18 | 2014-12-04 14:07 | -14 | 2014-12-03 15:16 | Structural Engineering - Reinforcement | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Improper resource allocation | Completed |  | Cxxx-COS-S-DWG-CR076_MS005-50013 Column W2c had bob bars used in place of straight bars (Bar Mark 20) in the derailment wall. Same achorage lenght was maintained as BM20 however an additional bob was included
| 03SR - Stations (RfL) | Cxxx-NCR-000105 | NCR | Bus Deck - BDU - East Upstand surface finish uneven |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2015-03-31 | 2015-01-29 13:59 | -61 | 2014-12-03 16:41 | Structural Engineering - Finishes | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Surface finish on the top of the Eastern upstand of the BDU has imprint from timber used to maintain the wall width when tightening up the dywidag ties. With out a accurate specification for the horizontal surface finish in this location __ has assumed a U4 finish.
| 03SR - Stations (RfL) | Cxxx-NCR-000106 | NCR | Bus Deck - Alfred Road Capping beam - Concrete finish |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2015-03-31 | 2015-01-13 12:55 | -77 | 2014-12-03 17:02 | Structural Engineering - Finishes | 2000 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Contamination | Completed |  | Surface finish on the top of the Alfred road capping beam uneven in locations near construction joints. With out a accurate specification for the horizontal surface finish in this location __ has assumed a U4 finish.
| 03SR - Stations (RfL) | Cxxx-NCR-000107 | NCR | New __ Batching Plant - Retaining Wall Concrete Finish |  | Contr | SKC | PNY - Paddington New Yard (West) |  | 2015-01-09 | 2015-01-09 16:09 | 0 | 2014-12-03 16:11 | Structural Engineering - Finishes | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | The concrete finish on some of the retaining wall panels requires attention. There are Blow holes greater than 10mm, deviation of joints between panels,and the general finish on the top of the retaining wall requires remedial works.
| 03SR - Stations (RfL) | Cxxx-NCR-000108 | NCR | Bus Deck - Pile Cap Z3 - Concrete pour exceeding 2hr limit |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2015-01-23 | 2015-01-20 15:03 | -3 | 2014-12-08 15:03 | Structural Engineering - Concrete Member | 500 |  | Planning | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Use of unapproved materials | Completed |  | The first two concrete deliveries for Pile Cap Z3 exceeded the 2hr limit as per Appendix 17/1.
| 03SR - Stations (RfL) | Cxxx-NCR-000109 | NCR | Bus Deck - Column AA3 - Concrete pour exceeding 2hr limit |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2015-01-23 | 2015-01-20 15:07 | -3 | 2014-12-08 14:53 | Structural Engineering - Concrete Member | 500 |  | Planning | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Use of unapproved materials | Completed |  | The concrete delivery for Column AA3 exceeded the 2hr limit as per Appendix 17/1.
| 03SR - Stations (RfL) | Cxxx-NCR-000110 | NCR | __ - Test and Anchor Piles Spacing |  | Crossrail | PDP | PNY - Paddington New Yard (West) |  | 2015-05-30 | 2015-05-27 15:18 | -3 | 2014-12-08 18:14 | Geotechnical Engineering - Geotechnical Engineering - General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Subcontractor Problems - Interfacing problems | Completed |  | The layout of the anchors for P89 and P100 was found to be at 1.75m centre from the test pile as shown on __ Design Document Cxxx-COS-S-RGN-CR076_SD006-50003. The minimum spacing indicated between the test and reaction piles does nnot appear to comply with Clause B15.9.5 of ICE Specificaction. The ICE specification states this spacing shall be no closer than three times the diameter of the test pile o 2m whichever is the greater.
| 03SR - Stations (RfL) | Cxxx-NCR-000111 | NCR | Alfred Road Retaining Wall Sheet Pile - As-built Toe Depth |  | Crossrail | PDP | PNY - Paddington New Yard (West) |  | 2014-12-23 | 2014-12-18 16:20 | -5 | 2014-12-09 12:18 | Geotechnical Engineering - Steel - Driven Pile | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Lack of procedure | Completed |  | Cxxx-RFI-000194 stipulated toe level for the sheet piles at 0-20.5 to be at 112.400m. Following close-out of the RFI, Cxxx stated via email for this to increase by 400mm to a new toe level of 112.000m. Contractor installed as per email confirmation.
| 03SR - Stations (RfL) | Cxxx-NCR-000112 | NCR | New __ Batch Plant - Aggregate Bin Piles not Integrity Tested |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2015-02-13 | 2015-01-22 11:39 | -22 | 2014-12-14 19:17 | Geotechnical Engineering - Concrete - Bored Pile | 1000 |  | Testing and Commissioning | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | The following piles for the __ aggregate bins did not have an integrity test performed at cut off level prior to construction the ground beams: • Pile 43 • Pile 44 • Pile 45 • Pile 46
| 03SR - Stations (RfL) | Cxxx-NCR-000113 | NCR | Bus Deck - Piles - AD2 & AD3 - P225, 226, 307 & 308 10mm concrete mix |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2015-01-30 | 2015-01-22 07:56 | -8 | 2014-12-16 16:07 | Geotechnical Engineering - Concrete - Bored Pile | 500 |  | Manufacturing Defect | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Use of unapproved materials | Completed |  | Piles P225, 226, 307 & 308 were all poured using an unapproved 10mm C32/40 concrete mix, because of the unavailability of a 20mm mix on the day. These piles were poured on Friday 12-12-14.
| 03SR - Stations (RfL) | Cxxx-NCR-000114 | NCR | New __ Batching Plant - Stormwater Wedge Pit Walls |  | Contr | SKC | PNY - Paddington New Yard (West) |  | 2015-04-30 | 2015-04-30 12:04 | 0 | 2014-12-17 15:34 | Structural Engineering - Concrete Member | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The top of the stormwater wedge pit wall undulates and does not have a smooth surface finish. Remdial works are required to rectify the finish.
| 03SR - Stations (RfL) | Cxxx-NCR-000115 | NCR | New __ Batching Plant - GTU Tower Base Concrete Finish |  | Contr | SKC | PNY - Paddington New Yard (West) |  | 2015-02-11 | 2015-01-16 10:07 | -26 | 2014-12-17 16:16 | Structural Engineering - Concrete Member | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | Areas on the GTU walls requires remedial attention. There are signs of concrete overspill from the slab pour on to the lower walls.
| 03SR - Stations (RfL) | Cxxx-NCR-000116 | NCR | __ Area - Change in paving concrete mix |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2015-01-19 | 2015-02-26 12:11 | 38 | 2015-01-05 14:18 | Civil - Concrete Pavement | 500 |  | Manufacturing Defect | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Use of unapproved materials | Completed |  | Due to the programme constraints to handover the initial paving slabs surrounding the batching plant to __’s fit-out contracts, __ requested __ supply an identical mix to the PAV2 90/40 with 5.4kg/m3 strux fibres stated by the designer but with a 40/50 N/mm2 strength to allow quicker curing. Despite our request, __ supplied a different mix (attached "MDC __ Cxxx Paddington RC50XF") on the day for on 4/12/14 for slabs A6-2 & A17-1 (see attached "complete paving areas"). Please confirm if this is acceptable to the design requirements.
| 03SR - Stations (RfL) | Cxxx-NCR-000117 | NCR | Bus Deck - Piling - AD3 - Pile P281 installed out of positional tolerance |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2015-04-30 | 2015-01-13 12:58 | -107 | 2015-01-08 17:18 | Geotechnical Engineering - Concrete - Bored Pile | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Pile 281 was installed 119mm out of position, outside the 75mm contruction tolerance.
| 03SR - Stations (RfL) | Cxxx-NCR-000118 | NCR | Bus Deck - Piling - AD3 - Pile P427 concrete tested by __ Engineer not __ due to technician been injured |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2015-01-22 | 2015-01-22 08:01 | 0 | 2015-01-08 17:35 | Geotechnical Engineering - Concrete - Bored Pile | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Worker not qualified | Completed |  | __ Concrete technician rolled his ankle at work and was taken to hosipital for his injury. __ had P427 open with concrete already booked. Concrete testing and sampling was completed by __ Site Engineer in his place
| 03SR - Stations (RfL) | Cxxx-NCR-000119 | NCR | Cxxx ITP & Certification Internal Quality Audit |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2015-02-15 | 2015-02-24 11:11 | 9 | 2015-01-09 12:52 | Systems - Systems Engineering General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | One of the key project deliverable is the ITP Schedule. Rev 7.0 Cxxx-COS-O4-TSC-CR076_SD006-50002 ITP schedule with decal 2, dated 22/09/14 was confirmed within the eB system. It was evident at the audit that this Schedule is not being revised and submitted on eB to meet the 4 weekly submissions as part of the deliverable requirement of the contract. It was also noted that the relevant section engineers were not taking full responsibility for the overall updating and maintenance of this Schedule to incorporate all inspections that have been undertaken within their areas to enable the 4 weekly submissions.
| 03SR - Stations (RfL) | Cxxx-NCR-000120 | NCR | Cxxx ITP, Surveillance & Certification Internal Quality Audit |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2015-02-15 | 2015-02-10 09:53 | -5 | 2015-01-09 12:58 | Systems - Systems Engineering General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | Section 4 of the Inspection & Testing procedure requires that Specimen Signatures of those authorised to carry out inspection and testing regime are maintained. There was no evidence found at the time of the audit that this document is maintained by the Agents. It could not be demonstrated how this had been enforced. In addition, prepare, check and approve responsibilities should also be identified within this document.
| 03SR - Stations (RfL) | Cxxx-NCR-000121 | NCR | Cxxx ITP, Surveillance & Certification Internal Quality Audit |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2015-02-15 | 2015-03-04 10:29 | 17 | 2015-01-09 13:08 | Systems - Systems Engineering General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | Certification Schedule has been produced and maintained within the project. Rev 4 Certification Schedule was confirmed within the second tap of Rev 4 336-COS-O4-LST-CR076_SD006-50001 of the Package Breakdown Structure decal 2, dated 28/10/14 on eB. The detailed of the proposed forecast dates of the completion of the works and the subsequent forecast submission dates to Crossrail were also confirmed within this document. In addition, the names of the various Agents assigned for various sections of the works were confirmed within the __. However, it was not evident during this audit that both Certificate Schedule and __ have not been updated and distributed on a weekly and 4 weekly basis to meet the requirement of the contract by the Certification Manager to enable the overall awareness of the upcoming packages and progress of package compilation.
| 03SR - Stations (RfL) | Cxxx-NCR-000122 | NCR | Cxxx ITP, Surveillance & Certification Internal Quality Audit |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2015-02-15 | 2015-04-15 12:42 | 59 | 2015-01-09 13:16 | Systems - Systems Engineering General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | There was no evidence of training or briefing of this procedure to the project team and the sub-contractors found during the audit. In addition, of the pre-start or progress meetings with the sub-contractors and client to ensure that the assurance documents are progressing. There was no evident found that the relevant compliers of the assurance documents and records are made aware of the time scales to complete and obtain approval of the packages. It was agreed that the Certification Manager is to invite the key __ and Sub-contractor representatives to the weekly Certification meeting and to provide the necessary briefing and training required to enable this process to be effectively implemented.
| 03SR - Stations (RfL) | Cxxx-NCR-000123 | NCR | Cxxx ITP, Surveillance & Certification Internal Quality Audit |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2015-02-08 | 2015-04-15 12:50 | 66 | 2015-01-09 13:22 | Systems - Systems Engineering General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The Surveillance Checklist, actions, report were not prepared or submitted within the timescale stated within the Surveillance procedure. In addition, the Observation Tracker was not regularly updated to reflect surveillance that has been undertaken. The Certification Manager is responsible for ensuring that this process is effectively managed and controlled. This CAR is raised based on the overall management of the Surveillance process.
| 03SR - Stations (RfL) | Cxxx-NCR-000124 | NCR | New __ Batching Plant - Retaining Wall General Finsihing - Sections 3 to 7 |  | Contr | SKC | PNY - Paddington New Yard (West) |  | 2015-04-30 | 2015-05-07 16:16 | 7 | 2015-01-09 14:23 | Structural Engineering - Finishes | 1000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The retaining wall sections 3 to 7 as shown on the attached sketch, require remedial works to smooth undulations on the top of the wall, fill blow holes and general finishing works.
| 03SR - Stations (RfL) | Cxxx-NCR-000125 | NCR | New __ Batching Plant - General concrete finishes on aggregate bins GL2-9 |  | Contr | SKC | PNY - Paddington New Yard (West) |  | 2015-02-14 | 2015-03-05 11:51 | 19 | 2015-01-09 14:37 | Structural Engineering - Finishes | 5000 |  | Workmanship | Repair | 3 (3-6k) | Complete | Material/Preservation Problems - Other | Completed |  | The external aggregate bin walls (specifically Gridlines 2-9 for the NCR) have general finishes that require remedial work: - Deviation of ply has created gaps between joints - The lower kicker to be made good - Tie holes to be filled and sanded - The areas between wall pours needs making good - Areas of discolouration to be remedied
| 03SR - Stations (RfL) | Cxxx-NCR-000126 | NCR | New __ Batch Plant - Skip Elevator Pit - South Wall Concrete Over 2hrs from Batch Time |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2015-02-15 | 2015-02-03 09:01 | -12 | 2015-01-10 13:21 | Structural Engineering - Concrete Member | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | During the concrete pour for the south wall of the skip elevator pit, the discharge of the concrete for the 3rd load was not completed until 3hrs 20mins after the batch time of the concrete. This was due to a delay on-site which results in the concrete pour being delayed and the concrete wagons backing up on-site. Note, the 1st and 2nd loads were also over hours from time of batch but these have been removed by hydro-demolition as part of NCR-000100.
| 03SR - Stations (RfL) | Cxxx-NCR-000127 | NCR | New __ Batch Plant - Aggregate Bins - Steel Reinforcement Not Displaced for Post Fix drilling |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2015-07-31 | 2015-06-11 15:56 | -50 | 2015-01-17 08:25 | Structural Engineering - Concrete Member | 1500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Previous Construction - Other | Completed |  | The steel reinforcement for the aggregate bin walls was to be fixed and displaced to suit the post fix position of C339 bolts for the cladding and superstructure of the aggregate bins. During the during the bolt holes, some bolt locations clash with steel reinforcement and cannot be drilled to full bolt fixing depth.
| 03SR - Stations (RfL) | Cxxx-NCR-000128 | NCR | Bus Deck: AD3 Piling - Pile 265 out of slump range |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2015-05-23 | 2015-04-29 10:15 | -24 | 2015-04-09 15:01 | Surveying - Instrumentation and Monitoring | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Use of unapproved materials | Completed |  | The concrete delivery ticket indicated the concrete was of S3 consistency, however the slump taken for Pile 265 was recorded as 190mm which is out of the slump range for an S3 mix of 90 - 180mm as defined in BS 8500-1.
| 03SR - Stations (RfL) | Cxxx-NCR-000130 | NCR | __'s Quality Management Audit |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2015-02-15 | 2015-02-19 13:24 | 4 | 2015-01-22 10:51 | Systems - Systems Engineering General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Other management problem | Completed |  | Document control – it is essential that going forward a robust system is implemented to ensure that relevant approved documentation is present on site complete with Crossrail signed decal. Better use of iCosNet will facilitate this and lessen the reliance upon email communication that may be lost.
| 03SR - Stations (RfL) | Cxxx-NCR-000132 | NCR | __ - Removal of Elevator Hopper Top Prop |  | Crossrail | PDP | PNY - Paddington New Yard (West) |  | 2015-02-12 | 2015-03-05 11:02 | 21 | 2015-01-29 12:37 | Geotechnical Engineering - Supported Excavations | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | The top prop at level 122.0 of the Elevator Hopper was removed (on 24th January 2015) prior to CRL hold point being signed off (26th January, 2015).
| 03SR - Stations (RfL) | Cxxx-NCR-000133 | NCR | __ Area: Settling pond wall pour 1 surface defect |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2015-02-12 | 2015-02-12 17:39 | 0 | 2015-01-29 18:03 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | There is an area of honey-combing and non-compliant blow holes in pour 1 of the settling ponds. Please see attached photos.
| 03SR - Stations (RfL) | Cxxx-NCR-000134 | NCR | New __ Batching Plant - Elevator Loader Hopper Reinforcement Clash with Cast In Angles |  | Contr | SKC | PNY - Paddington New Yard (West) |  | 2015-02-23 | 2015-02-12 12:25 | -11 | 2015-02-02 16:45 | Structural Engineering - Reinforcement | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The tangs on the cast-in angles for the elevator loader hopper frame, clash with the steel reinforcement from the previous wall pour.
| 03SR - Stations (RfL) | Cxxx-NCR-000135 | NCR | Bus Deck - Lightning Protection - Cable cast into Derailment wall base at P32 |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2015-02-13 | 2015-02-13 15:22 | 0 | 2015-01-30 14:25 | Systems - Earthing and Bonding | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The cable used for the lightning protection on pile P32 was not protected and was cast into the derailment wall base
| 03SR - Stations (RfL) | Cxxx-NCR-000136 | NCR | Bus Deck - Deck Slab - Slab Pour 1.1 missing M & E void inserts |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2015-02-13 | 2015-02-09 09:25 | -4 | 2015-01-30 15:38 | Structural Engineering - Inserts | 500 |  | Supervision/Management | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Insufficient information made available to the worker. | Completed |  | The deck pour 1.1 was completed without void formers for MEP services. Missing voids are for the dry fire main and 300x50 trunking. 50mm ducts were placed in the slab for lightning protection as shown in the attached drawing.
| 03SR - Stations (RfL) | Cxxx-NCR-000137 | NCR | Bus Deck AD2 - Derailment Wall Piles - Out of Positional Tolerance |  | Crossrail | PDP | PNY - Paddington New Yard (West) |  | 2015-03-04 | 2015-02-24 08:16 | -8 | 2015-02-04 14:45 | Geotechnical Engineering - Concrete - Bored Pile | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | An as-built survey carried out on AD2 derailment wall piles show a number of piles positional tolerances outside of the specified limits (75mm). P24 - 156mm P25 - 98mm P33 - 92mm P38 - 93mm P128 - 93mm P129 - 85mm P138 - 101mm The derailment wall base has been poured for P33-64. That for P23-25 is yet to be poured. Proposal is to Use-As-Is
| 03SR - Stations (RfL) | Cxxx-NCR-000138 | NCR | __ Area - Insufficent cover to settling ponds wall |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2015-02-25 | 2015-03-11 16:30 | 14 | 2015-02-04 17:37 | Civil - Civil Engineering General | 1000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The horizontal starter bars from the previous pour highlighted red on the attached (“Cxxx-TAR-C-DWG-CR076-50014-6.0 Insufficient cover”) were installed with insufficient cover to the west side. The reinforcement has been fixed for the next pour (highlighted in green) and as such the fixed lacers in this location have insufficient cover on the south side of this wall. In the green highlighted pour, the cover issue is localised to the area near the red highlighted pour. The minimum cover in this zone is 15mm (with an average of 30mm). Similarly thereis one starter bar that clashes with the box out. This effectively has zero cover (see attached photo).
| 03SR - Stations (RfL) | Cxxx-NCR-000139 | NCR | New Bus Deck ; AD3 piling- Piles constructed without approved drawing |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2015-02-20 | 2015-02-19 14:30 | -1 | 2015-02-06 12:53 | Civil - Structural Engineering | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Lack of procedure | Completed |  | In the revision 08 of the drawing Cxxx-COS-C-DWG-CR076_MS005-50002 which is still waiting for approval ,the piles P277-280 which were originally designed as solthread piles were changed to bored piles. Due to the construction sequence and programme the BG 18 rig thatwas used to construct the solthread piles was exchanged for the low head room soiltec piling rig hence the change in design. Inorder to achieve the piling completion date (13/02/2015), the above piles were constructed to the unapproved revision 08 rather than wait for approval and risk a programme over run.
| 03SR - Stations (RfL) | Cxxx-NCR-000140 | NCR | __ Room -MEP- Earthing Install |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2015-02-26 | 2015-03-10 14:53 | 12 | 2015-02-12 14:53 | Electrical - Electrical Engineering General | 1000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Conduit for cable into earth pit has been blocked and cable cannot be installed. No conduit installed for rebar connections to earth bar, and copper tape from earth mat to earth bar installed not close enough to wall location due to incorrect information at time of install.
| 03SR - Stations (RfL) | Cxxx-NCR-000141 | NCR | Bus Deck: Pile P30 - Concrete consistency over specification limits |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2015-02-25 | 2015-02-12 16:50 | -13 | 2015-02-11 12:04 | Civil - Civil Engineering General | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Use of unapproved materials | Completed |  | The specified slump class for the concrete mix used in piles is S3 as per the approved MCR,however, the fresh concrete discharged into the pile P30 had a consistency of 210mm whiich is outside the upper limits for an S3 sump class as specified in BS EN 206 -1 and confirmed by the concrete delivery ticket. Attached is the statistical analysis obtained from the concrete identity testing which highlights the non-conformance of this sample.
| 03SR - Stations (RfL) | Cxxx-NCR-000142 | NCR | New __ Batch Plant - Aggregate Bin Upper Walls TW Design Not Approved prior to Starting Works |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2015-02-17 | 2015-04-30 15:01 | 72 | 2015-02-12 11:13 | Structural Engineering - Structural Engineering - General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | The temporary works designs for the __ aggregate bins upper walls 1st and 2nd lifts were not approved by Crossrail at the time of construction. The designs had been checked by __ Engineering Services and a design check certificate issued.
| 03SR - Stations (RfL) | Cxxx-NCR-000143 | NCR | Bus Deck - AD2 - Derailment Wall GL 1 - Honey Combing South Side at approx GL T |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2015-02-27 | 2015-02-24 11:25 | -3 | 2015-02-13 11:13 | Structural Engineering - Finishes | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Derailment Wall 1 Base Pour 1 of AD2 it was noticed after striking the shutters that there was one small isolated spot of honey combing. Honey combing to be rectified as per the approved RAMS
| 03SR - Stations (RfL) | Cxxx-NCR-000144 | NCR | Bus Deck - Pile Caps - Footprint 2.4 Pile Caps S3 & Q3/Derailment Wall Base exceed 2hr pour limit |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2015-03-05 | 2015-02-24 08:18 | -9 | 2015-02-19 18:41 | Structural Engineering - Concrete Member | 500 |  | Planning | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | Concrete placed on Monday 26-1-15 in Pile Cap S3 and the loads which was used between Pile Cap Q3 / Derailment wall base exceeded the 2hour pour limits.
| 03SR - Stations (RfL) | Cxxx-NCR-000145 | NCR | New __ Batch Plant - Skip Elevator Pit - South Wall Cast In Plates Out of Position |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2015-04-30 | 2015-04-20 09:52 | -10 | 2015-02-17 18:10 | Structural Engineering - Concrete Member | 50000 |  | Incorrect Installation | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The 2no. steel cast in plates for the skip elevator south wall have been installed 100mm out of position with the centre line of the plates central to the centre line of the wall.
| 03SR - Stations (RfL) | Cxxx-NCR-000146 | NCR | Bus Deck - AD1 - Pour 1.2 - 10mm Aggregate Concrete not matching MCR |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2015-03-07 | 2015-02-24 08:21 | -11 | 2015-02-21 08:33 | Structural Engineering - Concrete Member | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | Concrete used in Pour 1.2 was a 10mm aggregate due to the unavailability of 20mm aggregate from the supplier. This did not breach the specification but did not match the approved MCR for the mix.
| 03SR - Stations (RfL) | Cxxx-NCR-000147 | NCR | __- MYRW- Blockwork remedial work |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2015-09-14 | 2015-09-11 12:19 | -3 | 2015-03-03 10:11 | Civil - Civil Engineering General | 2500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Subcontractor Problems - Other | Completed |  | Blockworks to the MYRW was damaged in few places due to ongoing construction works around the area, which requires remedial work to be carried out.
| 03SR - Stations (RfL) | Cxxx-NCR-000148 | NCR | Bus Deck - AD1 Piles - Piles P257 & P258 Integrity Testing Missed |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2015-03-17 | 2015-03-09 15:52 | -8 | 2015-03-03 11:41 | Geotechnical Engineering - Concrete - Bored Pile | 500 |  | Planning | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Upon Collating the integrity records for AD1 Piles it was noticed that the Piles in Pile-Cap AA-3, No. P257 & P258 were not integrity tested prior to the pile cap been constructed
| 03SR - Stations (RfL) | Cxxx-NCR-000149 | NCR | Bus Deck: P235 - Concrete Discharged more than 2 hours after being Batched |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2015-03-30 | 2015-03-18 10:28 | -12 | 2015-03-16 09:59 | Civil - Civil Engineering General | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | The concrete arrived on site one hour after it was batched , however due to Site congestion it was discharged another hour later. The slump taken just before discharge was 100, which was within the limits of the specified S3 mix.Attached is the concrete discharge and delivery record sheet from __.
| 03SR - Stations (RfL) | Cxxx-NCR-000150 | NCR | __ Quality Management Audit |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2015-04-27 | 2015-04-30 13:35 | 3 | 2015-03-12 16:41 | Systems - Systems Engineering General | 5000 |  | Documentation and Records | Repair | 3 (3-6k) | Complete | Management Problem - Inadequate administrative control | Completed |  | It was apparent at the audit that the procedure and process for managing design control and design changes including responsibility for verification and approval of drawings prior to issue were not being managed effectively. It was evident that there is a lack of communication between __ and the __’s Senior Design Manager where design is being changed. Also, there was no evidence found within the __’s Quality Plan on how the design change process is managed. __ are required to issue the Design Change Log to __ and discuss any changes of design during the weekly design meeting with __ going forward. In additional, to revise the QP to incorporate this process.
| 03SR - Stations (RfL) | Cxxx-NCR-000151 | NCR | __ Quality management Audit |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2015-04-27 | 2015-05-05 14:47 | 8 | 2015-03-12 16:45 | Systems - Systems Engineering General | 500 |  | Documentation and Records | Repair | 4 (0.5-3k) | Complete | Procedure Problem - Lack of procedure | Completed |  | __ have not produced a project specific QA Audit Programme for the project and have not undertaken any project specific quality audit based on the set processes and procedures detailed within the Quality Plan to ensure compliance with the requirements of the contract. In addition, there was no evident of monitoring or checks of the Quality processes or the key deliverables.
| 03SR - Stations (RfL) | Cxxx-NCR-000152 | NCR | __ - Removal of Elevator Skip Prop |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2015-04-02 | 2015-04-22 13:05 | 20 | 2015-03-19 08:58 | Structural Engineering - Bracing | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | The hold points on the ITP for the installation and removal of the prop for the Elevator Skip were missed by CRL. The prop at a level of 119.500 in the Elevator Skip was removed on 7th November 2014 prior to CRL hold point being signed off.
| 03SR - Stations (RfL) | Cxxx-NCR-000153 | NCR | Concrete Drying Bay (East) - Kicker Concrete Defects |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2015-03-31 | 2015-04-01 09:02 | 1 | 2015-03-27 13:32 | Civil - Civil Engineering General | 1000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Kicker to the Concrete Drying Bay (East) Slab was poured seperately. During striking of the kicker shutters, concrete along the kicker line was damaged at a few spots as per the attached photos.
| 03SR - Stations (RfL) | Cxxx-NCR-000154 | NCR | New __ Batch Plant - Skip Elevator Pit - Water Seepage in Pit Through Wall |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2015-09-14 | 2015-09-15 16:47 | 1 | 2015-04-07 17:28 | Structural Engineering - Concrete Member | 75000 |  | Workmanship | Repair | 1 (>60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | There is a slow seepage of water coming through the construction joint in the corner in the skip elevator pit walls between the south and western walls. Refer to the attached photo. The two cracks present in the photo are hair line cracks (1-2mm deep) and the water does not seem to come from these cracks. CRL will be updated once further investigation has taken place.
| 03SR - Stations (RfL) | Cxxx-NCR-000155 | NCR | Bus Deck - Columns - Grout Loss at Column-Derailment Wall construction joint |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2015-05-29 | 2015-05-29 14:10 | 0 | 2015-04-08 17:23 | Structural Engineering - Finishes | 1000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | There has been some grout loss at the base of columns at the derailment wall / column construction joint.
| 03SR - Stations (RfL) | Cxxx-NCR-000156 | NCR | Bus Deck - North abutment wall Piling: Top of steel level out of tolerance |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2015-05-30 | 2015-05-11 09:54 | -19 | 2015-04-16 11:49 | Civil - Geotechnical Engineering | 15000 |  | Incorrect Installation | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Following pile break down to cut off level within the North Abutment, a number of piles were found to have low reinforcement which were below the allowable tolerances of +150/-50mm as per the ICE SPERW cl B3.4.1. The as-builts of the non-confirming piles are listed below Pile As built TOS(mAOD) Design TOS(mAOD) Difference/mm P409 120.710 122.275 - 1.565mm P412 122.005 122.275 - 270mm P414 121.658 122.275 - 617mm P416 122.072 122.275 - 203mm P417 122.088 122.275 - 187mm P425 122.192 122.275 - 83mm P428 122.178 122.275 - 97mm P437 122.180 122.275 - 95mm P438 122.210 122.275 - 65mm
| 03SR - Stations (RfL) | Cxxx-NCR-000157 | NCR | Bus Deck - AD2 - Pile projection steel fractured in pile P108 |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2015-05-04 | 2015-04-30 12:08 | -4 | 2015-04-09 17:56 | Geotechnical Engineering - Concrete - Bored Pile | 1000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | When Cropping Pile P108, which was a working test pile the rebar has been damaged during cropping. Because it was a working test pile, the helicals continued to the top of the pile and no de-bonding foam was included in projection steel
| 03SR - Stations (RfL) | Cxxx-NCR-000158 | NCR | Bus Deck - AD2 - Pour 2.3 - Mix design change due to warmer ambient temperatures |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2015-04-27 | 2015-04-29 09:35 | 2 | 2015-04-13 12:02 | Structural Engineering - Concrete Member | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Use of unapproved materials | Completed |  | With summer approaching and warmer ambient temperatures the construction team decided to move forward with a mix design which would provide a longer workability duration particularly during warmer weather to mitigate possible cold joints and The new mix design MCR was submitted late Friday as the previous mix design (FCD-156) did not provide the workability we required. New trials were completed late last week and the following MCR Cxxx-COS-S-LRC-CR076_SD006-50042 provided the workabilty which was required. How ever this was not approved prior to been incorporated into the permanent works.
| 03SR - Stations (RfL) | Cxxx-NCR-000159 | NCR | Bus Deck - Deck Slab - Surface Cracking on top face |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2015-11-30 | 2015-11-27 11:19 | -3 | 2015-04-13 15:39 | Structural Engineering - Finishes | 50000 |  | Workmanship | Repair | 2 (6-60k) | Complete | Material/Preservation Problems - Not Defined | Completed |  | Cracking has been noticed on the top surface of the Deck Slab post pour 2.3.
| 03SR - Stations (RfL) | Cxxx-NCR-000160 | NCR | Royal Oak Portal - Platform Walls Cracks around Box Outs at 45 degrees |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2015-05-14 | 2015-05-14 17:02 | 0 | 2015-04-14 12:36 | Structural Engineering - Concrete Member | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | On the platform walls around the box outs there are cracks. These are superficial as anti-crack bars were installed around the box out positions, the reinforcement was installed as per the design Cxxx-COS-S-DWG-CR076_PT001-50502 Rev C02. Please see the attached photograph which shows that the anti-crack bars have been installed and photograph of the superficial cracks.
| 03SR - Stations (RfL) | Cxxx-NCR-000162 | NCR | Bus Deck - BDU - Secant pile couplers low in when tying into ramp slab |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2015-04-29 | 2015-04-30 12:14 | 1 | 2015-04-15 17:42 | Structural Engineering - Reinforcement | 5000 |  | Design | Use As-Is | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The design levels of secant piles and the ramp slab do not match correctly and are up to 2000mm below the required level. This means in a few locations the bottom bars are either within the level of the clayboard void former or in the bottom cover zone, the worst locations are Secant piles 15, 18,19,20,21,42, 44, 45, 46 & 47. The design requires 4no. B32 bars to tie the ramp slab to the secant piles (2 top, 2 bottom was the original design) however __ the piling subcontractor installed 6 couplers (3 top and 3 bottom) to mitigate against rotation of the pile cages during installation, there fore in most locations the most west bottom and the top three B32 bars can be installed - thus the 4no. B32 required. In the 4 piles SP18, 20 42 & 46 some slight roatation of the pile and the mismatch in design levels between couplers and design level of the slab dont match mean only 2 bars can be installed
| 03SR - Stations (RfL) | Cxxx-NCR-000163 | NCR | __ Pavement slab A14-4 levels |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2015-05-14 | 2015-04-29 09:45 | -15 | 2015-04-16 16:49 | Civil - Concrete Pavement | 6000 |  | Workmanship | Rework | 3 (3-6k) | Complete | Discipline/Workmanship - Other | Completed |  | Pavement slab A14-4 was pour higher than the design levels provided. The deviation from design levels is between +6 to +26 across whole slab. Please refer to the attached as-built survey.
| 03SR - Stations (RfL) | Cxxx-NCR-000164 | NCR | __ Pavement Slab A14-4 |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2015-05-29 | 2015-05-29 13:46 | 0 | 2015-04-22 12:50 | Civil - Concrete Pavement | 6000 |  | Incomplete Works | Use As-Is | 3 (3-6k) | Complete | Material/Preservation Problems - Insufficient quantity of material to do the job | Completed |  | __ pavement slab was partially poured today 22/04/15 due to delays in concrete delivery over one hour. If we continued placing the second concrete wagon we would have had a "Cold Joint". Therefore we decided to stop the pour and cancel the concrete.
| 03SR - Stations (RfL) | Cxxx-NCR-000165 | NCR | Bus Deck - BDU - Wall Pours - Concrete filler neck defect Wall 9 |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2015-05-18 | 2015-04-30 12:29 | -18 | 2015-04-23 18:14 | Structural Engineering - Finishes | 1000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | After stiking wall pour 9 of the BDU Secondary lining it was noticed that the plunger plate had been pushed into the finished surface level at the filler port reducing the cover zone.
| 03SR - Stations (RfL) | Cxxx-NCR-000166 | NCR | Bus Deck - AD2 - Pour 2.2 - Drainage Trench Honey Combing |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2015-07-15 | 2015-07-16 15:39 | 1 | 2015-05-07 17:50 | Structural Engineering - Finishes | 1500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Honey Combing noticed on the sides of the drainage trench in Pour 2.2 foot print.
| 03SR - Stations (RfL) | Cxxx-NCR-000167 | NCR | Bus Deck - BDU - Western Approach Transition Slab - corbel starter bars placed incorrectly |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2015-06-02 | 2015-05-26 10:11 | -7 | 2015-05-07 17:38 | Structural Engineering - Reinforcement | 5000 |  | Supervision/Management | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The starter hoop bars for the corbel supporting the Transition slab in the western approach upstand have been cast 200mm too high and are out of position.
| 03SR - Stations (RfL) | Cxxx-NCR-000168 | NCR | Bus Deck - AD2 - Derailment Wall and Pile Cap in 2.1 Concrete beyond 2hrs |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2015-07-15 | 2015-07-07 11:37 | -8 | 2015-05-22 16:11 | Structural Engineering - Concrete Member | 500 |  | Planning | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Use of unapproved materials | Completed |  | Concrete delivery for Derailment Wall 1 and Pile Cap B/3a pours exceeded the 2hr time limit as per Appendix 17/1.
| 03SR - Stations (RfL) | Cxxx-NCR-000169 | NCR | Bus Deck - BDU - Lifting Beams - Couplers out of position on North SWL 5t beam |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2015-06-15 | 2015-06-04 13:26 | -11 | 2015-05-20 15:31 | Structural Engineering - Bolted Connections | 1000 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | In 2no. locations a total of 3no. cast-in couplers are misaligned and cannot be connected to the prefabricated lifting UC beam. Please see attached sketch showing clearly these couplers and locations. • The first location has one of the four couplers misaligned • The second location is a different beam section (although they will be bolted together) has 2no. couplers misaligned , but one either side of the web thus still balanced.
| 03SR - Stations (RfL) | Cxxx-NCR-000170 | NCR | Bus Deck - Derailment Wall 2 - __ technician left before Concrete Arrived onsite (GL-B plus 5m east) |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2015-06-24 | 2015-06-22 17:22 | -2 | 2015-05-21 09:39 | Structural Engineering - Concrete Member | 2500 |  | Planning | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Improper resource allocation | Completed |  | Concrete Placed without being tested due to __ technician already left work for the day
| 03SR - Stations (RfL) | Cxxx-NCR-000171 | NCR | Late resubmission of the Temporary Works Schedule |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2015-06-04 | 2015-06-04 12:09 | 0 | 2015-05-21 12:52 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Decal 1, Rev 7.0 Cxxx-COS-Z-TSC-CR076_SD006-50002 Temporary Work Schedule dated 25/02/15 was confirmed on eB. However, it was evident at the audit that this document has not been submitted regularly as part of the 4 weekly deliverables requirements. CAR was also raised by Crossrail at the last audit on the 05/12/14 on this issue. TWC is required to update the schedule to reflect the title of the design certificates produced so far on the project.
| 03SR - Stations (RfL) | Cxxx-NCR-000172 | NCR | Bus Deck - AD2 - Columns B1b and B2a surface finish defects |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2015-07-15 | 2015-07-16 16:38 | 1 | 2015-05-27 11:04 | Structural Engineering - Concrete Member | 1000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Surface defects, lines of exposed aggregate less than 10mm deep, on columns B1b and B2a do not meet the standard of the approved column sample provided for Westminster City Council, as per table 17/3 of the HA 1700 series appendices.
| 03SR - Stations (RfL) | Cxxx-NCR-000173 | NCR | Bus Deck - BDU - __s - 2no. __s on the south upstand out of position |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2015-07-15 | 2015-07-16 12:13 | 1 | 2015-05-29 16:22 | Structural Engineering - Inserts | 3000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | 2no. __s in the southern upstand out of position. No good for use by follow on Contractor (LJH).
| 03SR - Stations (RfL) | Cxxx-NCR-000174 | NCR | Bus Deck: Paving underneath the Bus Deck -28 day concrete cube strength below specified. |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2015-10-20 | 2015-10-09 17:20 | -11 | 2015-06-30 14:42 | Civil - Concrete Pavement | 5000 |  | Material | Use As-Is | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Attached is the 28 day Concrete test cube report for one of the PAV 2 mix slab pours underneath the bus deck that shows the concrete did not achieve specified strength of 40N/mm2. The two 28 day crush strengths of 33.8 and 35.5 N/mm2 are also below the lower limit of specified strength -4N/mm2 as per the conformity criteria for individual compressive strength in BS EN 206: 2013 cl. 8.2.1.3.1.
| 03SR - Stations (RfL) | Cxxx-NCR-000175 | NCR | AD3 __ Sewer manhole positions |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2015-08-13 | 2015-08-06 16:43 | -7 | 2015-05-28 16:31 | Civil - Drainage | 10000 |  | Design | Use As-Is | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Due to issues regarding specification requirements, buildability and material standard dimensions the as-built positions of some __ sewer manholes are not conforming to the specification. The invert levels of the drainage are not affected by this non-conformance and are all within construction tolerances. The issues are described in the text below. The as-built positions of the __ sewer manholes and the difference from theoretical position are shown in the table attached. The calculated resultant delta is also shown, the total distance moved. From the table it is apparent that a number of the manholes are out of position tolerance, most notably manholes S501, S502, S503, S505, S508, S509, S510 and MH4/S507B. Manhole C115 has not yet been constructed but is included for clarity. 675-750mm Diameter Pipes The non-conformance has occurred due to issues surrounding jointing requirements, buildability and standard sizes of the concrete pipes:  The pipe jointing requirement is detailed in note 4 on drawing Cxxx-CSY-D-DDD-CR076_MS005-01553 Rev C03. This specifies that the joint should be as close as possible to the structure, with a maximum distance of 1.000 m (for pipes of diameter 675-750 mm). As the pipe is required to protrude a distance of at least 100mm inside the manhole, the precast manhole ring has a thickness of 80mm and the manhole surround is 150mm thick it can be concluded that the maximum length of cut pipe is: 1.000 + 0.100 + 0.080 + 0.150 = 1.330 m  For the purpose of buildability and to create an adequate seal on the pipe the minimum practical length of cut pipe is 0.750 m.  The standard length of a concrete pipe is 2.500m and the length of a rocker pipe is 0.600m for pipe diameters up to 600mm and 1.000m for diameters 675-750 (pages 6 and 7 of Material Compliance Record Cxxx-COS-U-LRC-CR076_SD006-50011 Rev 2.0). From the information above it can be concluded that there is a “dead band” length of cut pipe, which cannot be achieved, leading to position issues. To mitigate the problem on site __ used extra rocker pipes where practical, but this did not work in all cases as the rocker pipe is also a standard size. To use an example, for a 750 mm dia pipe, to work out the “dead band”: Maximum distance using 1 rocker: 2.500 + 1.000 + 1.330 = 4.830 Minimum distance using 1 rocker: 2.500 + 1.000 + 0.750 = 4.250 Maximum distance using 2 rockers: 1.000 + 1.000 + 1.330 = 3.330 Minimum distance using 2 rockers: 1.000 + 1.000 + 0.750 = 2.750 From this calculation it is clear that any length of pipe make-up from 4.830m to 4.250m can be achieved, as can any length from 3.330m to 2.750m. The dead band lies between 4.250m and 3.330m. This represents a distance of 920mm which cannot practically be achieved, meaning that a manhole with a 1.000m long rocker pipe may be required to move a maximum distance of 920 / 2 = 460 mm. 150-600mm Diameter Pipes For pipes of diameter 150-600 mm note 4 on drawing Cxxx-CSY-D-DDD-CR076_MS005-01553 Rev C03 specifies the maximum distance from the structure to the nearest joint as 0.600 m. The length of a rocker pipe is 0.600 m for pipe diameters up to 600mm. So to work out the “dead band” for a 600mm dia pipe: Maximum distance using 1 rocker: 2.500 + 0.600 + 0.930 = 4.030 Minimum distance using 1 rocker: 2.500 + 0.600 + 0.750 = 3.850 Maximum distance using 2 rockers: 0.600 + 0.600 + 0.930 = 2.130 Minimum distance using 2 rockers: 0.600 + 0.600 + 0.750 = 1.950 In this case a distance of 1720mm cannot be practically achieved so a manhole with a 0.600m long rocker pipe may be required to move a maximum distance of 1720 / 2 = 860 mm.
| 03SR - Stations (RfL) | Cxxx-NCR-000176 | NCR | Utilities - Utility Chamber at __'s Retaining Wall - |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2015-06-26 | 2015-06-10 09:19 | -16 | 2015-06-04 11:47 | Utilities Engineering - Utilities General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | Due to a failure in communication, the works to the utility chamber installed for the transfer of ducting through __'s Yard retaining wall proceeded prior to Crossrail approval of the temporary works design and check. Cxxx interface manager was consulted prior to works to ensure this did not require a Form C.
| 03SR - Stations (RfL) | Cxxx-NCR-000178 | NCR | Paddington New Yard - Green Lane Bridge - Anchor head encasement |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2015-06-22 | 2015-06-11 13:47 | -11 | 2015-06-08 15:35 | Civil - Civil Engineering General | 5000 |  | Incorrect Installation | Use As-Is | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Drawing Cxxx-COS-S-DDL-CR076_MS005_1-01701, Proposed Section A contains the following note: "Sealed anchor cap, no inspection required. Double corrosion protection as per fig C3 in BS EN 1537:2013" (standard attached) The figure in question specifies a plastic coated steel removable cap with gasket and clip. As per table C.2, paragraph 4 of the same specification, this plastic coated cap may be replaced by a galvanised cap of minimum 3mm wall thickness. Actual cap installed was a non-galvanised steel cap of 3mm wall thickness installed with gasket and sealant as per attached diagram "3-4 strand anchor head based on 32mm compact wedge". The use of a non-galvanised anchor head was covered in an RFI to __ Consulting (attached) who developed the detailed design of this element of works. It was agreed that with the anchor heads fully encased in concrete (secondary encasement beam), the galvanised anchor head was not necessary.
| 03SR - Stations (RfL) | Cxxx-NCR-000179 | NCR | Paddington New Yard - __ sewer guided auger bore - air test failure |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2015-06-22 | 2015-06-25 15:00 | 3 | 2015-06-08 15:48 | Civil - Drainage | 10000 |  | Testing and Commissioning | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Other | Completed |  | __ sewer pipe run between manholes S16 and S17 has been installed by guided auger bore. Pipe run is complete bar pipe sections to connect into the manholes S16 and S17 (1no pipe 2m pipe segment at either end). Product pipe installation was completed on 1/6/15 and has failed to pass an air test after several attempts with different sets of air test equipment.
| 03SR - Stations (RfL) | Cxxx-NCR-000180 | NCR | ROP - Lining Wall Extension Works - Void Under Box Out |  | Contr | SKC | PNY - Paddington New Yard (West) |  | 2015-08-31 | 2015-09-01 14:44 | 1 | 2015-06-11 18:39 | Structural Engineering - Concrete Member | 1500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | On striking the formwork for the lining wall extension works, a void could be seem underneath the box out. This is likely where the concrete has not been adequately placed and compacted around the large box out.
| 03SR - Stations (RfL) | Cxxx-NCR-000181 | NCR | Utilities - Alfred Road Ducting |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2015-07-15 | 2015-07-14 14:53 | -1 | 2015-06-15 17:29 | Civil - Utilities Engineering | 20000 |  | Incorrect Installation | Repair | 2 (6-60k) | Complete | Design Problem - Inadequate or defective design | Completed |  | On __ Cxxx's subcontractor __ attempting to pull cables through the LV electrical ducting installed by Cxxx on the 10th of June, 2015; it became evident that the orientation of the ducts in one section had been changed underground as they entered LV drawpit number 3. The area was subsequently excavated the following day, the ducts fully rectified and backfilled. __ then failed to pull the cables again on the 12th of June and it was determined that the ducts as specified in the Code 1 approved design were too small for the cable being pulled.
| 03SR - Stations (RfL) | Cxxx-NCR-000182 | NCR | __ - Alfred Road - LV Installation of __ Switchroom |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2015-07-15 | 2015-07-15 10:22 | 0 | 2015-06-17 13:10 | Electrical - LV Equipment | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Other management problem | Completed |  | The M&E Subcontractor __ have commenced their works within the LV side of the __ switchroom on Alfred Road. The works include the installation of LV equipment within the switchroom, but it has emerged that __ have been installating the LV gear according to a __ design drawing, Cxxx-COS-E-DDL-CR076_MS005_Z-01003, which is currently a preliminary drawing, P03, and not at an approved IFC stage. It is to be noted that __ have now finished their installation works, however the drawing is still not at a C01 Constuction stage. This error has occured due to a miscommunication bewteen __, __ and __.
| 03SR - Stations (RfL) | Cxxx-NCR-000183 | NCR | ROP- Commencing the earthing work without an accepted ITP |  | Crossrail | PDP | PNY - Paddington New Yard (West) |  | 2015-07-15 | 2015-07-07 10:49 | -8 | 2015-06-25 13:27 | Systems - Earthing and Bonding | 500 |  | Planning | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | __s - Commencing the earthing work without an accepted ITP
| 03SR - Stations (RfL) | Cxxx-NCR-000184 | NCR | Alfred Road Drawpits |  | Crossrail | XRL | PNY - Paddington New Yard (West) |  | 2015-09-30 | 2015-10-01 16:48 | 1 | 2015-06-25 15:38 | Civil - Utilities Engineering | 15000 |  | Damaged | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Whilst works were still in progress, an observation was raised during a Quality Surveillance Check concerning the buldging on the side wall of Draw pit number 2. With the completion of works now imminent, the same concern is present with the buldging on the side wall of the draw pit remains the same. It can be seen from the pictures attached that the buldging has caused gaps to show in the draw pit wall which could lead to leakages or the strength of the draw pits being compromised.
| 03SR - Stations (RfL) | Cxxx-NCR-000185 | NCR | Bus Deck - Type 3 Parapets on GL/1 - Rebar Clash between insitu beam and precast parapet |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2015-09-14 | 2015-09-07 17:06 | -7 | 2015-06-30 17:21 | Structural Engineering - Pre-cast | 50000 |  | Workmanship | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | __ offered up PS11 (Type 3) during a dry run on Thursday 25-6-15 at around 16:30. The dry run was not a success as the majority of the closed starter links on the parapet unit clashed with the slab links, this was not expected as __ had as-built all the deck starter bars and provided this information to __ so the bars could be adjusted in the precast yard to eliminate potential bar clashes.The main straight starter bars does not have any problems as they sit proud above the top slab reinforcement mat. 16-7-15 - Further Information Installation of Parapets has since continued and PS2 - PS19 have been lifting into position. Any Bar Clashes have been either bent over to avoid the clash or cut out to remove the clash. Section Engineer, Marian Lenihan spent the 29-6-2015 and from the 02-7-2015 until 10-7-2015 up with __ in their precast facility to assist with __'s rebar placement checks to ensure the bars were placed as per the as-built provixded by __.
| 03SR - Stations (RfL) | Cxxx-NCR-000186 | NCR | Bus Deck: Paving slab underneath Bus Deck - Below strength concrete |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2015-10-20 | 2015-10-22 16:28 | 2 | 2015-10-06 12:55 | Civil - Civil Engineering General | 1500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Subcontractor Problems - Other | Completed |  | The PAV 2 mix Concrete placed in slab 2 (see attached marked up drawing for location) did not gain specified 28 day Cube strength of 40 N/mm2. As per the attached test cube report it gained an average compressive test of 33 N/mm2 after 28 days. Additional cubes were crushed at 56 days and 70 days and the compressive strengths was measured at 35.5 and 40.1 N/mm2 respectively.
| 03SR - Stations (RfL) | Cxxx-NCR-000187 | NCR | Head House Slab - Earth Mat |  | Crossrail | XRL | PNY - Paddington New Yard (West) |  | 2015-08-17 | 2015-08-13 15:51 | -4 | 2015-06-28 16:33 | Systems - Earthing and Bonding | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Lack of approval Code 1 procedures excessive | Completed |  | The Head House Earth Mat was installed on 16 & 26 June -2015 with Cxxx working off Pre- Gated F1 drawings as there design reviewhas not successfully passed through the CEG Gate Design review panel . Therefore Cxxx are working at Risk as there are no Post Gated F1 & F2 drawings in place at the time of the installation.
| 03SR - Stations (RfL) | Cxxx-NCR-000189 | NCR | __'s Formwork Quality Management Audit |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2015-07-20 | 2015-07-27 16:01 | 7 | 2015-06-30 11:17 | Civil - Structural Engineering | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Other management problem | Completed |  | Contract Review is undertaken as part of the joint weekly meeting lead by __. The detailed minutes of the meeting records for ROP RC work, number Cxxx-COS-MPM-MIN-000003 14 and 15 dated 18/05/14 and 10/06/15 including actions are maintained. These were presented at the audit. However, there was no evidence found at the time of the audit that this meeting is undertaken by __ on weekly. __'s are required to arrange this meeting going forward to ensure all the key issues on the project are discussed and actioned.
| 03SR - Stations (RfL) | Cxxx-NCR-000190 | NCR | __'s Formwork Quality Management Audit |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2015-07-24 | 2015-07-22 09:20 | -2 | 2015-06-30 11:23 | Civil - Structural Engineering | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | __’s Formwork has undertaken some Toolbox Talk within the project. The Toolbox talks records for __ concrete dated 21/04/15 was presented at the audit. However, it was noted during the review that __’s have not undertaken any QA toolbox talk. Section 2.3 stated that monthly QA Toolbox talk will be undertaken. It was also not evident at the audit that __’s has maintained the List of Toolbox talk.
| 03SR - Stations (RfL) | Cxxx-NCR-000191 | NCR | __'s Formwork Quality Management Audit |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2015-07-20 | 2015-07-14 12:29 | -6 | 2015-06-30 11:31 | Structural Engineering - Structural Engineering - General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | The full processes for managing Packaging, Delivery, Storage and Handling of materials and equipment were confirmed within section 2.5 of the QP. Reinforcement concrete is delivered to site. The Deliver Call of Summary with the relevant reinforcement Call Off Schedule was presented at the audit. However, it was noted during the review of this document that PM signature on the Call Off Schedule and Delivery Notes confirming acceptance of this item to site were not taken.
| 03SR - Stations (RfL) | Cxxx-NCR-000192 | NCR | __'s Formwork Quality Management Audit |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2015-08-14 | 2015-08-14 16:36 | 0 | 2015-06-30 11:36 | Structural Engineering - Structural Engineering - General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | The individual Drawing Registers (RIR) with the relevant drawings are produced and maintained for the Bus Deck and __ area under document numbers Cxxx-XRL-Z-LRL-Z-LRL-CR076_SD006-50005 and Cxxx-COS-S-LRG-CR076_MS005-50001. The site folder containing these documents was verified at the audit. It was noted that wrong revision 14 RIR for bus deck was included within this folder. The correct number is revision 17. It was also evident during the verification of these documents that these are not being managed effectively. The statuses, references, date submitted to CRL, date accepted by CRL, close status were all missing from these Logs e.g. the NCR Log.
| 03SR - Stations (RfL) | Cxxx-NCR-000193 | NCR | __'s Quality Management Audit |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2015-07-24 | 2015-07-27 16:10 | 3 | 2015-06-30 11:40 | Systems - Systems Engineering General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | There was no evidence found at the time of the audit that __ have produced a Schedule of ITP. However, 3 ITP’s for Bus Deck, ROP and __ have been generated so far on the project. These were confirmed on eB under code 1. The project specific process for managing ITP was also confirmed within section 2.11 of the QP including ITP Register template attached under Appendix B.
| 03SR - Stations (RfL) | Cxxx-NCR-000194 | NCR | __'s Quality Management Audit |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2015-08-14 | 2015-08-14 14:42 | 0 | 2015-06-30 11:45 | Systems - Systems Engineering General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | The Quality audit process is identified within the section 2.12 of the QP. The responsibility for undertaking QA Audit is lay with the __ Internal Quality and Environmental Director and __ site Quality Representative. The list of proposed Quality Audits was confirmed within the QP. However, it was noted that the __ has not undertaken any QA audit on the project.
| 03SR - Stations (RfL) | Cxxx-NCR-000195 | NCR | Bus Deck - BDU - Plinth Level conflicting between Duo and Cxxx drawings |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2015-08-31 | 2015-08-21 11:47 | -10 | 2015-06-30 16:07 | Structural Engineering - Concrete Member | 5000 |  | Design | Repair | 3 (3-6k) | Complete | Design Problem - Conflicting information on drawings | Completed |  | one of the bearing plinths in the BDU has been cast to the Cxxx drawing level but LJH have manufactuered the steel work for the coveyor to Duo drawings. The drawings are out by 100mm for this particular plinth. LJH do not have an approved weld procedure to adjust the leg of the steel coveyor so adjustments to the plinth are required.
| 03SR - Stations (RfL) | Cxxx-NCR-000196 | NCR | Alfred Road Ducts at Draw Pit No 4 |  | Crossrail | XRL | PNY - Paddington New Yard (West) |  | 2015-09-30 | 2015-10-01 17:02 | 1 | 2015-07-02 10:21 | Utilities Engineering - Electricity | 5000 |  | Incorrect Installation | Use As-Is | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Alfred Road Ducts at Draw Pit No 4 On the 24-06-2015 it was noted that the electrical utilities ducts have been removed at the draw pit no 4 and the __ cables have been pulled through an open trench and then routed through existing installed ducts on route to the __ LV room. The installation is not inline with the approved drawing Cxxx-COS-U-DDA-CR076_MS005_Z-0134-CO1 and Spec ref: Cxxx-CSY-D-RSP-CR076_MS005-50004 Rev 9.0 (clause 5/2 point 3) The above has been raised with Cxxx Section Engineer and Construction Manager.
| 03SR - Stations (RfL) | Cxxx-NCR-000197 | NCR | Alfred Road – Cable Ducts – Draw Pits 1&2 |  | Crossrail | XRL | PNY - Paddington New Yard (West) |  | 2015-09-30 | 2015-10-01 17:51 | 1 | 2015-07-02 12:19 | Utilities Engineering - Electricity | 5000 |  | Incorrect Installation | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Alfred Road – Cable Ducts – Draw Pits 1&2 On the 29-06-2015 it was noted that the trench at the top of Alfred Road between draw pits 1 & 2 has been exposed and the electrical ducts linking the __ sub station removed. 4 No __ cables have been pulled through an open trench and then routed through existing installed ducts on route to the __ - LV room. The installation is not inline with the approved drawing Cxxx-COS-U-DDA-CR076_MS005_Z-0133-CO1 and Specification ref: Cxxx-CSY-D-RSP-CR076_MS005-50004 Rev 9.0 (clause 5/2 point 3) Also noted that some section of the cables spilt ducts has been installed for which no MCR or FCD has been submitted
| 03SR - Stations (RfL) | Cxxx-NCR-000198 | NCR | ROP External Walkway Lighting |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2015-08-17 | 2015-08-17 09:59 | 0 | 2015-07-03 09:30 | Electrical - General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Lack of approval Code 1 procedures excessive | Completed |  | Non conformance: Proceeding to installation prior to F1 Issue for Construction Acceptance. In order to mitigate programme delays __ have been instructed by __ to proceed to commence installation to the current F1 drawings which have yet to receive IFC status. In order to mitigate any potential risks __ have confirmed with __ that there are no comments outstanding on drawing Cxxx-COS-E-DDA-CR076_PT001_2-32041 Rev P04. __ have also updated this drawing to produce drawing Cxxx-COS-E-DDA-CR076_PT001_80304 Revision P01 Head House External Lighting Layout Walkway which includes F2 construction detail.
| 03SR - Stations (RfL) | Cxxx-NCR-000199 | NCR | __ - South Skip Plinth cracks |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2015-09-30 | 2015-09-28 11:31 | -2 | 2015-07-07 08:59 | Civil - Civil Engineering General | 1500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | After pouring the south Skip Plinth and curing the concrete, fine line cracks appeared on top surface of the plinth
| 03SR - Stations (RfL) | Cxxx-NCR-000200 | NCR | __ Utilities - 450 Concrete pipe from MH4 to __ Sewer |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2015-07-31 | 2015-07-17 08:19 | -14 | 2015-07-08 12:23 | Civil - Utilities Engineering | 2000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During excavation for Retaining Wall base by MH4 the 450mm Dia concrete pipe running from MH4 to __ Sewere was damaged between two collars. Please refer to attached photos.
| 03SR - Stations (RfL) | Cxxx-NCR-000201 | NCR | Bus Deck - Columns - Column S4a high reinforcement |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2015-07-31 | 2015-07-22 09:50 | -9 | 2015-07-09 15:28 | Structural Engineering - Reinforcement | 2500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The projection bob (L) bars are approximately 300mm to high.
| 03SR - Stations (RfL) | Cxxx-NCR-000203 | NCR | Bus Deck - Parapets - Painting of Parapets not completed off-site |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2015-08-15 | 2015-08-05 09:36 | -10 | 2015-07-22 17:08 | Structural Engineering - Concrete Member | 35000 |  | Planning | Rework | 2 (6-60k) | Complete | Management Problem - Other management problem | Completed |  | Pre-cast Parapets have been delivered to site without been painted. The type 3 parapets were never planned on been painted off-site as they are too large to be turned over to be painted off-site. Upon discussion with the Precaster, __ decided that the Type 2 Parapets and Fin panels will also be painted onsite. Type 2 parapets also had the difficulty of turn over to paint and the Fin Panels have the lifting sockets on the front face and keim paint needs to be applied evenly, therefore would be more suitable to be appiled onsite once lifted into final position With all the works then been completed onsite by the same subcontractor sothe same consistent standard would be maintained. No specification for offsite painting - Precasting ITP check sheets will record N/A on there check sheets under the painting
| 03SR - Stations (RfL) | Cxxx-NCR-000204 | NCR | Bus Deck - AD2 - Columns Q4a Concrete Mix |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2015-08-15 | 2015-08-03 08:45 | -12 | 2015-07-22 16:44 | Structural Engineering - Concrete Member | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Use of unapproved materials | Completed |  | The incorrect Concrete mix reference for Column Q4a was accidently ordered. Upon investigation and correspodence with __ it turns out the concrete mix designs are exactly the same. Mix Reference B2 (C40/50 for rib and beam) was ordered instead on mix reference B3 (C40/50 for Columns) but it turns out the mix is exactly the same as satisfies both specifications even the DC-3 exposure required for columns
| 03SR - Stations (RfL) | Cxxx-NCR-000205 | NCR | Filling of Old __ Sewer |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2015-08-05 | 2015-08-07 17:09 | 2 | 2015-07-13 16:41 | Civil - Drainage | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | Due to existing grout and obstructions within the __ sewer, the ITP was not able to be complied with. The ITP details a system of part concreting with P150 and following a 'top up' of 100-150mm of 5* grout to ensure that no voids are left. Due to several obstructions a decision was made where the voids and condition of the pipe was unsuitable for p150 concrete. It was decided to use 5* grout as its flowability and strength led itself to this purpose. This solution allowed the site teams to move on with the under pressure track formation ready for project completion. This 70MPa gout was far in excess of the 5MPa requirement outlined in the ITP. Where the steps of the ITP could be complied with, the general method of p150 and 5* grout (a asbuilt will be submitted showing what sections were done by each method). However due to the changes of methodolgy on site due to obstructions not all of the ITP stages were followed with regard to the collection of records.
| 03SR - Stations (RfL) | Cxxx-NCR-000207 | NCR | Brickwork on MH S507 |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2015-07-29 | 2015-07-23 14:59 | -6 | 2015-07-15 15:15 | Civil - Drainage | 1000 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | On Man Hole S507 of the __ Sewer the biscuit is at such a height that the brickwork riser is only one course high. Dwg Cxxx-CSY-D-DDD-CR076_MS005-01553 shows 2 to 4 courses are required. There are no other issues with the manhole.
| 03SR - Stations (RfL) | Cxxx-NCR-000208 | NCR | Bus Deck - Cover Meter Survey for Pile Caps |  | Crossrail | PDP | PNY - Paddington New Yard (West) |  | 2015-08-13 | 2015-07-22 09:15 | -22 | 2015-07-16 17:46 | Civil - Structural Engineering | 500 |  | Testing and Commissioning | Use As-Is | 4 (0.5-3k) | Complete | Verification Problems - Other | Completed |  | The SHW 1700 Series cause 1714 paragraph 8 stipulates cover meter survey to be carried out for all reinforced concrete surfaces. I have just noted this has not been carried out for Eevated Bus Deck pile caps prior to backfilling.
| 03SR - Stations (RfL) | Cxxx-NCR-000209 | NCR | ROP - North Wing Wall Concrete Pour |  | Contr | SKC | PNY - Paddington New Yard (West) |  | 2015-08-03 | 2015-07-27 16:33 | -7 | 2015-07-20 18:46 | Structural Engineering - Concrete Member | 1500 |  | Incomplete Works | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | The north wing wall was in the process of being poured with self-compacting concrete, but due to late arrival of concrete and slow handling of the concrete skips during discharge, the wall could only be poured half way as the concrete went out of specification with regards to the time since batching and was starting to stiffen. The decision was taken on site to stop the pour.
| 03SR - Stations (RfL) | Cxxx-NCR-000210 | NCR | Track Drainage Chamber TG02 |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2015-08-04 | 2015-07-22 13:00 | -13 | 2015-07-21 10:15 | Civil - Drainage | 1500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Subcontractor Problems - Insufficient surveillance of subcontractors | Completed |  | During install of track drainage chamber TG02 set out marks were read incorrectly and the chamber was installed 671mm away from its design location along the line of the track drainage run. Drawings are attached.
| 03SR - Stations (RfL) | Cxxx-NCR-000211 | NCR | Drying Bay East – Strength achieved on north wall pours |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2015-08-31 | 2015-08-19 17:00 | -12 | 2015-07-22 16:25 | Civil - Civil Engineering General | 5000 |  | Material | Use As-Is | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Drying Bay east – north wall was constructed in 6 pours and completed on 27/05/15, concrete samples were taken for each pour to be testedc(Ticket attached for each pour). Concrete statistical analysis shows that concrete samples for pours 1, 2 & 6 did not achieve the required strength. please refer to the attached sketch for the pour sequence. Concrete was also tested for slump for each pour and was within range (Copy attached, results highlighted red for each pour)
| 03SR - Stations (RfL) | Cxxx-NCR-000212 | NCR | Grey Water Wedge Pit- Concrete Finish |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2015-08-06 | 2015-08-03 08:37 | -3 | 2015-07-22 14:24 | Civil - Civil Engineering General | 1000 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Not Defined | Completed |  | Grey Water Wedge Pit base was poured with walls’ kicker. After striking the shutters, pour concrete finish was noted in many spots along the kicker line. Please refer to the attached PDF document showing the defects.
| 03SR - Stations (RfL) | Cxxx-NCR-000213 | NCR | __ - Skip Elevator Resin Injection - MCR |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2015-08-10 | 2015-08-03 13:06 | -7 | 2015-07-23 07:45 | Structural Engineering - Concrete Member | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Use of unapproved materials | Completed |  | An MCR was not submitted and code 1 before commencing the resin injection remedial works to the __ skip elevator pit.
| 03SR - Stations (RfL) | Cxxx-NCR-000214 | NCR | __ Sewer - Guided Auger - S14 position |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2015-08-06 | 2015-08-03 13:14 | -3 | 2015-07-23 12:23 | Civil - Drainage | 1500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Previous Construction - Interfacing issues | Completed |  | Due to the logistics of getting the required temporary works installed for the installation of manhole S14, it was not possible to construct the manhole in the design position. The manhole position in the specification requires the east segment of the manhole to be north of the ROP diaphragm wall (ie the west end of the ROP wall and the manhole partially overlap) meaning that the required temporary works (a square cofferdam consisting of trench sheets and shoring frames) could not be installed around the proposed position of the manhole. The temporary works were installed tight to the west end of the ROP north D-Wall and the manhole installed as close to the original position as possible, taking into account the depth of the sheets, the width of the shoring frame, and the 150mm concrete surround to the manhole. The revised manhole co-ordinates are thus: Original centre of manhole E: 75770.559 N: 36527.078 As-built position E: 75768.6195 N: 36527.4170
| 03SR - Stations (RfL) | Cxxx-NCR-000215 | NCR | Bus Deck - Concrete Chipped on Precast Parapet |  | Crossrail | PDP | PNY - Paddington New Yard (West) |  | 2015-10-11 | 2015-10-07 17:31 | -4 | 2015-07-24 17:28 | Structural Engineering - Pre-cast | 2000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Improper handling of material | Completed |  | Some small chips in the concrete have occurred on the tops of the parapets at the halfen lifting anchor. They have occurred on one of two lifting points at the top of approximately 25% of the parapets. Most of these occurred before arriving to site, a small number occurred while lifting the parapets vertically into place. The concrete chips have been caused because of the thin concrete at the halfen lifting anchor and pressure being put on this concrete by the halfen lifter while the parapet was lifted. These chips are superficial and do not affect the structural integrity of any of the parapets in any way. Please note checksheets include details of chips
| 03SR - Stations (RfL) | Cxxx-NCR-000216 | NCR | Keim Soldalit paint: application without approved MCR |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2015-08-11 | 2015-08-03 09:00 | -8 | 2015-07-28 12:09 | Architectural - Finishes | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Use of unapproved materials | Completed |  | Keim Soldalit paint was purchased and applied without an approved MCR for the product. There was an MCR in place for Keim Lasur and the non-inclusion of Soldalit for this was an oversight.
| 03SR - Stations (RfL) | Cxxx-NCR-000217 | NCR | ROP - Roof Slab 600mm Infill |  | Contr | SKC | PNY - Paddington New Yard (West) |  | 2015-09-14 | 2015-09-11 17:36 | -3 | 2015-07-29 16:29 | Structural Engineering - Concrete Member | 7500 |  | Incorrect Installation | Repair | 2 (6-60k) | Complete | Personnel Error - Inattention to detail | Completed |  | When constructing the portal roof slab, a setting out error meant that the stair opening has been cast 600mm too long (600mm further to the east).
| 03SR - Stations (RfL) | Cxxx-NCR-000218 | NCR | Bus deck south beam |  | Crossrail | PDP | PNY - Paddington New Yard (West) |  | 2015-09-11 | 2015-09-07 08:34 | -4 | 2015-07-31 15:47 | Structural Engineering - Reinforcement | 15000 |  | Incorrect Installation | Use As-Is | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The south beam of the parapet GL1 has been built with lots of the stirrups reinforcement out of tolerance. Please see the attached photos
| 03SR - Stations (RfL) | Cxxx-NCR-000219 | NCR | cut back the reibar (parapet SP 17) |  | Crossrail | PDP | PNY - Paddington New Yard (West) |  | 2015-09-30 | 2015-09-02 11:31 | -28 | 2015-07-31 16:00 | Structural Engineering - Reinforcement | 15000 |  | Workmanship | Repair | 2 (6-60k) | Complete | Subcontractor Problems - Interfacing problems | Completed |  | Further to NCR 185 , PS17 had been reported with PS17 – 25/41 bars Clashing 61.0% , CRL site inspection today fond that at least 20 bar out of 25 where not clashed and were not need to be cut back. Please see the attached photo
| 03SR - Stations (RfL) | Cxxx-NCR-000220 | NCR | ROP - North Wing Wall Finish |  | Contr | SKC | PNY - Paddington New Yard (West) |  | 2015-09-25 | 2015-09-08 14:09 | -17 | 2015-07-31 16:15 | Architectural - Finishes | 1500 |  | Material | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The north wing wall was poured using self-compacting concrete, on striking the shutter, some large blow holes have been identified within the door way opening. There is also a pour line noticeable on the inside face of the wall on the lower left hand side.
| 03SR - Stations (RfL) | Cxxx-NCR-000221 | NCR | heating of reinforcement |  | Crossrail | PDP | PNY - Paddington New Yard (West) |  | 2015-09-11 | 2015-09-07 08:36 | -4 | 2015-07-31 16:13 | Structural Engineering - Reinforcement | 5000 |  | Damaged | Use As-Is | 3 (3-6k) | Complete | Procedure Problem - Defective or inadequate procedure | Completed |  | CRL Engs noticed that some of the reinforcement on the parapet specifically BM02 had been heated in order to bend them, the Spec. doesn’t allow heating of reinforcement. Please see the attached photos
| 03SR - Stations (RfL) | Cxxx-NCR-000222 | NCR | Bus deck beam pour 3.4a out of tolerance reinforcement |  | Crossrail | PDP | PNY - Paddington New Yard (West) |  | 2015-09-11 | 2015-09-07 08:39 | -4 | 2015-07-31 16:51 | Structural Engineering - Reinforcement | 2500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The Bus deck pour 3.4a had been poured with out of tolerance stirrups reinforcement which will cause clash with the parapet reinforcement.
| 03SR - Stations (RfL) | Cxxx-NCR-000223 | NCR | Bus Deck - Lightning Protection - AA2 and AA3 sleeve out of position |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2015-08-18 | 2015-08-20 14:30 | 2 | 2015-08-04 18:11 | Structural Engineering - Inserts | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | 50mm diameter sleeves for lightning protection cable connections through the deck slab from columns AA2 and AA3 were cast in outside of design kerb line in deck pour 1.1. These need to be within the footpath to ensure they do not pass through the waterproofing layer on top of the concrete deck slab.
| 03SR - Stations (RfL) | Cxxx-NCR-000224 | NCR | Rain Water Groove missing on PS7 and PS11 |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2015-08-31 | 2015-08-11 12:20 | -20 | 2015-08-06 09:51 | Structural Engineering - Pre-cast | 1500 |  | Incomplete Works | Repair | 4 (0.5-3k) | Complete | Subcontractor Problems - Insufficient surveillance of subcontractors | Completed |  | Rain water groove not cast into pre-cast parapets PS7 and PS11. All other Parapets have since been cast-in
| 03SR - Stations (RfL) | Cxxx-NCR-000226 | NCR | Haunching on __ Manholes |  | Contr | HTM | PNY - Paddington New Yard (West) |  | 2015-08-21 | 2015-08-19 13:50 | -2 | 2015-08-07 08:40 | Civil - Drainage | 1000 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During the haunching of the ironwork to the brickwork on the __ Sewer the haunching has become cracked. The Haunching was done in early July when the temerature was in excess of 30 degrees. This caused the haunching to crack during curing. This occured on MH508 and 510 (photos attached) MH 510 required repointing and cleaning. Photos are attached.
| 03SR - Stations (RfL) | Cxxx-NCR-000227 | NCR | __- LV Room – Electrical Installation |  | Crossrail | XRL | PNY - Paddington New Yard (West) |  | 2015-08-24 | 2015-08-28 09:51 | 4 | 2015-08-10 14:20 | Electrical - General | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | __- LV Room – Electrical Installation On the quality surveillance carried out on the installation of the electrical installation and equipment located in the __ –LV room the following observations were found 1.0 An prior inspection of the installation had not been carried by the M&E contractor “__” or __ and the checks presented have not been signed by __. 2.0 The LV/SS board MCCB’s were found to be incorrectly wired and the gland banjo earth nut & bolt missing. Note this was corrected during the surveillance. 3.0 The test sheets presented did not match the ITP template with no verifying document references. On examination of the LV/SS test sheet it was found to be incorrect stating the Overcurrent Device rating of 63 amp when it is 40 amp. See attachments The matter has been raised in a discussion with the __ contracts manger on Friday 7th August 2015 who will now carry out a review and report back and put a procedure in place to ensure there is not a re-occurrence.
| 03SR - Stations (RfL) | Cxxx-NCR-000228 | NCR | Bus Deck - Recess For BDU LJH works clashing |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2015-09-14 | 2015-09-17 17:37 | 3 | 2015-08-10 15:47 | Structural Engineering - Structural Engineering - General | 2500 |  | Design | Repair | 4 (0.5-3k) | Complete | Previous Construction - Interfacing issues | Completed |  | Recess in western side of the derailment wall clashes with LJH steel work pushing it out of plumb by approximately 20-25mm
| 03SR - Stations (RfL) | Cxxx-NCR-000229 | NCR | Bus Deck - Parapets - West Elevation - PW17 Bar Clash |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2015-08-25 | 2015-08-28 07:43 | 3 | 2015-08-11 09:06 | Structural Engineering - Reinforcement | 1000 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | Parapet PW17D had 2no. bars cut to allow installation as they clashed with Main bars of the primary beam
| 03SR - Stations (RfL) | Cxxx-NCR-000230 | NCR | Bus Deck - 2.2 GL-3 Beam - Mechanical damage to soffit |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2015-11-30 | 2015-11-27 10:41 | -3 | 2015-08-11 10:47 | Structural Engineering - Finishes | 1500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | During excavation for interceptor pit C110 a 14t excavator struck the soffit on gridline 3 on the underside of bus deck with the top of its dipper arm while disposing of spoil. This caused minour damage to the soffit.
| 03SR - Stations (RfL) | Cxxx-NCR-000231 | NCR | Bus Deck - Interceptor Installation |  | Crossrail | PDP | PNY - Paddington New Yard (West) |  | 2015-09-18 | 2015-09-11 17:30 | -7 | 2015-08-11 17:52 | Mechanical - Pumps | 2500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Concrete cover to interceptor placed and not levelled. This makes it difficult to confirm it has achieved the minimum 225mm thick Type ST4 surround stipulated in the works information.
| 03SR - Stations (RfL) | Cxxx-NCR-000232 | NCR | Positional Tolerance on Track Drainage Chambers |  | Contr | HTM | PNY - Paddington New Yard (West) |  | 2015-08-25 | 2015-08-12 13:58 | -13 | 2015-08-11 19:45 | Civil - Drainage | 1500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | During construction of the track drainage it was noticed that some of the chambers moved slightly during the backfill operation with GEN3 concrete. This is generally not a large amount. This is shown on the attached spreadsheet for all of the track drainage chambers out of the +-15mm in the specification.
| 03SR - Stations (RfL) | Cxxx-NCR-000233 | NCR | Bus deck: Pile 274 - Low reinforcement |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2015-08-27 | 2015-08-28 07:38 | 1 | 2015-08-13 07:49 | Civil - Civil Engineering General | 2000 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Reinforcement to pile 274 was found to be low. As built is as below. As built Top of Steel = 120.390mATD Design Top of Steel = 120.625mATD Difference = - 0.235m
| 03SR - Stations (RfL) | Cxxx-NCR-000234 | NCR | Transition Slab Damage |  | Contr | HTM | PNY - Paddington New Yard (West) |  | 2015-09-18 | 2015-09-15 10:31 | -3 | 2015-08-13 16:43 | Civil - Drainage | 2500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During the positioning of Track Drainage chamber TK07 in the Royal Oak Portal it was found that the transition slab clashes with the chamber (a seperate FCD has been raised for the relocation of the chamber). Through a lack of communication between the subcontractors crew, a corner of the Transition slab was damaged. The damage covers an area on the corner of approx. 500mmx500mm.
| 03SR - Stations (RfL) | Cxxx-NCR-000235 | NCR | Bus Deck - AD1 & AD2 - Derailment Wall and Column concrete beyond 2hrs |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2015-09-14 | 2015-08-20 14:37 | -25 | 2015-08-17 10:48 | Structural Engineering - Concrete Member | 500 |  | Planning | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Improper handling of material | Completed |  | During the preparation of preparing ITP deliverable records for handover it has been noticed that numerous column and derailment wall pours have had discharges longer than 2 hours. The following column results have concrete discharges longer than 2 hours: E1 (2h 32m), L1c & L2a (2h 52m), T1b & U4a (2h 37m), U1 & V4 (2h 21min), U2 & V3 (2h 28m), X3 (2h 36m) The following derailment results have concrete discharges longer than 2 hours: Derailment Wall 1 - Pour 2A (2h 42m and 2h 51m), 5A (2h 20m) & 10B (2h 25m and 2h 27m) Derailment Wall 2 - Pour 3A (2h 12m), 5A (2h 14m), 6A (2h 21m), 7A (2h 36m), 10A (2h 31m), 11A (2h 28m), 5B (2h 11m), 7B (2h 8m), 10B (2h 20m) & 12B (2h 22m & 2h 26m). All the above the in-situ cube results show that the design strengths have been reached within the correct timescales, and all the slump tests were within the required values. Cube results for the above column pours range from 61.55 to 72.3 with the required design strength being 50 N/m (28 day crush results) Cube results for the above derailment pours range from 49 to 68.3 with the required design strength being 40 N/m (28 day crush results) Slump test range for the above pours range from 150 to 240 with the required range being 140 to 240
| 03SR - Stations (RfL) | Cxxx-NCR-000236 | NCR | Bus wash Facility Plinth relocation to suit subcontractor’s Drawing |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2015-09-25 | 2015-09-18 11:24 | -7 | 2015-08-17 15:06 | Civil - Structural Engineering | 2500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Previous Construction - Interfacing issues | Completed |  | Rebar as built of the Wash facility plinth were installed as per setting out information on drawing number Cxxx-CSY-S-DDA-CR076_MS005-01135 Rev C03 which does not correspond to Subcontractor (KARCHER) drawing number (0-)002 Rev C1. As the bars were cast in place as part of the bus deck pour, corrective action is required prior to pouring wash facility plinths.
| 03SR - Stations (RfL) | Cxxx-NCR-000237 | NCR | Royal Oak Portal - Fire Main Box Out in Platform Internal East Wall |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2015-09-30 | 2015-09-09 09:06 | -21 | 2015-08-20 07:44 | Structural Engineering - Concrete Member | 2500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Design Problem - Conflicting information on drawings | Completed |  | The box out in the east internal wall for the fire main under the ROP intervention platform slab has been cast with the bottom of the box out at 114.170m. This was based on the information on the C150 drawing.
| 03SR - Stations (RfL) | Cxxx-NCR-000238 | NCR | __ - Grey Water Pit Wall Concrete Finish |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2015-10-28 | 2015-10-27 10:24 | -1 | 2015-09-08 18:50 | Structural Engineering - Concrete Member | 1000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The concrete finish for the grey water wedge pit walls is not as per the __ concrete specification: Vertical finish - • There are large blow holes and areas of poor compaction. • There are ridges between ply sheets in excess of 0mm tolerance. • There is excessive grout loss at the kickers. Horizontal finish - • The top of some sections of the walls varies by more than the +/-3mm tolerance. There may be possible cover issues. • The finish is not smooth hard finish and there is excessive laitance.
| 03SR - Stations (RfL) | Cxxx-NCR-000239 | NCR | ROP - 20mm dip in the platform slab |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2015-09-25 | 2015-09-24 13:39 | -1 | 2015-08-21 15:17 | Civil - Civil Engineering General | 2500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | There is a dip of approximately 20mm in the Royal Oak Portal platform slab that was poured recently. Please find attached photos The root cause of the issue is workmanship. Being a small area __ Formwork did not use screen rails in the instance.
| 03SR - Stations (RfL) | Cxxx-NCR-000240 | NCR | ROP - Diaphragm wall concrete overbreak |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2015-09-10 | 2015-09-11 14:14 | 1 | 2015-08-21 18:05 | Civil - Structural Engineering | 1500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Due to the nature of diaphragm wall construction there were areas where the concrete protruded from the wall face. In an attempt to create an even wall profile for __ cable tray installation __ undertook to break off some of these protrusions. The operatives inadvertently broke to too far a depth of concrete in one location, exposing some of the wall steel. See attached photo.
| 03SR - Stations (RfL) | Cxxx-NCR-000241 | NCR | __ - MCR for Palisade Fencing Fixings Not Code 1 |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2015-09-10 | 2015-08-26 11:27 | -15 | 2015-08-23 14:29 | Architectural - Handrail | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | The MCR for the palisade fencing fixings and resin (Cxxx-COS-Z-LRC-CR076_SD006-50020 (1.0)) was not code 1 at the time of usage of the products on-site.
| 03SR - Stations (RfL) | Cxxx-NCR-000242 | NCR | Drainage - Under Bus Deck Drainage - Incorrect Manhole Type |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2015-09-25 | 2015-09-21 13:36 | -4 | 2015-08-26 11:37 | Civil - Drainage | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | __ Cxxx wish to raise a non-conformance regarding drainage under the bus deck, in particular Manholes C109 and C111. In the drainage specification, these are listed as 'Type 7' manholes with a small catchpit base below the pipe inlet/outlets. These two manholes have instead been installed as Type B Flatbed Manholes, without the catchpit base. As a result the Western end of Pipe Run has been 100.007 has been elevated to match the IL of the Manhole. • IL Western end of Pipe Run 100.007 is now 120.600m Cxxx __ would like to note that Manhole C111 is the same in configuration to C114 yet in the specification, it is a Type B manhole which suggests the Type B manhole may be suitable for the two incorrect installations also.
| 03SR - Stations (RfL) | Cxxx-NCR-000243 | NCR | Bus Deck - AD1 - GL1 Stitch - Concrete pour exceeding 2hr limit |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2015-10-07 | 2015-10-07 17:34 | 0 | 2015-09-03 17:06 | Structural Engineering - Concrete Member | 500 |  | Planning | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate resources | Completed |  | Concrete delivery for GL1 stitch (pour number 2) exceeded the 2hr time limit as per Appendix 17/1.
| 03SR - Stations (RfL) | Cxxx-NCR-000244 | NCR | __ - Fencing Works Commenced without ITP Code 1 |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2015-09-02 | 2015-09-07 12:38 | 5 | 2015-08-31 18:19 | Architectural - Handrail | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Verification Problems - Other | Completed |  | The fencing in the __ batch plant commeneced prior to the ITP being code 1.
| 03SR - Stations (RfL) | Cxxx-NCR-000245 | NCR | ROP - Plinths below platform slab |  | Contr | HTM | PNY - Paddington New Yard (West) |  | 2015-10-15 | 2015-09-30 08:27 | -15 | 2015-09-01 16:54 | Structural Engineering - Concrete Member | 1000 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | Due to a miscommunication with the subcontractor, the entire area between the two mass concrete surround plinths was also poured to the same level as per the attached sketch. This is mass concrete plinth to a height of 1580mm above the base slab floor.
| 03SR - Stations (RfL) | Cxxx-NCR-000246 | NCR | Bus Deck - Concrete Parapet Stitch - Increased structural concrete thickness |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2015-10-09 | 2015-09-25 17:14 | -14 | 2015-09-02 16:47 | Structural Engineering - Concrete Member | 1500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | As a result of the additionall reinforcement installed as per NCR 185 and the related FCD's the concrete thickness had to be increased to ensure that the minimum concrete cover was acheived after a template was created to ensure minimum cover was compliant. As a result of the additional reinforcement and the compounding effect of the concrete slump the original design (as per Cxxx-CSY-S-DDD-CR076_MS005-01096 Detail 4) illustrating a flat surface with a sloped surface on the parapet face became negligable/ unconstructable.
| 03SR - Stations (RfL) | Cxxx-NCR-000247 | NCR | ROP - Headhouse cold rolled steel - MCR approvals |  | Contr | HTM | PNY - Paddington New Yard (West) |  | 2015-10-01 | 2015-09-23 08:44 | -8 | 2015-09-03 10:49 | Structural Engineering - Steel Member | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Lack of approval Code 1 procedures excessive | Completed |  | Erection of the cold rolled steel for the Royal Oak Portal has proceeded onsite without an approved MCR. The MCR Cxxx-COS-S-LRC-CR076_PT001-50003 is currently Code 3. MCR was code 3 due to the loadings not being verified.
| 03SR - Stations (RfL) | Cxxx-NCR-000248 | NCR | Bus Deck - Cover Meter Results out of tolerance (AD1, AD2 and AD3) |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2015-09-17 | 2015-09-15 17:56 | -2 | 2015-09-03 15:09 | Structural Engineering - Reinforcement | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | On review of cover meter results it has been noticed that there are some instances where the reinforcement steel shows results out of tolerance (+/- 10mm). At no point is the reinforcement more than 5mm above the upper limit or 5mm below the lower limit. The highest precentage of readings being above the upper limit is 5.5% over 1000 readings with the largest reading being 3mm above the upper limit, with a standard deviation of 2.4mm.
| 03SR - Stations (RfL) | Cxxx-NCR-000249 | NCR | Bus Deck - North Abutment Retaining Wall - Require installation of mechanical couplers |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2015-09-29 | 2015-09-25 17:10 | -4 | 2015-09-04 18:46 | Structural Engineering - Reinforcement | 5000 |  | Planning | Use As-Is | 3 (3-6k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | During the construction of the North Abutment retaining wall, Reinforcement construction has commenced from the stop end of the next pour working back towards the previous poor. This has been caused by the need to prefabricate the north abutment cages to accelerate production and prevent any potential downtime associated with waiting for the formwork to be struck. As a result of the reinforcement being prefabricated prior to installation the prefabricated top section was unable to be installed without cutting the existing lap lengths protruding from the previous poor.
| 03SR - Stations (RfL) | Cxxx-NCR-000250 | NCR | Bus Deck - AD1 - GL1 Stitch - Concrete pour exceeding 2hr limit (Pour 4) |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2015-10-07 | 2015-10-07 17:36 | 0 | 2015-09-04 09:23 | Structural Engineering - Concrete Member | 500 |  | Planning | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Use of unapproved materials | Completed |  | Concrete delivery for GL1 stitch (pour number 2) exceeded the 2hr time limit as per Appendix 17/1.
| 03SR - Stations (RfL) | Cxxx-NCR-000251 | NCR | Bus Deck - Low Reinforcement - Pile Cap B/5a (Pile 299 and P301) |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2015-10-06 | 2015-09-25 17:03 | -11 | 2015-09-04 16:56 | Geotechnical Engineering - Concrete - Bored Pile | 2500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Following pile break down to cut off level within Pile Cap B/5a, two piles were found to have low reinforcement which were below the allowable tolerances of +150/-50mm as per the ICE SPERW cl B3.4.1. (Similair problems as per Cxxx-NCR-000156) Pile 299 is between 1.0m - 1.5m low and Pile 301 is ~200mm low (Actual as-built levels will be provided prior to close out)
| 03SR - Stations (RfL) | Cxxx-NCR-000252 | NCR | Bus Deck - Pile Cap B/5a - Concrete Beyond 2hrs |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2015-10-13 | 2015-10-07 17:37 | -6 | 2015-09-09 15:07 | Structural Engineering - Concrete Member | 500 |  | Planning | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Use of unapproved materials | Completed |  | Concrete delivery for B/5a exceeded the 2hr time limit as per Appendix 17/1.
| 03SR - Stations (RfL) | Cxxx-NCR-000253 | NCR | Bus Deck - AD2 - Bus Wash - Upstand Concrete Pour |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2015-10-08 | 2015-10-08 13:40 | 0 | 2015-09-17 18:53 | Civil - Civil Engineering General | 500 |  | Planning | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Use of unapproved materials | Completed |  | Concrete arrived on site 61 minutes after batching at 1334hrs and arrived onsite at 1435hrs, with the discharge commencing at 1526 hrs with the discharge completed at 1550hrs. As a result the concreted exceeded the 2hr time limit by 18 minutes. At the time the concrete was called in it was expected that all works would be completed prior to the concrete trucks arriving onsite (On-site personal underestimated the time required to complete the remaining works). Discussion held with the Bus Deck team about the importance of ensuring concrete is not ordered too early to avoid the concrete exceeding the 2hr time limit. As soon as the costain engineer identified that the concrete had exceeded the 2hr time limit, a stop end was installed and the pour called off. As a result a construction joint will be formed in BWD02 (Bus wash Plinth) Concrete was slumped at 150mm immediately before the concrete was placed complying with the required S4 slump. __ will provide the cube results to prove the 28 day design strength is achieved. Please find attahed concrete delivery ticket, concrete pour records and cube request certificate for you reference.
| 03SR - Stations (RfL) | Cxxx-NCR-000254 | NCR | Bus Deck - Blow holes on surface of western edge Parapets |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2016-01-29 | 2016-01-22 08:48 | -7 | 2015-09-11 18:23 | Civil - Civil Engineering General | 2500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | There is blowholes on the surface of Western edge parapets No. PW18, PW17D, PW17E and PW17F (painted and unpainted outside/ exposed face) – inconsistent with the specified F4 finish.
| 03SR - Stations (RfL) | Cxxx-NCR-000255 | NCR | Bus Deck: Deck Slab pour 3.4b - Remedial action to displaced stop end |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2015-10-06 | 2015-09-23 13:30 | -13 | 2015-09-14 15:04 | Civil - Civil Engineering General | 5500 |  | Workmanship | Use As-Is | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During Bus Deck slab pour 3.4b on Friday 11/09/15 the last row of void formers moved at approximately 18:30 when concrete reached approx. 70% of the trough height.
| 03SR - Stations (RfL) | Cxxx-NCR-000256 | NCR | __ - Retaining Wall (Wall SOP04-05) - Discharge completion time exceeds 2 hours after being batched |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2015-09-30 | 2015-09-23 09:00 | -7 | 2015-09-16 08:53 | Civil - Civil Engineering General | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Use of unapproved materials | Completed |  | Concrete arrives on site almost an hour after being batched. Due to site logistics, discharge did not commence until 50mins later. Discharge had commenced within 2 hours of batching, however, the time taken to complete discharge exceeded the 2 hour mark. Concrete was poured at high consistency 170mm and at overcast weather conditions, reducing the likelihood of quick setting concrete.
| 03SR - Stations (RfL) | Cxxx-NCR-000257 | NCR | __ - Paving Slab A3-5 Low Strength at 28 Days |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2015-10-23 | 2015-10-16 10:02 | -7 | 2015-09-16 13:37 | Civil - Concrete Pavement | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Subcontractor Problems - Other | Completed |  | The 28 day concrete strength for __ paving slab A3-5 has not reached the design strength of 40N/mm2. It has reached 34N/mm2.
| 03SR - Stations (RfL) | Cxxx-NCR-000258 | NCR | __ - Retaining Wall (Wall SOP05-06) - Discharge completion time exceeds 2 hours after being batched |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2015-10-20 | 2015-10-15 14:58 | -5 | 2015-09-17 13:11 | Civil - Civil Engineering General | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Subcontractor Problems - Other | Completed |  | Concrete arrives on site 50mins after being batched. Discharge did not commence until an hour after arrival (within 2 hours of batch time) . The Concrete pour overruns, and exceeds the 2 hour mark by 24 minutes. The concrete was slumped at a high consitency of 230mm S4, and so workability could be maintained for longer duration.
| 03SR - Stations (RfL) | Cxxx-NCR-000259 | NCR | Bus Deck - Parapet Stitching - Concrete Beyond 2 hrs |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2015-11-09 | 2015-10-22 07:43 | -18 | 2015-10-12 09:26 | Structural Engineering - Concrete Member | 500 |  | Planning | Use As-Is | 4 (0.5-3k) | Complete | Subcontractor Problems - Other | Completed |  | A number of concrete deliveries for the Parapet stitch exceeded the 2hr time limit as per Appendix 17/1.
| 03SR - Stations (RfL) | Cxxx-NCR-000261 | NCR | ROP - Fixing of Cable Riser to Electrical Cabinet |  | Contr | SKC | PNY - Paddington New Yard (West) |  | 2015-11-10 | 2015-10-26 16:04 | -15 | 2015-09-23 13:57 | Structural Engineering - Steel Member | 1500 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Conflicting information on drawings | Completed |  | Due to conflicting to heights between drawings C150-CSY-S-DDL-CR076_PT001-01300 and Cxxx-COS-A-DDB-CR076_PT001_Z-20112 of the base height of the cable riser there is 60mm of grout to be placed between top of electrical cabinet and the cable riser. This would mean the specified __ HAS-F M12 100 stud anchor will not achieve full embedment depth in the cabinet roof slab.
| 03SR - Stations (RfL) | Cxxx-NCR-000262 | NCR | __ - pavement Slab A19-1 - Low 28 Day Strength |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2015-10-23 | 2015-10-15 14:47 | -8 | 2015-09-24 14:49 | Civil - Concrete Pavement | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Subcontractor Problems - Other | Completed |  | The concrete strength for __ pavement slab A19-1 (light duty fibre mix) has not reached the design strength of 40N/mm2 at 28 days. It has reached 37.5N/mm2.
| 03SR - Stations (RfL) | Cxxx-NCR-000263 | NCR | __ - Pavement Slab A3-3 - Low 28 Day Strength |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2015-10-23 | 2015-10-15 14:50 | -8 | 2015-09-24 14:54 | Civil - Concrete Pavement | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Subcontractor Problems - Other | Completed |  | The concrete strength for __ pavement slab A3-3 has not reached the design strength of 40N/mm2 at 28 days. It has reached 38.5N/mm2.
| 03SR - Stations (RfL) | Cxxx-NCR-000264 | NCR | __ - Pavement Slab A15-2 - Low 28 Day Concrete Strength |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2015-10-30 | 2015-10-22 16:18 | -8 | 2015-09-24 14:58 | Civil - Concrete Pavement | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Subcontractor Problems - Other | Completed |  | The concrete strength for __ pavement slab A15-2 has not reached the design strength of 40N/mm2 at 28 days.
| 03SR - Stations (RfL) | Cxxx-NCR-000265 | NCR | __ - Pavement Slab A10-1 - Low 28 Day Concrete Strength |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2015-10-23 | 2015-10-15 15:10 | -8 | 2015-09-24 15:12 | Civil - Concrete Pavement | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Other | Completed |  | The concrete strength for __ pavement slab A10-1 has not reached the design strength of 40N/mm2 at 28 days. It has reached 37N/mm2 at 28 days.
| 03SR - Stations (RfL) | Cxxx-NCR-000266 | NCR | __ - Pavement Slab A1-2 - Low 28 Day Concrete Strength |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2015-10-23 | 2015-10-15 15:15 | -8 | 2015-09-24 15:14 | Civil - Concrete Pavement | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Other | Completed |  | The concrete strength for __ pavement slab A19-1 (light duty fibre mix) has not reached the design strength of 40N/mm2 at 28 days. The concrete reached 38N/mm2.
| 03SR - Stations (RfL) | Cxxx-NCR-000267 | NCR | Bus Deck - AD2 - Bus Wash - TBD4 Installation on the Bus Deck |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2016-01-22 | 2016-01-19 14:46 | -3 | 2015-10-09 14:20 | Civil - Structural Engineering | 1500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Karcher UK Limited, commenced the installation process of the Bus Wash on site on 21/09/2015. It was noted by __ that some of the anchor bolts used for the Bus Wash Posts were not installed correctly an have been drilled into the concrete at an angle (Please see attached pictures). When __ raised the question, Karcher confirmed that some of the anchor bolts could not be installed correctly due to the high steel congestion in the Bus Deck Upstands. Karcher also confirmed that the current installation will not affect the wash operation or the structural rigidity of the posts.
| 03SR - Stations (RfL) | Cxxx-NCR-000268 | NCR | ROP - Intervention Stairwell Opening Chamfer |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2015-10-20 | 2015-10-20 10:47 | 0 | 2015-10-06 07:53 | Structural Engineering - Concrete Member | 1500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Other | Completed |  | As per the attached marked up photo a section of the constructed stairwell chamfer potrudes past the design line of the blockwork. The protusion is at maximum 15-20mm from design line of brickwork, the exact potrusion will need to be measured once false work has been removed from stairwell.
| 03SR - Stations (RfL) | Cxxx-NCR-000269 | NCR | ROP - Platform Slab HV Riser Penetration Constructed to Incorrect Size |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2015-10-29 | 2015-10-28 18:29 | -1 | 2015-10-05 07:43 | Structural Engineering - Concrete Member | 2500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | The HV riser penetration in the intervention platform slab on the west side of the electrical cupboards was constructed 100mm too small in the east-west direction. Drawing C150-CSY-S-DDA-CR076_PT001-00701 (C04) (refer attached) shows the dimensions as 500mm x 600mm. However, a PMI-00169 was issued to change the dimensions to 650mm x 600mm. The MEP drawing was updated but the structural drawing was not and subsequently the penetration constructed to the incorrect dimension.
| 03SR - Stations (RfL) | Cxxx-NCR-000270 | NCR | __ - Grey Water Wedge Pit - Wall Pour 1 - Low 28 Day Strength |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2015-10-19 | 2015-10-15 15:20 | -4 | 2015-10-05 15:58 | Civil - Civil Engineering General | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Subcontractor Problems - Other | Completed |  | The concrete compression strength for the Grey Water Wedge Pit Wall pour 1 has not reached the specified strength of 40N/mm2 at 28 days. Instead it has reached 37N/mm2. 28 Day and 56 Day Cube Reports attached.
| 03SR - Stations (RfL) | Cxxx-NCR-000271 | NCR | ROP - FSC and Plinth concrete exceeding 2hr limit |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2015-11-06 | 2015-10-13 16:18 | -24 | 2015-10-09 17:26 | Structural Engineering - Concrete Member | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Subcontractor Problems - Other | Completed |  | Some of the concrete poured for the First Stage Concrete and plinths between the platform slabs exceeded the 2 hour from batching time placement limit. These were with the following concrete: FSC North Side 3rd Layer, FSC South side 3rd layer, FSC Infill 1st Layer and the Platform Plinth Pour 1 The cube results for the pours have been provided as well as the delivery and placement records. There were not any cubes taken for the platform plinth pour 1 due to the volume of the pour being only 2m3 and cube sets are only required per 24m3. It is deemed unnecessary to take cubes for this structure as it is non-structural and simply mass fill. That being said, a stronger strength C40/50 concrete was used to pour the plinth as shown on the attached records.
| 03SR - Stations (RfL) | Cxxx-NCR-000272 | NCR | ROP - Platform slab concrete exceeding 2 hour limit |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2015-11-07 | 2015-10-13 16:21 | -25 | 2015-10-10 08:46 | Structural Engineering - Concrete Member | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Subcontractor Problems - Other | Completed |  | Some of the concrete placed in pours 1, 3 & 4 of the ROP platform slab exceeded the 2 hour placement limit. The concrete pour check sheets and cube results have been provided and demonstrate that the required concrete 50N/mm2 strength has been achieved. Also attached is an email from __ confirming that the concrete can be placed well after the 2hour limit.
| 03SR - Stations (RfL) | Cxxx-NCR-000273 | NCR | __ - Hopper Pit Ramp/Slab Pour 1 - Discharge completion time exceeds 2 hours after batch |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2015-10-27 | 2015-10-15 15:21 | -12 | 2015-10-06 09:24 | Civil - Civil Engineering General | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Subcontractor Problems - Other | Completed |  | Concrete arrives on site an hour after being batched. Access to area of pour blocked due to lifting operation, and so discharge could not commence until 1hr later. Discharge began within 2 hours of batching, however, the time taken to complete discharge exceeded the 2 hour mark. Note: Discharge to structural pour completed at 1425hrs, as noted on the attached ticket.
| 03SR - Stations (RfL) | Cxxx-NCR-000274 | NCR | ROP - Platform Wall concrete pour exceeding 2 hour limit |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2015-10-29 | 2015-10-13 09:37 | -16 | 2015-10-10 09:12 | Structural Engineering - Concrete Member | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Subcontractor Problems - Other | Completed |  | The following concrete placement for the Platform Walls exceeded the 2 hour limit: Platform Wall North Pour 1 Platform Wall South Pour 1 Platform Wall South Pour 4 The concrete pour check sheets and cube results have been provided and demonstrate that the required concrete 50N/mm2 strength has been achieved. Also attached is an email from __ confirming that the concrete can be placed well after the 2hour limit.
| 03SR - Stations (RfL) | Cxxx-NCR-000275 | NCR | __ - Grey Water Wedge Pit - Wall Pour 2 - Discharge completion time exceeds 2 hours after batch |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2015-10-20 | 2015-10-15 14:44 | -5 | 2015-10-06 17:42 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Subcontractor Problems - Other | Completed |  | Concrete arrives on site at 1700hrs. Discharge commences as soon as wagon tested, however due to logistics and complexity of pour; the pour overan by 29 minutes. Concrete sampled, and has achieved more than the specified strength, failing at 41.6 N/mm2 - 28 days (Attached).
| 03SR - Stations (RfL) | Cxxx-NCR-000276 | NCR | ROP - Concrete exceeding 2 hour limit for stair walls and roof slab upstand wall |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2015-10-28 | 2015-10-13 16:32 | -15 | 2015-10-10 10:40 | Structural Engineering - Concrete Member | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Supervision - Other | Completed |  | Some of the concrete placed in the stair walls and the roof slab upstand wall exceeded the 2 hour placement limit. The concrete pour check sheets and cube results have been provided and demonstrate that the required concrete 50N/mm2 strength has been achieved. Also attached is an email from __ confirming that the concrete can be placed well after the 2hour limit.
| 03SR - Stations (RfL) | Cxxx-NCR-000277 | NCR | Head House - Missing Holes for CMS in Slab |  | Crossrail | XRL | PNY - Paddington New Yard (West) |  | 2015-11-30 | 2015-11-27 11:33 | -3 | 2015-10-09 17:13 | Civil - Civil Engineering General | 1500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Misunderstand the definition of the requirement | Completed |  | 2 No holes have not been constructed within the Head House slab.These holes provide the CMS routes for the sump pump and the small power and lighting to the platform as detailed on drawing Cxxx-COS-E-DDA-CR076_PT001_1-31012
| 03SR - Stations (RfL) | Cxxx-NCR-000278 | NCR | ROP - Platform slab and stair kicker concrete low 28 day strength |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2015-10-24 | 2015-10-12 17:30 | -12 | 2015-10-10 11:04 | Structural Engineering - Concrete Member | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Other management problem | Completed |  | The 28 day concrete test result for the ROP platform slab pour 3 and the stair kickers pours 3 ,4 & 5 was below strength at 44N/mm2. The 56 day test results have reached the desired strength and is 51.6N/mm2
| 03SR - Stations (RfL) | Cxxx-NCR-000279 | NCR | ROP - Platform slab pour 2 low strength concrete results |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2015-10-28 | 2015-10-12 17:33 | -16 | 2015-10-10 11:50 | Structural Engineering - Concrete Member | 1000 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Other management problem | Completed |  | The concrete strength for the platform slab did not reach the designed 50N/mm2. The concrete reults show the 28 day test results are 42.5N/mm2 and 43.1N/mm2 and the 56 day result is 45.1N/mm2. As shown on the attached sketch, the pour only relates to a small area at the west end of the platform that has a maximum unsupported span of 1.6m.
| 03SR - Stations (RfL) | Cxxx-NCR-000280 | NCR | ROP - Platform Level Plinths low 28 day concrete strength |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2015-10-28 | 2015-10-12 17:35 | -16 | 2015-10-10 12:05 | Structural Engineering - Concrete Member | 2500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Other management problem | Completed |  | The concrete strength for the platform plinths did not reach the designed 50N/mm2. The 28 day test results are slightly under at 47.0N/mm2 and 46.1N/mm2 . The areas affected are shown on the attached sketch.
| 03SR - Stations (RfL) | Cxxx-NCR-000281 | NCR | Bus Deck - North Abutment Retaining Wall - Concrete Beyond 2 hrs |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2015-11-09 | 2015-11-05 13:55 | -4 | 2015-10-12 10:01 | Structural Engineering - Concrete Member | 500 |  | Planning | Use As-Is | 4 (0.5-3k) | Complete | Subcontractor Problems - Other | Completed |  | A number of concrete deliveries for the North Abutment Retaining Wall exceeded the 2hr time limit as per Appendix 17/1.
| 03SR - Stations (RfL) | Cxxx-NCR-000282 | NCR | __ - Grey Water Wedge Pit - Base slab surface detail |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2015-10-27 | 2015-10-22 16:38 | -5 | 2015-10-13 10:55 | Civil - Civil Engineering General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Error in equipment or material selection | Completed |  | It has come to our attention that a small detail, in the construction of the Grey water wedge pit had been missed out. Notes 6. in the dwg attached states that ‘Unformed surfaces shall be class U3 (Steel float finish +-3mm), however an additional annotation on the drawing labels the base slab with a tamped finish.
| 03SR - Stations (RfL) | Cxxx-NCR-000283 | NCR | ROP - Retaining wall concrete beyond 2 hours |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2015-10-30 | 2015-10-21 13:20 | -9 | 2015-10-16 09:49 | Structural Engineering - Concrete Member | 500 |  | Planning | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Concrete delivery for Access Road retaining Wall Pour 1 exceeded the 2hr time limit as per Appendix 17/1.
| 03SR - Stations (RfL) | Cxxx-NCR-000284 | NCR | ROP - suspended slab concrete beyond 2 hours |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2015-10-30 | 2015-10-22 07:41 | -8 | 2015-10-16 09:52 | Structural Engineering - Concrete Member | 500 |  | Planning | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Other management problem | Completed |  | Concrete delivery for Suspended slab exceeded the 2hr time limit as per Appendix 17/1.
| 03SR - Stations (RfL) | Cxxx-NCR-000285 | NCR | __ - White Lining - ITP Not Code 1 Prior to Commencing Works |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2015-10-30 | 2015-10-23 11:30 | -7 | 2015-10-17 09:54 | Civil - Concrete Pavement | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - No evidence of program review from Contractor's Quality Manager or Management | Completed |  | ITP Cxxx-COS-Z-ITP-CR076_SD006-50014 Rev 1.0 for the __ white lining was not code 1 prior to commencement of works.
| 03SR - Stations (RfL) | Cxxx-NCR-000286 | NCR | __ - White Lining MCR Not Code 1 Prior to Starting Works |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2015-10-30 | 2015-10-26 18:29 | -4 | 2015-10-17 10:00 | Civil - Concrete Pavement | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Use of unapproved materials | Completed |  | MCR Cxxx-COS-C-LRC-CR076_SD006-50105 was not code 1 prior to starting works for the __ white lining.
| 03SR - Stations (RfL) | Cxxx-NCR-000287 | NCR | ROP - darinage channel infill low 28 day cube result |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2015-11-02 | 2015-10-21 16:59 | -12 | 2015-10-19 12:03 | Structural Engineering - Concrete Member | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Other management problem | Completed |  | The 28 day result for the drainage channel infill in the ROP area is 22.5 and 23N/mm2 respectively. The 56 day results have reached the C20/25 strength as shown in the attachment
| 03SR - Stations (RfL) | Cxxx-NCR-000288 | NCR | ROP - Staff toilet drainage pipe to wall interface |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2015-11-03 | 2015-10-21 17:23 | -13 | 2015-10-20 11:14 | Civil - Drainage | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Previous Construction - Problems based on previous construction errors | Completed |  | Due to the lid on the drain in the headhouse staff toilet being larger than the pipe, the external frame holding the lid onto the pipe protrudes into the blockwork as shown in attached photos. __ propose to Use As-Is, with mortar used to provide an even surface finish to allow for painting.
| 03SR - Stations (RfL) | Cxxx-NCR-000289 | NCR | ROP - Earth Cable Core Partially Beneath Blockwork |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2015-11-03 | 2015-10-21 17:05 | -13 | 2015-10-20 10:38 | Architectural - Brickworks/Blockworks | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Previous Construction - Problems based on previous construction errors | Completed |  | The most Eastern core hole in Switch Room Low Voltage 2 (1/667) which is for the earth cable as per Cxxx-RFI-000849 is partially covered by the blockwork wall. This core hole is 150mm diameter and the blockwork covers 20mm of the Eastern side of the hole, this hole is only required to be 100mm diameter for the earth cable. As there will be no reduction on the required 100mm diameter __ propose to Use As-Is.
| 03SR - Stations (RfL) | Cxxx-NCR-000290 | NCR | ROP - Retaining Wall Pour 1 - Finish to top of wall |  | Contr | SKC | PNY - Paddington New Yard (West) |  | 2015-12-15 | 2015-12-04 13:12 | -11 | 2015-10-20 18:38 | Structural Engineering - Concrete Member | 5000 |  | Incorrect Installation | Repair | 3 (3-6k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | On striking the formwork on retaining wall pour 1 (west), the finish on the top of the wall was found to be unsatisfactory.
| 03SR - Stations (RfL) | Cxxx-NCR-000291 | NCR | ROP - Retaining Wall Pour 2 - South side finish |  | Contr | SKC | PNY - Paddington New Yard (West) |  | 2015-11-03 | 2015-11-05 15:33 | 2 | 2015-10-20 18:52 | Structural Engineering - Concrete Member | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Personnel Error - Verbal communication problem | Completed |  | A step has occurred in the surface of the retaining wall pour 2 on the south side, of around 13mm between adjacent shutters.
| 03SR - Stations (RfL) | Cxxx-NCR-000292 | NCR | ROP - Retaining wall pour 3 concrete beyond 2 hours |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2015-11-04 | 2015-11-05 16:20 | 1 | 2015-10-21 10:23 | Structural Engineering - Concrete Member | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Subcontractor Problems - Other | Completed |  | Concrete delivery for Access Road retaining Wall Pour 3 exceeded the 2hr time limit as per Appendix 17/1.
| 03SR - Stations (RfL) | Cxxx-NCR-000293 | NCR | Bus Deck - BDU - Out of Position __s |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2015-11-05 | 2015-10-22 15:40 | -14 | 2015-10-22 08:01 | Structural Engineering - Bolted Connections | 3000 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Not Defined | Completed |  | BDU __s out of Position
| 03SR - Stations (RfL) | Cxxx-NCR-000294 | NCR | __ - Pavement Slab - Survey - Slab Levels out of Tolerance |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2015-11-05 | 2015-10-27 09:58 | -9 | 2015-10-22 16:15 | Civil - Civil Engineering General | 1500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | Ground Slab survey (Attached) shows levels in some slabs to be out of the specified tolerance (for concrete structures).
| 03SR - Stations (RfL) | Cxxx-NCR-000295 | NCR | ROP - Platform Lighting & CMS Clash |  | Crossrail | XRL | PNY - Paddington New Yard (West) |  | 2015-11-19 | 2015-11-19 16:39 | 0 | 2015-10-22 18:28 | Electrical - Lighting | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Not Defined | Completed |  | There is a clash with a lighting location and the installed Cxxx CMS trunking on the platform. This was raised at the Cxxx – Quality Focus meeting 19-10-2015 raising concerns that this has been ongoing for some time and to date no resolution has been proposed.
| 03SR - Stations (RfL) | Cxxx-NCR-000296 | NCR | Clash of Cleats bolts with the Reinforcements cage of the Aggregate bin |  | Crossrail | PDP | PNY - Paddington New Yard (West) |  | 2015-11-10 | 2015-11-03 11:57 | -7 | 2015-10-27 09:43 | Civil - Civil Engineering General | 3000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Subcontractor Problems - Interfacing problems | Completed |  | When drilling the Aggregate Bin concrete structure to fix supporting cleats for steel work rebar was struck at multiple locations around the structure. As part of the design package drawings were provided so that Cxxx contractors could displace steel so that all bolts could be drilled for and installed without issue. A design review took place after Cxxx identified the number of locations where issues had arisen so that the permissible cleat bolt loadings were not compromised. __e and Associates also reviewed the findings and advised which locations diamond drilling of the rebar must not happen, Cxxx used this information to drill the holes as required
| 03SR - Stations (RfL) | Cxxx-NCR-000297 | NCR | Bus Deck - 3.6 Deck pour - No slump taken on the final wagon |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2015-11-16 | 2015-11-12 14:27 | -4 | 2015-10-27 14:09 | Structural Engineering - Testing | 500 |  | Testing and Commissioning | Use As-Is | 4 (0.5-3k) | Complete | Subcontractor Problems - Insufficient work planning by the subcontractors | Completed |  | Last concrete load (25) was not slumped because the truck was delayed and the technician had to go to AD4 to test and make cubes for concrete delivered there.
| 03SR - Stations (RfL) | Cxxx-NCR-000298 | NCR | Bus Deck - MCR for Chryso Cure HPE not code 1 prior to using the material |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2015-11-10 | 2015-11-11 16:47 | 1 | 2015-10-27 14:15 | Structural Engineering - Structural Engineering - General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Misunderstand the definition of the requirement | Completed |  | The Material compliance record for Chryso Cure HPE: Cxxx-COS-Z-LRC-CR076_SD006-50022 Rev 1.0 was not code 1 prior to using the material.
| 03SR - Stations (RfL) | Cxxx-NCR-000299 | NCR | ROP – Headhouse __ cill detail on the west elevation |  | Contr | HTM | PNY - Paddington New Yard (West) |  | 2016-01-15 | 2015-12-16 15:41 | -30 | 2015-10-27 15:41 | Architectural - General | 5000 |  | Design | Repair | 3 (3-6k) | Complete | Subcontractor Problems - Interfacing problems | Completed |  | The bottom cladding rail and __ panels have been installed/procured to suit the attached F2 detail drawing Cxxx-COS-A-DDD-CR076_PT001_F2-40515-0015 on the western elevation to the Headhouse. This detail shows the levels in this area incorrectly, as it does not account for the 75mm screed on the back deck of the building. Please refer to the attached sketch. It is proposed to trim the __ panels (in factory) and modify the bottom cladding rail to suit. Moving the bottom cladding rail up will include onsite drilling and fixing to the steel columns, and onsite cutting to the existing cleats. Please confirm this is acceptable.
| 03SR - Stations (RfL) | Cxxx-NCR-000300 | NCR | ROP drainage - manhole C215 |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2015-11-30 | 2015-11-19 16:18 | -11 | 2015-10-27 17:07 | Civil - Drainage | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | Due to requirements of the coring contractors to core into the Ranelagh Sewer at a 90˚, the alignment of the 600mmØ Ductile Iron pipe entering the Ranelagh sewer was altered. The pipe projecting from the ranelagh did not point directly towards the design location of C215. Two 11.25˚ bends were used so the pipe run could tie into Catch-Pit C215. Because of the additional length of pipe used and the requirement of maintaining a stub and a rocker out of the Catch-Pit, the position of C215 has moved 1.3m west along the alignment of Pipe Run C215. The 11.25˚ bends also resulted in the ‘design’ invert level of the 600mmØ Ductile Iron Pipe not being achieved at the outlet of C215, therefore to maintain the Type 7 Catch-Pit design of a minimum 300mm sump, C215 was lowered by 208mm. This 208mm drop in the outlet invert should have no affect on the flow from C215 into the Ranelagh Sewer as a fall of 1:6 has been achieved from C215 outlet to the Ranelagh sewer connection point. Note that a 300mm sump has been maintained in the manhole. C215 As-Built Centre Coordinates: E: 76277.694m N: 36440.928m C215 downstream IL: E: 76278.343m N: 36440.679m El: 119.094m C215 upstream IL: E: 76277.170m N: 36441.019m El: 119.421m
| 03SR - Stations (RfL) | Cxxx-NCR-000301 | NCR | 2015 Quality Management Audit |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2016-01-08 | 2015-12-09 11:15 | -30 | 2015-12-08 10:46 | Structural Engineering - Structural Engineering - General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate resources | Completed |  | __ main Contract Programme was verified at the audit. It was noted during the review that this document has not being reviewed or revised since July 2015. TC Labour Forecast Histogram template was confirmed within appendix 3.22 of the QP. It was also noted at the audit that this document have not being updated to include Labour that are currently use on the project. This document should have been revise inline TC Contract Programme. TC are required to revise and resubmit both documents on eB.
| 03SR - Stations (RfL) | Cxxx-NCR-000302 | NCR | 2015 Quality Management Audit |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2016-01-08 | 2015-12-08 12:50 | -31 | 2015-12-08 10:51 | Systems - Systems Engineering General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Subcontractor Problems - Insufficient surveillance of subcontractors | Completed |  | __ has maintained a very detailed generic List of Toolbox Talk within files A & B for Health & Safety. However, it was noted during the review of the List that Quality and ITP Toolbox Talks were not included within this List. This issue was previously identified as an observation during the last TC audit by __ in October 2014. It was noted at the audit that Toolbox talks for ITP and TC Quality Plan have been given to the site team. The TB record for QP dated 20/04/15 was presented at the audit. However, the TB record for the ITP is not maintained. It was agreed at the audit that Lists of QA Toolbox talk is to be generated and Toolbox talk are to be provided on key MEP activities and processes to site team. QA Toolbox Talk list is not maintained. Therefore it unclear what QA Toolbox has been provided to the site team by TC.
| 03SR - Stations (RfL) | Cxxx-NCR-000303 | NCR | 2015 Quality Management Audit |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2016-01-08 | 2015-12-08 13:15 | -31 | 2015-12-08 10:54 | Structural Engineering - Structural Engineering - General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Subcontractor Problems - Insufficient surveillance of subcontractors | Completed |  | The Quality audit process is identified within the section 2.12 of the QP. The project specific QA Audit Schedule was also confirmed within the QP. However, it was noted at the review that __ has only undertaken one audit since the beginning of the job. The remaining four Audits have not been undertaken as per the QA Programme within the QP. It was agreed at the audit that the Audit schedule is to be updated to include relevant audits based on the current site activities.
| 03SR - Stations (RfL) | Cxxx-NCR-000304 | NCR | 2015 Quality Management Audit |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2016-01-02 | 2015-12-08 13:30 | -25 | 2015-12-08 10:56 | Structural Engineering - Structural Engineering - General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Subcontractor Problems - Insufficient surveillance of subcontractors | Completed |  | The Non-conformance Report Template was confirmed within the Appendix 3.19. However, it was noted that Non-conformance Register was not found within the QP at the time of the audit. It was also noted that __ has raised 2 NCR’s under (NCR-000198) ROP external lighting and (NCR-000135) Bus Deck Lighting protection. These NCR’s are not added into the NCR Register to enable __ to track and close actions. In addition, there was no evidence found at the time of the audit how Quality processes/ procedures CAR, NCR and Observation are managed and tracked on the project. TC are not following the procedure / process stated within their QP
| 03SR - Stations (RfL) | Cxxx-NCR-000305 | NCR | ROP - Headhouse Earth Cable Damage |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2016-09-16 | 2016-07-27 14:56 | -51 | 2015-11-03 16:02 | Electrical - General | 1000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | As identified in the attached photos, 2 of the earth cables in the ROP Head house have damaged sheaths.
| 03SR - Stations (RfL) | Cxxx-NCR-000306 | NCR | ROP - Electrical Cabinet Painting Without Approved MCR |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2015-11-19 | 2015-11-11 13:50 | -8 | 2015-11-05 14:17 | Architectural - Finishes | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | Painting of the electrical cabinet commenced without MCR for water based matt emulsion paint not being
| 03SR - Stations (RfL) | Cxxx-NCR-000307 | NCR | ROP - Platform Lghting |  | Crossrail | XRL | PNY - Paddington New Yard (West) |  | 2015-11-27 | 2015-11-17 08:57 | -10 | 2015-11-06 16:55 | Electrical - Lighting | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | The Eastbound Platform Lighting layout does not reflect the mirror layout of the Westbound platform as per the Gated F1 drawings. Cxxx-COS-E-DDA-CR076_PT001_2-32021 -P03 Cxxx-COS-E-DDA-CR076_PT001_2-32022 -P01.
| 03SR - Stations (RfL) | Cxxx-NCR-000308 | NCR | ROP - HV Riser ITP not Code 1 |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2015-11-27 | 2015-11-24 12:25 | -3 | 2015-11-09 20:25 | Electrical - General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | The ITP for the installation of the ROP HV riser __ was not code 1 prior to commencing works on-site.
| 03SR - Stations (RfL) | Cxxx-NCR-000309 | NCR | ROP - HV Riser __ RAMS not Code 1/4 |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2015-11-27 | 2015-11-16 12:36 | -11 | 2015-11-09 20:56 | Electrical - General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | The RAMS for the installation of the ROP HV riser __ was not code 1/ 4 prior to commencing works on-site.
| 03SR - Stations (RfL) | Cxxx-NCR-000310 | NCR | ROP - HV Riser __ MCR not Code 1 |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2015-12-23 | 2015-12-04 14:11 | -19 | 2015-11-09 20:59 | Electrical - General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | The MCR for the installation of the ROP HV riser __ was not code 1/2 prior to commencing works on-site.
| 03SR - Stations (RfL) | Cxxx-NCR-000313 | NCR | ROP - Clear openings on EXD01 & EXD02 |  | Contr | HTM | PNY - Paddington New Yard (West) |  | 2015-12-15 | 2015-12-15 16:06 | 0 | 2015-11-17 17:57 | Architectural - Doors | 2500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | It has been identified that the clear openings of the door posts are 20mm less than design for both EXD01 & EXD02. EXD01 has a minimum clear opening of 2210mm. EXD02 has a minimum clear opening of 2120mm. It has also been identified that the steel door posts are not perfectly plumb and the clear opening varies by approximately 25mm between the top and the bottom of the doors.
| 03SR - Stations (RfL) | Cxxx-NCR-000314 | NCR | ROP - MEP - Fire Main Landing Valves and Butterfly Valves |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2015-12-18 | 2015-12-10 14:26 | -8 | 2015-11-25 12:25 | Mechanical - Mechanical Engineering General | 5000 |  | Incorrect Installation | Rework | 3 (3-6k) | Complete | Management Problem - Inadequate supervision | Completed |  | The butterfly valves installed in the ROP fire main were the wrong type.
| 03SR - Stations (RfL) | Cxxx-NCR-000315 | NCR | ROP - Code 1 lintels installed without CE Marking |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2016-01-31 | 2016-01-30 08:12 | -1 | 2015-11-23 17:57 | Structural Engineering - Concrete Member | 5000 |  | Material | Use As-Is | 3 (3-6k) | Complete | Material/Preservation Problems - Lack or improper material identification and traceability | Completed |  | Naylor Concrete lintels that were recommended in Cxxx-RFI-000580 response from C150 and approved in MCR Cxxx-COS-C-LRC-CR076_PT001-50007 have been installed into the Royal Oak Portal Headhouse above doors and builders work holes. This issue is applicable to all lintels installed up until the 20/11/15 the remainder of the lintels Upon further review it has been found that the concrete lintels are not CE compliant as testing has not been completed on the product.
| 03SR - Stations (RfL) | Cxxx-NCR-000317 | NCR | ROP - Headhouse Blockwork Damage to Facework |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2015-12-11 | 2015-12-03 12:02 | -8 | 2015-11-27 16:34 | Architectural - Brickworks/Blockworks | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Subcontractor Problems - Insufficient work planning by the subcontractors | Completed |  | As shown in attached photo the corner of one brick in the doorway of the UPS \ Battery Room was damaged during the incident on site.
| 03SR - Stations (RfL) | Cxxx-NCR-000318 | NCR | Bus deck column reinforcement |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2015-12-18 | 2015-12-14 12:49 | -4 | 2015-12-03 19:48 | Civil - Civil Engineering General | 1500 |  | Planning | Repair | 4 (0.5-3k) | Complete | Subcontractor Problems - Other | Completed |  | The top steel reinforcement (bob bars) of Columns A4a, A4 and A5 were partially removed so that the concrete could be poured into these columns. See attached photos Photo 1100092: shows how a normal column looks inside the shutter Photo 1100126: shows the reinforcement inside the shutter Photo 1100795 and 1100801: shows what columns A4a, A4 and A5 look like inside the shutter
| 03SR - Stations (RfL) | Cxxx-NCR-000319 | NCR | Rib beam soffit finish - deck slab 3.4b |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2016-05-20 | 2016-05-09 07:57 | -11 | 2015-12-03 20:11 | Civil - Civil Engineering General | 5000 |  | Workmanship | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Other | Completed |  | Poor concrete finish to rib beam soffit in deck slab 3.4b, east and west of gridline R. During pour of slab 3.4b, the last two rows of void formers moved in the direction of the pour. __ Formwork installed a secondary shutter stop end immediately on the third last void former row and completed the pour. The last two void former rows and all rebar past the secondary stop end was removed the following day leaving sufficient lap lengths on all reinforcement starters. After the false work was struck to the soffit of the 3.4b decking, __ Formworks performed a cover meter survey and visual inspection on the rib beams.
| 03SR - Stations (RfL) | Cxxx-NCR-000320 | NCR | Cxxx CONTRACT QUALITY PLAN - QA AUDIT |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2016-01-30 | 2016-01-29 06:43 | -1 | 2015-12-14 14:55 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Other management problem | Completed |  | __ has produced and maintained an Organisational Chart for the Project. Rev 4.0, Cxxx-COS-Z2-HRR-CR076_SD006-50027 Organisational Chart updated to include team photographs, new starters and the key supply chains within the project were confirmed on eB. The Organisation Chart will required continuous monitoring and updating going forward to reflect various phases of the project. Revision 2.0, Cxxx-COS-O4-STP-CR076_SD006-50006 Competency Management Plan has been produced and implemented on the project. However, it was evident at the audit that this document was last reviewed on the 15/09/2014 and it has not been reviewed or revised since.
| 03SR - Stations (RfL) | Cxxx-NCR-000321 | NCR | __ Cxxx Contract Quality Plan- QA audit |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2016-01-30 | 2016-01-29 06:46 | -1 | 2015-12-14 15:01 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | The RACI Competency Matrix identifying personnel competencies are also maintained. The signed roles and responsibility of all the applicable members of the project team are also maintained. However, it was noted at the audit that both of these documents are to be updated and managed effectively in line within the Organisational Chart.
| 03SR - Stations (RfL) | Cxxx-NCR-000325 | NCR | __ - MCR not submitted for the use of Naylor Lintels |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2016-02-12 | 2016-02-01 16:39 | -11 | 2015-12-15 13:39 | Architectural - Masonary | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Lack or improper material identification and traceability | Completed |  | There was no MCR submitted to CRL for the two 1100mm x 215mm x 215mm Naylor lintels installed across the cable trench in the __ (Highlighted in Yellow). It was assumed that as the lintels were specified on the attached Cxxx drawing reference: Cxxx-CSY-S-DDL-CR076_MS005-01805 Rev C03 that an MCR was not required as it was not considered to be a change to the employer’s requirements. Note: The structure in which this NCR applies, has now been handed over.
| 03SR - Stations (RfL) | Cxxx-NCR-000326 | NCR | __ - MCR not submitted for the Naylor Lintels used on __ Switchroom |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2016-03-18 | 2016-03-17 12:11 | -1 | 2015-12-15 13:49 | Architectural - Masonary | 0 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Lack or improper material identification and traceability | Completed |  | There was no MCR submitted to CRL for the one 1100mm x 215mm x 145mm Naylor lintels installed above the personnel access door of the __ switchroom (Highlighted yellow). It was assumed that as the lintel was specified on the attached TARMAC drawing reference: Cxxx-TAR-C-DWG-CR076-50028 Rev 5.0 that an MCR was not required as it was not considered to be a change to the employer’s requirements. Note: The structure in which this NCR applies, has now been handed over.
| 03SR - Stations (RfL) | Cxxx-NCR-000327 | NCR | ROP - Platform IP4X Trunking |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2016-03-25 | 2016-03-21 17:24 | -4 | 2015-12-15 16:26 | Electrical - Cable Management | 3000 |  | Material | Repair | 4 (0.5-3k) | Complete | Personnel Error - Inattention to detail | Completed |  | Following the Crossrail review with the CEG (MG) 14-12-2015 it was observed that the electrical trunking installation on the platform level does not comply with the Cxxx-COS-E-RSP-CR076_PT001-50001 Rev 3.0 electrical specification and the Material & Workmanship specification CRL1-XRL-M_RSP_CR001-500079 clause JY60.1306 sub clause E and S requiring IP4X trunking.
| 03SR - Stations (RfL) | Cxxx-NCR-000328 | NCR | ROP - Platform Use of Cable Ties on Vertical CMS |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2016-03-30 | 2016-03-29 11:59 | -1 | 2015-12-15 17:34 | Electrical - General | 2000 |  | Material | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Following the Crossrail review with the CEG (MG) 14-12-2015 it was observed that the cable installed using stainless cable ties on the vertical cable riser / tray in the platform level does not comply with the Cxxx-COS-E-RSP-CR076_PT001-50001 Rev 3.0 electrical specification and the Material & Workmanship specification CRL1-XRL-M_RSP_CR001-500078 clause JY61.3203 sub clause L which requires cable cleats.
| 03SR - Stations (RfL) | Cxxx-NCR-000329 | NCR | Corrosion Risk Assessment |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2016-02-12 | 2016-01-21 14:07 | -22 | 2015-12-15 17:31 | Electrical - Cable Management | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Concerns have been raised by Crossrail regarding the Corrosion Risk Assessment at code 3 and the current corrosion category of the installed Royal Oak Portal MEP works namely: CMS in the emergency walkway not category 5 CMS and fire main brackets in the Platform sump Pits not category 5
| 03SR - Stations (RfL) | Cxxx-NCR-000330 | NCR | Cables passing through structure without Sleeve |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2016-03-25 | 2016-04-13 17:07 | 19 | 2015-12-17 16:57 | Electrical - General | 1500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Cables routed through the structure without passing through a sleeve prior to making good. JY61.3101 clause m) JY61.3202 clause J) refers.
| 03SR - Stations (RfL) | Cxxx-NCR-000331 | NCR | Cables bunched on Vertical Runs of Tray |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2016-04-25 | 2016-03-31 16:23 | -25 | 2015-12-18 09:46 | Electrical - Power Distribution | 5000 |  | Workmanship | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Worker not correctly instructed | Completed |  | Cables bunched on vertical runs of tray.
| 03SR - Stations (RfL) | Cxxx-NCR-000332 | NCR | Bus Deck - Concrete Splashes on GL1 fin panels |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2016-03-31 | 2016-01-22 08:46 | -69 | 2016-01-08 17:15 | Structural Engineering - Concrete Member | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | During the Southern Parapet stitch pour along the GL1 parapets concrete has splashed through the gaps and expansion joints between the Type 3 Parapets.
| 03SR - Stations (RfL) | Cxxx-NCR-000333 | NCR | ROP - Incorrect drainage materials installed by previous contractor |  | Contr | SKC | PNY - Paddington New Yard (West) |  | 2016-02-26 | 2016-01-30 08:22 | -27 | 2016-01-12 17:52 | Civil - Drainage | 5000 |  | Incorrect Installation | Use As-Is | 3 (3-6k) | Complete | Material/Preservation Problems - Use of unapproved materials | Completed |  | Drawing C150-CSY-D-DDL-CR076_PT001-00503 shows drainage ducts installed by previous contractor C330 within the capping beam around the head house. Plastic pipe has been cast into the capping beam and left protruding at the top of the slab. The specification that Cxxx are working to calls for the use of cast iron pipe.
| 03SR - Stations (RfL) | Cxxx-NCR-000334 | NCR | Bus Deck - AD2 - Bus Wash Steel Frame - Holding Down Bolt Mis-Allignment |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2016-01-29 | 2016-01-19 13:47 | -10 | 2016-01-12 18:32 | Civil - Civil Engineering General | 15000 |  | Manufacturing Defect | Rework | 2 (6-60k) | Complete | Subcontractor Problems - Insufficient work planning by the subcontractors | Completed |  | During the installation of the steel frames for the Bus Wash, it was noted by __ that some of the Holding Down Bolts used for the steel beams mis-aligned during the process. Upon further inspection and liaising with the sub-contractor in charge, it could be identified that due to a slight error in the fabrication process, the 4No. beams were not fabricated as per IFC and Fabrication Drawings. This observation has been fed back to Karcher Uk Ltd, who are currently liaising with their designers to identify a rectifying method. __ are expecting a proposal by COB Wednesday 13/01/2016. The rectifying works are expected to be carried out and completed by COB Friday 22/01/2016.
| 03SR - Stations (RfL) | Cxxx-NCR-000336 | NCR | Bus Deck - Cut off levels to the high level piles above working level |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2016-02-02 | 2016-01-20 15:21 | -13 | 2016-01-19 14:27 | Structural Engineering - Concrete Member | 500 |  | Planning | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | Due to the restriction of the existing retaining wall and risk of collapse the working platform as required by the piling rigs have been installed to its maximum height to both west and eastern sides of the existing retaining wall. This was done due to the lack of the design information from the client and not to impose any risk of collapse to the existing retaining wall. It must be noted that there is no new retaining wall at these locations and that the design is based on the existing retaining wall levels. Segmental casings were used for installation for up to 4 meters in depth and this required a minimum pile breakdown of 500mm to form a construction joint and to prove integrity before being extend to design level. The contractors is unable to allow for protrusion of reinforcement starters above the pile mat at the piling stage due to access and working restrictions. Therefore pile extensions will be required to tie into the structural slab/ pile cap at high level as per design.
| 03SR - Stations (RfL) | Cxxx-NCR-000337 | NCR | Bus Deck - Concrete placed with no __ technician being present |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2016-02-26 | 2016-01-30 08:27 | -27 | 2016-01-26 15:05 | Structural Engineering - Concrete Member | 1500 |  | Planning | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | Concrete placed with no __ technician being present
| 03SR - Stations (RfL) | Cxxx-NCR-000338 | NCR | Commence MEP works to Non Construction issue drawings |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2016-08-15 | 2016-08-02 13:11 | -13 | 2016-01-25 13:45 | Electrical - General | 0 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Use of unapproved drawings | Completed |  | At time of commencement of the MEP works at Royal Oak Portal Headhouse the Register & Issue Record (RIR) Cxxx-COS-Z-LRG-CR076_PT001-50002 is at Revision 11.0. Within the RIR Rev11 there are a number of drawings which remain at Provisional status and have yet to receive Construction issue status. These drawings are currently being approved by Crossrail as part of PMI-00197.
| 03SR - Stations (RfL) | Cxxx-NCR-000339 | NCR | Incorrect installation of Fire Main pipe brackets clips |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2016-03-30 | 2016-03-21 18:17 | -9 | 2016-01-26 14:24 | Mechanical - Piping | 5000 |  | Incorrect Installation | Rework | 3 (3-6k) | Complete | Discipline/Workmanship - Other | Completed |  | The Fire Main installation within the platform area has used the incorrect method of pipe brackets clips which do not comply with the detail stated on drawing Cxxx-COS-M-DDD-CD076_PT001_Z-00804 C01 with the pipe clip has being install on a insulation block and metal cladding not direct to the pipe as detailed on the drawing and condition survey.
| 03SR - Stations (RfL) | Cxxx-NCR-000340 | NCR | S18A - Wall Pour 1 - Discharge completion time exceeds 2h after been batched |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2016-02-26 | 2016-02-17 11:30 | -9 | 2016-02-04 15:56 | Civil - Drainage | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Insufficient information made available to the worker. | Completed |  | Concrete arrived on site 1h15min after been batched. Wagon turned up to Gate 1 instead of Gate 4a and wasn't sent to the right location until 30min later. Discharge began within 2h of batching, however, the time taken to complete discharge exceeded the 2 hour mark. Discharge completed at 18h24min as noted on the attached ticket.
| 03SR - Stations (RfL) | Cxxx-NCR-000341 | NCR | Bus Deck - AD1 - Lighting Column Installation - HDB |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2016-02-26 | 2016-02-25 16:48 | -1 | 2016-02-02 17:09 | Civil - Civil Engineering General | 2500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Not Defined | Completed |  | See attached __ design for the lighting and CCTV column holding down bolts. Bolt lengths as installed and as per design are 600mm long with bolts positioned on the stitch invert level as shown. The stitch depth is typical 300mm plus 25mm for mortar bedding under kerbs and 255mm for HB2 kerb height = 580mm to top of footpath (1:40 fall not included so looking at 590mm). The design is therefore not sufficient as the anchor bolts will only have 10 – 20 mm protrusion above finish footpath level which will not accommodate for 25mm base plate grouting plus 10mm base plate thickness and top nut 25mm with thread protruding.
| 03SR - Stations (RfL) | Cxxx-NCR-000342 | NCR | Bus Deck - Cut Rebar on the Western Parapets |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2016-03-27 | 2016-03-14 10:52 | -13 | 2016-02-04 15:19 | Structural Engineering - Concrete Member | 2500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During the installation of PW17A it was identified that the internal and external angles for deck pour 2.1 changed at two separate locations. With the internal angle changing direction before the external angle. As a result 10no parapet starter bars had to be cut so that the parapet could be installed (Please refer to the attached picture)
| 03SR - Stations (RfL) | Cxxx-NCR-000343 | NCR | ROP Headhouse Lightning Protection installation commenced without F2 drawings |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2016-12-30 | 2016-10-20 12:28 | -71 | 2016-02-04 17:23 | Electrical - General | 0 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Use of unapproved drawings | Completed |  | The Lightning Protection installation works have proceeded on site without the F2 design drawings listed below been issued on eB (at placeholder only) and therefore non-compliant with 1.2 Hold Point of ITP - Cxxx-COS-E-ITP-CR076_PT001-50007. Cxxx-COS-E-DWG-CR076_PT001-50016 Head House Earthing & Lighting Protection Layout Cxxx-COS-E-DWG-CR076_PT001-50037 Head House Lightning Protection Plan Roof level Cxxx-COS-E-DWG-CR076_PT001-50008 Head House Below Slab Earthing and Lightning Protection Layout Only limited works have been carried out as there would have been no access after the cladding was installed and too mitigate delays to the program.
| 03SR - Stations (RfL) | Cxxx-NCR-000344 | NCR | Bus Deck - Bus Wash Plinth - Concrete placed with no __ technician being present |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2016-03-29 | 2016-02-17 14:22 | -41 | 2016-02-15 11:28 | Structural Engineering - Concrete Member | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | On the 17th of September there was no concrete technician present due to the technician falling ill on his way to site. We phoned __ as soon as we were aware of the problem to try and arrange a replacement technician (__ were unable to confirm another technician at the time but would try and source a technician from elsewhere). Prior to __ being able to confirm the non-attendance of a technician the concrete for the bus wash plinth had already been confirmed. __ site engineers took the initiative to make a set of concrete cubes for this pour (Please find attached the 28day results - 65.1 and 61.9 N/mm2)), but were unable to carry out slump tests as there was no slumping equipment onsite.
| 03SR - Stations (RfL) | Cxxx-NCR-000345 | NCR | ROP Headhouse - Roof Water Ingress |  | Contr | HTM | PNY - Paddington New Yard (West) |  | 2016-06-06 | 2016-05-25 15:05 | -12 | 2016-02-19 09:55 | Architectural - Roofing & Exterior Treatment | 5000 |  | Workmanship | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Other | Completed |  | Water ingress has been observed on the entire south side of the ROP Headhouse building. It is penetrating the __ fil roof membrane, ponding in the ceiling void and dripping through the durasteel ceiling.
| 03SR - Stations (RfL) | Cxxx-NCR-000346 | NCR | Bus Deck - AD2 - Re-Positioning of LV Ducts at Entry into the Re-Fuellling Compound |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2016-04-01 | 2016-03-31 17:11 | -1 | 2016-02-19 18:14 | Civil - Civil Engineering General | 3000 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Change to drawings not provided on time | Completed |  | 3No. LV Ducts were cast in and installed within the Re-Fuelling Slab below deck based on design drawings, Cxxx-COS-E-DDD-CR076_MS005_Z-10003 C01 and Cxxx-COS-M-DDA-CR076_MS005_B-03101 C01. During the installation process it became apparent that there were a few changes in the duct positioning and location (as advised by M&E Sub-Contractor, __). Two FCDs were raised to capture the change in duct entry and the re-location of the LV Drawpit, north of the Re-Fuelling Compound. Despite the fact that these changes were captured and incorporated within the installation, it has been noted by __ that the current location of the duct within the slab will not be sufficient for the installation of the LV Distribution Panel on top of the ducts. As per design drawing Cxxx-COS-E-DWG-CR076_MS005-50011 C03, the duct entry within the Panel is shown in the middle of the panel rather than on the northern edge (as referred to in drawing Cxxx-COS-E-DDD-CR076_MS005_Z-10003 C01). The __ generated drawing Cxxx-COS-E-DWG-CR076_MS005-50011 C03 and the drawings used by the site teams Cxxx-COS-E-DDD-CR076_MS005_Z-10003 C01 and Cxxx-COS-M-DDA-CR076_MS005_B-03101 C01 do not show the same detail for the duct positioning. __ would like to stress that despite the fact that drawing Cxxx-COS-E-DDD-CR076_MS005_Z-10003 C01 was re-issued for construction after the final issue of drawing Cxxx-COS-E-DWG-CR076_MS005-50011 C03, the drawings do not cross-reference each-other. The ducts were installed in line with the Code 1 approved IFC design.
| 03SR - Stations (RfL) | Cxxx-NCR-000347 | NCR | Bus Deck - AD3 - Damages Ductile Iron Pipe |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2016-04-21 | 2016-03-21 09:09 | -31 | 2016-02-25 09:18 | Mechanical - Piping | 3000 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Supervision - Insufficient supervision | Completed |  | During the installation of the Ductile Iron Pipes for the Bus Deck, __ have come across a damaged pipe item which had to be replaced. While installing the Drainage Run 210.001 in preparation for the final Bus Deck Pour 3.1, it was noticed that the drainage run between DP2 - DG7, 210.002, was not passing the air test of 100mB. An estimated 15 metres of pipe were previously installed as part of 2010.002, during the construction of the North Abutment Wall and were backfilled with shingle. To continue the installation of 210.001 and to re-connect to pipe run 210.002, the backfill had to be excavated to expose the pipe termination point. __ believe that the pipe must have gotten damaged during this excavation process. The damaged pipe run was removed from the drainage line, was replaced with a new pipe length and the installation was continued. Prior to completion, pipe run 210.002 was successfully air tested. Upon completion the entire run from 210.000 - 210.001 - 210.002 was successfully air tested.
| 03SR - Stations (RfL) | Cxxx-NCR-000348 | NCR | Bus Deck - AD2 - Bus Wash - Damage to Framework Baseplates |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2016-05-31 | 2016-06-30 08:46 | 30 | 2016-02-25 09:04 | Civil - Structural Engineering | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | During the Construction of the Steel Framework as part of the Bus Wash Facility, it was noted by __ that the bottom base plates of the a number of steel beams had become damaged during the installation process. Due to structural damage on the plates, the galvanizing cover has been damaged. This was noted by __ and reported to Karcher who have confirmed that the Baseplates will be re-sprayed, with a galvanizing primer to ensure that the damaged areas of the base plate are covered with a galvanised layer.
| 03SR - Stations (RfL) | Cxxx-NCR-000349 | NCR | Bus Deck - Over bent steel from the North Abutment Retaining Wall reducing cover to 3.1,3.2 and 3.3 slabs |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2016-04-14 | 2016-04-06 09:24 | -8 | 2016-02-29 14:28 | Structural Engineering - Concrete Member | 3000 |  | Manufacturing Defect | Repair | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | During the installation of the top mat steel for the ground slabs in AD3 (3.1,3.2 and 3.3) it was noticed that the steel for the tie in with the North Abutment Retaining Wall was incorrectly bent (The reinforcement was slightly over bent). As a result there was excessive cover during the fixing of the top mat reinforcement. Additional reinforcement was installed to the same size or greater than the designed top mat. Please find attached pictures showing the additional reinforcement
| 03SR - Stations (RfL) | Cxxx-NCR-000350 | NCR | Bus Deck - AD3 - Rebar Clash between insitu beam and precast parapet |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2016-03-14 | 2016-03-14 10:59 | 0 | 2016-02-29 13:01 | Structural Engineering - Pre-cast | 2500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | During the installation of the Pre-cast parapets in AD3 numerous starter links have clashed with the slab links. Templates have been used by both __'s and __ but due to the bottom mat steel spacing's and the requirement to space with 150mm spacing's rebar clashes have therefore become unavoidable.
| 03SR - Stations (RfL) | Cxxx-NCR-000351 | NCR | ROP Headhouse - __ Ceiling Plan - Code 3 drawing |  | Contr | HTM | PNY - Paddington New Yard (West) |  | 2016-04-20 | 2016-04-12 12:06 | -8 | 2016-02-24 08:46 | Architectural - Ceilings & Soffits | 0 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Use of unapproved drawings | Completed |  | Works have proceeded on the __ ceiling without a Code 1 or 2 drawing. The comments on the drawing include the partition in the suspended slab room which has not yet been completed onsite. Other comments included issues with blockwork fixings and these were resolved in Cxxx-FCD-000367 & with additional comments from __.
| 03SR - Stations (RfL) | Cxxx-NCR-000352 | NCR | Bus Deck - Bus Wash - Washer Arm base plates |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2016-05-18 | 2016-04-25 12:35 | -23 | 2016-02-26 15:28 | Mechanical - Mechanical Engineering General | 0 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | It was noticed during a Cxxx / CRL Quality walk that there were small gaps under the washer arm base plates, possibly due to minor surface irregularities in the concrete finish and during the installation of the washer arm base plates concrete dust from the drilling process may also have settled underneath the base plates.
| 03SR - Stations (RfL) | Cxxx-NCR-000353 | NCR | Bus Deck - AD3 Piles - Piles P277 - P280 Integrity Testing Missed |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2016-04-11 | 2016-03-21 17:41 | -21 | 2016-02-29 16:55 | Geotechnical Engineering - Concrete - Bored Pile | 0 |  | Planning | Use As-Is | 4 (0.5-3k) | Complete | Personnel Error - Inattention to detail | Completed |  | Upon Collating the integrity records for AD3 Piles it was noticed that the Piles in Pile-Cap K/4a, No. P277,278,279 & 280 were not integrity tested prior to the pile cap being constructed
| 03SR - Stations (RfL) | Cxxx-NCR-000354 | NCR | Bus Deck - Bus Wash Screeding slabs |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2016-05-11 | 2016-04-12 16:54 | -29 | 2016-03-16 10:03 | Civil - Concrete Pavement | 3000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Supervision - Other | Completed |  | After pouring the bus wash screed surronding the bus wash plant room it was identified that there was insufficient fall from East to West and as a result ponding has occured on both the north and south sides of the bus wash plant room. (Please refer to the attached pictures).
| 03SR - Stations (RfL) | Cxxx-NCR-000356 | NCR | ROP - MCR not submitted for the use of sump pump drainage pipe coupling |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2016-06-06 | 2016-05-06 15:24 | -31 | 2016-04-01 16:34 | Mechanical - Piping | 0 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Use of unapproved materials | Completed |  | During the site visit it was noticed that the pipe fittings used on the sump pump drainage pipe between Head House and the valve chamber were not approved , as there was no MCR submitted to CRL for the Viking pipe coupling.
| 03SR - Stations (RfL) | Cxxx-NCR-000357 | NCR | Fire Compartmentation |  | Crossrail | XRL | PNY - Paddington New Yard (West) |  | 2016-07-22 | 2016-07-14 07:52 | -8 | 2016-04-08 11:06 | Architectural - Walls | 0 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | The wall construction between Fan room 1/791 and MCC room 1/777 and Circulation Area 1/074 does not meet the 60 minutes fire rated construction required as stated on section 8.1 of Fire Engineering Report Cxxx-COS_E1-STP_CR076_PT001-50002 Rev 4.0. A fire may spread through the gaps in the cladding and wall or through the cladding see attached photo taken between 1/791 and 1/777.
| 03SR - Stations (RfL) | Cxxx-NCR-000359 | NCR | Damper Panel |  | Crossrail | XRL | PNY - Paddington New Yard (West) |  | 2016-07-28 | 2016-07-28 14:47 | 0 | 2016-04-12 13:58 | Fire - Fire Systems & General | 0 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | Cxxx RIBA – F fire/smoke damper design is non - compliant. The Damper control panel has been removed from the RIBA E design, refer to drawing No C150-CSY-E-DDE-CR076_PT001-0081. The damper controls do not meet the performance requirements as detailed in the C150 RIBA – E specification C150-CSY-E-RSP-CR076_PT001-00004 Rev 6.0 and Cxxx-COS-E-RSP-PT001-50001- JW50.1304. Also the Fire Alarm system and MCC drawings Cxxx-COS-E-DDE-CR076_PT001_Z-33031 and Cxxx-COS-E-DDE-CR076_PT001_Z-31034 does not indicate any damper control interface units within the fire alarm loop
| 03SR - Stations (RfL) | Cxxx-NCR-000360 | NCR | Bus Deck - Bus Wash Screed Finish Delaminating |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2016-06-01 | 2016-05-13 07:53 | -19 | 2016-04-20 18:32 | Civil - Concrete Pavement | 1500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Upon a quality walk around on top of the Bus Deck it has been noticed that there is some concrete delamination on the Bus wash screed. It appears as though water has been used whilst finishing the concrete to make the concrete more workable for the concrete finishers and as a result the concrete has delaminated.
| 03SR - Stations (RfL) | Cxxx-NCR-000361 | NCR | Cable Tray – 25% spare capacity not provided |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2016-06-30 | 2016-05-23 08:47 | -38 | 2016-04-20 12:37 | Electrical - Cable Management | 4000 |  | Design | Repair | 3 (3-6k) | Complete | Design Problem - Inadequate or defective design | Completed |  | Following the Cxxx and CEG site visit of 07-04-2016 it was observed that the cable tray (supply A) at the platform area which supplies the sump pump cables is non-compliant to the Material & Workmanship specifications CRL1-XRL-M-RSP-CR001-50081 - JY63 clause .1302 - A (Cable tray shall be sized to provide 25% spare capacity.) See attached photo.
| 03SR - Stations (RfL) | Cxxx-NCR-000362 | NCR | Non-compliance of LV Switch Panels Flash Test to Bus Bar Sections |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2016-07-07 | 2016-04-25 10:35 | -73 | 2016-04-20 08:49 | Electrical - LV Equipment | 0 |  | Testing and Commissioning | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | The LV switch panels A & B Flash test on the bus bar sections recording 2 kV for 5 seconds was carried out during the AF Switch Gear Ltd FAT (Factory Acceptance Test ) on 15-02-2016 and again on site 18-03-2016 for LV panel A is non-compliant to the Material & Workmanship specifications JY71.2201 – part b ( 4kV for 1 minute )
| 03SR - Stations (RfL) | Cxxx-NCR-000363 | NCR | Non-compliance of installed Distribution Boards within Head House |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2016-07-29 | 2016-08-04 15:16 | 6 | 2016-05-03 13:29 | Electrical - LV Equipment | 4000 |  | Material | Repair | 3 (3-6k) | Complete | Design Problem - Other | Completed |  | Following CEG site visit on 14 -04-2016 it was observed that the installed Distribution Boards are non-compliant to the Material & Workmanship specifications JY71.1303 - A4 and 1304 - A2 (IP 31 rating)
| 03SR - Stations (RfL) | Cxxx-NCR-000364 | NCR | S19 - Base - Discharge completion time exceeds 2h after been batched |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2016-06-30 | 2016-05-31 15:24 | -30 | 2016-04-27 14:33 | Civil - Drainage | 0 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | External Phenomenon - Other | Completed |  | Discharge of concrete began within 2h of batching, however, the time taken to complete discharge exceeded the 2 hour mark due to plant issues. Discharge completed at 13h15min as noted on the attached ticket.
| 03SR - Stations (RfL) | Cxxx-NCR-000366 | NCR | Damaged cables and cable crimps within trunking at WPBD |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2016-10-28 | 2016-09-30 14:19 | -28 | 2016-06-17 14:05 | Electrical - Cable Management | 3000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Whilst installing the single cabling within the trunking system the cable insulation on 6 number cables was damaged exposing the conductors core, cable crimps were also found to be used for the connection of cabling on one number circuit. To note the inspection was carried out prior to being offered up for inspection by the contractor.
| 03SR - Stations (RfL) | Cxxx-NCR-000367 | NCR | Non-compliance of LV Switch Panels Labelling |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2016-10-12 | 2016-09-07 10:41 | -35 | 2016-06-22 16:13 | Electrical - LV Equipment | 3000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | LV Switch Panels A&B at ROP Head House installed by AF Switch Gear Ltd have incorrect labelling. All current labels on both panels have been fixed by white plastic rivets and have a text size of 3.14 mm. This is non-compliant to the Material & Workmanship specification "JY71.3201 Clause R and S LV Switchgear and Distribution Boards" which requires labels to be fixed by means of chrome finished mushroom headed bolt secured by spring washer and nut and text size no less then 6 mm. Also, 3 position sector switch has a wrong configuration and labelling and currently reads AUTO/LOCAL/REMOTE. This is non-complaint to to the Material & Workmanship specifications "JV20.1301 Clause I LV Distribution" which requires configuration and label to have following sequence LOCAL/REMOTE/AUTOMATIC. Please note that manufacturing drawings showing current labelling layout have been accepted by CRL Code 1, furthermore the FAT was attended by CRL by where these items could have been advised and remedial works carried out efficiently within factory conditions.
| 03SR - Stations (RfL) | Cxxx-NCR-000368 | NCR | Head House - External Fire Main Box |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2017-03-28 | 2017-02-02 13:15 | -54 | 2016-06-23 10:57 | Fire - Fire Systems & General | 2000 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | With the fire main manifold installed within the eastern wall of the Head House the door of it's cabinet fouls the cover caps to the connection points. The wall is constructed with an internal skin of blockwork and external skin of cladding. The back side of the manifold is currently installed a tight to the blockwork as possible so it cannot be moved back any further without additional breaking/ coring to this wall. To enable the door to be closed with the manifold in it's current position the cabinet would need to be moved forward 25mm proud of the external cladding. Drawing Cxxx-COS-M-DDD-CR076_PT001_Z-00804 –CO1 detailed a 310 mm diameter hole and from the photo below a 200mm hole was cut.
| 03SR - Stations (RfL) | Cxxx-NCR-000369 | NCR | LU10 Ducts - Maintaining 3.9m bend radius |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2016-09-30 | 2016-07-11 14:20 | -81 | 2016-06-23 11:29 | Electrical - Power Distribution | 6000 |  | Incorrect Installation | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | The Emtelle ducts have been installed to the west side of the LU10 turning pit chamber and as installed the minimum bend radius of 3.9m cannot be achieved. They are currently installed to 2 metres from the chamber.
| 03SR - Stations (RfL) | Cxxx-NCR-000371 | NCR | ROP - LU10 Duct Block - 28 Day Concrete Cube Results, low compressive strength |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2016-08-16 | 2016-07-25 14:00 | -22 | 2016-06-30 07:52 | Civil - Utilities Engineering | 0 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Subcontractor Problems - Other | Completed |  | The 28 day compressive strength results for LU10 Duct Block (Pour 1), was lower than the specified 40N/mm2. The results achieved 39.6 and 38.4N/mm2.
| 03SR - Stations (RfL) | Cxxx-NCR-000372 | NCR | Karcher Bus wash CMS installation |  | Crossrail | XRL | PNY - Paddington New Yard (West) |  | 2016-09-16 | 2016-08-22 15:38 | -25 | 2016-07-04 15:18 | Electrical - Cable Management | 5000 |  | Incorrect Installation | Rework | 3 (3-6k) | Complete | Discipline/Workmanship - Other | Completed |  | The cable management installation for the Bus washes and plant room is not to the required standard or specification, as detailed in the Electrical Specification (Cxxx-COS-E-RSP-CR076_SD006-50001), appendix A Material & workmanship specifications, clauses Y63.2020A & Y63.3010. 1. Factory fittings have not been used throughout the installation. 2. Cable tray fitings, such as bends & tees do not have gusseted corners. 3. Tray lengths are not joined using manufacturers couplers. 4. Cuts ends have not been deburred or painted with zinc rich paint. 5. Holes cut in trays are not fitted with grommets or bushes. 6. Cabled bunched. 7. Cables. 8. Cables unsupported (ie missing cable tray). 9. Spare capacity not allowed for. 10. Shakeproof washer have not been installed. 11. Cabling crushed by water/hydraulic pipework.
| 03SR - Stations (RfL) | Cxxx-NCR-000373 | NCR | ROP - Landscaping Geotextile Membrane |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2016-09-30 | 2016-07-26 13:39 | -66 | 2016-07-14 16:57 | Civil - Landscaping | 0 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Use of unapproved materials | Completed |  | Material installed without having an approved MCR. Approximately 100 m2 of non 90% recycled material geotextile has been installed under Ranleagh Bridge and due to time constraints it could not be removed by the end of the shift.
| 03SR - Stations (RfL) | Cxxx-NCR-000374 | NCR | ROP - Bollards' reflective tape |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2016-08-17 | 2016-08-18 14:01 | 1 | 2016-07-20 08:18 | Civil - Street Furniture | 1000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Supervision - Other | Completed |  | Materials not inspected at the time of delivery.
| 03SR - Stations (RfL) | Cxxx-NCR-000375 | NCR | Head House - Fire Proofing of __ Insulation |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2016-12-22 | 2016-10-20 10:31 | -63 | 2016-07-28 14:55 | Fire - Compartmentation | 0 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Verification Problems - Other | Completed |  | A number of builders work openings have been cut through the __ cladding in the external elevations of the Head House. They have been cut to the size of the installed asset (louvre for instance) and the cowling and flange of this installed object used to complete. It has been identifies that this may not be in line with the __ recommendations for walls considered for fire compartmentation.
| 03SR - Stations (RfL) | Cxxx-NCR-000376 | NCR | AD4 - Incorrect Orientation of Lighting Kiosk Plinth |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2016-10-14 | 2016-08-05 14:08 | -70 | 2016-07-28 15:14 | Electrical - Lighting | 3000 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | The lighting kiosk plinth has been installed to the referenced drawings. When the block paved emergency walkway was set out (and later installed) it was clear that it penetrated the alignment of the northern footpath edging by approximately 400mm. This restricted the footpath width in this immediate area down from the required 2 metres.
| 03SR - Stations (RfL) | Cxxx-NCR-000377 | NCR | AD4 - Position of Lighting Column Bases |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2016-10-21 | 2016-09-07 15:02 | -44 | 2016-07-28 16:30 | Electrical - Lighting | 2000 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | This NCR has been raised about the position of Lighting Columns 1, 2 and 3 (the first from the Head House to the North). These were installed as far to the north as possible so they did not get directly impacted by the protruding toe of the Harrow Road Retaining Wall and HV cable trench (tunnel supplies and cable between HV Compounds 4 and 2). It has since become evident that the bollards cannot be installed as per design due to the available distance between the lighting column and the emergency walkway footprint.
| 03SR - Stations (RfL) | Cxxx-NCR-000378 | NCR | ROP - Emergency Lighting Circuit Integrity |  | Crossrail | XRL | PNY - Paddington New Yard (West) |  | 2019-03-18 16:43 | 2019-03-04 16:44 | -14 | 2016-08-01 08:47 | Electrical - Lighting | 0 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | BS7671, paragraph 560.8, states, “The wiring system selected shall meet the requirements of the relevant code of practice appropriate to the application and shall be mounted and installed in such a way that the circuit integrity will not be impaired during a fire”. The emergency lighting circuits for the headhouse, platform area & evacuation walkway use plug & sockets and rely on the fire survivability of these sockets, as the cabling is looped in and out of it. The sockets used for connecting the luminaires do not meet the BS7671 requirement above and are not tested in accordance with BS EN 50200:2006.
| 03SR - Stations (RfL) | Cxxx-NCR-000379 | NCR | Bus Deck - No concrete technician onsite |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2016-10-28 | 2016-10-14 09:28 | -14 | 2016-08-12 15:35 | Civil - Civil Engineering General | 0 |  | Testing and Commissioning | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Other | Completed |  | On the 24th of June the final footpath section was poured with no __ concrete technician being onsite. This was due to the previous days concrete pour having to be cancelled due to the concrete pump breaking down and therefore unable to pump the concrete. Upon cancelling the days concrete pour and re-arranging for the concrete pump to attend the following day. __ where contacted to arrange a concrete technician but unable to supply a concrete technician at late notice. It should be noted that this concrete is not structural and all previously tested concrete has been within the allowable slump range and all cubes reaching the required strength within 28days.
| 03SR - Stations (RfL) | Cxxx-NCR-000383 | NCR | ROP - Loading bay steps |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2016-12-19 | 2016-10-26 15:54 | -54 | 2016-10-12 08:50 | Architectural - Flooring | 2000 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Conflicting information on drawings | Completed |  | The Contractor identified discrepancies in levels between the loading bay design on the Eastern elevation of the Head House (already built at that time) and the access road levels resulting in a rise for the 1st step not acceptable by the Approved Document M of the Building Regulations.
| 03SR - Stations (RfL) | Cxxx-NCR-000384 | NCR | Sump pump control panel MCR |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2017-02-28 | 2017-01-10 17:30 | -49 | 2016-11-01 13:22 | Mechanical - Pumps | 0 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Use of unapproved materials | Completed |  | The MCR for the sump pump control panel was not approved by Crossrail due to missing manufacturer's certificates prior to commencing works on-site
| 03SR - Stations (RfL) | Cxxx-NCR-000385 | NCR | Design changes for Fire Dampers are not captured |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2017-10-31 | 2019-03-23 09:52 | 508 | 2016-11-23 14:22 | Fire - Fire Systems & General | 3000 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Design Problem - Conflicting information on drawings | Completed |  | The type of dampers installed in the ROP Head House is different from Mechanical specification Cxxx-COS-M-RSP-CR076_PT001-50001_rev 6.0. The damper type listed in latest Mechanical Schedule is RABR MAP UK , however the type of the dampers installed on site is BSK4 MAP UK.
| 03SR - Stations (RfL) | Cxxx-NCR-000387 | NCR | Trace heating power junction box |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2019-06-01 | 2019-03-23 09:46 | -70 | 2016-11-22 17:30 | Systems - Drainage/Pumping Systems | 3000 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Not Defined | Completed |  | Position of trace heating power junction box has been observed as being too low and poses a H&S risk as informed by CRL.
| 03SR - Stations (RfL) | Cxxx-NCR-000388 | NCR | Air conditioning refrigeration pipe clips |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2017-05-24 | 2017-09-12 11:12 | 111 | 2016-12-06 14:20 | Mechanical - Heating Ventilation & Air Conditioning | 3000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Pipe clips are not as per the accepted MCR and drawing reference Cxxx-COS-M-DDD-CR076_PT001_Z-00802
| 03SR - Stations (RfL) | Cxxx-NCR-000389 | NCR | Non compliance of FP 400 cable on emergency lighting circuits |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2017-09-29 | 2017-10-07 09:54 | 8 | 2016-12-09 14:39 | Electrical - General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | As part of the Crossrail MOHS Cxxx were required to handover the trackside areas early to Cxxx to allow their works to progress as planned into the tunnel areas. At the point in time when the installation of the emergency lighting installation, adjacent to the tracks, was required the MEP design had yet to achieve Construction Issue status. A project decision was made to proceed with the procurement and installation of the emergency lighting adjacent to the tracks, at risk prior to MCR or construction issue design approval, in order to mitigate any delay to the overall Crossrail programme. An NCR was raised at the time to cover proceeding prior the construction issue acceptance. At this point in time the information contained within the MEP specifications was an FP400 cable for emergency circuits. Subsequently the gated construction issued design detailed FP600 cables which have been utilised on all other emergency circuits throughout the Royal Oak Portal Headhouse.
| 03SR - Stations (RfL) | Cxxx-NCR-000390 | NCR | Bus Deck - Landscaping Geotextile membrane |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2017-02-28 | 2017-02-13 09:45 | -15 | 2016-12-08 16:37 | Civil - Landscaping | 6000 |  | Material | Use As-Is | 3 (3-6k) | Complete | Material/Preservation Problems - Use of unapproved materials | Completed |  | The landscaping geotextile membrane (Geotec 1000 - Cxxx-COS-LRC-CR076_SD006-50051) used for the Landscaping at westbourne park was approved code 2. The engineers proceeded with the use of this product it has only recently been noticed that this doesn't fully comply with the 90% recycled material requirement. The Geotec provider has stated that "It would be difficult to get consistency of strength and other aspects relating to geotextile performance from recycled material and the overall integrity and durability of the installation (depending on the specifics of the application) could be reduced by using recycled products. In general , to achieve the consistency required by CE standards , geotextiles from recycled materials are not available for separation applications to the best of my knowledge."
| 03SR - Stations (RfL) | Cxxx-NCR-000391 | NCR | Benching to Foul water manhole at the Royal Oak Portal headhouse |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2017-05-22 | 2017-07-28 10:52 | 67 | 2017-02-21 08:48 | Civil - Drainage | 1500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Benching in FW manhole immediately outside toilet not compliant with Sewers for Adoption 7th edition, BS EN 752 and drawing no C150-CSY-D-DDD-CR076_PT001-00501.
| 03SR - Stations (RfL) | Cxxx-NCR-000392 | NCR | S18A Manhole - dip from cover to access ladder in excess of BS EN 752 |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2017-08-01 | 2018-06-21 14:51 | 324 | 2017-02-21 09:05 | Civil - Drainage | 1500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Design Problem - Not Defined | Completed |  | First rung of access ladder into manhole S18 A is not within 675mm from top of cover as required by BS EN 752 and Sewers for Adoption 7th edition
| 03SR - Stations (RfL) | Cxxx-NCR-000394 | NCR | Spalling Concrete EBD |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2017-07-31 | 2017-10-20 14:05 | 81 | 2017-03-09 15:52 | Civil - Civil Engineering General | 15000 |  | Design | Rework | 2 (6-60k) | Complete | Discipline/Workmanship - Other | Completed |  | Concrete spalling at the northern corner of the corbel located below the southern entrance to the rear of the bus garage. It is believed that the cause of this is due to insufficient movement capacity in the joint at the northern end of the corbel, between the corbel and the parapet extension that wraps around the side of the corbel, to accommodate temperature and concrete shrinkage movements.
| 03SR - Stations (RfL) | Cxxx-NCR-000396 | NCR | Conduit Termination to Fire Alarm Call Points |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2017-09-01 | 2017-09-12 11:19 | 11 | 2017-03-22 15:29 | Electrical - General | 2500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The 25mm conduit termination to the FA call point is unacceptable, 25 to 20mm reducer and 25mm flange coupling used.
| 03SR - Stations (RfL) | Cxxx-NCR-000397 | NCR | Uncoordinated Conduit Installation |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2017-07-20 | 2017-05-26 14:20 | -55 | 2017-03-22 15:36 | Electrical - Lighting | 1500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Uncoordinated Conduit installation with the stairwell light fittings has resulted in excessive lengths of flexible conduits which has to be fixed to the wall with conduit saddles. Unacceptable installation. As CRL-OBS-13583
| 03SR - Stations (RfL) | Cxxx-NCR-000398 | NCR | Water Damage to High Level Trunking |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2017-07-20 | 2017-10-24 14:01 | 96 | 2017-03-22 15:41 | Electrical - Cable Management | 1500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | External Phenomenon - Other | Completed |  | High level trunking has water damage to the finish and joints have started to corrode CRL-OBS-13582 refers
| 03SR - Stations (RfL) | Cxxx-NCR-000399 | NCR | LV Switch Room B (2) |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2017-09-01 | 2017-09-12 11:25 | 11 | 2017-03-22 15:45 | Electrical - General | 1500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | 1) section of Alloy turnbuckle trunking lid fitted, should be screw fixed. Specification non compliance. 2) ALL Fused connection unit to have neon indicators. Specification non compliance. 3) Mandatory safety signage to be installed. Specification non compliance. Health and Safety. EaW. CRL-OBS-13579 refers
| 03SR - Stations (RfL) | Cxxx-NCR-000400 | NCR | UPS Room 1/664 |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2017-07-20 | 2017-05-26 14:24 | -55 | 2017-03-22 15:48 | Electrical - General | 1500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Sections of Alloy turn buckle lid fixed to the trunking. Non compliant with specification. CRL-OBS-13577 refers
| 03SR - Stations (RfL) | Cxxx-NCR-000401 | NCR | UPS Room 1/664 |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2018-04-06 08:58 | 2019-06-01 07:52 | 421 | 2017-03-22 15:54 | Electrical - General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | Flexible conduits fixed to tray, the tray in parts is cutting into the flexible conduit. The installation is unsatisfactory. Remedial work is required. CRL-OBS-13574 refers
| 03SR - Stations (RfL) | Cxxx-NCR-000402 | NCR | UPS Room 1/664 |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2017-11-22 14:02 | 2018-08-20 10:02 | 271 | 2017-03-22 16:03 | Electrical - General | 1500 |  | Design | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The cable termination of the SWA cabling within the UPS is unacceptable in terms of workmanship and for access and maintenance to the PCB board loacated behind the cabling. CRL-OBS-13573 refers
| 03SR - Stations (RfL) | Cxxx-NCR-000403 | NCR | LV Switch Room A |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2017-08-16 | 2017-05-26 14:27 | -82 | 2017-03-22 16:09 | Electrical - General | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The LV switchpanel has been energised albeit on temp power. There are insufficient mandatory electrical safety signs installed. CRL-OBS-13572
| 03SR - Stations (RfL) | Cxxx-NCR-000404 | NCR | Blank plates missing from Dis Boards |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2017-08-23 | 2017-09-12 11:36 | 20 | 2017-03-22 16:14 | Electrical - General | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Blank plates missing from distribution boards. Labels attached using plastic rivets instead of nuts & bolts. CRL-OBS-13549
| 03SR - Stations (RfL) | Cxxx-NCR-000405 | NCR | Incorrect Labelling on ATS |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2017-08-15 | 2017-05-26 14:43 | -81 | 2017-03-22 16:21 | Electrical - General | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Labelling on ATS refers to incoming supplies as Normal & Emergency instead of LV-A and LV-B. Labels to be replaced. Statement applies to all ATS's within the portal building. CRL-OBS-13549
| 03SR - Stations (RfL) | Cxxx-NCR-000406 | NCR | 13A twin socket fitted in HV switch rooms |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2017-08-07 | 2017-10-07 09:37 | 61 | 2017-03-22 16:24 | Electrical - General | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | 13A twin socket fitted in HV switch rooms. Replace with 16A BSEN 60309 protected socket as required by JV22. CRL-OBS-13546 refers
| 03SR - Stations (RfL) | Cxxx-NCR-000407 | NCR | Damaged __ Acti-9 internal cover plate |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2017-09-12 | 2017-09-12 11:48 | 0 | 2017-03-22 16:27 | Electrical - General | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Damaged __ Acti-9 internal cover plate requires replacement CRL-OBS-13548 refers
| 03SR - Stations (RfL) | Cxxx-NCR-000408 | NCR | __ Q2 switch cabinet handle is not secured properly and the locking mechanism doesn't work easily. |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2017-08-02 | 2017-10-07 09:39 | 66 | 2017-03-22 16:33 | Electrical - General | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | __ Q2 switch cabinet handle is not secured properly and the locking mechanism doesn't seem to work easily. Review and rectify the locking mechanism for the cabinet. CRL-OBS-13440 refers
| 03SR - Stations (RfL) | Cxxx-NCR-000409 | NCR | Insufficient meters to meet Part L requirements |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2017-11-07 13:27 | 2017-10-24 13:40 | -14 | 2017-03-22 16:45 | Electrical - General | 500 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | LV switchboards have very few meters and meters are not installed on spare breakers. Provide sufficient meters on connected feeders and on spare feeders rated 63A and above to meet the building regulations part L requirement. CRL-OBS-13439 refers
| 03SR - Stations (RfL) | Cxxx-NCR-000410 | NCR | CER Room 1/731. |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2017-08-21 | 2017-09-12 11:53 | 22 | 2017-03-22 16:49 | Electrical - General | 1000 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | SWA cable damaged. Outer sheath damaged exposing armourings. This requires remedial action before this cable is made live. CRL-OBS-13375
| 03SR - Stations (RfL) | Cxxx-NCR-000411 | NCR | Openings within the sump structures that require to be sealed off |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2017-09-01 | 2017-12-08 14:18 | 98 | 2017-03-22 16:56 | Civil - Civil Engineering General | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Subcontractor Problems - Insufficient surveillance of subcontractors | Completed |  | During the sump site inspection, it was observed that there are a series of openings within the sump structures that require to be sealed off (please refer to the attached photo). All the openings to the sump need to be sealed off to stop debris/rubbish from entering the sump. Currently the opening for the rising mains and fire mains have been left open and the opening for gas detection holes needs to be sealed off. The track drainage incoming pipes (East and West tunnel) have been sealed off but not with the correct materials. It appears it’s been sealed off with sand and cement and not plugs. Contractor to ensure these incoming pipes to be opened up prior to the final hand over and incoming pipes to be inspected for any damage which may be caused when they got sealed off. In addition, contractor to confirm track drainage incoming pipe levels are lower down the overflow levels. Furthermore, additional electrical cables were observed inside the sump for which their purpose was unknown. Contractor to investigate the reason for these cables and if not necessary please remove them. It was observed that the sump structural wall has the construction joint. Contractor to carry out the remedial work and cover the joint. CRL-OBS-13054 refers
| 03SR - Stations (RfL) | Cxxx-NCR-000412 | NCR | Ppe lagging unsuitable for inside the sump environment |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2018-03-03 07:50 | 2018-02-17 07:51 | -14 | 2017-03-22 17:00 | Mechanical - Mechanical Engineering General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Fire mains have been installed inside the sump and to the underside of the sump slab as per drawings Cxxx-COS-M-DWG-CR076_PT001-50020 and 50021 . Contractor to demonstrate/show evidence that the pipe lagging is suitable for inside the sump environment and is not going to degrade?
| 03SR - Stations (RfL) | Cxxx-NCR-000413 | NCR | Sump Pump Lifting Beam |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2018-01-02 10:43 | 2017-12-19 10:44 | -14 | 2017-03-22 17:04 | Civil - Civil Engineering General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | The sump pump lifting beam has been constructed as per drawings (C150-CSY-A-DDB-CR076_PT001-20102 Rev C04 & C150-CSY-A-DDF-CR076_PT001-50100 Rev C03). However, the contractor failed to provide maintenance, access, replacement and strategy (MARS) report to demonstrate the maintenance of the pump or replacement of pumps as the lifting beam can only be used for lowering or lifting equipment to the top of the sump level. Contractor should issue the MARS report to CEG for review. CRL-OBS-13050
| 03SR - Stations (RfL) | Cxxx-NCR-000414 | NCR | Three phase emergency pump socket have not been provided within vicinity of the sump pumps |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2017-08-16 | 2017-10-31 08:04 | 76 | 2017-03-22 17:09 | Mechanical - Mechanical Engineering General | 2500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | Three phase emergency pump socket have not been provided within vicinity of the sump pumps. A 32A 400V three phase emergency pump socket to BS EN 60309-1 shall be provided in the vicinity of the pump rooms as per requirement in LU standard 1-069 Issue A2 clause 3.6.2
| 03SR - Stations (RfL) | Cxxx-NCR-000415 | NCR | ROP room spaces 1/398 and the FER do not have any ventilation |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2017-12-21 | 2018-12-15 13:05 | 359 | 2017-03-23 08:27 | Mechanical - Heating Ventilation & Air Conditioning | 1500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | The unallocated spaces 1/398 and the FER did not have any ventilation provided. Ventilation by natural means to outside should be provided. CRL-OBS-10869 refers
| 03SR - Stations (RfL) | Cxxx-NCR-000417 | NCR | LUL Cat 1 standard 1-069 clause 3.2.9 |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2019-03-13 10:08 | 2019-02-27 10:15 | -14 | 2017-03-23 08:32 | Civil - Civil Engineering General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | LUL Cat 1 standard 1-069 clause 3.2.9 states "Switch room floor shall be arranged relative to external floors such that the build up of moisture in or near the equipment is prevented." The floor has not been raised, and no concession to cover this departure has been submitted.
| 03SR - Stations (RfL) | Cxxx-NCR-000418 | NCR | Fire Main Supports |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2017-08-09 | 2017-06-29 10:33 | -41 | 2017-03-23 08:39 | Fire - Fire Systems & General | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | If a PN25 Pressure Regulating Landing Valve is used, a compliant PN25 flange with bolts become mandatory by default. CRL-OBS-10528 refers
| 03SR - Stations (RfL) | Cxxx-NCR-000419 | NCR | Support structure for M&E services |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2019-09-30 14:21 | 2019-09-16 15:08 | -14 | 2017-03-23 09:01 | Mechanical - Mechanical Engineering General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Support structure for M&E services in the corridor appears to be weak Provide evidence that loading calculations are carried out for the supports provided CRL-OBS-10523 refers
| 03SR - Stations (RfL) | Cxxx-NCR-000420 | NCR | Fire stopping is directly applied on cables. |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2018-03-12 | 2018-09-24 13:59 | 196 | 2017-03-23 09:08 | Fire - Fire Systems & General | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Fire stopping is directly applied on cables. The specification section JY63.1305 requires all cables to be contained in sleeves. These cables are contained in metal sleeves now and the photographic evidence is attached. Provide sleeves for the cables. CRL-OBS-10520
| 03SR - Stations (RfL) | Cxxx-NCR-000421 | NCR | Lightning Protection Tape |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2017-04-06 | 2017-09-12 12:08 | 159 | 2017-03-23 09:13 | Electrical - Electrical Engineering General | 1500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The LPS tape installation method is not in accordance with JW52.1304 C), d) Cxxx to re-route the LPS tape to avoid flash over. CRL-OBS-10519 refers
| 03SR - Stations (RfL) | Cxxx-NCR-000422 | NCR | Metal trunking is non compliant with section JY60 of the specification |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2017-04-06 | 2017-09-13 10:59 | 160 | 2017-03-23 09:17 | Electrical - Electrical Engineering General | 1000 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The trunking is non compliant with section JY60 of the specification. All trunking to be IP4X Cxxx are to provide IP4X rated trunking. CRL-OBS-10518
| 03SR - Stations (RfL) | Cxxx-NCR-000423 | NCR | Chemical Anchors |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2017-07-12 | 2017-10-24 13:39 | 104 | 2017-03-23 09:36 | Mechanical - Mechanical Engineering General | 1500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Fire main supported from droppers fixed in with chemical fixings. Note that chemical fixings are not permitted for use in soffits/ceilings on Crossrail. Replace with approved fixings CRL-OBS-10514 refers
| 03SR - Stations (RfL) | Cxxx-NCR-000424 | NCR | Fire Main gapping strategy |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2017-04-06 | 2017-07-28 11:48 | 113 | 2017-03-23 09:47 | Fire - Fire Systems & General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | Field design change to be submitted for change is gapping strategy of less than 2 metre Cxxx to submit FDC
| 03SR - Stations (RfL) | Cxxx-NCR-000425 | NCR | LU10 Turning Pit Chamber - Drainage |  | Contr | HTM | PNY - Paddington New Yard (West) |  | 2018-04-30 | 2019-10-29 15:06 | 547 | 2017-03-28 15:30 | Civil - Drainage | 1500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | The LU10 HV turning pit chamber has been installed as per approved drawing Cxxx-COS-U-DDD-CR076_PT001_Z-00800 Rev C02. The reinforced concrete chamber has been constructed without any drainage, which was recommended as per response to Cxxx-RFI-001105
| 03SR - Stations (RfL) | Cxxx-NCR-000426 | NCR | Smoke Damper control |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2018-02-25 10:07 | 2018-06-19 08:02 | 114 | 2017-09-06 14:03 | Fire - Fire Systems & General | 2500 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | The design for the smoke dampers showed a system that did not incorporate a Damper Control Panel. This design would not fulfil the requirements of the specification. The installed smoke damper position reporting is not what is required in accordance with the Crossrail Specification. The specification is asking for open / closed and mid point reporting, and the install, as is, will not report this. The install does indicate the open and closed status of the dampers, but not the mid point status. On review of the design, the way to report all three statuses to comply with the Crossrail Specification, which incorporate the LU Cat 1 Standards and 1-081, 1-082, and 1-085 as well as other relevant requirements, is to have a Damper Control Panel as part of the system. This will then be able to indicate what the status of the damper position as well as isolation of the supply.
| 03SR - Stations (RfL) | Cxxx-NCR-000427 | NCR | Non-Conforming __ fixing |  | Crossrail | PDP | PNY - Paddington New Yard (West) |  | 2018-01-29 08:55 | 2019-06-01 07:56 | 488 | 2017-12-02 12:06 | Electrical - General | 500 |  | Damaged | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | tec-screws have been cut short by unknown persons after installation by specialists
| 03SR - Stations (RfL) | Cxxx-NCR-000428 | NCR | Westbourne Park Elevated Bus Deck (EBD) - Cracking to the Northern Corbel |  | Contr | MRG | PNY - Paddington New Yard (West) |  | 2017-11-20 11:25 | 2018-12-03 14:14 | 378 | 2017-10-25 08:08 | Civil - Structural Engineering | 5000 |  | Design | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Other | Completed |  | Cracking has been observed to the underside of the northern corbel constructed at the northern entrance to the rear of the bus garage leading onto Westbourne Park Elevated Bus Deck (EBD) - as marked-out on the attached drawing Cxxx-CSY-D-DDA-CR076_MS005-01090 rev C07. The extent of the cracking is not yet known but may need to be investigated should remedial works be deemed necessary. Please refer to the attached photographs. The design of the reinforced concrete corbel has been completed by the FCD (Cxxx) i.e. __ . It is believed that the cracking observed may have been due insufficient design tolerances and/or insufficient allowances for movement. As this is not a contractor designed structure, the FDC is to advise of the remedial actions necessary.
| 03SR - Stations (RfL) | Cxxx-NCR-000429 | NCR | Westbourne Park (Elevated) Bus Deck - Cracking to Concrete Footpath |  | Contr | MRG | PNY - Paddington New Yard (West) |  | 2017-12-16 08:31 | 2018-12-03 14:17 | 352 | 2017-11-02 11:34 | Civil - Concrete Pavement | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Not Defined | Completed |  | Cracking has been observed in a number of locations on the surface of the concrete footpath constructed at the Westbourne Park Elevated Bus Deck (EBD) - as highlighted on the attached drawing Cxxx-CSY-D_DDA-CR076_MS005-01560 rev C03 and Cxxx-CSY-D_DDA-CR076_MS005-01561 rev C03 . The extent of the cracking is not yet known but may need to be investigated should remedial works be deemed necessary. Please refer to the attached photographs. The design of the footpath has been completed by the FCD (Cxxx) i.e. __ . It is believed that the cracking observed may have been due insufficient design tolerances and/or insufficient allowances for movement within the concrete footpath - as previously requested in RFI-001050. As this is not a contractor designed structure, the FDC is to advise of the remedial actions necessary.
| 03SR - Stations (RfL) | Cxxx-NCR-000430 | NCR | Westbourne Park (Elevated Bus Deck) - Loose 'chequer plate' service covers and missing fixings |  | Contr | MRG | PNY - Paddington New Yard (West) |  | 2017-11-30 | 2017-12-02 08:32 | 2 | 2017-11-23 18:14 | Civil - Street Furniture | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Cxxx received notification (via email on 15/09/17 - attached) from Crossrail Site Manager, __ advising that Tower Transit Operations Limited (TTOL) had reported a 'loose metal cover' on the main walkway from the fuel islands to the Westbourne Park Bus Depot. On inspection, Cxxx observed that these metal 'chequer plate' service covers protecting the CMS containment for the electrical services (within the Bus Deck) were missing some fixings in locations. This had seemingly resulted in some of the covers being unsecure and becoming loose.
| 03SR - Stations (RfL) | Cxxx-NCR-000431 | NCR | MEP installations not in accordance with Earthing and Bonding Standard |  | Crossrail | PDP | PNY - Paddington New Yard (West) |  | 2019-04-08 10:19 | 2019-03-02 09:28 | -37 | 2018-01-11 11:40 | Electrical - Earthing & Bonding | 25000 |  | Design | Repair | 2 (6-60k) | Complete | Design Problem - Not Defined | Completed |  | The Contractors Earthing and Bonding Design and subsequent installation does not comply with the Central Section Earthing & Bonding Strategy Cxxx-MMD-O8-XST-CR001-00002 and requires modification in order to ensure the bonding conductors are capable of withstanding traction fault currents of 12kA for a period of 200ms.
| 03SR - Stations (RfL) | Cxxx-NCR-000432 | NCR | TTOL Bus Deck - Non-Complaince with WCC Condition 7 Noise Limits |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2018-02-27 | 2019-09-27 14:56 | 577 | 2018-02-13 13:10 | Consents - Environment | 500 |  | Planning | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Error in equipment or material selection | Completed |  | The predicted noise levels shown above (Table 6 on page 15 of the referenced report) indicate that the operation of the bus deck’s fixed plant does not comply with Westminster City Council’s requirements for condition 7 of the decision notice at 5 of the 7 assessed nearest noise-sensitive receptors. The main contributing noise source at all the assessed receptor locations where the night-time criterion has been exceeded has been found to be the hand-held jet wash. The following observations should be born in mind when interpreting these results: - Our calculations are based on "forced" commissioning testing conditions and based on a very worst-case where all the plant operates simultaneously at full capacity; which may not be representative of real bus deck operations. In addition to that, the measurement of the jet wash was undertaken in a fixed location, with an operator holding the jet wash spraying into the air (not against a bus) and only pointing in one direction. It is expected that normal operation of the jet wash may involve more random movements, scattering its sound propagation, potentially generating lower noise emission levels. - The plant noise assessment report undertaken by Anderson Acoustics in May 2015 (reference Cxxx-COS-K2-RGN-CR076_SD006-50001), to discharge planning condition 7 of WCC’s decision notice (ref. 12/04534/FULL); assumed a Karcher jet wash of a sound power level of 83 dB(A). This jet wash model was measured in an existing bus depot facility in Croydon. The measured jet wash in Westbourne Park seems to have different noise emissions, with a sound power level of 101 dB(A). This significant difference is a clear indication of the higher results of the commissioning exercise when compared to the plant noise assessment report. - The agreed criterion was set based on a background noise level measured in 2009, which may not be representative of the future background noise at the assessment locations when the current Crossrail construction works terminate.
| 03SR - Stations (RfL) | Cxxx-NCR-000433 | NCR | inadequate access provided to void above durasteel ceiling |  | Crossrail | PDP | PNY - Paddington New Yard (West) |  | 2019-08-10 08:34 | 2019-07-14 16:42 | -27 | 2018-05-09 13:09 | Fire - Compartmentation | 5000 |  | Design | Repair | 3 (3-6k) | Complete | Design Problem - Other | Completed |  | The Contractor's designed access arrangements for inspection and maintenance of the structure above the durasteel ceiling are insufficient to allow inspection of all areas
| 03SR - Stations (RfL) | Cxxx-NCR-000434 | NCR | Position of Builders Work Hole for External Louvre - Room 1/665 |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2018-10-30 | 2019-02-18 14:15 | 111 | 2018-06-18 16:29 | Architectural - Brickworks/Blockworks | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | The position of the Builderswork gap through the blockwork wall does not meet the design location. The As built location of penetration ID EL16 is approx 126.875m ATD. The design level in the current works information shows 127.025m ATD. i.e. the hole is 150mm too low. This means that from inside the room the vent location clashes with the horizontal cladding support members and the penetration should not be cut out until a corrected location is provided.
| 03SR - Stations (RfL) | Cxxx-NCR-000436 | NCR | Leak in Royal Oak Portal Head House Roof |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2018-07-16 | 2019-02-16 12:50 | 215 | 2018-07-02 13:21 | Architectural - Roofing & Exterior Treatment | 2500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | We have discovered a leak in the Royal Oak Portal Head House Roof.
| 03SR - Stations (RfL) | Cxxx-NCR-000438 | NCR | ROP Damaged cable to internal door contact MD008 |  | Contr | SMN | PNY - Paddington New Yard (West) |  | 2019-03-13 10:39 | 2019-03-02 09:41 | -11 | 2018-11-08 12:38 | Communications and Control Systems - SCADA/Central Management System | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | The internal wiring that comes from the internal door MD008 to the Cxxx junction box has been trapped in between the frame and the lintel and the cable has been damaged, preventing a signal from the contact.
| 03SR - Stations (RfL) | Cxxx-NCR-000439 | NCR | ROP Construction of FOSCs Structures (Fire Resilient Cladding) |  | Contr | MRG | PNY - Paddington New Yard (West) |  | 2018-12-12 | 2019-06-08 08:13 | 178 | 2018-11-12 17:22 | Communications and Control Systems - Fibre Optic Network | 1500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Further to the receipt of Cxxx-PMI-00543 the installation of the cladding works to the 2No. Fibre-Optic Splicing Cabinet i.e. FOSC1 and FOSC 2 at the Royal Oak Portal have commenced. The construction of the FOSC’s and manufacture of the materials have been constructed as per the design outlined in Cxxx-FCD-000473. __ ‘__’ cladding and doors has been selected to provide the required 2 hour fire protection to the FOSC and the other enclosed assets. Following the completion of the cladding to FOSC 1 (please see photograph 1 – attached) it has been noted that the enclosure designed and manufactured to suit FOSC 2 (please see photograph 2 – attached) can no longer suitably interface with the associated cable management (trunking, trays and ducting). The current designed __ cladding enclosure is now too large to be installed at FOSC 2 and will need to be reduced in height to fit around the open framed structure that has been designed (by others).
| 03SR - Stations (RfL) | Cxxx-NCR-000440 | NCR | ROP Earth cable missing from marshalling panel |  | Contr | SMN | PNY - Paddington New Yard (West) |  | 2018-11-27 | 2018-12-03 16:03 | 6 | 2018-11-13 09:03 | Electrical - Earthing & Bonding | 500 |  | Incomplete Works | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The main scada marshaling panel has no mechanical earth protection
| 03SR - Stations (RfL) | Cxxx-NCR-000441 | NCR | ROP Door internal door contact missing |  | Contr | SMN | PNY - Paddington New Yard (West) |  | 2019-01-15 | 2019-03-02 09:48 | 46 | 2018-11-16 13:29 | Communications and Control Systems - SCADA/Central Management System | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The internal door contact for the door 1/662 at Royal Oak Portal is missing the magnet side which is built into the door leaf.
| 03SR - Stations (RfL) | Cxxx-NCR-000442 | NCR | Fire Main - Joint failed during pressure testing |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2018-12-13 | 2019-02-16 12:58 | 65 | 2018-11-29 15:35 | Systems - Fire Detection systems and Mains | 1500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Not Defined | Completed |  | During the pressure testing of the Fire Main system a joint failed on a manufactured GRE tee installed in the westbound platform. The contractor believes the cause was that the rubber failed (which can happen on very rare occasions).
| 03SR - Stations (RfL) | Cxxx-NCR-000443 | NCR | ROP Headhouse WC room pipework insulation aluminium cladding |  | Crossrail | XRL | PNY - Paddington New Yard (West) |  | 2019-03-01 | 2019-03-01 17:00 | 0 | 2019-02-06 09:28 | Mechanical - Piping | 500 |  | Incomplete Works | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The pipework insulation in the WC room is located at low level and exposed to view in the back of house. An aluminium cladding is required to protect the insulation from mechanical damage. Refer to Cxxx-COS-M-RSP-CR076_PT001-50001 JY50.1309. Currently there is no aluminium cladding over the pipework insulation. Link to CRL-OBS-24092
| 03SR - Stations (RfL) | Cxxx-NCR-000444 | NCR | Commenicing works without an accepted ITP in place |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2019-02-21 | 2019-06-29 08:11 | 128 | 2019-02-07 11:46 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | Harrow Road Retaining Wall works were commenced prior to the submission of the completed ITP.
| 03SR - Stations (RfL) | Cxxx-NCR-000445 | NCR | Platform handrails in front of FOSC 1 & 2 |  | Crossrail | XRL | PNY - Paddington New Yard (West) |  | 2019-04-03 | 2019-10-14 12:47 | 194 | 2019-03-18 13:17 | Architectural - Handrail | 3000 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | The platform handrails have not been installed in accordance to the sketch attached under Cxxx-PMI-581. The installed handrails are currently obstructing the FOSC room doors from opening, and are impeding access into the FOSC rooms. The installed handrails to be replaced with removable sections as instructed in the PMI and indicated on the sketch which was attached to the PMI.
| 03SR - Stations (RfL) | Cxxx-NCR-000446 | NCR | Fire Inspection |  | Crossrail | XRL | PNY - Paddington New Yard (West) |  | 2019-11-12 14:32 | 2019-10-29 17:04 | -14 | 2019-03-20 12:18 | Fire - Fire Systems & General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Verification Problems - Not Defined | Completed |  | Inspection carried out to witness the operation of the system with Fire engineer Robin Hatwell and CEG Fire engineer __. Incorrect installation of items where identified on site.
| 03SR - Stations (RfL) | Cxxx-NCR-000447 | NCR | Mechanical Pipes Installed Through Walls & Floor Without Sleeves |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2019-05-27 15:35 | 2019-05-13 15:36 | -14 | 2019-04-01 13:19 | Mechanical - Piping | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Not Defined | Completed |  | Mechanical services have been installed, tested, commissioned and fire-proofed without the installation of sleeves. Installation is not in accordance with the specification clauses below. Refer also to Cxxx-PWK-00258.
| 03SR - Stations (RfL) | Cxxx-NCR-000448 | NCR | ROP Headhouse Intervention Stairs Handrails |  | Crossrail | XRL | PNY - Paddington New Yard (West) |  | 2019-07-08 16:04 | 2019-06-29 08:13 | -9 | 2019-03-28 15:08 | Architectural - Handrail | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | The handrails on the Intervention Staircase in the ROP Headhouse is currently not painted yellow to comply with LUL 1-462 clause 3.1.6.2.
| 03SR - Stations (RfL) | Cxxx-NCR-000449 | NCR | 2.3 testing LV Boards |  | Crossrail | XRL | PNY - Paddington New Yard (West) |  | 2019-11-01 14:57 | 2019-10-18 15:07 | -14 | 2019-03-29 16:17 | Electrical - Switchgear | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | 1. Make amendments to the I/O schedule and LV Board PLCs as per the attached from Cxxx 2. Complete the wiring within the LV Battery transformers 3. The I/O schedule should not include a signal to trip the NC Circuit Bus coupler as this is a dummy switch. 4. Ensure Cxxx remove their lock on the B Board for the Cxxx retest on the TLPP supplies 5. Correct the PLC issue on ‘Spare 4’ within board ‘B’ 6. Correct labelling on the spares to ensure each can correlate with the I/O schedule
| 03SR - Stations (RfL) | Cxxx-NCR-000450 | NCR | Leak in Royal Oak Portal Head House Roof |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2019-06-30 | 2019-07-03 16:15 | 3 | 2019-04-01 15:57 | Architectural - Roofing & Exterior Treatment | 2500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Signs of moisture have appeared in corridor 1/231 in the ROP head house intervention corridor, close to ceiling hatch No. 13. Upon further investigation, a small leak has been discovered between two adjoining sections of flashing.
| 03SR - Stations (RfL) | Cxxx-NCR-000451 | NCR | Functional testing LV Boards |  | Crossrail | XRL | PNY - Paddington New Yard (West) |  | 2019-08-16 13:58 | 2019-08-02 14:06 | -14 | 2019-04-02 11:11 | Electrical - Switchgear | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | 1. The PLC requires changing to ensure that the bus coupler can be opened when the boards are ‘Auto’ mode 2. Carry out an injection test on the ‘B’ REF relay (before energisation) 3. Correct the Key Switch Control label to show correct operation for Auto, Local & Remote
| 03SR - Stations (RfL) | Cxxx-NCR-000452 | NCR | Fire Alarm and Lighting Control Interface |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2019-08-05 | 2019-07-24 13:20 | -12 | 2019-06-17 10:34 | Fire - Fire Systems & General | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | An issue has been identified whereby the SCADA RTU cab and __ lighting control system have been given the same VFCs from the Fire alarm panel. This means the power supplies within the SCADA cab and the __ system have been connected via the common / IO points.
| 03SR - Stations (RfL) | Cxxx-NCR-000454 | NCR | Fire doors installed by firm not currently registered under a third party accredited scheme |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2019-08-16 11:59 | 2019-08-09 14:17 | -7 | 2019-08-08 09:21 | Fire - Compartmentation | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | A door supplier was chosen who could best deliver the combination of security and fire ratings for the external doors of the ROP head house. Post-installation, it was evident that the supplier was not registered under a third party accredited fire door installer scheme, as required by Section L20, Clause 809 of the architectural specification (Cxxx-COS-A-RSP-CR076_SD006-50001).
| 03SR - Stations (RfL) | Cxxx-NCR-000455 | NCR | HRRW Security Fence – Unapproved Epoxy Resin Mortar used to Fix Anchors into HRRW |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2019-08-29 | 2019-08-29 13:28 | 0 | 2019-08-21 14:24 | Civil - Civil Engineering General | 500 |  | Planning | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Use of unapproved materials | Completed |  | It has been identified that the fencing installer has used an unapproved epoxy resin mortar, B+BTEC Vinylester BIS-V420, to fix the M24 threaded anchor rods in the HRRW. The specification and drawings called for __ HIT-HY 200-A or equal and approved. Informal discussions had taken place in relation to changing the epoxy resin mortar prior to using the B+BTEC Vinylester BIS-V420, however formal approval had not been sought.
| 03SR - Stations (RfL) | Cxxx-NCR-000456 | NCR | HRRW Security Fence – Epoxy Resin Mortar Failure |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2019-09-17 11:32 | 2019-09-26 09:25 | 9 | 2019-08-22 11:36 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Improper storage of material | Completed |  | In a post-installation inspection of the 4no UC posts for the HRRW Security Fence Extension it was visible that the epoxy resin mortar (B+BTEC Vinylester BIS-V420) used to fix the M24 threaded anchor rods into the HRRW had not set properly. The M24 threaded anchor rods had tilted towards the bottom of the holes in the HRRW and displaced the epoxy resin mortar beneath them whilst creating a void above them. The initial approx. 100mm of epoxy resin mortar had become soft and malleable and was easily deformed by pressing on it. Note that prior to erecting the 4no UC posts, pull out tests were conducted by __ in accordance with BS8539:2012. Initially pullout tests on 8 of 16 threaded anchor rods were conducted, however after 1no failure it was decided to test the remaining 8no threaded anchor rods. No further failures were detected (15 of 16 passed). The failure was removed and reset in the HRRW. No apparent previous occurrence of the epoxy resin mortar not setting properly is evident on the previously installed 93no UC posts. Potential reasons for the epoxy resin mortar not setting properly this time could be that the product was reaching its shelf life (set to expire in September 2019) or that it was not stored correctly in the extremely hot weather leading up to its use.
| 03SR - Stations (RfL) | Cxxx-NCR-000457 | NCR | HRRW Security Fence – Unapproved Mesh Panels |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2019-10-10 13:16 | 2019-09-26 13:22 | -14 | 2019-08-30 15:25 | Civil - Civil Engineering General | 0 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Not Defined | Completed |  | It has been identified that the fencing installer has used an mesh panel, Protek 358, on the HRRW security fence. The specification and drawings called for Securifor 358 or equivalent approved product. Informal discussions had taken place in relation to changing the mesh prior to using the Protek 358, however formal approval had not been sought.
| 03SR - Stations (RfL) | Cxxx-NCR-000458 | NCR | Use of __ __ Silicone Sealant Without LU 1-085 Compliance |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2019-11-06 | 2019-11-11 12:54 | 5 | 2019-09-03 11:28 | Fire - Compartmentation | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Verification Problems - Other | Completed |  | This NCR is to document the installation of __ __ Silicone Sealant in a quantity greater than that specified in the MCR. Rev 1.0 of the MCR specifies less than 1 tube of sealant will be used and that the LU 1-085 specification in therefore not applicable. Subsequently a greater quantity of sealant was used for the installation of __ throughout the headhouse and compliance with LU 1-085 was not addressed. In addition to this NCR, the following were raised to document the approval process: Cxxx-RFI-001246 Cxxx-COS-M-LRC-CR076_PT001-50001 Rev 2.0 (Attached)
| 03SR - Stations (RfL) | Cxxx-NCR-000459 | NCR | Egress Staircase components wrongly powder coated |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2019-09-30 | 2019-11-13 14:22 | 44 | 2019-09-16 09:56 | Architectural - Finishes | 500 |  | Manufacturing Defect | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | It has been discovered that the fabricator of the egress staircase has wrongly powder coated the staircase handrail posts as well as the gate goal posts green (RAL 6005) despite the specification stating these components are to be unpainted galvanised steel work. __ was enquired to confirm the finishes of the components of the staircase however the subcontactor failed to wait for a response.
| 03SR - Stations (RfL) | Cxxx-NCR-000460 | NCR | Collasped pipe found during CCTV |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2019-12-13 14:22 | 2019-12-04 16:24 | -9 | 2019-11-29 13:43 | Civil - Drainage | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Previous Construction - Other | Completed |  | During the CCTV survey of the drainage a section of collapsed pipe was detected 6 metres in from C207 heading toward C208.
| 03SR - Stations (RfL) | Cxxx-NCR-000461 | NCR | New Harrow Road Egress Stair - Gate Quality Issues |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2020-01-09 | 2020-01-31 12:30 | 22 | 2019-12-12 16:31 | Civil - Civil Engineering General | 500 |  | Manufacturing Defect | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The original gates installed on Friday 15th November 2019 where not accepted as they had a number of issues as highlighted on the attached document "Original Gate Issues". Replacement gates were delivered on Wednesday 11th December 2019 and it was evident that they too had a number of issues and could not be accepted. Refer to the attached document "Replacement Gate Issues".
| 03SR - Stations (RfL) | Cxxx-NCR-000462 | NCR | Gravity Drainage Air Test to BS EN 1610 Failures |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2020-10-10 | 2020-10-05 12:37 | -5 | 2020-02-24 10:27 | Civil - Drainage | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Verification Problems - Other | Completed |  | Cxxx-PMI-00659 was issued on 13/12/19 instructing the Contractor to undertake additional air testing to BS EN 1610 on the projects gravity drainage system. Upon undertaking this testing it was identified that 3no drainage runs did not pass this test. These drainage runs are identified by reference numbers 200.000, 200.003 and 200.006 As well as the above 3no. manholes were water tested these were; C207, C208 and C210. All manholes tested failed the water test. This Non-Conformance notes as failure against BS EN 1610:2015. The requirement to test against this standard was instructed by PMI-659 on 13/12/2019. The test scope and method was originally agreed on the Drainage ITP: Cxxx-COS-D-ITP-CR076_SD006-50012 Rev 5.0, accepted by Crossrail on 02/07/2015. This referenced testing criteria from the C150 Drainage Specification: C150-CSY-D-RSP-CR076_PT001-00005 - V6 and Appendix 1/5: Testing to be Carried Out by the Contractor: C150-CSY-C-RSP-CR076_PT001-00001 7.0. As there was no definitive advice, the test method from the Specification for Highway Works, Series 500, Drainage and Service Ducts was agreed. This was the general template used for the Crossrail specific Specifications and gives the following guidance: Clause 507-8: Requires only chambers on foul drains to be tested for water tightness. Clause 509-2: Includes the test procedure we used for the approved Inspection and Test Plan. Pipes only. Clause 509-8: Mentions permeability testing may be introduced in Contract Specific Appendix 5/1 (not clear if this is pipe or manhole specific so I consider both). Our ‘Testing to be Carried out by the Contractor’ document was Appendix 1/5 with no specifics. This is silent on any pipe or manhole testing. Appendix is also not in the back of the C150 Series 500 Drainage Specification. The pipes were tested as per the methodology in the ITP around 14th July 2016, passed and approved within Deliverable Records: Cxxx-COS-D-ITP-CR076_PT001-50003. The Contractor believes they have completed their Contract requirement. It is not clear whether C150 designed the manholes to be fully submerged, or the pipe is expected to normally operate with open channel flow. No specific water retaining elements appear to be considered that may include: water retaining concrete, specialist compound around pipe infill, reinforced surround, water bar or kicker joints. The Specification for Highway Works does not include surface water manholes in their guidance to test. A specialist and experienced drainage contractor was used for the construction. They have been contacted and they refute their workmanship can be held responsible. At this stage they do not intend to rectify anything without instruction. The attached and available photos appear to show well-constructed manhole interiors. The Contractor requests that an instruction is raised to repair manholes and/or pipe to allow these to pass the more onerous BS EN 1610:2015 testing requirements. With repairs and test satisfactorily complete it will allow this NCR to be closed.
| 03SR - Stations (RfL) | Cxxx-NCR-000463 | NCR | RAM Demonstration - Supplier Forms |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2020-03-25 12:29 | 2020-03-11 12:36 | -14 | 2020-02-24 13:35 | Systems - Other | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Not Defined | Completed |  | Small area of non-compliance against the Cxxx Royal Oak Portal Head House - RAM Specification and Demonstration Plan Cxxx-COS-M-STP-CR076_PT001-50001 section 5 re completion of supplier forms shown in Appendix 2. This is considered very low risk.
| 03SR - Stations (RfL) | Cxxx-NCR-000464 | NCR | Fire Stopping Inspection and Testing Plan |  | Contr | COS | PNY - Paddington New Yard (West) |  | 2020-10-01 09:49 | 2020-09-17 10:01 | -14 | 2020-09-14 12:24 | Fire - Compartmentation | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Verification Problems - Not Defined | Completed |  | As identified on the CRAF2 audit, the Cxxx Inspection & Testing Plan for Fire Stopping (Cxxx-COS-M-ITP-CR076_PT001-50017 Rev 1.0) was approved after the completion of the applicable works. The requirement for ITPs is stated in the Works Information, Volume 2B, Clause 20.8. This was a repeating task with 428 separate locations so was previously being assured through the Fire Stopping Log (Cxxx-COS-E4-LLG-CR076_PT001-50001 Rev 1.0). This was then referenced in the ATU master document list (Cxxx-COS-E1-LRC-CR076_PT001-50002 Rev 2.0). Cxxx were led by the ATU process and the assurance was previously aligned to achieve this. The fire stopping was installed by __ to approved design drawings and details. FCD-496 was raised with an approved fire stopping process and three benchmarks were produced and approved. All fire stopping was inspected and signed-off by Fire Engineers of both the Contractor and the Contractor's designer on 18th June 2020 (Cxxx-COS-E7-LRC-CR076_PT001-50018 Rev 1.0). The Client's Fire Engineer and members of the CRAF2 team also surveyed the installations against the Fire Stopping Log on 18th August 2020 to their satisfaction. The Inspection and Test Plan was completed at a later date, but the Contractor confirms that the fire stopping has been installed to the requirements contained within.
| 03SR - Stations (RfL) | Cxxx-NCR-000004 | NCR | test |  | Crossrail | XRL | PNY - Paddington New Yard (West) |  | 2014-05-23 | 2014-05-16 10:21 | -7 | 2014-05-09 14:56 | Archaeology - General | 0 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Counterfeit Items | Completed |  | test
| 03SR - Stations (RfL) | Cxxx-NCR-000005 | NCR | Started work on cladding without approved ITP |  | Contr | DUO | PNY - Paddington New Yard (West) |  | 2015-05-27 | 2015-05-15 16:56 | -12 | 2015-05-07 15:43 | Architectural - General | 500 |  | Documentation and Records | Reject | 4 (0.5-3k) | Complete | Management Problem - Misunderstand the definition of the requirement | Completed |  | Started work on cladding without approved ITP
| 03SR - Stations (RfL) | Cxxx-NCR-000006 | NCR | Wrong cladding format to southern elevation |  | Contr | DUO | PNY - Paddington New Yard (West) |  | 2015-06-06 | 2015-06-02 14:34 | -4 | 2015-05-07 15:59 | Architectural - General | 10000 |  | Material | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The lower run of cladding sheets on the southern elevation have been supplied at the wrong length so as a result does not match fully with the approved planning drawing SK11
| 02SL - Stations (LUL) | Cxxx-NCR-000335 | NCR | Late submission of MCR for DLR noise barrier precast foundations |  | Contr |  | VID - Victoria Dock Portal (Central) |  | 2012-10-26 | 2012-11-14 15:38 | 19 | 2012-10-19 | Civil - Civil Engineering General | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | Cxxx issued the MCR for the prcast units of the noise barrier to CRL on 18 October 2012, they intend to commence installing the units during the first possession weekend during 20 to 22 October 2012. Insufficient time has been given to properly review the MCR. In addition ITP Cxxx-VIN-C-ITP-CR144_PT003-50028, for the noise barrier item 2.2 approval of peranment materials is a hold point which has not been observed.
| 02SL - Stations (LUL) | Cxxx-NCR-000336 | NCR | Use of Aqua Railgrid Geogrid LBO370 |  | Contr |  | VID - Victoria Dock Portal (Central) |  | 2012-12-23 | 2012-11-19 14:33 | -34 | 2012-10-22 | Track - Track Bed | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | 2 layers of Aqua geogrid have been used under the East Bound track between Ch 160 and Ch 190. This product has an aperture size of 65 x 65 and a max tensile stength of 30 kN/m per layer. This material had not been submitted to crossrail for approval. The approved product was Tensar SS40.
| 02SL - Stations (LUL) | Cxxx-NCR-000338 | NCR | Control of Documents |  | Contr |  | VID - Victoria Dock Portal (Central) |  | 2012-11-08 | 2012-11-23 17:37 | 15 | 2012-10-24 | Structural Engineering - Structural Engineering - General | 500 |  | System Defect | Rework |  | Complete |  | Completed |  | The consolidated set of Contract drawings contained revision C02 of this drawing and not the latest revision.
| 02SL - Stations (LUL) | Cxxx-NCR-000340 | NCR | Use of fill material which has not yet been approved by CRL |  | Contr |  | VID - Victoria Dock Portal (Central) |  | 2012-11-08 | 2012-12-17 12:51 | 39 | 2012-10-24 | Civil - Fill | 500 |  | Material | Rework |  | Complete |  | Completed |  | Class 6F4 material was utilised as sub Ballast during the weekend possession on 20th / 21st October 2012. The MCR for this material had been raised and submitted after the content was discussed with CRL. At the time of submision it was understood that it would be returned Code 2. When CRL reviewed the submission, additional information was identified as being required which meant the document could only be returned at Code 3. Therefore, non-approved material has been used in the works.
| 02SL - Stations (LUL) | Cxxx-NCR-000356 | NCR | Drainage pipe perforations |  | Contr |  | VID - Victoria Dock Portal (Central) |  | 2012-11-23 | 2012-12-05 16:10 | 12 | 2012-11-09 | Track - Track Bed | 500 |  | Supervision/Management | Rework |  | Complete |  | Completed |  | 280mm OD Demco Terra drain will half barrel perforations has been installed. The pipe has been installed with the perforations at the top of the pipe.
| 02SL - Stations (LUL) | Cxxx-NCR-000364 | NCR | DLR track drain bedding material |  | Contr |  | VID - Victoria Dock Portal (Central) |  | 2012-11-30 | 2012-12-19 10:02 | 19 | 2012-11-15 | Track - Track Bed | 500 |  | Supervision/Management | Rework |  | Complete |  | Completed |  | 40 mm single size material has been used as a pipe bedding
| 02SL - Stations (LUL) | Cxxx-NCR-000365 | NCR | Drainage surround material |  | Contr |  | VID - Victoria Dock Portal (Central) |  | 2012-12-14 | 2012-12-19 11:44 | 5 | 2012-11-16 | Civil - Drainage | 500 |  | Material | Rework |  | Complete |  | Completed |  | Delivery notes reviewed during CRL surveillance of 13th November documented the delivery of 40mm single size aggregate. The delivery notes did not document the aggregate source. Visual inspection and measurement of aggregates on a stockpile of deliver single size aggregate showed a number of oversize stones in the region of 60 to 70mm. No grading results were available for material delivered to site.
| 02SL - Stations (LUL) | Cxxx-NCR-000376 | NCR | 6F4 Sub base materail |  | Contr |  | VID - Victoria Dock Portal (Central) |  | 2012-11-30 | 2012-12-19 10:09 | 19 | 2012-11-28 | Track - Track Bed | 500 |  | Material | Rework |  | Complete |  | Completed |  | Material which is non-compliant to the specification for highway works 6F4 has been used. failed on PSD to much fine content. location where rework will be undertaken is east bound track Ch 165 to 195 and West bound 140 to 154 and backfill to UTX
| 02SL - Stations (LUL) | Cxxx-NCR-000389 | NCR | Non notification for a CRL witness inspection intervention |  | Contr |  | VID - Victoria Dock Portal (Central) |  | 2013-01-11 | 2012-12-20 11:01 | -22 | 2012-12-06 | Civil - Fill | 500 |  | Planning | Use As-Is |  | Complete |  | Completed |  | No notification was given to Crossrail for this inspection so they were not given the opportunity to attend.
| 02SL - Stations (LUL) | Cxxx-NCR-000390 | NCR | Works commenced without an accepted ITP in place |  | Contr |  | VID - Victoria Dock Portal (Central) |  | 2012-12-23 | 2012-12-19 10:17 | -4 | 2012-12-06 | Track - Rails and Sleepers | 500 |  | System Defect | Use As-Is |  | Complete |  | Completed |  | Initial prfabrication of trackwork panels has commenced at Pod-Track's facility in Dagenham. The ITP for these works has not been accepted.
| 02SL - Stations (LUL) | Cxxx-NCR-000395 | NCR | Sub Ballast segregrating under compaction |  | Contr |  | VID - Victoria Dock Portal (Central) |  | 2012-12-21 | 2012-12-20 11:07 | -1 | 2012-12-07 | Civil - Fill | 500 |  | Material | Rework |  | Complete |  | Completed |  | Material placed on Tuesday 4th December has segregated under compaction. It is likely that this material had a water content lower than the specified limits.
| 02SL - Stations (LUL) | Cxxx-NCR-000414 | NCR | Class 6F4 Sub Ballast failed to meet plate bearing test requirement following compaction |  | Contr |  | VID - Victoria Dock Portal (Central) |  | 2013-01-18 | 2013-01-14 16:25 | -4 | 2012-12-26 | Civil - Fill | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | Plate Bearing tests at Chainages 285, 310 and 335 achieved between 50 and 71MPa. Severely inclement weather before and during placement of the Class 6F4 is likely to have caused the material to be wetter than required. As these works were possession works, it was not possible to delay placeemnt or to bring in alternative materials.
| 02SL - Stations (LUL) | Cxxx-NCR-000415 | NCR | DLR Realignment - high formation |  | Contr |  | VID - Victoria Dock Portal (Central) |  | 2013-01-31 | 2013-01-14 16:31 | -17 | 2013-01-02 | Civil - Fill | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | At chainage 330, the top of sub ballat is betwee design +30 to design +40mm.
| 02SL - Stations (LUL) | Cxxx-NCR-000416 | NCR | Fixing of conductor rail brackets to sleepers using resin fixings |  | Contr |  | VID - Victoria Dock Portal (Central) |  | 2013-02-28 | 2013-01-14 16:40 | -45 | 2013-01-03 | Track - Rails and Sleepers | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | In a numbe rof places (5 No), Brecknell Willis used resin fixings in lieu of the standard coach bolts. Brecknell Willis did not advise __ of this in advance and therefore the activity was not included in the ITP and no material Compliance Record had been prepared. The locations affected are: Up Road CH 209,211,238 and 241, Down Road CH207
| 02SL - Stations (LUL) | Cxxx-NCR-000444 | NCR | Class 6F5 material - Marginal failure of Particle Size Distribution (PSD) |  | Contr |  | VID - Victoria Dock Portal (Central) |  | 2013-03-15 | 2013-02-26 18:18 | -17 | 2013-02-05 | Civil - Fill | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | 12 tests have been carried out on the material stockpiled at McGee's facility at Silvertown. of these, 8 No. met the grading requirements. With the remaining 4 tests, 100% passed the 80mm sieve. The spec requires no more than 99% passing this sieve.
| 02SL - Stations (LUL) | Cxxx-NCR-000452 | NCR | Damage to Precast Concrete Retaining Wall Units - DLR Realignment |  | Contr |  | VID - Victoria Dock Portal (Central) |  | 2013-03-29 | 2013-03-26 10:55 | -3 | 2013-02-13 | Civil - Civil Engineering General | 500 |  | Damaged | Repair |  | Complete |  | Completed |  | 2 No. units have suffered damage to formed edges which are outside what could be considered acceptable for incorporation into the permanent works.
| 02SL - Stations (LUL) | Cxxx-NCR-000454 | NCR | 1.8m high noise barrier on north elevation of the DLR realignment ch 200 to 259.5 |  | Contr |  | VID - Victoria Dock Portal (Central) |  | 2013-04-03 | 2013-04-02 16:12 | -1 | 2013-02-19 | Track - Track General | 500 |  | Planning | Rework |  | Complete |  | Completed |  | The noise barrier foundations have been drilled to the setting out of 2.6m track offset from ch 200 to ch 259.5
| 02SL - Stations (LUL) | Cxxx-NCR-000455 | NCR | Precast retaining wall units cast out of square |  | Contr |  | VID - Victoria Dock Portal (Central) |  | 2013-04-03 | 2013-03-26 15:20 | -8 | 2013-02-19 | Civil - Civil Engineering General | 500 |  | Workmanship | Rework |  | Complete |  | Completed |  | On some of the units, the horizontal leg is not square to the vertical leg. This has resulted in excessive and varying gaps between units. As a result, the standard joint detail cannot be applied.
| 02SL - Stations (LUL) | Cxxx-NCR-000457 | NCR | Grout to Retaining wall units - workmanship and protection |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2015-02-06 | 2015-02-06 10:22 | 0 | 2013-02-20 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The water used during the grouting was not maintained ata high enough temperature throughout the mixing process. Insufficient protection was used over the grouted areas during the works. Heavy rain occured at the time.
| 02SL - Stations (LUL) | Cxxx-NCR-000462 | NCR | Pile mat - failed plate bearing test |  | Contr |  | VID - Victoria Dock Portal (Central) |  | 2013-03-29 | 2013-03-26 11:09 | -3 | 2013-02-22 | Civil - Fill | 500 |  | Material | Rework |  | Complete |  | Completed |  | At Chainage 85895, the maximum deflection was 16.35mm at 600Kn/m2.
| 02SL - Stations (LUL) | Cxxx-NCR-000465 | NCR | unsuccessful pull out test on post fix anchors for 1.8m high DLR noise barrier |  | Contr |  | VID - Victoria Dock Portal (Central) |  | 2013-04-26 | 2013-04-25 13:49 | -1 | 2013-02-26 | Track - Track General | 500 |  | Material | Rework |  | Complete |  | Completed |  | A number of anchors have failed to achieve this (see attached sheets)
| 02SL - Stations (LUL) | Cxxx-NCR-000468 | NCR | Non Notification of Witness Point |  | Contr |  | VID - Victoria Dock Portal (Central) |  | 2013-04-12 | 2013-04-09 11:40 | -3 | 2013-03-06 | Civil - Civil Engineering General | 500 |  | System Defect | Use As-Is |  | Complete |  | Completed |  | For the first set of guide walls cast, this witness point was not notified to Crossrail so the witness point was not observed
| 02SL - Stations (LUL) | Cxxx-NCR-000469 | NCR | Works commenced without an ITP |  | Contr |  | VID - Victoria Dock Portal (Central) |  | 2013-04-12 | 2013-04-09 11:55 | -3 | 2013-03-06 | Civil - Street Furniture | 500 |  | System Defect | Use As-Is |  | Complete |  | Completed |  | The installation of street lighting ducts for the Excel lorry park was carried out on the weekend of 2nd / 3rd March 2013. The associated ITP (Cxxx-VIN-C-ITP-CR144_PT003-50032 is currently at Code 3.
| 02SL - Stations (LUL) | Cxxx-NCR-000489 | NCR | Incorrect installation of shallow datum |  | Contr |  | VID - Victoria Dock Portal (Central) |  | 2013-04-19 | 2013-04-09 12:03 | -10 | 2013-03-14 | Geotechnical Engineering - Geotechnical Monitoring | 500 |  | Workmanship | Rework |  | Complete |  | Completed |  | The following issues have been identified during installation of the first Shallow Datum: Borehole drilled too deep Anchor installed 1m below invert 5mm Diwidag bars used Metal sleeve used instead of HDPE These issues appear to heve arisen because the installation team used an existing standard detail, rather than the detail for this project
| 02SL - Stations (LUL) | Cxxx-NCR-000499 | NCR | Weekly monitoring reports not being formally issued to Crossrail |  | Contr |  | VID - Victoria Dock Portal (Central) |  | 2013-04-26 | 2013-05-23 11:18 | 27 | 2013-03-19 | Geotechnical Engineering - Geotechnical Monitoring | 500 |  | System Defect | Rework |  | Complete |  | Completed |  | The reports , tabled at the weekly monitoring meeting, have not been formally issued via eB for Crossrail acceptance. In addition, some of the reports have contained errors (e.g. wrong chainages).
| 02SL - Stations (LUL) | Cxxx-NCR-000500 | NCR | No sight lines between primary and secondary setting out and survey control points |  | Contr |  | VID - Victoria Dock Portal (Central) |  | 2013-05-10 | 2013-05-24 17:01 | 14 | 2013-03-19 | Surveying - GIS Engineering & Land Surveying | 500 |  | Planning | Rework |  | Complete |  | Completed |  | The lines of sight within the secondary control network have been obscured by the hoarding and other physical obstructions. This is preventing adequate checks within the secondary control network. In addition, whilst carrying out setting out activities, engineers have not been setting up on a known control station and have been referencing reflectors attached to the excel car park and Royal Victoria Station instead of other secondary of primary control points.
| 02SL - Stations (LUL) | Cxxx-NCR-000523 | NCR | Kerbs installed without an approved MCR |  | Contr |  | VID - Victoria Dock Portal (Central) |  | 2013-05-24 | 2013-05-14 15:45 | -10 | 2013-04-10 | Civil - Kerbs | 500 |  | System Defect | Use As-Is |  | Complete |  | Completed |  | During the installation of shallow datums for monitoring of the excavation and piling works approximately 7 No. kerbs needed to be replaced along Victoria Dock Road. As a result of the urgency in getting the road reopened to traffic, the kerbs were procured and installed without an MCR being raised.
| 02SL - Stations (LUL) | Cxxx-NCR-000524 | NCR | Covers and frames installed without an approved MCR in place |  | Contr |  | VID - Victoria Dock Portal (Central) |  | 2013-05-24 | 2013-05-14 15:40 | -10 | 2013-04-10 | Geotechnical Engineering - Geotechnical Engineering - General | 500 |  | System Defect | Use As-Is |  | Complete |  | Completed |  | Covers and frames were procured for placing on top of the instrumentation protection chambers. Some of these are in temporary locations but 3 no. are within Victoria Dock Road. When the covers / Frames were delivered the need for an MCR was discussed. The __ engineer was asked to discuss the requirement for an MCR with Crossrail in advance of the items being used. This was not done and the items were installed without the MCR in place
| 02SL - Stations (LUL) | Cxxx-NCR-000525 | NCR | Failure of bedding to cover and frame |  | Contr |  | VID - Victoria Dock Portal (Central) |  | 2013-05-24 | 2013-05-17 13:13 | -7 | 2013-04-10 | Civil - Streets & Highways | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | The bedding to the cover and frame has partially failed resulting in movement of the cover and damage to the adjacent surfacing
| 02SL - Stations (LUL) | Cxxx-NCR-000538 | NCR | Instrumentation and Monitoring Data not uploaded to UCIMS |  | Contr |  | VID - Victoria Dock Portal (Central) |  | 2013-05-31 | 2013-06-07 11:07 | 7 | 2013-04-18 | Geotechnical Engineering - Geotechnical Monitoring | 500 |  | Supervision/Management | Repair |  | Complete |  | Completed |  | A review of UCIMS on the 18/04/2013 noted that Monitoring Data as provided via the SRG's CTC's and ERP have not been uploaded as per the requirements set out in the Specification for Constrol of Ground Movement.
| 02SL - Stations (LUL) | Cxxx-NCR-000541 | NCR | Reinforcement cage to LDA piles installed out of tolerance (Level) |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2013-10-18 | 2013-10-11 11:59 | -7 | 2013-04-26 | Geotechnical Engineering - Concrete - Bored Pile | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | In the 2 referenced piles (N172 and N168) the cages were set at finished level +100mm to allow for movement during concreting and casing removal. During extraction of the casings, the cages dropped to 75mm below theoretical (i.e. 25mm outside tolerance)
| 02SL - Stations (LUL) | Cxxx-NCR-000552 | NCR | Records being provided not in accordance with the ITP |  | Contr |  | VID - Victoria Dock Portal (Central) |  | 2013-05-31 | 2013-05-15 17:38 | -16 | 2013-04-30 | Geotechnical Engineering - Concrete - Bored Pile | 500 |  | System Defect | Repair |  | Complete |  | Completed |  | The records actually being provided do not align with this ITP. The records, however, are correct for the type of piling being carried out.
| 02SL - Stations (LUL) | Cxxx-NCR-000555 | NCR | Instrumentation and Monitoring - Checksheets |  | Contr |  | VID - Victoria Dock Portal (Central) |  | 2013-06-03 | 2013-05-21 17:17 | -13 | 2013-05-02 | Geotechnical Engineering - Geotechnical Monitoring | 500 |  | Supervision/Management | Rework |  | Complete |  | Completed |  | See above.
| 02SL - Stations (LUL) | Cxxx-NCR-000561 | NCR | Unapproved method of testing concrete consistence used on pile concrete |  | Contr |  | VID - Victoria Dock Portal (Central) |  | 2013-06-21 | 2013-06-21 10:54 | 0 | 2013-05-08 | Geotechnical Engineering - Concrete - Bored Pile | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | Our sub-contractor’s supplier advised that due to the sensitivity of the mix to variations in ambient temperature and moisture content the specified testing methods may not be applicable. On 29/04/13 and again on 30/04/13 our sub-contractor used a Slump-Flow test (BS EN 12350-8) on some of the concrete loads delivered after deeming them to be acceptable consequently installed it on site.
| 02SL - Stations (LUL) | Cxxx-NCR-000563 | NCR | Piezometer installed in revised position without the relevant FCD approved |  | Contr |  | VID - Victoria Dock Portal (Central) |  | 2013-05-31 | 2013-05-15 17:05 | -16 | 2013-05-09 | Geotechnical Engineering - Geotechnical Monitoring | 500 |  | System Defect | Use As-Is |  | Complete |  | Completed |  | The location drawings for the instrumentation showed Piezometer PVG0000G4 in a position that could not be achieved. FCD507 was raised to amend the position. This had been returned by Crossrail requesting a revised plan showing the proposed location. The Piezometer was installed in the revised location whilst the FCD is still open.
| 02SL - Stations (LUL) | Cxxx-NCR-000565 | NCR | Inclinometers installed to an incorrect toe depth |  | Contr |  | VID - Victoria Dock Portal (Central) |  | 2013-06-28 | 2013-06-18 15:46 | -10 | 2013-05-09 | Geotechnical Engineering - Geotechnical Monitoring | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | The following inclinometers have been installed to a shallower depth than required by the following amounts: IM007 - 650mm IM012 - 500mm IM013 - 900mm
| 02SL - Stations (LUL) | Cxxx-NCR-000566 | NCR | Excessive spacing between links in pile reinforcement at Splice position |  | Contr |  | VID - Victoria Dock Portal (Central) |  | 2013-06-28 | 2013-05-17 13:48 | -42 | 2013-05-13 | Geotechnical Engineering - Concrete - Bored Pile | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | The reinforcement cage manufacturer has included the “Safe Splice” internally welded steel band as part of the transverse reinforcement. They then reduced the number of links in this area, resulting in spacings between links of up to 500mm
| 02SL - Stations (LUL) | Cxxx-NCR-000570 | NCR | Incorrect link spacing on pile reinforcement cage |  | Contr |  | VID - Victoria Dock Portal (Central) |  | 2013-06-14 | 2013-05-17 12:54 | -28 | 2013-05-13 | Geotechnical Engineering - Concrete - Bored Pile | 500 |  | Material | Reject |  | Complete |  | Completed |  | Link spacing was manufactured at 300mm on the upper section of the cage. Cage had been off loaded and checked by BSL however link spacing error missed.
| 02SL - Stations (LUL) | Cxxx-NCR-000571 | NCR | Cubes not stored correctly following removal from mould |  | Contr |  | VID - Victoria Dock Portal (Central) |  | 2013-06-28 | 2013-06-21 11:02 | -7 | 2013-05-13 | Geotechnical Engineering - Concrete - Bored Pile | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | The concrete cubes for Pile N154 were taken on saturday 20th April 2013. The cubes were observed being stored out of their cube moulds but not in the cube tank on Monday 22nd April.
| 02SL - Stations (LUL) | Cxxx-NCR-000572 | NCR | Failed weld following restressing of DLR tracks |  | Contr |  | VID - Victoria Dock Portal (Central) |  | 2013-07-12 | 2013-07-02 12:23 | -10 | 2013-05-13 | Track - Welding | 500 |  | Material | Rework |  | Complete |  | Completed |  | Following restressing of the DLR tracks on the weekend of 4th and 5th May 2013, a weld installed following restressing of the DLR tracks failed.
| 02SL - Stations (LUL) | Cxxx-NCR-000580 | NCR | No Earthing Electrodes in Pile N104 |  | Contr |  | VID - Victoria Dock Portal (Central) |  | 2013-06-28 | 2013-06-24 15:35 | -4 | 2013-05-23 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Repair |  | Complete |  | Completed |  | On 17 May 2013 Pile N104 was installed without earthing electrodes installed.
| 02SL - Stations (LUL) | Cxxx-NCR-000582 | NCR | Secant Pile N070 - Concrete Loss |  | Crossrail | XRL | VID - Victoria Dock Portal (Central) |  | 2013-12-06 | 2013-12-06 09:17 | 0 | 2013-05-23 | Geotechnical Engineering - Concrete - Bored Pile | 1000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Reported on the 29/04/2013 that an additional 9.7m3 of concrete was during construction of the bored pile. Refer Pile Record attached for additional information.
| 02SL - Stations (LUL) | Cxxx-NCR-000583 | NCR | Secant Pile N078 - Concrete Loss |  | Crossrail | XRL | VID - Victoria Dock Portal (Central) |  | 2013-12-06 | 2013-12-06 10:40 | 0 | 2013-05-23 | Geotechnical Engineering - Concrete - Bored Pile | 1000 |  |  | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Reported on the 03/05/2013 that an additional 8.2m3 of concrete was during construction of the bored pile. Refer Pile Record attached for additional information.
| 02SL - Stations (LUL) | Cxxx-NCR-000586 | NCR | Inclinometer IE00011 installed to the incorrect depth |  | Contr |  | VID - Victoria Dock Portal (Central) |  | 2013-06-28 | 2013-06-17 15:28 | -11 | 2013-05-24 | Geotechnical Engineering - Geotechnical Monitoring | 500 |  | Workmanship | Rework |  | Complete |  | Completed |  | The sensors have been installed in a string at 3m interval depth. This has resulted in the lowest sensor being at a depth of 84.286. The borehole and casing have been installed to the correct depth.
| 02SL - Stations (LUL) | Cxxx-NCR-000588 | NCR | Unapproved concrete mix used in LDA piles |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2013-09-06 | 2013-09-04 09:18 | -2 | 2013-05-24 | Geotechnical Engineering - Concrete - Bored Pile | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | In the following LDA piles and amended mix was used containing a retarder. 70, 130, 74, 122, 68, 78, 72, 126, 80, 114, 76, 124, 88, 110, 120, 106, 90, 118, 100, 62, 84, 94, 112, 44, 104, 54, 96, 86, 46, 102, 38, 64, 92, 108, 28, 50.
| 02SL - Stations (LUL) | Cxxx-NCR-000589 | NCR | Material changed without following the correct approval procedure |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2013-08-01 | 2013-08-06 09:36 | 5 | 2013-05-24 | Geotechnical Engineering - Concrete - Bored Pile | 500 |  | System Defect | Rework | 4 (0.5-3k) | Complete |  | Completed |  | The concrete mix for the LDA piles in the secant piled wall was amended by the subcontarctor without obtaining the approval of __ or Crossrail
| 02SL - Stations (LUL) | Cxxx-NCR-000594 | NCR | Unapproved concrete mix used in LDA piles |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2013-09-06 | 2013-09-04 09:26 | -2 | 2013-06-04 | Geotechnical Engineering - Concrete - Bored Pile | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | In the following LDA piles and amended mix was used containing a retarder. 58 and 82. Note - these piles should have been included on NCR 588 but were ommitted in error.
| 02SL - Stations (LUL) | Cxxx-NCR-000595 | NCR | Flash set of concrete during placement in Bored LDA pile |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2014-09-26 | 2014-10-30 16:48 | 34 | 2013-06-06 | Geotechnical Engineering - Concrete - Bored Pile | 500 |  | Material | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | During concreting, as the casing was being extracted, the concrete underwent a flash set. As a result, the reinforcement cage lifted with the casing by approximately 600mm. In addition, as a result of the flash set, there is not confidence that the concrete flowed adequately into the void left by the casing. This may have resulted in the pile not being to the correct diameter along it's full length.
| 02SL - Stations (LUL) | Cxxx-NCR-000599 | NCR | Earth electrode bars not installed in specified piles |  | Contr |  | VID - Victoria Dock Portal (Central) |  | 2013-07-12 | 2013-07-01 10:06 | -11 | 2013-06-19 | Geotechnical Engineering - Concrete - Bored Pile | 500 |  | Material | Rework |  | Complete |  | Completed |  | The following piles have been installed without the earth electrodes present: N62, N76, N90, N118, N132, N146 and N160. Note N104 also affected but covered under NCR 580.
| 02SL - Stations (LUL) | Cxxx-NCR-000600 | NCR | Reinforcement cages delivered with spacer bars damaged |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2013-07-31 | 2013-07-29 15:00 | -2 | 2013-06-24 | Geotechnical Engineering - Concrete - Bored Pile | 500 |  | Material | Repair | 4 (0.5-3k) | Complete |  | Completed |  | The cages delivered for piles S158 and S166 had a number of damaged spacers noted during a routine inspection prior to use. The pile cage for Pile S172 was observed to have some damaged spacers as it was being installed.
| 02SL - Stations (LUL) | Cxxx-NCR-000601 | NCR | Unapproved material used to backfill investigation boreholes |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2013-07-31 | 2013-07-30 16:52 | -1 | 2013-06-18 | Geotechnical Engineering - Ground Investigation | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | In error, the first 2 No. Boreholes backfilled used a Bentonite / Cement mix instead of the GM10 grout.
| 02SL - Stations (LUL) | Cxxx-NCR-000602 | NCR | DLR tracks not installed to agreed design alignment |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2015-11-30 | 2017-02-13 14:24 | 441 | 2013-06-10 | Track - Track General | 190000 |  | Workmanship | Rework | 1 (>60k) | Complete | Discipline/Workmanship - Worker not correctly instructed | Completed |  | During lifting and slewing of the tracks to the alignment instructed under PMI 121 (Possession EP6 – Easter 2013) two issues were encountered, as follows: 1, Incorrect programming of the tamper’s computer over lifted a section of the track above the values stated in the design. 2, The tamping machine could not position and compact the ballast under the sleepers to the required line and level of the design and DLR Standard ES401 construction tolerances. As a result, the current constructed track alignment between Royal Victoria and Custom House stations is not in accordance with the design alignment instructed under PMI 121.
| 02SL - Stations (LUL) | Cxxx-NCR-000606 | NCR | Conductor rail to sleeper fixings working loose |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2013-07-15 | 2013-07-16 12:14 | 1 | 2013-06-24 | Track - Track General | 30000 |  | Workmanship | Rework | 2 (6-60k) | Complete |  | Completed |  | During an inspection it has been noted that a number of fixings appear to have worked loose such that they are no longer to the required torque. This appears to have affected approximately 30% of the installed fixings
| 02SL - Stations (LUL) | Cxxx-NCR-000624 | NCR | Use of unapproved concrete mix due to plant breakdown |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2013-09-13 | 2013-09-10 14:08 | -3 | 2013-07-08 | Geotechnical Engineering - Concrete - Bored Pile | 1000 |  | Equipment Breakdown | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Use of unapproved materials | Completed |  | Following a plant breakdown at s Silvertown Plant discussions took place between __ and CRL where it was proposed to use s Greenwich Plant to supply concrete for the female piles until the Silvertown Plant was repaired. The mix design for Greenwich is identical except for the source of the concrete sand which was from an alternative source. In view of the criticality of the programme it was agreed that Greenwich Plant could be used as an interim measure subject to shrinkage tests being undertaken and demonstration of the concrete meeting the required strengths. It was accepted that the use of the concrete would proceed in advance of recieving acceptance of the MCR for the mix and an NCR raised. The piles cast with the concrete from Greenwich are: S87, S89, S95, S97, S101, S103, S105, S131, S133, S137 and S145
| 02SL - Stations (LUL) | Cxxx-NCR-000627 | NCR | Inclinometer installed to incorrect depth |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2013-09-13 | 2013-07-24 16:13 | -51 | 2013-07-16 16:13 | Civil - Geotechnical Engineering | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Inclinometer IM00002 should have been installed to a depth of 5m below the secant pile toe (i.e. to a depth of 77m ATD. The inclinometer has actually been installed to a depth of 77.694m ATD (i.e. 694mm too high)
| 02SL - Stations (LUL) | Cxxx-NCR-000628 | NCR | Pile cage installed without earth electrode incorporated |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2013-09-06 | 2013-09-06 14:18 | 0 | 2013-07-19 13:11 | Civil - Geotechnical Engineering | 2000 |  | Material | Repair | 4 (0.5-3k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | The pile cage for Pile S132 did not have the 2 No. 32mm earth electrode bars incorporated.
| 02SL - Stations (LUL) | Cxxx-NCR-000629 | NCR | Pile reinforcement damaged during pile breakdown |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2013-09-27 | 2013-08-22 16:23 | -36 | 2013-07-23 12:51 | Civil - Civil Engineering General | 500 |  | Damaged | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During breakdown of pile S42 some of the Pile reinforcement has been damaged.
| 02SL - Stations (LUL) | Cxxx-NCR-000630 | NCR | Pile reinforcement damaged during pile breakdown |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2013-09-27 | 2013-08-21 16:34 | -37 | 2013-07-23 17:06 | Civil - Civil Engineering General | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During breakdown of pile S44, some of the Pile reinforcement has been damaged.
| 02SL - Stations (LUL) | Cxxx-NCR-000631 | NCR | void in pile N32 |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2013-10-11 | 2013-10-10 16:34 | -1 | 2013-07-31 16:38 | Civil - Civil Engineering General | 1500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Contamination | Completed |  | On excavation of pile N32 for pile breakdown a void has been exposed below pile cut-off level. See attached sketch for details.
| 02SL - Stations (LUL) | Cxxx-NCR-000632 | NCR | Pile reinforcement damaged during pile breakdown |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2013-09-27 | 2013-08-14 16:33 | -44 | 2013-08-06 17:59 | Civil - Civil Engineering General | 500 |  | Damaged | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During breakdown of pile S52, 1no. pile reinforcement has been damaged
| 02SL - Stations (LUL) | Cxxx-NCR-000633 | NCR | De-bonding below pile cut off level |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2013-10-11 | 2013-10-11 11:40 | 0 | 2013-08-06 11:54 | Civil - Geotechnical Engineering | 5000 |  | Workmanship | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Contamination | Completed |  | Debonding sleeves enbedded concrete below cut-off level of secant pile wall.
| 02SL - Stations (LUL) | Cxxx-NCR-000634 | NCR | Bent pile cage reinforcement bars |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2013-08-22 | 2013-08-21 16:43 | -1 | 2013-08-08 18:21 | Civil - Civil Engineering General | 1000 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During pile break down, 2no pile reinforcement bars were found to have been bent within pile number N42. Please see attached photos
| 02SL - Stations (LUL) | Cxxx-NCR-000635 | NCR | Cutting out of the GFRP pile reinforcement at the Head Wall during the pile breakdown |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2013-09-27 | 2013-09-06 09:48 | -21 | 2013-08-14 14:32 | Civil - Civil Engineering General | 5000 |  | Planning | Rework | 3 (3-6k) | Complete |  | Completed |  | The Contractor is required to saw cut across the pile at cut off level to prevent damage to the GFRP reinforcement below. This does not meet the requirement of the Works Information which shows the pile reinforcement embedded into the capping beam.
| 02SL - Stations (LUL) | Cxxx-NCR-000636 | NCR | Pile reinforcement out of tolerance ( piles S22,S24,S26,S34,S36,S38,S42,S44,S46) |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2013-09-30 | 2013-08-22 16:47 | -39 | 2013-08-16 16:09 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The reinforcement of secant pile numbers S22, S24, S26, S34, S36, S38, S42, S44, S46 are out of the allowed tolerance of 75mm and 115mm
| 02SL - Stations (LUL) | Cxxx-NCR-000637 | NCR | Pile S85 damaged below cut off level |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2013-09-30 | 2013-09-27 10:08 | -3 | 2013-08-19 09:41 | Civil - Civil Engineering General | 1000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Pile S85 has been damaged below cut off level whilst undertaking pile break down
| 02SL - Stations (LUL) | Cxxx-NCR-000638 | NCR | Earth bar connection incorrectly completed within capping beam (Piles N22 - N46) |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2013-09-30 | 2013-08-27 17:37 | -34 | 2013-08-22 13:48 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The T12 earth bar within the capping beam from Pile N22 to Pile N46 has not been connected with a threaded coupler as per the design detail.
| 02SL - Stations (LUL) | Cxxx-NCR-000639 | NCR | Excess cover to capping beam reinforcement at Pile S8 |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2013-09-30 | 2013-09-02 10:14 | -28 | 2013-08-29 11:43 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Locally to Pile S8, the cover to the reinforcement exceeds the design range of 40mm to 80mm. The maximum cover in this location is 90mm.
| 02SL - Stations (LUL) | Cxxx-NCR-000640 | NCR | Inadequate pile rebar anchorage into capping beam (Pile N006 and N014) |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2013-10-19 | 2013-10-18 09:47 | -1 | 2013-08-30 17:15 | Civil - Civil Engineering General | 750 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Reinfocement to Pile N006 and N014 were installed at levels short of the 800mm minimum requirment for anchorage into the capping beam
| 02SL - Stations (LUL) | Cxxx-NCR-000641 | NCR | Inadequate pile rebar anchorage into capping beam (Pile N034 and N096) |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2013-10-01 | 2013-09-27 09:40 | -4 | 2013-09-03 18:08 | Civil - Civil Engineering General | 1000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Reinfocement to Pile N034 and N096 were installed at levels short of the 800mm minimum requirment for anchorage into the capping beam ( N034 is 40mm short and N096 is 102mm short)
| 02SL - Stations (LUL) | Cxxx-NCR-000642 | NCR | Inadequate pile rebar anchorage into capping beam (Pile number S78) |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2013-10-30 | 2013-10-23 10:23 | -7 | 2013-09-04 15:36 | Civil - Civil Engineering General | 1000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Reinfocement to Pile number S78 was installed at levels short of the 800mm minimum requirment for anchorage into the capping beam (S078 - short by 50mm)
| 02SL - Stations (LUL) | Cxxx-NCR-000643 | NCR | Overbreak of Pile number S108 |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2013-10-30 | 2013-10-23 10:29 | -7 | 2013-09-04 16:20 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During pile break down, a section of pile S108 (400x400x 49 deep) was broken below the cut off level
| 02SL - Stations (LUL) | Cxxx-NCR-000644 | NCR | Capping beam concrete cover out of tolerance of 40mm - 80mm |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2013-10-30 | 2013-10-23 10:35 | -7 | 2013-09-04 17:00 | Civil - Civil Engineering General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | To achive the minimum cover of 40mm to the capping beam rebar between pile numbers N46 to N70, the construction of the shuttering resulted in an excess cover of 85mm at the location of pile N60.
| 02SL - Stations (LUL) | Cxxx-NCR-000645 | NCR | PVG0005 not installed to correct depth |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2013-11-07 | 2013-10-30 14:57 | -8 | 2013-09-09 15:37 | Geotechnical Engineering - Geotechnical Monitoring | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | PVG0005 has been installed at a depth of 95m ATD. During installation the push-in CPTU probe could not penetrate the ground past 95mATD. There was no time left during possession to be able to move rig and start again.
| 02SL - Stations (LUL) | Cxxx-NCR-000646 | NCR | Pile S039 Cut off below lower tolerance limit |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2013-10-25 | 2013-10-22 16:03 | -3 | 2013-09-16 16:42 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During a surveillance of the pile breakdown activities, 3 No piles were checked for cut off level. Pile S039 was found to be cut off to a maximum level of 99.907mATD. The allowable range (including tolerances) is 99.975mATD to 99.925mATD. This pile is outside the allowable tolerance.
| 02SL - Stations (LUL) | Cxxx-NCR-000647 | NCR | Piles N088, N089, N091 and N093 Cut off below lower tolerance limit |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2013-10-25 | 2013-10-18 09:53 | -7 | 2013-09-16 17:12 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Following completion of as-built surveys on cut down piles, Piles N088, N089, N091 and N093 were found to be cut off to levels outside the allowable range (including tolerances) of 99.975mATD to 99.925mATD. The as-built survey record for these piles is attached
| 02SL - Stations (LUL) | Cxxx-NCR-000648 | NCR | Piles N100, N101, N102 and N104 Cut off below lower tolerance limit |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2013-10-25 | 2013-10-18 10:00 | -7 | 2013-09-16 17:19 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Following completion of as-built surveys on cut down piles, Piles N100, N101, N102 and N104 were found to be cut off to levels outside the allowable range (including tolerances) of 99.975mATD to 99.925mATD. The as-built survey record for these piles is attached
| 02SL - Stations (LUL) | Cxxx-NCR-000649 | NCR | Piles N106, N110, N111, N113, N117, N121, N122, N123, N125, N126 and N127 Cut off below lower tolerance limit |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2013-10-25 | 2013-10-18 10:07 | -7 | 2013-09-16 17:26 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Following completion of as-built surveys on cut down piles, Piles N106, N110, N111, N113, N117, N121, N122, N123, N125, N126 and N127 were found to be cut off to levels outside the allowable range (including tolerances) of 99.975mATD to 99.925mATD. The as-built survey record for these piles is attached
| 02SL - Stations (LUL) | Cxxx-NCR-000650 | NCR | Piles S099 and S104 cut off below lower tolerance limit |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2013-10-25 | 2013-10-23 10:09 | -2 | 2013-09-16 17:33 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Following completion of as-built surveys on cut down piles, Piles S099 and S104 were found to be cut off to levels outside the allowable range (including tolerances) of 99.975mATD to 99.925mATD. The as-built survey record for these piles is attached
| 02SL - Stations (LUL) | Cxxx-NCR-000651 | NCR | Pile N124 - Insufficient reinforcement embedment into capping beam |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2013-10-25 | 2013-10-23 10:15 | -2 | 2013-09-17 09:26 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Following the carrying out of an as built survey of the reinforcement cage levels following pile breakdown it has been noted that in Pile N124, the reinforcement level only provides 773mm embedment into the capping beam concrete. A minimum of 800mm is required.
| 02SL - Stations (LUL) | Cxxx-NCR-000652 | NCR | Base Slab Pour B32 - Piles N006/008 - Pilecor boxout position outside tolerance |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2013-12-13 | 2013-12-12 15:58 | -1 | 2013-09-25 07:33 | Civil - Geotechnical Engineering | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Following survey, it has been identified that the pilecor boxouts in Piles N006 and N008 are lower than the tolerance position of +100mm / -50mm.
| 02SL - Stations (LUL) | Cxxx-NCR-000653 | NCR | Base Slab Pour B31 - Piles N014/016 and S018 - Pilecor boxout position outside tolerance |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2013-12-20 | 2013-12-19 14:44 | -1 | 2013-09-25 07:34 | Civil - Geotechnical Engineering | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Following survey, it has been identified that the pilecor boxouts in Piles N014, N016 and S018 are lower than the tolerance position of +100mm / -50mm.
| 02SL - Stations (LUL) | Cxxx-NCR-000654 | NCR | Base Slab Pour B30 - Piles N026/N028/N030 and S020/S022 - Pilecor boxout position outside tolerance |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2014-01-16 | 2014-01-13 11:17 | -3 | 2013-09-25 07:35 | Civil - Geotechnical Engineering | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Following survey, it has been identified that the pilecor boxouts in Piles N026/N028/N030 and S020/S022 are lower than the tolerance position of +100mm / -50mm.
| 02SL - Stations (LUL) | Cxxx-NCR-000655 | NCR | Base Slab Pour B29 - Piles N034 and S040 - Pilecor boxout position outside tolerance |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2014-01-24 | 2014-01-23 14:35 | -1 | 2013-09-25 07:36 | Civil - Geotechnical Engineering | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Following survey, it has been identified that the pilecor boxouts in Piles N034 and S040 are lower than the tolerance position of +100mm / -50mm.
| 02SL - Stations (LUL) | Cxxx-NCR-000656 | NCR | Base Slab Pour B27 - Piles S058/060 - Pilecor boxout position outside tolerance |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2014-02-07 | 2014-02-06 14:12 | -1 | 2013-09-25 07:37 | Civil - Geotechnical Engineering | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Following survey, it has been identified that the pilecor boxouts in Piles S058 and N060 are lower than the tolerance position of +100mm / -50mm.
| 02SL - Stations (LUL) | Cxxx-NCR-000657 | NCR | Base Slab Pour B26 - Piles S070 - Pilecor boxout position outside tolerance |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2014-02-14 | 2014-02-13 09:07 | -1 | 2013-09-25 07:38 | Civil - Geotechnical Engineering | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Following survey, it has been identified that the pilecor boxouts in Pile S070 are lower than the tolerance position of +100mm / -50mm.
| 02SL - Stations (LUL) | Cxxx-NCR-000658 | NCR | Base Slab Pour B25 - Piles N072/078/082 and S072/078/084 - Pilecor boxout position outside tolerance |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2014-07-25 | 2014-07-22 11:34 | -3 | 2013-09-25 07:39 | Civil - Geotechnical Engineering | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Following survey, it has been identified that the pilecor boxouts in Piles N072/078/082 and S072/078/084 are lower than the tolerance position of +100mm / -50mm.
| 02SL - Stations (LUL) | Cxxx-NCR-000659 | NCR | Drainage Sump Base Pour - Piles N086 and S084/086 - Pilecor boxout position outside tolerance |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2014-05-23 | 2014-04-11 15:44 | -42 | 2013-09-25 07:42 | Civil - Geotechnical Engineering | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Following survey, it has been identified that the pilecor boxouts in Piles N086, S084 and S086 are lower than the tolerance position of +100mm / -50mm.
| 02SL - Stations (LUL) | Cxxx-NCR-000660 | NCR | Base Slab Pour B24 - Piles N086 and S086 - Pilecor boxout position outside tolerance |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2014-07-25 | 2014-07-17 14:30 | -8 | 2013-09-25 07:45 | Civil - Geotechnical Engineering | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Following survey, it has been identified that the pilecor boxouts in Piles N086 and S086 are lower than the tolerance position of +100mm / -50mm.
| 02SL - Stations (LUL) | Cxxx-NCR-000661 | NCR | Base Slab Pour B23 - Piles N096/108 and S096/098/100/106 - Pilecor boxout position outside tolerance |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2014-06-27 | 2014-06-23 15:18 | -4 | 2013-09-25 07:47 | Civil - Geotechnical Engineering | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Following survey, it has been identified that the pilecor boxouts in Piles N096/108 and S096/098/100/106 are lower than the tolerance position of +100mm / -50mm.
| 02SL - Stations (LUL) | Cxxx-NCR-000662 | NCR | Base Slab Pour B22 - Piles N114 and S112 - Pilecor boxout position outside tolerance |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2014-06-27 | 2014-06-25 10:12 | -2 | 2013-09-25 07:49 | Civil - Geotechnical Engineering | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Following survey, it has been identified that the pilecor boxouts in Piles N114 and S112 are lower than the tolerance position of +100mm / -50mm.
| 02SL - Stations (LUL) | Cxxx-NCR-000663 | NCR | Pile S12 - Concrete has failed to achieve the required strength at 28 days |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2013-11-29 | 2013-11-29 10:56 | 0 | 2013-09-30 16:16 | Civil - Geotechnical Engineering | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Verification Problems - Other | Completed |  | The concrete deliverd on ticket number 65250015 and used in Pile S12 has failed to achieve the required strength (40N/mm) at 28 days. Tests on the spare cube at 56 days have also failed to achieve the required strength.
| 02SL - Stations (LUL) | Cxxx-NCR-000664 | NCR | Base Slab Pour B21 - Piles N122/124 and S120/122/124/126- Pilecor boxout position outside tolerance |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2014-06-27 | 2014-06-26 11:30 | -1 | 2013-09-25 16:30 | Civil - Geotechnical Engineering | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Following survey, it has been identified that the pilecor boxouts in Piles N122/124 and S120/122/124/126 are lower than the tolerance position of +100mm / -50mm.
| 02SL - Stations (LUL) | Cxxx-NCR-000665 | NCR | Base Slab Pour B20 - Piles N130 and S130/134 - Pilecor boxout position outside tolerance |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2014-06-20 | 2014-06-20 09:01 | 0 | 2013-09-25 16:47 | Civil - Geotechnical Engineering | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Following survey, it has been identified that the pilecor boxouts in Piles N130 and S130/134 are lower than the tolerance position of +100mm / -50mm.
| 02SL - Stations (LUL) | Cxxx-NCR-000666 | NCR | Base Slab Pour B19 - Piles N144 and S138 - Pilecor boxout position outside tolerance |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2014-06-20 | 2014-06-19 13:23 | -1 | 2013-09-25 17:00 | Civil - Geotechnical Engineering | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Following survey, it has been identified that the pilecor boxouts in Piles N144 and S138 are lower than the tolerance position of +100mm / -50mm.
| 02SL - Stations (LUL) | Cxxx-NCR-000667 | NCR | Base Slab Pour B18 - Pile N156 - Pilecor boxout position outside tolerance |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2014-06-20 | 2014-06-11 13:59 | -9 | 2013-09-25 17:12 | Civil - Geotechnical Engineering | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Following survey, it has been identified that the pilecor boxouts in Piles N156 are lower than the tolerance position of +100mm / -50mm.
| 02SL - Stations (LUL) | Cxxx-NCR-000668 | NCR | Base Slab Pour B17 - Piles N160 and S160/162 - Pilecor boxout position outside tolerance |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2014-06-20 | 2014-06-18 16:44 | -2 | 2013-09-25 17:18 | Civil - Geotechnical Engineering | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Following survey, it has been identified that the pilecor boxouts in Piles N160 and S160/162 are lower than the tolerance position of +100mm / -50mm.
| 02SL - Stations (LUL) | Cxxx-NCR-000669 | NCR | Base Slab Pour B16 - Piles N168/172/174 - Pilecor boxout position outside tolerance |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2014-06-20 | 2014-06-19 13:27 | -1 | 2013-09-25 17:25 | Civil - Geotechnical Engineering | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Following survey, it has been identified that the pilecor boxouts in Piles N168/172/174 are lower than the tolerance position of +100mm / -50mm.
| 02SL - Stations (LUL) | Cxxx-NCR-000670 | NCR | North Lining wall Pour B32 - Piles N006/008 - Pilecor boxout position outside tolerance |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2015-09-25 | 2015-08-18 13:36 | -38 | 2013-09-26 07:36 | Civil - Geotechnical Engineering | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Following survey, it has been identified that the pilecor boxouts in Piles N006 and N008 are lower than the tolerance position of +100mm / -50mm.
| 02SL - Stations (LUL) | Cxxx-NCR-000671 | NCR | South Lining Wall Pour B26 - Pile S060 - Pilecor boxout position outside tolerance |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2015-02-06 | 2014-10-08 13:47 | -121 | 2013-09-26 07:41 | Civil - Geotechnical Engineering | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | Following survey, it has been identified that the pilecor boxouts in Pile S060 is lower than the tolerance position of +100mm / -50mm.
| 02SL - Stations (LUL) | Cxxx-NCR-000672 | NCR | North Lining Wall Pour B31 - Piles N014/016 - Pilecor boxout position outside tolerance |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2015-09-25 | 2015-07-29 16:40 | -58 | 2013-09-26 07:44 | Civil - Geotechnical Engineering | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Following survey, it has been identified that the pilecor boxouts in Piles N014 and N016 are lower than the tolerance position of +100mm / -50mm.
| 02SL - Stations (LUL) | Cxxx-NCR-000673 | NCR | South Lining Wall Pour B31 - Pile S018 - Pilecor boxout position outside tolerance |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2015-09-25 | 2015-09-10 11:53 | -15 | 2013-09-26 07:47 | Civil - Geotechnical Engineering | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Following survey, it has been identified that the pilecor boxouts in Pile S018 is lower than the tolerance position of +100mm / -50mm.
| 02SL - Stations (LUL) | Cxxx-NCR-000674 | NCR | North Lining Wall Pour B30 - Pile N026 - Pilecor boxout position outside tolerance |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2015-09-25 | 2015-07-17 10:59 | -70 | 2013-09-26 07:51 | Civil - Geotechnical Engineering | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Following survey, it has been identified that the pilecor boxouts in Pile N026 is lower than the tolerance position of +100mm / -50mm.
| 02SL - Stations (LUL) | Cxxx-NCR-000675 | NCR | South Lining Wall Pour B30 - Pile S022 - Pilecor boxout position outside tolerance |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2015-09-25 | 2015-09-10 11:54 | -15 | 2013-09-26 07:58 | Civil - Geotechnical Engineering | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Following survey, it has been identified that the pilecor boxouts in Pile S022 is lower than the tolerance position of +100mm / -50mm.
| 02SL - Stations (LUL) | Cxxx-NCR-000676 | NCR | North Lining Wall Pour B29 - Pile N034 - Pilecor boxout position outside tolerance |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2015-02-06 | 2015-01-05 11:03 | -32 | 2013-09-26 08:01 | Civil - Geotechnical Engineering | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Following survey, it has been identified that the pilecor boxouts in Pile N034 is lower than the tolerance position of +100mm / -50mm.
| 02SL - Stations (LUL) | Cxxx-NCR-000677 | NCR | Piles S106, S110, S120 and S122 - Insufficient reinforcement embedment into capping beam |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2013-11-15 | 2013-11-08 12:16 | -7 | 2013-09-26 09:53 | Civil - Geotechnical Engineering | 1000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Not Defined | Completed |  | Following the carrying out of an as built survey of the reinforcement cage levels following pile breakdown it has been noted that in the following piles, the reinforcement level provides insufficient embedment into the capping beam concrete. A minimum of 800mm is required. S106 762mm S110 730mm S120 715mm S122 778mm
| 02SL - Stations (LUL) | Cxxx-NCR-000678 | NCR | Piles S106, 110, 115 and 122 Cut off below lower tolerance limit |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2013-11-15 | 2013-11-08 12:24 | -7 | 2013-09-26 10:00 | Civil - Civil Engineering General | 1000 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | Following completion of as-built surveys on cut down piles, Piles S106, 110, 115 and 122 were found to be cut off to levels outside the allowable range (including tolerances) of 99.975mATD to 99.925mATD. The as-built survey record for these piles is attached
| 02SL - Stations (LUL) | Cxxx-NCR-000679 | NCR | CH 85834 - 85836 North Wall - Concrete overbreak |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2013-12-06 | 2013-12-06 09:59 | 0 | 2013-10-07 17:17 | Civil - Geotechnical Engineering | 1000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Following excavation of the portal, it has been observed that there is a section of overbreak on the pile construction between CH 85834 and CH 85836 as follows: Height of overbreak 0.8m Depth out from pile face 1.25m Length along pile wall 3m level of top of overbreak 98.5m ATD
| 02SL - Stations (LUL) | Cxxx-NCR-000680 | NCR | CH 85828 - 85829 North Wall - Concrete overbreak |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2014-01-31 | 2014-01-24 16:11 | -7 | 2013-12-05 07:37 | Civil - Geotechnical Engineering | 1500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Following excavation of the portal, it has been observed that there is a section of overbreak on the pile construction between CH 85828 and CH 85829 as follows: Height of overbreak 0.4m Depth out from pile face 0.6m Length along pile wall 1.5m level of top of overbreak 98.0m ATD
| 02SL - Stations (LUL) | Cxxx-NCR-000681 | NCR | CH 85818 - 85822 North Wall - Concrete overbreak |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2013-12-06 | 2013-12-06 10:19 | 0 | 2013-10-07 17:21 | Civil - Geotechnical Engineering | 1000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Following excavation of the portal, it has been observed that there is a section of overbreak on the pile construction between CH 85818 and CH 85822 as follows: Height of overbreak 0.6m Depth out from pile face 2m Length along pile wall 4m level of top of overbreak 98.0m ATD
| 02SL - Stations (LUL) | Cxxx-NCR-000682 | NCR | CH 85820 - 85822 South Wall - Concrete overbreak |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2013-12-06 | 2013-12-06 10:52 | 0 | 2013-10-07 17:23 | Civil - Geotechnical Engineering | 1000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Following excavation of the portal, it has been observed that there is a section of overbreak on the pile construction between CH 85820 and CH 85822 as follows: Height of overbreak 0.2m Depth out from pile face 0.7m Length along pile wall 1.5m level of top of overbreak 97.5m ATD
| 02SL - Stations (LUL) | Cxxx-NCR-000683 | NCR | CH 85832 - 85834 South Wall - Concrete overbreak |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2013-12-06 | 2013-12-06 11:01 | 0 | 2013-10-17 08:00 | Civil - Geotechnical Engineering | 1000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Following excavation of the portal, it has been observed that there is a section of overbreak on the pile construction between CH 85832 and CH 85834 as follows: Height of overbreak 0.8m Depth out from pile face 1.3m Length along pile wall 2m level of top of overbreak 98.0m ATD
| 02SL - Stations (LUL) | Cxxx-NCR-000684 | NCR | West Headwall Piles W15 - W17 - Concrete overbreak |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2013-12-06 | 2013-12-06 11:11 | 0 | 2013-10-07 17:31 | Civil - Geotechnical Engineering | 1000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Following excavation of the portal, it has been observed that there is a section of overbreak on the pile construction between Pile W15 and Pile W17 as follows: Height of overbreak 0.5m Depth out from pile face 1.0m Length along pile wall 2.0m level of top of overbreak 97.8m ATD
| 02SL - Stations (LUL) | Cxxx-NCR-000685 | NCR | CH 85801 - 85803 North Wall - Concrete overbreak |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2013-12-06 | 2013-12-06 11:17 | 0 | 2013-10-07 17:37 | Civil - Geotechnical Engineering | 1000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Following excavation of the portal, it has been observed that there is a section of overbreak on the pile construction between CH 85801 and CH 85803 as follows: Height of overbreak 0.7m Depth out from pile face 0.8m Length along pile wall 2.0m level of top of overbreak 97.7m ATD
| 02SL - Stations (LUL) | Cxxx-NCR-000686 | NCR | CH 85804 - 85806 North Wall - Concrete overbreak |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2013-12-06 | 2013-12-06 11:24 | 0 | 2013-10-07 17:42 | Civil - Geotechnical Engineering | 1000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Following excavation of the portal, it has been observed that there is a section of overbreak on the pile construction between CH 85804 and CH 85806 as follows: Height of overbreak 0.6m Depth out from pile face 0.5m Length along pile wall 1.5m level of top of overbreak 97.7m ATD
| 02SL - Stations (LUL) | Cxxx-NCR-000687 | NCR | CH 85812 - 85814 North Wall - Concrete overbreak |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2013-12-06 | 2013-12-06 11:34 | 0 | 2013-10-07 17:46 | Civil - Geotechnical Engineering | 1000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Following excavation of the portal, it has been observed that there is a section of overbreak on the pile construction between CH 85812 and CH 85814 as follows: Height of overbreak 0.6m Depth out from pile face 0.9m Length along pile wall 2.1m level of top of overbreak 98.3m ATD
| 02SL - Stations (LUL) | Cxxx-NCR-000688 | NCR | CH 85831 - 85833 North Wall - Concrete overbreak |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2013-12-06 | 2013-12-06 11:43 | 0 | 2013-10-08 07:42 | Civil - Geotechnical Engineering | 1000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Following excavation of the portal, it has been observed that there is a section of overbreak on the pile construction between CH 85831 and CH 85833 as follows: Height of overbreak 1.1m Depth out from pile face 1.1m Length along pile wall 2.0m level of top of overbreak 98.4m ATD
| 02SL - Stations (LUL) | Cxxx-NCR-000689 | NCR | CH 85842 - 85844 North Wall - Concrete overbreak |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2013-12-06 | 2013-12-06 11:52 | 0 | 2013-10-08 07:48 | Civil - Geotechnical Engineering | 1000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Following excavation of the portal, it has been observed that there is a section of overbreak on the pile construction between CH 85842 and CH 85844 as follows: Height of overbreak 0.5m Depth out from pile face 1.1m Length along pile wall 2.0m level of top of overbreak 97.8m ATD
| 02SL - Stations (LUL) | Cxxx-NCR-000690 | NCR | CH 85846 - 85848 North Wall - Concrete overbreak |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2013-12-13 | 2013-12-06 12:42 | -7 | 2013-10-08 07:55 | Civil - Geotechnical Engineering | 1000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Following excavation of the portal, it has been observed that there is a section of overbreak on the pile construction between CH 85846 and CH 85848 as follows: Height of overbreak 0.8m Depth out from pile face 2.3m Length along pile wall 1.3m level of top of overbreak 98.1m ATD
| 02SL - Stations (LUL) | Cxxx-NCR-000691 | NCR | CH 85838 - 85839 South Wall - Concrete overbreak |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2013-12-13 | 2013-12-06 12:50 | -7 | 2013-10-08 08:20 | Civil - Geotechnical Engineering | 1000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Following excavation of the portal, it has been observed that there is a section of overbreak on the pile construction between CH 85838 and CH 85839 as follows: Height of overbreak 0.5m Depth out from pile face 0.5m Length along pile wall 1.2m level of top of overbreak 98.7m ATD
| 02SL - Stations (LUL) | Cxxx-NCR-000692 | NCR | CH 85842 - 85843 South Wall - Concrete overbreak |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2013-12-13 | 2013-12-06 12:56 | -7 | 2013-10-08 08:30 | Civil - Geotechnical Engineering | 1000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Following excavation of the portal, it has been observed that there is a section of overbreak on the pile construction between CH 85842 and CH 85843 as follows: Height of overbreak 0.4m Depth out from pile face 0.4m Length along pile wall 1.1m level of top of overbreak 98.4m ATD
| 02SL - Stations (LUL) | Cxxx-NCR-000693 | NCR | CH 85844 - 85848 South Wall - Concrete overbreak |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2013-12-13 | 2013-12-06 13:02 | -7 | 2013-10-08 12:59 | Civil - Geotechnical Engineering | 1000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Following excavation of the portal, it has been observed that there is a section of overbreak on the pile construction between CH 85844 and CH 85848 as follows: Height of overbreak 0.8m Depth out from pile face 1.2m Length along pile wall 4.0m level of top of overbreak 98.5m ATD
| 02SL - Stations (LUL) | Cxxx-NCR-000694 | NCR | CH 85850 - 85851 South Wall - Concrete overbreak |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2013-12-13 | 2013-12-06 13:15 | -7 | 2013-10-08 13:06 | Civil - Geotechnical Engineering | 1000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Following excavation of the portal, it has been observed that there is a section of overbreak on the pile construction between CH 85850 and CH 85851 as follows: Height of overbreak 0.6m Depth out from pile face 0.5m Length along pile wall 1.2m level of top of overbreak 99.8m ATD
| 02SL - Stations (LUL) | Cxxx-NCR-000695 | NCR | Rain damage to capping beam pour surface finish - CH85929 - CH85953 - South |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2013-12-13 | 2013-11-27 15:14 | -16 | 2013-10-08 13:33 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Following pouring of the capping beam between Chainage 85929 and chainage 85953, rain has damaged the finished surface resulting in a substandard finish
| 02SL - Stations (LUL) | Cxxx-NCR-000696 | NCR | Poor concrete finish - Cappng Beam - CH85905 - 85929 |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2013-12-13 | 2013-12-12 12:15 | -1 | 2013-10-08 13:51 | Civil - Civil Engineering General | 750 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Poor concrete finish has been noted on the capping beam pour between CH85905 and 85929 on the south side of the portal. This includes excessive depth / diameter of blowholes
| 02SL - Stations (LUL) | Cxxx-NCR-000697 | NCR | Piles N154, N157, N159 and N167 cut off below lower tolerance limit |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2013-12-13 | 2013-11-18 17:00 | -25 | 2013-10-08 17:33 | Civil - Geotechnical Engineering | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Following completion of as-built surveys on cut down piles, Piles N154, N157, N159 and N167 were found to be cut off to levels outside the allowable range (including tolerances) of 99.975mATD to 99.925mATD. The as-built survey record for these piles is attached
| 02SL - Stations (LUL) | Cxxx-NCR-000698 | NCR | Pile N32 - Leakage at interface with Pile N33 |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2014-11-28 | 2014-08-15 10:39 | -105 | 2013-10-09 16:23 | Civil - Geotechnical Engineering | 1500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Following excavation of the portal, leakage at the interface between pile N32 and N33 has been identified. See attached photographs
| 02SL - Stations (LUL) | Cxxx-NCR-000699 | NCR | South Lining Wall Pour B29 - Pile S040 - Pilecor boxout position outside tolerance |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2015-02-06 | 2015-01-05 11:08 | -32 | 2013-10-15 17:49 | Civil - Geotechnical Engineering | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Following survey, it has been identified that the pilecor boxouts in Pile S040 are lower than the tolerance position of +100mm / -50mm.
| 02SL - Stations (LUL) | Cxxx-NCR-000700 | NCR | South Lining Wall Pour B27 - Piles S058/060 - Pilecor boxout position outside tolerance |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2015-02-06 | 2014-10-17 12:29 | -112 | 2013-10-15 17:53 | Civil - Geotechnical Engineering | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Following survey, it has been identified that the pilecor boxouts in Piles S058 and N060 are lower than the tolerance position of +100mm / -50mm.
| 02SL - Stations (LUL) | Cxxx-NCR-000701 | NCR | North Lining Wall Pour B25 - Piles N072/078/082 - Pilecor boxout position outside tolerance |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2014-09-19 | 2014-09-17 15:07 | -2 | 2013-10-17 07:40 | Civil - Geotechnical Engineering | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Following survey, it has been identified that the pilecor boxouts in Piles N072/078/082 are lower than the tolerance position of +100mm / -50mm.
| 02SL - Stations (LUL) | Cxxx-NCR-000702 | NCR | South Lining Wall Pour B25 - Piles S072/078/084 - Pilecor boxout position outside tolerance |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2014-10-31 | 2014-10-13 10:52 | -18 | 2013-10-17 07:43 | Civil - Geotechnical Engineering | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Following survey, it has been identified that the pilecor boxouts in Piles S072/078/084 are lower than the tolerance position of +100mm / -50mm.
| 02SL - Stations (LUL) | Cxxx-NCR-000703 | NCR | North Lining Wall Pour B24 - Pile N086 - Pilecor boxout position outside tolerance |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2014-10-03 | 2014-09-26 11:43 | -7 | 2013-10-17 07:46 | Civil - Geotechnical Engineering | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Following survey, it has been identified that the pilecor boxouts in Pile S086 is lower than the tolerance position of +100mm / -50mm.
| 02SL - Stations (LUL) | Cxxx-NCR-000704 | NCR | South Lining Wall Pour B24 - Pile S086 - Pilecor boxout position outside tolerance |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2014-10-03 | 2014-10-02 13:07 | -1 | 2013-10-17 07:50 | Civil - Geotechnical Engineering | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Following survey, it has been identified that the pilecor boxouts in Pile S086 is lower than the tolerance position of +100mm / -50mm.
| 02SL - Stations (LUL) | Cxxx-NCR-000705 | NCR | North Lining Wall Pour B23 - Piles N096/108 - Pilecor boxout position outside tolerance |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2014-10-17 | 2014-10-17 10:45 | 0 | 2013-10-17 07:54 | Civil - Geotechnical Engineering | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Following survey, it has been identified that the pilecor boxouts in Piles N096/108 are lower than the tolerance position of +100mm / -50mm.
| 02SL - Stations (LUL) | Cxxx-NCR-000706 | NCR | South Lining Wall Pour B23 - Piles S096/098/100/106 - Pilecor boxout position outside tolerance |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2014-10-17 | 2014-10-17 09:45 | 0 | 2013-10-18 07:42 | Civil - Geotechnical Engineering | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Following survey, it has been identified that the pilecor boxouts in Piles S096/098/100/106 are lower than the tolerance position of +100mm / -50mm.
| 02SL - Stations (LUL) | Cxxx-NCR-000723 | NCR | Water ingress through piles - S18/S19 joint, S21/S22 joint and S22/S23 joint |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2015-09-25 | 2015-08-18 13:41 | -38 | 2013-11-06 08:02 | Civil - Geotechnical Engineering | 1000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Following a survey, water ingress has been identified at the following pile positions: Joint between S18 and S19 Joint between S21 and S22 Joint between S22 and S23
| 02SL - Stations (LUL) | Cxxx-NCR-000724 | NCR | Water ingress through piles - S25/S26 joint and S29/S30 joint |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2015-09-25 | 2015-08-18 13:45 | -38 | 2013-11-06 08:09 | Civil - Geotechnical Engineering | 1000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Following a survey, water ingress has been identified at the following pile positions: Joint between S25 and S26 Joint between S29 and S30
| 02SL - Stations (LUL) | Cxxx-NCR-000725 | NCR | Water ingress through piles - S34/S35 joint |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2014-11-27 | 2014-08-15 10:37 | -104 | 2013-11-06 08:13 | Civil - Geotechnical Engineering | 1500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Following a survey, water ingress has been identified at the following pile position: Joint between S34 and S35
| 02SL - Stations (LUL) | Cxxx-NCR-000726 | NCR | Water ingress through piles - S51/S52 joint |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2014-11-07 | 2014-08-15 10:32 | -84 | 2013-11-06 08:16 | Civil - Geotechnical Engineering | 1500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Following a survey, water ingress has been identified at the following pile position: Joint between S51 and S52
| 02SL - Stations (LUL) | Cxxx-NCR-000727 | NCR | Water ingress through piles - S53/S54 joint and S56 |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2014-11-07 | 2014-08-15 10:34 | -84 | 2013-11-06 08:21 | Civil - Geotechnical Engineering | 1500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Following a survey, water ingress has been identified at the following pile positions: Joint between S53 and S54 Pile face S56
| 02SL - Stations (LUL) | Cxxx-NCR-000728 | NCR | Water ingress through piles - S60/S61 joint, S61/S62 joint and S62/S63 joint |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2014-11-07 | 2014-08-15 10:35 | -84 | 2013-11-06 08:30 | Civil - Geotechnical Engineering | 1500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Following a survey, water ingress has been identified at the following pile positions: Joint between S60 and S61 Joint between S61 and S62 Joint between S62 and S63
| 02SL - Stations (LUL) | Cxxx-NCR-000729 | NCR | Water ingress through piles - S69/S70 joint, S70/S71 joint, S71/S72 joint S72/S73 joint and pile S81 |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2014-09-26 | 2014-09-26 09:11 | 0 | 2013-11-06 08:37 | Civil - Geotechnical Engineering | 1500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Following a survey, water ingress has been identified at the following pile positions: Joint between S69 and S70 Joint between S70 and S71 Joint between S71 and S72 Joint between S72 and S73 Pile Face S81
| 02SL - Stations (LUL) | Cxxx-NCR-000730 | NCR | Water ingress through piles - S93/S94 joint and S94/S95 joint |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2014-09-26 | 2014-09-26 09:21 | 0 | 2013-11-06 08:48 | Civil - Geotechnical Engineering | 1500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Following a survey, water ingress has been identified at the following pile positions: Joint between S93 and S94 Joint between S94 and S95
| 02SL - Stations (LUL) | Cxxx-NCR-000731 | NCR | Modification to footbridge baseplates - works commenced without an MCR in place |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2013-12-13 | 2013-11-14 15:57 | -29 | 2013-11-08 07:59 | Structural Engineering - Steel Member | 500 |  | System Defect | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Lack of approval Code 1 procedures excessive | Completed |  | __ were instructed to carry out modifications to the temporary footbridge baseplate to accomodate services passing over the footbridge for Contract Cxxx. An MCR had been prepared and informally reviewed but not formally issued for acceptance. Works commenced to the modifications which involved welding of RSAs to the baseplate before this MCR was accepted.
| 02SL - Stations (LUL) | Cxxx-NCR-000732 | NCR | Pile N66 - Void around pile |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2014-01-31 | 2014-01-30 14:59 | -1 | 2013-11-13 18:27 | Civil - Geotechnical Engineering | 3000 |  | Material | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | A Void has been discovered in Pile N066 at approximately 95mATD during excavation of the portal box. This has been determined to be an annulus around the male pile extending from just below 97mATD and extends for at least 3m.
| 02SL - Stations (LUL) | Cxxx-NCR-000733 | NCR | Instrumentation data not being uploaded to UCIMS |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2013-12-20 | 2013-12-20 10:49 | 0 | 2013-11-13 18:34 | Surveying - Instrumentation and Monitoring | 500 |  | System Defect | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | It has been identified that some of the instrumentation data has not been uploaded onto UCIMS or the points have been referenced incorrectly as follows: - PVG5 is shown in the wrong place (located west of the TBM Reception Chamber), - PVG6 is not displayed. - Inpile inclinometers IE1, 3, 4, 5, 6, 8, 9 and 10 are not displayed. - Capping Beam Prisms RP8, 9, 10, 11, 12, 13 and 14 are not displayed. - 6 additonal levelling points along Vic Dock Road (LP1005, 1010, 1015, 1105, 1110 and 1115) are not displayed.
| 02SL - Stations (LUL) | Cxxx-NCR-000734 | NCR | Piles N143, N145, N146, N149, N151 and N152 cut off below lower tolerance limit |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2013-12-20 | 2013-11-22 17:27 | -28 | 2013-11-20 10:26 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Following completion of as-built surveys on cut down piles, Piles N143, N145, N146, N149, N151 and N152 were found to be cut off to levels outside the allowable range (including tolerances) of 99.975mATD to 99.925mATD.
| 02SL - Stations (LUL) | Cxxx-NCR-000735 | NCR | Pile N58 - Pilecor not found whilst excavating |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2015-02-06 | 2014-09-17 15:32 | -142 | 2013-12-03 17:33 | Civil - Geotechnical Engineering | 1500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Whilst excavating for the portal, the pilecor in PIle N58 has not been located in the expected position
| 02SL - Stations (LUL) | Cxxx-NCR-000736 | NCR | Excavation continued beyond agreed limit without further temporary works in place |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2014-01-31 | 2014-01-06 09:58 | -25 | 2013-12-11 15:39 | Civil - Excavation | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Misunderstand the definition of the requirement | Completed |  | FCD 666 allowed for localised over-dig to gain plant access under prop L15. This set a constraint that excavation could not go below 97.0mATD beyond where the waler had been grouted. On Sat 30th Nov it was noted that the excavation had extended slightly beyond this.
| 02SL - Stations (LUL) | Cxxx-NCR-000737 | NCR | Commencement of temporary waler beam installation without an approved MCR in place |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2014-01-31 | 2013-12-19 17:22 | -43 | 2013-12-11 15:52 | Materials - Approval | 500 |  | System Defect | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | Installation of the channels for the U Trough Waler beams commenced without an accepted MCR in place. The MCR had been submitted but CRL had not been given sufficient time to review before the works commenced
| 02SL - Stations (LUL) | Cxxx-NCR-000738 | NCR | Excavation in U Trough - CH86105 to 86120 |  | Crossrail | XRL | VID - Victoria Dock Portal (Central) |  | 2014-01-17 | 2014-01-13 16:40 | -4 | 2013-12-11 19:06 | Civil - Excavation | 500 |  | Supervision/Management | Repair | 4 (0.5-3k) | Complete | Personnel Error - Violation of requirement or procedure | Completed |  | Failure to notify Inspection/Intervention points associated with activities noted on ITP for U Trough Excavation and Propping (ref Cxxx-VIN-C-ITP-CR144_PT003-50088 Rev 3.0) for excavation works between CH86105 to 86120. Details as follows: - Activity 4.1.1: I&M installed and functioning: This is a Review Point for CRL and sign off on the associated Excavation Check Sheet prior to start of excavation. Furthermore, trigger limits have not been established for a number of monitoring points (references RP00023 & RP00024) which are within this area of works. Refer attached email for details. - Activity 4.1.3: Permit to Penetrate the Ground: This is a Witness Point for CRL and sign off on the associated Excavation Check Sheet prior to start of excavation.
| 02SL - Stations (LUL) | Cxxx-NCR-000739 | NCR | Non-Calibrated sensor used in IPI number IE00001 |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2014-01-24 | 2014-01-13 10:19 | -11 | 2013-12-13 12:54 | Geotechnical Engineering - Geotechnical Monitoring | 500 |  | Equipment Breakdown | Use As-Is | 4 (0.5-3k) | Complete | External Phenomenon - Other | Completed |  | __ have advised that, on receipt of the calibration certificates for the IPI sensors, they have discovered that the lowest sensor (of 8 No.) in IE00001 has not been correctly calibrated.
| 02SL - Stations (LUL) | Cxxx-NCR-000740 | NCR | CH 85883 - CH 85884 North Wall - Concrete Overbreak |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2014-02-28 | 2014-02-26 17:41 | -2 | 2013-12-20 13:00 | Civil - Geotechnical Engineering | 1500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Following excavation of the portal, it has been observed that there is a section of overbreak on the pile construction between CH 85834 and CH 85836 as follows: Height of overbreak 0.5m Depth out from pile face 0.8m Length along pile wall 1.4m level of top of overbreak 98.2m ATD
| 02SL - Stations (LUL) | Cxxx-NCR-000741 | NCR | CH 85886 - CH 85887 North Wall - Concrete Overbreak |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2014-02-28 | 2014-02-27 12:15 | -1 | 2013-12-20 13:12 | Civil - Geotechnical Engineering | 1500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Following excavation of the portal, it has been observed that there is a section of overbreak on the pile construction between CH 85886 and CH 85887 as follows: Height of overbreak 1.0m Depth out from pile face 0.6m Length along pile wall 1.3m level of top of overbreak 98.8m ATD
| 02SL - Stations (LUL) | Cxxx-NCR-000742 | NCR | Watertightness of secant pile wall - Headwall |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2014-01-24 | 2014-01-17 11:17 | -7 | 2013-12-20 13:25 | Civil - Geotechnical Engineering | 1500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Following a survey, water ingress / damp patches have been identified at the following pile positions: When undertaking the Watertightness assessment of the headwall (Piles W1-W19) 3no locations where deemed to be damp patches greater than 4m2 as stated in ICE Specification for Piling and embedded retaining walls – Section 1.9. These where located; 1. W9-W11 approx 12m2 (noted during inspection by TW and CRL that it is drying out) 2. W1-N2 approx 7.6m2 (2.6m2 on W1 and 7m2 on N2 respectively). 3. W19 approx 9.5m2. This particular location is immediately below a hole through the capping beam (required for concrete installation) that was observed to have allowed rainwater to run down the face of the pile for the last 7days. It was noted that while a previous leak had been identified ~1.5m below the capping no running water was observed and that the pile was damp above this location (~0.5m below the hole in the capping beam). Item 2 and 3 have further developed on 9th/10th January to include running water.
| 02SL - Stations (LUL) | Cxxx-NCR-000743 | NCR | CH 85888 - CH 85889 North Wall - Concrete Overbreak |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2014-02-28 | 2014-02-27 12:23 | -1 | 2013-12-20 15:20 | Civil - Geotechnical Engineering | 1500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Following excavation of the portal, it has been observed that there is a section of overbreak on the pile construction between CH 85888 and CH 85889 as follows: Height of overbreak 0.5m Depth out from pile face 1.2m Length along pile wall 1.8m level of top of overbreak 98.5m ATD
| 02SL - Stations (LUL) | Cxxx-NCR-000744 | NCR | CH 85903 - CH 85904 North Wall - Concrete Overbreak |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2014-02-28 | 2014-02-27 12:30 | -1 | 2013-12-20 15:25 | Civil - Geotechnical Engineering | 1500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Following excavation of the portal, it has been observed that there is a section of overbreak on the pile construction between CH 85903 and CH 85904 as follows: Height of overbreak 0.5m Depth out from pile face 3.0m Length along pile wall 1.0m level of top of overbreak 97.5m ATD
| 02SL - Stations (LUL) | Cxxx-NCR-000745 | NCR | CH 85915 - CH 85917 North Wall - Concrete Overbreak |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2014-02-28 | 2014-02-27 12:34 | -1 | 2013-12-20 15:33 | Civil - Geotechnical Engineering | 1500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Following excavation of the portal, it has been observed that there is a section of overbreak on the pile construction between CH 85915 and CH 85917 as follows: Height of overbreak 1.8m Depth out from pile face 1.8m Length along pile wall 1.0m level of top of overbreak 97.2m ATD
| 02SL - Stations (LUL) | Cxxx-NCR-000746 | NCR | Damage to Base Slab 30 |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2014-03-07 | 2014-03-05 17:15 | -2 | 2014-01-10 16:59 | Civil - Structural Engineering | 1500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | At 2 locations along the joint between Base slab 30 and base slab 29, a small section of concrete has broken off down to the top mat of reinforcement. In addition, the couplers connecting the reinforcement between the 2 slabs have failed.
| 02SL - Stations (LUL) | Cxxx-NCR-000747 | NCR | Pile N116 - overbreak broken back to expose reinfrocement in Pile |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2015-01-23 | 2014-11-07 09:25 | -77 | 2014-01-06 17:17 | Civil - Geotechnical Engineering | 1000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During breaking back of overbreak between 85915 and 85917 - North Wall, the reinforcement in the pile has been exposed.
| 02SL - Stations (LUL) | Cxxx-NCR-000749 | NCR | Upload of Cxxx Monitoring Data to UCIMS |  | Crossrail | XRL | VID - Victoria Dock Portal (Central) |  | 2014-02-14 | 2014-02-20 13:17 | 6 | 2014-01-08 13:25 | Geotechnical Engineering - Geotechnical Monitoring | 1000 |  | Supervision/Management | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The Specification for Control of Ground Movement requires monitoring data by Cxxx to be uploaded to UCIMS. A review of the Cxxx monitoring data in UCIMS (up to the 31-12-2013) has identified that incomplete or incorrect monitoring data has transferred from the Cxxx monitoring system. The review covered the following instrumentation: - Levelling Points, - Shallow Datums, - Rod Extensometers, - Strain Gauges, - Piezometers, - Prisms, - Electronic Inclinometers, High level items identified are as follows: 1. periods where data has not been uploaded for various instrumentation, 2. incorrect readings recorded against monitoring data, 3. inconsistencies in the durations for readings for similar instrumentation, 4. duplication of readings for various instrumentation, Further details are included in the attached spreadsheet (6 number tabs).
| 02SL - Stations (LUL) | Cxxx-NCR-000750 | NCR | Witness points not notified for sewer lining works |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2014-01-30 | 2014-01-17 11:56 | -13 | 2014-01-16 16:08 | Civil - Utilities Engineering | 500 |  | System Defect | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The witness points for items 4.17 to 4.20 on ITP number Cxxx-VIN-C-ITP-CR144_PT003-50087 were not notified to CRL
| 02SL - Stations (LUL) | Cxxx-NCR-000751 | NCR | CH 85917 - 85920 North Wall - Concrete overbreak |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2014-02-28 | 2014-02-27 12:40 | -1 | 2014-01-20 14:50 | Civil - Geotechnical Engineering | 1000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Following excavation of the portal, it has been observed that there is a section of overbreak on the pile construction between CH 85834 and CH 85836 as follows: Height of overbreak 0.6m Depth out from pile face 0.6m Length along pile wall 1.2m level of top of overbreak 97.5m ATD
| 02SL - Stations (LUL) | Cxxx-NCR-000752 | NCR | CH 85921 - 85926 North Wall - Concrete overbreak |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2014-02-28 | 2014-02-27 12:47 | -1 | 2014-01-20 14:55 | Civil - Geotechnical Engineering | 1000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Following excavation of the portal, it has been observed that there is a section of overbreak on the pile construction between CH 85921 and CH 85926 as follows: Height of overbreak 1.1m Depth out from pile face 1.1m Length along pile wall 5m level of top of overbreak 97.6m ATD
| 02SL - Stations (LUL) | Cxxx-NCR-000753 | NCR | CH 85915 - 85920 South Wall - Concrete overbreak |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2014-02-28 | 2014-02-27 12:52 | -1 | 2014-01-20 15:00 | Civil - Geotechnical Engineering | 1000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Following excavation of the portal, it has been observed that there is a section of overbreak on the pile construction between CH 85915 and CH 85920 as follows: Height of overbreak 0.4m Depth out from pile face 0.4m Length along pile wall 4m level of top of overbreak 97.0m ATD
| 02SL - Stations (LUL) | Cxxx-NCR-000754 | NCR | Removal of Prop L6 - Failure to notify witness and review points |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2014-03-07 | 2014-02-27 14:48 | -8 | 2014-01-22 15:36 | Civil - Geotechnical Engineering | 500 |  | System Defect | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | Prior to removal of Prop L6, the ITP contains requirements to review / check the following documentation: 1. a check of slab strengths and survey results (in this case slab 29), - Item 4.1, 2. a check of I&M – Item 4.2, 3. a check of the permit to load – Item 4.3 In this instance, these checks were not notified to CRL (The checks were carried out by TW)
| 02SL - Stations (LUL) | Cxxx-NCR-000755 | NCR | Base Slab B1 - unapproved concrete mix placed into pour |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2014-02-14 | 2014-02-17 13:51 | 3 | 2014-01-22 15:46 | Civil - Civil Engineering General | 5000 |  | Material | Rework | 3 (3-6k) | Complete | Subcontractor Problems - Insufficient surveillance of subcontractors | Completed |  | Mitchellson (MFCE) commenced concreting to Base slab B1 on 21st January. The first 2 loads of concrete (16m3 in total) when it was noticed that the mix being poured was not in accordance with the approved MCR. A CEMIII mix (GGBS) was being used instead of a CEMII mix (PFA).
| 02SL - Stations (LUL) | Cxxx-NCR-000756 | NCR | Base Slab 28 - Surface defects |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2014-02-28 | 2014-03-07 16:07 | 7 | 2014-01-29 09:16 | Civil - Civil Engineering General | 1000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | Following pouring of Base slab 28 on 20/01/2014, a number of issues have been identified with the surface finishes on the slab: Footprint within the concrete (down to rebar level) Indentations on the slab surface due to materials being placed too soon on the slab Damage at the construction joint for the next slab (Bay 27) Poor finish on the kicker edge (Blow holes)
| 02SL - Stations (LUL) | Cxxx-NCR-000757 | NCR | Waterbar damaged at junction between base slab 32, headwall and north and south lining walls |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2014-02-28 | 2014-02-28 14:13 | 0 | 2014-01-29 09:24 | Civil - Civil Engineering General | 1000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | When striking the kicker shutters to base slab 32 (headwall kickers), the waterbar cast in to the kicker has been pulled out. This covers both the north and lining wall junctions
| 02SL - Stations (LUL) | Cxxx-NCR-000758 | NCR | Excess cover to reinforcement in kickers cast with base slab 28 |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2014-03-28 | 2014-02-28 17:21 | -28 | 2014-02-05 13:42 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The reinforcement within the kickers to base slab 28 have excess cover (maximum 115mm) in a number of locations. This applies to both the north and south kickers
| 02SL - Stations (LUL) | Cxxx-NCR-000760 | NCR | Planned arrangements for cold weather concreting |  | Crossrail | XRL | VID - Victoria Dock Portal (Central) |  | 2014-03-20 | 2014-03-18 12:17 | -2 | 2014-02-06 10:06 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Procedure Problem - Lack of procedure | Completed |  | Surveillance was carried on B01 base slab on the 21st January 2014. The Contractor was requested to provide a copy of their planned arrangements for cold weather concreting in line with the specification Cxxx-HYD-Z-RSP-CR144_PT003-50004 rev 5.0 KF11.1104.
| 02SL - Stations (LUL) | Cxxx-NCR-000761 | NCR | Permeation Grouting - grout cubes not tested |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2014-03-07 | 2014-02-07 11:48 | -28 | 2014-02-06 16:37 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Verification Problems - Other | Completed |  | Permeation grouting below sheet piles ITP (Cxxx-VIN-C-ITP-CR144_PT003-50093 R1.0) required grout cubes to be taken each day that grout injection was undertaken. These were to be strength tested by a UKAS laboratory. Between the 10/12/13 and 13/12/13 grout cubes were manufactured but never delivered to the laboratory. Consequently strength testing was never undertaken. This was only identified when the sub-contractor submitted their final report including all the Cube Test Reports they had obtained.
| 02SL - Stations (LUL) | Cxxx-NCR-000762 | NCR | Non-Issue of Contractors RIR for Red Line Drawing Submissions |  | Crossrail | XRL | VID - Victoria Dock Portal (Central) |  | 2014-03-03 | 2014-02-27 14:07 | -4 | 2014-02-10 14:17 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | To date, the Contractor's redline drawings have not been incorportated within the Contractor's Record and Issue Record. Clause 13.3.6.1 of Volume 2B of the Cxxx Conformed Contract requires the Contractor's RIR to be issued when transmitting Redline Drawings for review and acceptance.
| 02SL - Stations (LUL) | Cxxx-NCR-000763 | NCR | Inclinometer Installation - Spiral probe calibration certificate out of date |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2014-03-28 | 2014-02-28 17:25 | -28 | 2014-02-24 12:46 | Civil - Geotechnical Engineering | 500 |  | System Defect | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | It has been brought to our attention by __ that the calibration certificate for the Spiral probe used to verify correct installtion orientation of the inclinometer casing was out of date at the time of the inclinometer installation.
| 02SL - Stations (LUL) | Cxxx-NCR-000764 | NCR | On-Site Fabrication of Temporary Footbridge Across Portal Excavation |  | Crossrail | PDP | VID - Victoria Dock Portal (Central) |  | 2014-04-11 | 2014-04-11 15:34 | 0 | 2014-02-25 11:23 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Personnel Error - Violation of requirement or procedure | Completed |  | The contractor is proposing to ercect a temporary walkway bridge spanning across the portal excavation between caapping beams. On-site fabrication of steelwork for this bridge, utilising a redundant steel beam from the secant pile propping system and additional steeel sections, has taken place without the following documentation being accepted by CRL at either Code 1 or Code 2 status: 1. Temporary Works Design 2. ITP 3. MCR's 4. Welding Method Statement 5. Welding Documentation Pack
| 02SL - Stations (LUL) | Cxxx-NCR-000765 | NCR | Changes to Issued For Construction Status drawings |  | Crossrail | PDP | VID - Victoria Dock Portal (Central) |  | 2014-03-18 | 2014-03-18 12:10 | 0 | 2014-03-04 09:16 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | On 3rd March 2014, CRL Field Engineeering observed __ steel fixers installing reinforcement to the protal sump base slab working to 'C' status IFC Cxxx Reinforcement drawings. The drawings seen by the CRL Field Engineer were anotated with red-line changes. None of these changes to the IFC drawings had been communicated to CRL.
| 02SL - Stations (LUL) | Cxxx-NCR-000766 | NCR | Pile reinforcement anchorage into U trough base slab - Piles T200, T203 and T207 |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2014-05-02 | 2014-05-02 12:13 | 0 | 2014-03-06 15:41 | Civil - Geotechnical Engineering | 1000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | During pile breakdown of the CFA tension piles in base slab 8, 3no. piles have had rebar cut off below the specified level. Pile T200 and T207 have had 1no. 20mm bar cut off at 200mm above pile cut off level, and pile T203 has had 2no. bars cut off 200mm above pile cut off level, rather than the specified min of 1350mm above cut off level in order to achieve the required lap with the U-trough base slab top mat reinforcement.
| 02SL - Stations (LUL) | Cxxx-NCR-000767 | NCR | Base slab 28 - Only 1 28 day cube crushed of 3rd set taken |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2014-04-25 | 2014-03-14 14:44 | -42 | 2014-03-06 16:34 | Civil - Civil Engineering General | 500 |  | Testing and Commissioning | Rework | 4 (0.5-3k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | When crushing the 28 day cubes for base slab 28, only 1 of the 2 cubes for the 3rd set taken was crushed. This cube passed but is not valid as a pair is required to meet the requirements of EN206.
| 02SL - Stations (LUL) | Cxxx-NCR-000768 | NCR | Base slab 27 - Lining wall kicker - exceeds flatness tolerance |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2014-07-25 | 2014-07-24 14:16 | -1 | 2014-03-12 07:36 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | A survey of the south lining wall kicker to bay 27 has identified that part of the kicker exceeds the allowable flatness tolerance of 9mm over 2m length of wall. A survey is attached showing that the flatness over a 3m stretch is approximately 13mm deviation over 2m.
| 02SL - Stations (LUL) | Cxxx-NCR-000769 | NCR | Base slab 27 - North Lining Wall Kicker - Waterbar not fully embedded into concrete |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2015-02-27 | 2014-12-08 13:58 | -81 | 2014-03-18 15:57 | Civil - Civil Engineering General | 1000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Not Defined | Completed |  | Between CH 85852 and 85854 approx, over a distance of 1.6m, the central waterbar in the lining wall kicker has not been cast fully embedded into the concrete
| 02SL - Stations (LUL) | Cxxx-NCR-000770 | NCR | North Lining Wall Kicker - Junction between bay 28 and bay 29 - Waterbar not embedded into concrete |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2015-02-27 | 2014-12-08 14:15 | -81 | 2014-03-20 14:54 | Civil - Civil Engineering General | 1000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | At the junction between B28 and B29 on the north lining wall kicker, the waterbar is not embedded fully into the concrete.
| 02SL - Stations (LUL) | Cxxx-NCR-000771 | NCR | Base slabs B17 - B22 - Poor quality blinding |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2014-06-27 | 2014-06-26 13:41 | -1 | 2014-03-25 08:42 | Civil - Civil Engineering General | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | The blinding placed under base slabs 17 to 22 is losing some of the aggregate on the top surface. This will have the potential to contaminate the lower part of the subsequent base slab pours
| 02SL - Stations (LUL) | Cxxx-NCR-000772 | NCR | Failure by Cxxx to verify Cxxx Monitoring Data |  | Crossrail | PDP | VID - Victoria Dock Portal (Central) |  | 2014-05-09 | 2014-05-09 09:42 | 0 | 2014-03-28 10:49 | Surveying - Instrumentation and Monitoring | 500 |  | Supervision/Management | Repair | 4 (0.5-3k) | Complete | External Phenomenon - Other | Completed |  | It is a requirement of the Works Information (Cxxx Specification for Control of Ground Movement) and of the Cxxx contractor's 'Construction Management Plan - Instrumentation & Monitoring' for the Cxxx contractor to interrogate and verify the 'raw' monitoring data for the automated DLR track monitoring, supplied by Cxxx. Due to a failure of one of the Cxxx Remote Total Stations (RTS 9) on 19/03/14, Cxxx failed to receive data from the Cxxx monitoring system for horizontal movement of the DLR tracks betwen DLR Ch120 & Ch 510. This problem was not reported by Cxxx at any of the daily Shift Review Groups (SRG's) or at the Weekly Engineering Panel (ERP) meeting held on 20/3/14, and was first reported to CRL at the SRG on 26/03/14, the day when Cxxx first notified Cxxx of the problem with RTS 9. At the ERP meeting on 27/03/14, the Cxxx contractor advised that they had not been verifying the 'raw' monitoring data supplied by Cxxx and hence had been unaware of the loss of full data from the Cxxx monitoring system until advised of such by Cxxx on 26/03/14. This is a failure by Cxxx to follow the approved process.
| 02SL - Stations (LUL) | Cxxx-NCR-000773 | NCR | P:ilecor in Piles S142 and S144 not to the correct depth |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2014-06-27 | 2014-06-25 09:10 | -2 | 2014-04-15 14:47 | Civil - Geotechnical Engineering | 1000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | On exposing the pilecor in Piles S142 and S144, it has been discovered that the depth of the pilecor is only 150mm (400mm is required)
| 02SL - Stations (LUL) | Cxxx-NCR-000774 | NCR | Plugging of tie holes to south wall - Bay 1 |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2014-09-26 | 2014-09-17 15:51 | -9 | 2014-04-16 14:38 | Civil - Civil Engineering General | 1000 |  | Material | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Insufficient information made available to the worker. | Completed |  | Whilst carrying out finishing works to the bay 1 south wall, the finishing team took it upon themselves to plug the tie holes. The material used was a repair mortar which was packed into the void, rather than the accepted five star grout which should have been injected into the void.
| 02SL - Stations (LUL) | Cxxx-NCR-000775 | NCR | Concrete cubes were kept in moulds for more than 72 hours after casting- ref; BS EN 1239-2 (Testing of Specimen) 5.5.1. |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2014-07-30 | 2014-06-12 14:51 | -48 | 2014-04-24 16:13 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Improper handling of material | Completed |  | Concrete cubes were kept in moulds for more than 72 hours after casting, the clause states that the concrete cubes must be removed from the moulds no later than 72 hours after casting.- ref; BS EN 1239-2 (Testing of Specimen) 5.5.1.
| 02SL - Stations (LUL) | Cxxx-NCR-000776 | NCR | Incorrect bending of Rebar to Bay 1 Flood Wall |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2014-09-30 | 2014-09-30 16:41 | 0 | 2014-05-01 17:47 | Civil - Civil Engineering General | 1000 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | To allow for the installation of shutters to the B1 south Parapet Wall, the rebar to Bay 1 Flood Wall was incorrectly bent in excess of bending radius. Upon re-straightening the bars, 7no. were found to have sheared, and a number of bars had substantial crack damages on them.
| 02SL - Stations (LUL) | Cxxx-NCR-000777 | NCR | Pile N152 - pilecor not found whilst excavating |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2014-09-30 | 2014-09-04 11:59 | -26 | 2014-05-01 18:30 | Civil - Geotechnical Engineering | 1500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Whilst excavating for the portal, the pilecor in Pile N152 has not been locatedin the expected position.
| 02SL - Stations (LUL) | Cxxx-NCR-000778 | NCR | Portal sump - slump test of concrete not carried out in accordance with BS EN 12350 part 2 |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2014-06-13 | 2014-06-12 14:03 | -1 | 2014-05-06 15:42 | Civil - Civil Engineering General | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | During a routine surveillance on site, it was observed that the slump test carried out to the east wall / mass concrete fill to the sump area of the portal was not carried out correctly. Excessive tamping of the concrete in the cone was witnessed (40 tamps rather than the 25 tamps specified in BS EN 12350:2 - 2009) In addition, there was a question mark over the slump measured. The technician concerned was asked to carry out a second test and the same errors in method were witnessed.
| 02SL - Stations (LUL) | Cxxx-NCR-000779 | NCR | Base slab – Bay 11 - Rebar debonding material installed too low in CFA piles |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2014-06-13 | 2014-06-05 13:14 | -8 | 2014-05-08 07:31 | Civil - Geotechnical Engineering | 1000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The debonding material for the following CFA piles has been installed too low. T129, T121, T113
| 02SL - Stations (LUL) | Cxxx-NCR-000780 | NCR | Base slab – Bay 12 - Rebar debonding material installed too low in CFA piles |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2014-06-27 | 2014-06-26 09:43 | -1 | 2014-05-08 07:34 | Civil - Geotechnical Engineering | 1000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The debonding material for the following CFA piles has been installed too low. T99, T97, T91
| 02SL - Stations (LUL) | Cxxx-NCR-000781 | NCR | Base slab - Bay 12 - CFA piles broken down too low |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2014-06-27 | 2014-06-26 16:19 | -1 | 2014-05-08 07:43 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The following CFA piles have been locally broken down below the design cut off level: T89, T90, T80, T79
| 02SL - Stations (LUL) | Cxxx-NCR-000782 | NCR | Secant box Capping beam - CH 85975 - damage to capping beam - North and South |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2014-09-26 | 2014-09-26 10:25 | 0 | 2014-05-08 09:42 | Civil - Concrete Pavement | 1000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | External Phenomenon - Other | Completed |  | During excavation of the secant box, damage has been sustained to the end of the capping beam at CH 85975 to both the north and south of the portal
| 02SL - Stations (LUL) | Cxxx-NCR-000783 | NCR | Failure to respond to black triggers on strain gauges |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2014-06-13 | 2014-06-12 14:21 | -1 | 2014-05-08 10:17 | Geotechnical Engineering - Geotechnical Monitoring | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Personnel Error - Violation of requirement or procedure | Completed |  | Over the weekend of 3-5th May 2014, a number of black triggers were breached on strain gauges on 3 props in the secant box. Subsequent investigations have determined that the triggers were due to a fault in an electrical box. The on call engineer for the monitoring did not respond to the triggers and the PFE for Cxxx was not informed of the triggers (The PFE did receive the trigger alerts and tried to contact the on call engineer withour success. As a result, the requirements to implement the Trigger level action plan as required by the Site Wide MRAP were not instigated.
| 02SL - Stations (LUL) | Cxxx-NCR-000784 | NCR | Missing lacer bars between B28 and B29 interface for Median wall |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2014-06-30 | 2014-06-25 11:14 | -5 | 2014-05-13 14:44 | Civil - Civil Engineering General | 750 |  | Supervision/Management | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | A number of lacer bars designed to extend between B28 and B29 interface for Median wall are missing
| 02SL - Stations (LUL) | Cxxx-NCR-000785 | NCR | Hold Point missed for watertightness of secant piles prior to fixing lining wall reinforcement |  | Crossrail | PDP | VID - Victoria Dock Portal (Central) |  | 2014-06-13 | 2014-06-12 15:27 | -1 | 2014-05-15 09:17 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Personnel Error - Violation of requirement or procedure | Completed |  | ITP- Lining & Median Walls (Cxxx-VIN-C-ITP-CR144_PT003-50050) contains a Hold Point for CRL against Activity 4.5 - 'Watertightness Check on Secant Pile Wall' prior to installation of reinforcement to the portal lining walls. On 14/5/14 a CRL Field Engineer observed that __ had commenced fixing reinforcement for the sump/secant pile lining walls in Bay B24 without water leeks to the secant piles within this area having been sealed to comply with the requirments of the Works Information and the ITP Hold Point for checks on the watertightness of the secant pile wall being 'signed off' by CRL
| 02SL - Stations (LUL) | Cxxx-NCR-000786 | NCR | Excess cover to Base Slab 21 |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2014-08-29 | 2014-08-15 10:18 | -14 | 2014-05-19 15:17 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Cover to Reinforcement in Base Slab 21 is in excess of the designed tolerance of 80mm to the bottom mat. The top mat cover is to the excat maximum limit of 80mm
| 02SL - Stations (LUL) | Cxxx-NCR-000787 | NCR | Excess cover to Base Slab 22 |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2014-08-29 | 2014-08-15 10:19 | -14 | 2014-05-19 15:17 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Cover to Reinforcement in Base Slab 22 is in excess of the designed tolerance of 80mm to the bottom mat. The top mat cover is to the excat maximum limit of 80mm
| 02SL - Stations (LUL) | Cxxx-NCR-000788 | NCR | Defects to concrete Finish in Lower Sump wall |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2014-09-30 | 2014-09-29 16:49 | -1 | 2014-05-20 08:58 | Civil - Civil Engineering General | 1500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | After striking the shutters to the Lower Sump walls, Honeycombing and excessive Pin-holes were visible in the wall, especially around the jambs as shown in the attached photos.
| 02SL - Stations (LUL) | Cxxx-NCR-000789 | NCR | Excessive tamping during slump testing of fresh concrete for Bay 06 south wall |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2014-06-30 | 2014-06-23 15:13 | -7 | 2014-05-27 14:49 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Personnel Error - Violation of requirement or procedure | Completed |  | During the sampling of fresh concrete for Bay 06 south wall, __ Technician, Dawid Wieczorek was observed tamping each layer concrete for the Slump test in excess of 40 times and not the required 25 as per stated in BS EN 12350-2. This resulted in a Slump measure of 60mm and the concrete load was consequently rejected.
| 02SL - Stations (LUL) | Cxxx-NCR-000790 | NCR | Snapped rebar in Pile T65 at Bay 13 |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2014-08-29 | 2014-08-13 15:21 | -16 | 2014-05-29 14:36 | Civil - Civil Engineering General | 1000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | A rebar in Pile T65 at Bay 13 was noticed to have snapped after breaking down of CFA Piles in the U-Trough area.
| 02SL - Stations (LUL) | Cxxx-NCR-000791 | NCR | Blemishes in the North concrete Lining wall in the Sump area at Bay 24 |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2014-09-26 | 2014-09-19 14:33 | -7 | 2014-05-29 18:08 | Civil - Civil Engineering General | 1000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | After striking the shutters to the North Lining wall in the Sump area at Bay 24, Honeycomb was found to have developed at various locations along the base of the wall.
| 02SL - Stations (LUL) | Cxxx-NCR-000792 | NCR | Changes to IFC Drawings not being red-lined as construction proceed |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2014-10-31 | 2015-01-30 15:00 | 91 | 2014-06-02 17:39 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Information not detailed | Completed |  | During a planned Audit carried out on Redlining of IFC drawings, it was observed that updates to changes such as NCR, FCD other relevant data were not being marked up on the drawing as required by the Works information.
| 02SL - Stations (LUL) | Cxxx-NCR-000793 | NCR | Step in Bay 29 South Lining Wall concrete finish |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2014-07-24 | 2014-07-22 09:49 | -2 | 2014-06-04 15:14 | Civil - Civil Engineering General | 1000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | After striking the shutter to Bay 29 South Lining wall, there is a step in the concrete finish (approximately 18mm); running vertically up the wall. (Please see attached photos)
| 02SL - Stations (LUL) | Cxxx-NCR-000794 | NCR | Lip on Bay 24 North Lining wall concrete finish in the Sump area |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2014-10-15 | 2014-10-06 09:48 | -9 | 2014-06-05 17:10 | Civil - Civil Engineering General | 750 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | There is a Lip in the concrete finish (approximately 10mm) running up the wall in Bay 24 sump North Lining wall (Please see attached photos)
| 02SL - Stations (LUL) | Cxxx-NCR-000795 | NCR | Voids in Pile S54 |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2014-08-31 | 2014-08-21 14:43 | -10 | 2014-06-09 17:51 | Civil - Civil Engineering General | 1500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Voids have been exposed within the shaft of Pile S54 just below the pilecore, possibly as a result of removal of clay logged within the concrete.
| 02SL - Stations (LUL) | Cxxx-NCR-000796 | NCR | Concrete Testing and Sampling not carried out by a competent Technician |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2014-07-24 | 2014-07-22 11:29 | -2 | 2014-06-09 18:18 | Civil - Civil Engineering General | 500 |  | Planning | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Worker not qualified | Completed |  | __, who are the approved test house to test __ concrete were not on site on Saturday 07/06/2014 to carry out concrete compliance testing. As a result, Mitchellson's senior Engineer though not certified, carried out the slump test and made cubes.
| 02SL - Stations (LUL) | Cxxx-NCR-000797 | NCR | The SW20 Installed into the kicker between Bay 17/18 is too close to the face of the concrete |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2014-08-15 | 2014-08-14 12:16 | -1 | 2014-06-10 17:51 | Civil - Civil Engineering General | 750 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The SW20 built into the kicker between Bay 17/18 is too close to the face of the concrete as shown on the attached photos.
| 02SL - Stations (LUL) | Cxxx-NCR-000798 | NCR | Void in kicker concrete finish on Bay18 South |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2014-09-30 | 2014-09-17 16:28 | -13 | 2014-06-13 15:38 | Civil - Civil Engineering General | 1000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | A Void is in the concrete finish of the kicker on Bay18 South (Photo attached)
| 02SL - Stations (LUL) | Cxxx-NCR-000799 | NCR | Honeycomb in Bay 29 North concrete Lining Wall finish |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2015-03-27 | 2015-02-19 14:46 | -36 | 2014-06-17 17:59 | Civil - Civil Engineering General | 1000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Two separate areas on the finished concrete to Bay 29 North Lining wall shows honeycombing, which may have developed due to grout lose or lack of compaction.
| 02SL - Stations (LUL) | Cxxx-NCR-000800 | NCR | Defective equipment in use for Pull-out Test on Lining Wall Anchors in B26 south |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2014-08-14 | 2014-07-18 17:03 | -27 | 2014-06-18 14:15 | Civil - Civil Engineering General | 750 |  | Equipment Breakdown | Rework | 4 (0.5-3k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | During a onsite Surveillance carried out on 17/06/2014 on the construction of the Lining Walls, it was noticed that there was a drop in pressure from 100KN to 80KN on the test equipment in use i.e. Pump SN 808202-P and jack SN 808202-R (both due for next calibration on 11/08/2014). Activity 47a of ITP Cxxx-VIN-C-ITP-CR144_PT003 specifies pull out test force of 100KN 6 number anchors had already been tested earlier in the day and red spray paint applied to indicate it has passed. Two more anchors were tested during the surveillance using the faulty equipment and John Scanlon, the Lorclon operative noted one as passed and the other as failed.
| 02SL - Stations (LUL) | Cxxx-NCR-000801 | NCR | Incorrect bending of starter bars from Base Slab 15 for Base Slab 14 |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2014-07-31 | 2014-07-22 11:54 | -9 | 2014-06-24 10:06 | Civil - Civil Engineering General | 2500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Counterfeit Items | Completed |  | Starter bars at the interface between Base Slab 14/15 has been incorrectly bent in excess of bending radius. Sub-contractor bent the bars to allow for the installation of reinforcement to Base Slab 14. Please see attached photos.
| 02SL - Stations (LUL) | Cxxx-NCR-000802 | NCR | Blemishes on Bay 29 Median Wall concrete finish |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2015-03-27 | 2015-02-19 15:09 | -36 | 2014-06-25 14:29 | Civil - Civil Engineering General | 2000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | - Lip on Bay 29 Median Wall (south face) concrete finish - Honeycomb on a small patch of the north face of the concrete finish - Honeycomb on a small patch of the south face of the concrete finish
| 02SL - Stations (LUL) | Cxxx-NCR-000803 | NCR | Damaged Starter bars form Base Slab 26 for Base Slab 25 |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2014-09-19 | 2014-08-15 10:29 | -35 | 2014-06-27 10:44 | Civil - Civil Engineering General | 750 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | A number of starter bars extending from Base Slab 26 for Base Slab 25 have been bent out of shape
| 02SL - Stations (LUL) | Cxxx-NCR-000804 | NCR | Lip on Bay 8 north wall (1st pour) concrete finish |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2014-10-31 | 2014-10-30 11:31 | -1 | 2014-06-30 15:59 | Civil - Civil Engineering General | 1000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | There is a Lip on the 1st pour of Bay 8 north wall concrete finish
| 02SL - Stations (LUL) | Cxxx-NCR-000805 | NCR | Unapproved repair to a Lip on the 1st pour of Bay 8 north wall concrete finish |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2014-09-26 | 2014-09-17 16:13 | -9 | 2014-06-30 16:20 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Worker not correctly instructed | Completed |  | Repairs to a Lip on the 1st pour of Bay 8 north wall concrete finish was carried out without waiting for the NCR to be raised and a proposed remedial agreed
| 02SL - Stations (LUL) | Cxxx-NCR-000807 | NCR | Incorrect installation of UTX ducts in Bay 23 south |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2014-07-31 | 2014-07-22 11:52 | -9 | 2014-07-02 13:37 | Civil - Civil Engineering General | 1500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During a planned inspection carried out by Neville Leary of CRL on 03/07/2013, it was identified that the UTX ducts in Bay 23 south has not been installed as per approved design and partly bedded in concrete.
| 02SL - Stations (LUL) | Cxxx-NCR-000808 | NCR | Storage of cubes outside the permitted temperature range. |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2014-08-29 | 2014-08-15 10:21 | -14 | 2014-07-03 11:17 | Civil - Civil Engineering General | 1000 |  | Supervision/Management | Repair | 4 (0.5-3k) | Complete | External Phenomenon - Other | Completed |  | At 15:40 on 02/07/2014, the temperature within the Mitchelsons on site cube store was observed to be 31.7 which is outside the permitted temperature range. There were cubes in moulds taken form concrete pour on 01/07/2014 in the store at the time of the observation.
| 02SL - Stations (LUL) | Cxxx-NCR-000809 | NCR | B20 South Lining Wall - Failure to Notify Witness Point to Crossrail |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2014-08-08 | 2014-07-18 11:48 | -21 | 2014-07-11 12:38 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | Failure to provide the agreed 24 hours notice of notification of Witness Point to CRL for Concrete Compliance Testing (__-IR 1847) and Concrete Pour (__-IR 1848) for Bay 20 Lining Wall on 8 July 2014.
| 02SL - Stations (LUL) | Cxxx-NCR-000810 | NCR | Excessive Rebar Spacing - Bays 15/16 South Lining Wall |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2014-09-30 | 2014-09-19 14:42 | -11 | 2014-07-16 17:17 | Civil - Civil Engineering General | 750 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Bays 15/16 South Lining Wall Rebar Spacing at the interface is in excess of the required 150 c/c (photo attached)
| 02SL - Stations (LUL) | Cxxx-NCR-000811 | NCR | Design Queries from __ to __ |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2014-10-10 | 2014-10-17 09:28 | 7 | 2014-07-25 15:23 | Civil - Civil Engineering General | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Personnel Error - Violation of requirement or procedure | Completed |  | Emails are being used to communicate a design query to __ from __ and not via the TQ form.
| 02SL - Stations (LUL) | Cxxx-NCR-000812 | NCR | Design Changes issued to Crossrail |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2014-10-10 | 2014-10-17 09:30 | 7 | 2014-07-25 15:24 | Civil - Civil Engineering General | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Personnel Error - Violation of requirement or procedure | Completed |  | Some design changes have not been formally issued through FCD to Crossrail
| 02SL - Stations (LUL) | Cxxx-NCR-000813 | NCR | Honeycomb in Bay 21 North concrete Lining Wall finish |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2014-09-30 | 2014-09-19 14:54 | -11 | 2014-07-24 08:39 | Civil - Civil Engineering General | 1500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | A large section of the exposed North Lining Wall in Bay 21 shows honeycombing possibly due to ineffective compaction
| 02SL - Stations (LUL) | Cxxx-NCR-000814 | NCR | Lip on Bay 17 South Lining Wall concrete finish |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2014-09-30 | 2014-09-19 14:59 | -11 | 2014-07-24 14:28 | Civil - Civil Engineering General | 1000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | A Lip ( 0 - 12mm) is on Bay 17 South Lining Wall concrete finish - Photos attached
| 02SL - Stations (LUL) | Cxxx-NCR-000815 | NCR | Honneycomb on Bay 17 South Lining Wall concrete finish |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2014-09-30 | 2014-09-30 16:04 | 0 | 2014-07-24 14:40 | Civil - Civil Engineering General | 1500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The exposed South concrete Lining Wall finish has patches of Honeycomb at the lower section of the wall - Photo attached.
| 02SL - Stations (LUL) | Cxxx-NCR-000816 | NCR | Blowholes in Bay 21 North concrete Lining Wall finish |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2014-09-30 | 2014-09-19 15:07 | -11 | 2014-07-24 15:37 | Civil - Civil Engineering General | 750 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | There are blow holes at various section of Bay 21 North concrete Lining Wall finish
| 02SL - Stations (LUL) | Cxxx-NCR-000817 | NCR | Kicker to bay 20 South Parapet Wallwall out of alignment |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2014-09-30 | 2014-09-19 15:17 | -11 | 2014-07-24 17:00 | Civil - Civil Engineering General | 1000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Parapet Wall kicker south wall bay 20 has moved out of alignment up to 10mm, which has allowed the concrete to overhang the capping beam. (Photo attached)
| 02SL - Stations (LUL) | Cxxx-NCR-000818 | NCR | Blowholes in Bay 20 South Parapet Wall Kicker |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2014-09-30 | 2014-09-19 15:26 | -11 | 2014-07-25 09:59 | Civil - Civil Engineering General | 750 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Bay 20 South Parapet Wall Kicker has a number of blow holes in the concrete finish.
| 02SL - Stations (LUL) | Cxxx-NCR-000819 | NCR | Blowholes in Bay 21 South Parapet Wall |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2014-09-30 | 2014-09-30 15:55 | 0 | 2014-07-25 17:01 | Civil - Civil Engineering General | 750 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Bay 21 South Parapet Wall has a number of blow holes on both faces of the concrete finish.
| 02SL - Stations (LUL) | Cxxx-NCR-000820 | NCR | Exposed aggregate in chamfer on Bay 21 South parapet wall |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2014-09-30 | 2014-09-30 16:15 | 0 | 2014-07-25 17:02 | Civil - Civil Engineering General | 1000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Exposed aggregate in chamfer on top of Bay 21 South parapet wall
| 02SL - Stations (LUL) | Cxxx-NCR-000821 | NCR | Isolated gaps between underside of capping beam and top of the south lining wall concrete (Bay 19-21) |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2014-10-31 | 2014-09-19 16:47 | -42 | 2014-07-25 17:03 | Civil - Civil Engineering General | 1500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Isolated gaps are showing in the concrete finish between underside of capping beam and top of the south lining wall (Bay 19-21)
| 02SL - Stations (LUL) | Cxxx-NCR-000822 | NCR | Excessive Honeycombing and voids in the concrete finish of the top layer of Bay 11 North wall (1st pour) |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2014-10-30 | 2014-09-19 16:33 | -41 | 2014-07-25 17:25 | Civil - Civil Engineering General | 2000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Excessive Honeycombing, voids and isolated areas of exposed Rebar has been formed in the concrete finish of the top 150mm (kicker) of Bay 11 North wall (1st pour).
| 02SL - Stations (LUL) | Cxxx-NCR-000823 | NCR | Honeycombing in Bay 20 North concrete Lining Wall finish |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2014-09-30 | 2014-09-26 10:13 | -4 | 2014-08-29 16:36 | Civil - Civil Engineering General | 2000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Sections of the exposed North Lining Wall in Bay 20 shows honeycombing possibly due to ineffective compaction
| 02SL - Stations (LUL) | Cxxx-NCR-000824 | NCR | Blowholes in Bay 20 North concrete Lining Wall finish |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2014-09-30 | 2014-09-26 10:46 | -4 | 2014-07-28 16:09 | Civil - Civil Engineering General | 750 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Excessive blow holes at various section of Bay 20 North concrete Lining Wall finish
| 02SL - Stations (LUL) | Cxxx-NCR-000825 | NCR | Cold Joint in Bay 20 North concrete Lining Wall |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2014-09-30 | 2014-09-26 11:08 | -4 | 2014-07-28 14:51 | Archaeology - General | 1500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | After striking the shutter to Bay 20 North concrete Lining Wall, a Cold Joint appears to have formed on the finish wall
| 02SL - Stations (LUL) | Cxxx-NCR-000826 | NCR | Gaps between the underside of capping beam and top of Bay 20 North lining wall concrete |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2014-09-30 | 2014-09-26 11:22 | -4 | 2014-07-28 16:31 | Civil - Civil Engineering General | 1500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Gaps are showing in the concrete finish between underside of capping beam and top of Bay 20 North lining wall
| 02SL - Stations (LUL) | Cxxx-NCR-000827 | NCR | Voids between underside of capping beam and top of Bay 16 South lining wall |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2014-09-30 | 2014-09-19 15:34 | -11 | 2014-07-30 17:35 | Civil - Civil Engineering General | 1500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | A number of voids and sections of exposed Rebar are showing in the concrete finish between underside of capping beam and top of Bay 16 South lining wall.
| 02SL - Stations (LUL) | Cxxx-NCR-000828 | NCR | Cold Joint in Bay 16 South concrete Lining Wall |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2014-09-30 | 2014-09-19 15:42 | -11 | 2014-07-30 17:37 | Civil - Civil Engineering General | 3000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | A cold joint has formed within a section of Bay 16 South concrete Lining Wall
| 02SL - Stations (LUL) | Cxxx-NCR-000829 | NCR | Concrete to Bay 16 south Parapet Walls Kicker exceeded specified 2hrs from batching to placement |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2014-09-30 | 2014-09-30 16:26 | 0 | 2014-08-04 14:08 | Civil - Civil Engineering General | 500 |  | System Defect | Rework | 4 (0.5-3k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | Concrete to Bay 16 south Parapet Walls Kicker was placed 2hrs and 15mins after batching. This exceeded specified 2hrs hours max time within which concrete should be placed from batching (ITP Cxxx-VIN-C-ITP-CR144_PT003-50023 Activity 4.12)
| 02SL - Stations (LUL) | Cxxx-NCR-000830 | NCR | Blowholes in Bay 20 South Parapet Wall |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2014-09-30 | 2014-09-19 15:52 | -11 | 2014-08-05 14:57 | Civil - Civil Engineering General | 750 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Bay 20 South Parapet Wall has a number of blow holes in the concrete finish.
| 02SL - Stations (LUL) | Cxxx-NCR-000831 | NCR | Step on Bay 18 South Lining Wall |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2014-10-15 | 2014-09-19 16:14 | -26 | 2014-08-06 14:34 | Civil - Civil Engineering General | 1000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Bay 18 South Lining Wall shows vertical and horizontal Steps in the concrete finish (approximately 10mm)
| 02SL - Stations (LUL) | Cxxx-NCR-000832 | NCR | Honeycomb in Bay 18 South concrete Lining Wall finish |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2014-10-15 | 2014-10-13 10:34 | -2 | 2014-08-06 14:55 | Civil - Civil Engineering General | 1000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Bay 18 South concrete Lining Wall finish has Honeycombing along the construction joint
| 02SL - Stations (LUL) | Cxxx-NCR-000833 | NCR | Blownoles in Bay 27 South Lining Wall finish |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2014-09-26 | 2014-09-26 09:47 | 0 | 2014-08-11 14:22 | Civil - Civil Engineering General | 750 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Areas on Bay 27 South Lining Wall finish has Blowholes
| 02SL - Stations (LUL) | Cxxx-NCR-000834 | NCR | Excessive blowholes in Bay 16 North Lining wall finish |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2014-09-30 | 2014-09-30 16:33 | 0 | 2014-08-11 16:33 | Civil - Civil Engineering General | 750 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Bay 16 North Lining wall finish has Excessive blowholes (See attached 3no photos)
| 02SL - Stations (LUL) | Cxxx-NCR-000835 | NCR | Step on Bay South Parapet Wall finish between Bay 16 and 17 |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2014-09-30 | 2014-09-19 15:58 | -11 | 2014-08-14 09:21 | Civil - Civil Engineering General | 1000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | A Step (between 5 to 7mm) is on the South Parapet Wall finish between Bay 16 and 17
| 02SL - Stations (LUL) | Cxxx-NCR-000836 | NCR | Step at both ends of Bay 18 South Parapet Wall finish |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2014-09-30 | 2014-09-19 16:06 | -11 | 2014-08-14 09:32 | Civil - Civil Engineering General | 1000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Steps (3 - 7mm) are on both ends of Bay 18 South Parapet Wall finish. This is at the joints between bay 17/18 and bay 18/19
| 02SL - Stations (LUL) | Cxxx-NCR-000837 | NCR | Blowholes in concrete finish at tappered end of Roof Slab 5 |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2015-05-29 | 2015-03-20 09:35 | -70 | 2014-08-15 17:21 | Civil - Civil Engineering General | 1000 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The tappered end of Roof Slab 5 shows significant amount of blow holes in the concrete finish
| 02SL - Stations (LUL) | Cxxx-NCR-000838 | NCR | Blowholes in Bay 16 South concrete Lining Wall finish |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2014-10-15 | 2014-10-06 10:16 | -9 | 2014-08-15 15:33 | Civil - Civil Engineering General | 1000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | There are blow holes at various section of Bay 16 South concrete Lining Wall finish
| 02SL - Stations (LUL) | Cxxx-NCR-000839 | NCR | North Lining Wall B25 - Piles N80 - Pilecor boxout position outside tolerance |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2014-10-17 | 2014-10-17 09:58 | 0 | 2014-08-18 08:37 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Following survey, it has been identified that the pilecor boxout in Pile N80 is out of tolerance in position of +100mm / -50mm.
| 02SL - Stations (LUL) | Cxxx-NCR-000840 | NCR | North Lining Wall B23 - Pile N102 - Pilecor boxout position outside tolerance |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2014-10-17 | 2014-10-17 10:33 | 0 | 2014-08-18 08:39 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Following survey, it has been identified that the pilecor boxout in Pile 102 is out of tolerance in position of +100mm / -50mm.
| 02SL - Stations (LUL) | Cxxx-NCR-000841 | NCR | North Lining Wall B26 - Piles N62, N64, N66 - Pilecor boxout positions outside tolerance |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2014-10-17 | 2014-10-17 10:08 | 0 | 2014-08-18 08:41 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Following survey, it has been identified that the pilecor boxouts in Piles N62, N64, N66 are out of tolerance in position of +100mm / -50mm.
| 02SL - Stations (LUL) | Cxxx-NCR-000842 | NCR | South Lining Wall B26 - Pile S68 - Pilecor boxout position outside tolerance |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2014-10-17 | 2014-10-17 10:18 | 0 | 2014-08-18 09:35 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Following survey, it has been identified that the pilecor boxout in Pile S68 is out of tolerance in position of +100mm / -50mm.
| 02SL - Stations (LUL) | Cxxx-NCR-000843 | NCR | The Asbuilt level of Base Slab 3 exceeds the allowable tolerance |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2014-09-30 | 2014-09-11 15:35 | -19 | 2014-08-18 16:20 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Asbuilt levels taken on Base Slab 3 shows the levels are in excess of the allowable tolerance of the design
| 02SL - Stations (LUL) | Cxxx-NCR-000844 | NCR | The Asbuilt level of base slab 5 exceeds the allowable tolerance |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2014-09-30 | 2014-09-11 15:31 | -19 | 2014-08-18 16:40 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Asbuilt levels taken on Base Slab 5 shows the levels are in excess of the allowable tolerance of the design
| 02SL - Stations (LUL) | Cxxx-NCR-000845 | NCR | Unaccepted Shear Link used in Roof Slab 5 |  | Crossrail | XRL | VID - Victoria Dock Portal (Central) |  | 2014-09-12 | 2014-09-11 10:03 | -1 | 2014-08-21 14:30 | Civil - Civil Engineering General | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Change to drawings not provided on time | Completed |  | A revised reinforcement sheer link design has been used in roof slab 5. This was a direct result of the difficulty presented with installation of the sheer links in the previous two cast roof slabs (7 and 6) where the top of the sheer link required opening to allow for a suitable fit around the top mat reinforcement. The revised sheer link design has been incorporated into the roof slab without acceptance by the Project Manager and differs to the accepted drawings contained in Cxxx-VIN-C-DWG-CR144_PT003-50004 Rev 4.
| 02SL - Stations (LUL) | Cxxx-NCR-000846 | NCR | Bay 16 south parapet wall construction joint location |  | Crossrail | XRL | VID - Victoria Dock Portal (Central) |  | 2014-09-12 | 2014-09-11 10:13 | -1 | 2014-08-21 15:08 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Design Problem - Change to drawings not provided on time | Completed |  | The south parapet wall at Bay 16 has its construction joint finishing approximately 500mm short of the position indicated on Cxxx-PMI-000172. Bay 16 south parapet wall was cast without discussing or acceptance from the Project Manager on the location of the construction joint, this fails to comply with Clause KF11.1305, part 3 of the Materials and Workmanship Specification Cxxx-HYD-Z-RSP-CR144_PT003-50004 v5.0 where it states “The location of construction joints shall be accepted by the Project Manager”
| 02SL - Stations (LUL) | Cxxx-NCR-000847 | NCR | Honeycomb in Bay 18 North Parapet Wall finish |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2014-10-31 | 2014-10-24 14:48 | -7 | 2014-08-22 10:10 | Civil - Civil Engineering General | 1500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Sections of the exposed Bay 18 North Parapet Wall finish shows honeycombing possibly due to 1. ineffective compaction on the south face 2. grout lose between Bay 18/19 joint on both faces and Wall and Kicker
| 02SL - Stations (LUL) | Cxxx-NCR-000848 | NCR | Starting a concrete pour before a Pre-pour inspection is witnessed by CRL - Bay 20 North Parapet |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2014-11-20 | 2014-09-11 15:13 | -70 | 2014-08-22 17:53 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | CRL were notified of a pre-pour inspection for the morning of the 05/08/2014 but the exact time was not specified as the section of work was not ready. Cxxx Engineer later invited CRL Field Engineer for the inspection after he (Cxxx Engineer) had carried out a pre-inspection. When CRL and Cxxx Engineers arrived on site to carry out the joint pre-pour inspection, it was evident that the Sub-contractor had already started the pour.
| 02SL - Stations (LUL) | Cxxx-NCR-000849 | NCR | Excess cover and reduced spacing between inner and outer Rebar in Bay 22 south Lining Wall |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2014-10-30 | 2014-10-13 11:17 | -17 | 2014-08-28 14:40 | Civil - Civil Engineering General | 1000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | 1) Up to 1m2 above the kicker of the wall by Bay 22/23 construction joint, the spacing between the inner and the outer face Rebar that has been achieved on site is 130mm as against designed spacing of 200mm 2) 1m below the capping beam and across the full length of the wall, there is excess cover of 100mm as against the design of up to 80mm
| 02SL - Stations (LUL) | Cxxx-NCR-000851 | NCR | Bay B25 South Lining Wall near face Starter bars (2 No.) moved towards Secant piles |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2014-09-26 | 2014-09-10 14:31 | -16 | 2014-09-03 09:38 | Structural Engineering - Reinforcement | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Bay B25 south lining wall near face vertical starter bars (first 2 No. of starter bars from east construction joint) have been moved towards secant pile wall because, during the erection of steel at bay B25 base slab, there was not enough room to put the starter bars at correct location (Reinforcements were so crowded at this location). First starter bar from construction joint has got 120mm cover and second one has got 90mm cover.
| 02SL - Stations (LUL) | Cxxx-NCR-000852 | NCR | Excess cover to reinforcement to B22 North Lining Wall |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2014-10-10 | 2014-10-07 14:59 | -3 | 2014-09-08 15:32 | Structural Engineering - Reinforcement | 1500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | 1m below the capping beam and across the full length of the wall, there is excess cover at 100mm.
| 02SL - Stations (LUL) | Cxxx-NCR-000853 | NCR | Reduced cover to reinforcement to Parapet Wall Bay 21 South |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2014-10-10 | 2014-10-07 15:10 | -3 | 2014-09-08 17:01 | Civil - Civil Engineering General | 1000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Reduced cover to reinforcement to high level of Parapet Wall Bay 21 South
| 02SL - Stations (LUL) | Cxxx-NCR-000854 | NCR | Out of Tolerance spacing of Reinforcement - Bay 25 South Lining Wall |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2014-10-10 | 2014-10-09 11:50 | -1 | 2014-09-08 15:56 | Civil - Civil Engineering General | 1000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | At bay B25 south lining wall (west end) near face-1 couplers spacing are out of tolerance (5 No of Couplers starting from 2m above kicker level) . Spacing are more than 150mm continuously. Photos are attached.
| 02SL - Stations (LUL) | Cxxx-NCR-000855 | NCR | Lip on Bay 12 North Parapet Wall |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2014-10-10 | 2014-10-08 13:42 | -2 | 2014-09-08 16:55 | Civil - Civil Engineering General | 1000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | There is a lip in the concrete surface on Bay 12 North Parapet Wall greater than 3mm
| 02SL - Stations (LUL) | Cxxx-NCR-000856 | NCR | Lip on Bay 12 South Parapet Wall |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2014-10-10 | 2014-10-13 11:08 | 3 | 2014-09-08 17:00 | Civil - Civil Engineering General | 1000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | There is a lip in the concrete surface on Bay 12 South Parapet Wall greater than 3mm
| 02SL - Stations (LUL) | Cxxx-NCR-000857 | NCR | Lip at the construction joint of concrete finish between Bay 25 and 26 Median wall |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2014-10-31 | 2014-10-24 15:06 | -7 | 2014-09-09 09:38 | Civil - Civil Engineering General | 1000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Steps greater than 3mm is present on both the north and south face of the finished concrete at the construction joint between Bay 25 & 26 Median Wall
| 02SL - Stations (LUL) | Cxxx-NCR-000858 | NCR | Lip of 6mm on Bay 10 south (1st pour) wall finish |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2014-10-30 | 2014-10-13 11:29 | -17 | 2014-09-11 17:41 | Civil - Civil Engineering General | 1000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | A Lip of up to 8mm is showing on Bay10 south (1st pour) wall finish
| 02SL - Stations (LUL) | Cxxx-NCR-000859 | NCR | Grout loss to section of Bay 22 South Lining Wall |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2014-10-31 | 2014-10-30 12:17 | -1 | 2014-09-15 08:38 | Civil - Civil Engineering General | 1500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Sections of Bay 22 South Lining Wall finish shows evidence of Grout loss to the concrete.
| 02SL - Stations (LUL) | Cxxx-NCR-000860 | NCR | Step of more than 3mm on Bay 26 north Lining Wall concrete |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2014-11-17 | 2014-10-13 11:44 | -35 | 2014-09-16 10:51 | Civil - Civil Engineering General | 1500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Step of more than 3mm is on Bay 26 north Lining Wall concrete finish at the construction joint between Bay 25 and 26
| 02SL - Stations (LUL) | Cxxx-NCR-000861 | NCR | Grout loss to sectons of Bay 25 north Lining Wall concrete finish |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2014-11-17 | 2014-10-13 11:55 | -35 | 2014-09-16 11:49 | Civil - Civil Engineering General | 1000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Bay 25 north Lining Wall concrete finish shows areas of grout loss
| 02SL - Stations (LUL) | Cxxx-NCR-000862 | NCR | Grout loss to sectons of Bay 22 north Lining Wall concrete finish |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2014-11-17 | 2014-11-07 09:07 | -10 | 2014-09-16 14:24 | Civil - Civil Engineering General | 1500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Bay 22 north Lining Wall concrete finish shows areas of grout loss.
| 02SL - Stations (LUL) | Cxxx-NCR-000863 | NCR | Asbuilt position of starter bar for Bay 22 North Parapet wall out of tolerance |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2014-11-17 | 2014-11-07 09:34 | -10 | 2014-09-17 18:22 | Civil - Civil Engineering General | 1000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The Asbuilt position of the starter bars for Bay 22 North Parapet wall is out of tolerance. This has created excess cover of between 90 to 100mm in the Parapet at an area approx. 3000mm x 1500mm from construction joint 21/22
| 02SL - Stations (LUL) | Cxxx-NCR-000864 | NCR | Blowholes on Bay 22 North Lining Wall |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2014-11-17 | 2014-11-07 09:18 | -10 | 2014-09-18 15:35 | Civil - Civil Engineering General | 1000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | There are Blowholes at various section on Bay 22 North Lining Wall
| 02SL - Stations (LUL) | Cxxx-NCR-000865 | NCR | Damage to Bay15 south Parapet wall (1st lift) |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2014-11-17 | 2014-10-13 12:05 | -35 | 2014-09-19 17:46 | Civil - Civil Engineering General | 1500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | A section of Bay15 south Parapet wall (1st lift) has been damaged as a result of lifting operations. A number of starter bars have been exposed and marginally bent out of position.
| 02SL - Stations (LUL) | Cxxx-NCR-000866 | NCR | Step on Bay 11 North Parapet wall Finish |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2014-11-28 | 2014-11-07 09:43 | -21 | 2014-09-24 09:44 | Civil - Civil Engineering General | 1500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | A Step of up to 15mm is on Bay 11 North Parapet wall Finish at the Construction joint with Bay 10
| 02SL - Stations (LUL) | Cxxx-NCR-000867 | NCR | Step on Bay 22 North Parapet wall Finish |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2014-11-28 | 2014-11-07 09:50 | -21 | 2014-09-24 17:47 | Civil - Civil Engineering General | 1000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | A Step of more than 3mm is on Bay 22 North Parapet wall Finish at the Construction joint with Bay 21
| 02SL - Stations (LUL) | Cxxx-NCR-000868 | NCR | Easystrip installed at incorrect level in Bay 21 South Parapet wall |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2014-11-28 | 2014-11-28 09:34 | 0 | 2014-09-25 15:58 | Civil - Civil Engineering General | 2500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The Easystrip in Bay 21 South Parapet wall was installed approx. 75mm higher than the required level As built level survey attached
| 02SL - Stations (LUL) | Cxxx-NCR-000869 | NCR | Roof slab R5,6 and 7 As-built levels out of tolerance |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2014-11-28 | 2014-09-25 12:02 | -64 | 2014-09-24 09:38 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The As-built levels of Roof slab R5,6 and 7 are up to a maximum of 4mm out of the design tolerance of 10mm.
| 02SL - Stations (LUL) | Cxxx-NCR-000870 | NCR | B23 North & South Lining wall Excess Cover Rectification |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2014-10-30 | 2014-10-30 11:46 | 0 | 2014-09-25 18:09 | Structural Engineering - Reinforcement | 1000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | There is excess cover of 100mm along entire bottom of capping beam area (around 2m length) and vertically below 1.5m height
| 02SL - Stations (LUL) | Cxxx-NCR-000871 | NCR | Honeycomb/grout loss on Bay 24 north Lining Wall at construction joint end for Bay 23 wall |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2014-11-28 | 2014-11-07 09:59 | -21 | 2014-09-30 16:27 | Civil - Civil Engineering General | 1000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Honeycomb and grout loss identified on Bay 24 north Lining Wall, at the construction joint end to Bay 23 wall
| 02SL - Stations (LUL) | Cxxx-NCR-000872 | NCR | Rapid Ties stuck in plastic sleeves in Bay 25 north Lining Wall |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2014-11-28 | 2014-11-07 10:12 | -21 | 2014-10-01 08:32 | Civil - Civil Engineering General | 1000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Four Rapid Ties stuck in plastic sleeves in Bay 25 North Lining Wall after striking the shuttering
| 02SL - Stations (LUL) | Cxxx-NCR-000875 | NCR | Reduced cover to reinforcement at high level of B16 north Parapet Wall |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2014-10-29 | 2014-10-30 12:01 | 1 | 2014-10-01 12:44 | Structural Engineering - Reinforcement | 1000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Reduced cover of 30mm to reinforcement at high level of B16 north Parapet Wall (Top North Face horizontal Bar at Construction joint location B16/B15)
| 02SL - Stations (LUL) | Cxxx-NCR-000877 | NCR | Lining walls B22 to B16 (South & North), plan and Verticality positions are outside tolerance |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2014-10-16 | 2014-10-06 08:55 | -10 | 2014-10-02 14:32 | Civil - Civil Engineering General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Bay B22 to Bay B16 area lining walls (South and North) was casted inline with already casted Capping beam and Lining wall kicker (find the attached sketch). Capping Beam plan tolerance is +/- 25mm, But Lining wall Plan tolerance is +/- 10mm and Verticality tolerance is +/- 15mm. when we constructed the lining walls, Lining walls couldn’t meet the plan tolerance limit of +/- 10mm and verticality tolerance of +/- 15mm. The following Lining walls are out of tolerance ( As built Survey is attached) B16 North.......plan and verticality - out of tolerance B16 South.......plan and Verticality - out of tolerance B17 South ......plan and Verticality - out of tolerance B18 North.......plan and verticality - out of tolerance B18 South.......plan and Verticality - out of tolerance B19 North.......Plan - Out of Tolerance B19 South ......plan and Verticality - out of tolerance B20 South ......plan and Verticality - out of tolerance B21 North .......Verticality - Out of tolerance B21 South ......plan and Verticality - out of tolerance B22 South ......plan and Verticality - out of tolerance
| 02SL - Stations (LUL) | Cxxx-NCR-000878 | NCR | Parapet walls B22 to B16 (South & North) plan positions are outside tolerance |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2014-10-16 | 2014-10-06 10:49 | -10 | 2014-10-02 15:54 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Bay B22 to Bay B16 area Parapet walls (South and North) was constructed in line with already casted Capping beam (find the attached sketch). Capping Beam plan tolerance is +/- 25mm, But Parapet wall Plan tolerance is +/- 10mm. when we constructed the parapet walls, parapet walls couldn’t meet the plan tolerance limit of +/- 10mm. The following Parapet walls are out of tolerance (As built Survey is attached) B16 North.......plan position - out of tolerance B16 South....... plan position - out of tolerance B17 South ...... plan position - out of tolerance B18 South....... plan position - out of tolerance B19 South ...... plan position - out of tolerance B20 South ...... plan position - out of tolerance B21 North ....... plan position - out of tolerance B21 South ...... plan position - out of tolerance B22 North ....... plan position - out of tolerance B22 South ...... plan position - out of tolerance
| 02SL - Stations (LUL) | Cxxx-NCR-000879 | NCR | Commencement of Preparation of Making Good to Parapet Wall Bay 14 North prior to Post Concrete Inspection |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2014-10-31 | 2014-10-17 12:46 | -14 | 2014-10-02 17:54 | Civil - Civil Engineering General | 1000 |  | Supervision/Management | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Preparation for making good was commenced prior to the holding of the Post Concrete Inspection at Parapet Wall Bay 14 North.
| 02SL - Stations (LUL) | Cxxx-NCR-000880 | NCR | Damage to North Capping Beam - Bay 23 |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2014-12-19 | 2014-12-10 09:25 | -9 | 2014-10-03 09:14 | Civil - Civil Engineering General | 1000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | A section of the edge of North Capping Beam in the location of Bay 23 has chipped off
| 02SL - Stations (LUL) | Cxxx-NCR-000881 | NCR | Bay 5 OHLE reinforcement (bar mark 161) installed lower than design |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2014-11-28 | 2014-11-19 12:18 | -9 | 2014-10-03 18:13 | Civil - Civil Engineering General | 750 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Bar mark 161 in the reinforcement of Bay 5 OHLE Plinth was installed lower than the design position. It has been identified that, cover to the lower section of B. mark 161 reinforcement will be compromised if the Plinth is concreted in as per design.
| 02SL - Stations (LUL) | Cxxx-NCR-000882 | NCR | Lining wall Kickers at B24/B23 Noth side are outside of tolerance |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2014-11-03 | 2014-10-09 12:01 | -25 | 2014-10-06 18:27 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Lining wall kickers at B24 and B23 north side (2.5m both side from construction Joint B24/B23) are outside plan tolerance of 10mm. Check the attached as built Drawing please. B24 north lining wall was already casted and within tolerance of 10mm. So there is a lip between the kicker and Lining wall bottom ( max of 15mm). B23 area entire kicker has got required cover to starter bars. We plan to cast B23 north lining wall inline with original ( theoretical) line, so again we will get a lip on the kicker level around 2.5m from construction joint B23/B24.
| 02SL - Stations (LUL) | Cxxx-NCR-000883 | NCR | Lack of temperature control in concrete cube store. |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2014-11-28 | 2014-11-28 17:12 | 0 | 2014-10-07 16:28 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | A surveillance carried out on 03/10/2014 at between 15:30 - 16:00 by Cxxx and CRL observed that, the temperature in the Michelson concrete cube storage area was as high as 30oc (see picture of thermometer attached ) It was also observed that a cut-out hole previously used to house the air conditioning unit outlet duct has not been covered. The attached log sheet shows that the minimum and maximum temperatures recorded at 10:15 that morning was within specified range, but the 30oc reading at between 15:30 - 16:00 by Cxxx and CRL was 5oc out of specification. This show lack of continuous monitoring of the air temperature of the store by Mitchellson (sub-contractor), to ensure the proper control measures are in place, especially as there were cubes in the store at the time of the surveillance.
| 02SL - Stations (LUL) | Cxxx-NCR-000885 | NCR | Honeycombing in Bay 24 Sump Shaft & Median Wall concrete finish - South Face |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2014-12-19 | 2014-12-08 12:33 | -11 | 2014-10-20 13:43 | Civil - Civil Engineering General | 1500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The lower level of Bay 24 Sump Shaft & Median Wall concrete finish - South Face, shows grout loss and honeycombing at isolated areas
| 02SL - Stations (LUL) | Cxxx-NCR-000886 | NCR | Honeycombing in Bay 24 Sump Shaft & Median Wall concrete finish - North Face |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2014-12-19 | 2014-12-08 12:42 | -11 | 2014-10-20 13:46 | Civil - Civil Engineering General | 1500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The lower level of Bay 24 Sump Shaft & Median Wall concrete finish - North Face, shows grout loss and honeycombing as per attached photos. Please note; Attachment IMG 0395 JPG is not relevant to this NCR.
| 02SL - Stations (LUL) | Cxxx-NCR-000887 | NCR | Lips on Bay 24 Sump Shaft & Median Wall concrete finish - South Face |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2014-12-19 | 2014-12-08 12:48 | -11 | 2014-10-21 10:56 | Civil - Civil Engineering General | 1500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | 2no lips and are on Bay 24 Sump Shaft & Median Wall concrete finish - South Face
| 02SL - Stations (LUL) | Cxxx-NCR-000888 | NCR | Damage to Wall Bay 5 North (1st Lift) |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2014-11-28 | 2014-11-07 10:23 | -21 | 2014-10-20 17:38 | Civil - Civil Engineering General | 1000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Damage to concrete face of Wall Bay 5 North (1st Lift)
| 02SL - Stations (LUL) | Cxxx-NCR-000889 | NCR | Commencement of Repair to Damage to Wall Bay 5 North prior to Post Concrete Inspection |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2014-11-28 | 2014-11-07 10:31 | -21 | 2014-10-20 17:57 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Commencement of Repair to Damage to Wall Bay 5 North prior to Post Concrete Inspection
| 02SL - Stations (LUL) | Cxxx-NCR-000890 | NCR | Lip and indentation on Bay 24 Sump Shaft & Median Wall concrete finish - North Face |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2014-12-19 | 2014-12-08 12:53 | -11 | 2014-10-21 16:50 | Civil - Civil Engineering General | 1500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | There is a Lip and indentation on Bay 24 Sump Shaft & Median Wall concrete finish - North Face
| 02SL - Stations (LUL) | Cxxx-NCR-000891 | NCR | Grout loss to section of wall in Bay 14 South Parapet wall |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2014-12-19 | 2014-12-08 14:26 | -11 | 2014-10-24 14:50 | Civil - Civil Engineering General | 1000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | A section of wall (2nd Lift) in Bay 14 South Parapet wall shows grout loss as a result of an indent that was formed at the top of the 1st lift.
| 02SL - Stations (LUL) | Cxxx-NCR-000892 | NCR | Honeycomb in Bay 23 South Lining Wall next to Capping Beam |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2014-12-19 | 2014-12-19 09:45 | 0 | 2014-10-28 11:23 | Civil - Civil Engineering General | 1000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Adjacent to the capping beam in Bay 23 South Face, shows honeycombing at an isolated area.
| 02SL - Stations (LUL) | Cxxx-NCR-000893 | NCR | Steps with Kicker in Bay 23 South Lining Wall |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2014-12-19 | 2014-12-19 09:37 | 0 | 2014-10-28 11:36 | Civil - Civil Engineering General | 1000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | At low level of Bay 23 South Lining Wall, there are steps with the kicker.
| 02SL - Stations (LUL) | Cxxx-NCR-000894 | NCR | Lip on Bay 23 South Lining Wall Concrete Finish |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2014-12-19 | 2014-12-19 09:50 | 0 | 2014-10-28 11:38 | Civil - Civil Engineering General | 1000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | There is a Lip on Bay 23 South Lining Wall Concrete Finish.
| 02SL - Stations (LUL) | Cxxx-NCR-000895 | NCR | Eazistrip installed at incorrect level in Bay 20 South Parapet wall |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2014-11-28 | 2014-11-28 09:42 | 0 | 2014-10-29 12:35 | Civil - Civil Engineering General | 2500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The Easystrip in Bay 20 South Parapet wall was installed approx. 75mm higher than the required level.
| 02SL - Stations (LUL) | Cxxx-NCR-000896 | NCR | Waterbar cast too deep into top of Bay 24 North Lining Wall |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2014-12-19 | 2014-11-18 11:26 | -31 | 2014-10-30 12:52 | Civil - Civil Engineering General | 1000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Waterbar cast too deep into top of Bay 24 North Lining Wall. This will not allow the appropriate embedment into the roof slab to be constructed on top of this section of the Lining Wall.
| 02SL - Stations (LUL) | Cxxx-NCR-000897 | NCR | Step Bay 23 North Lining Wall |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2014-12-19 | 2014-12-19 09:57 | 0 | 2014-10-30 15:49 | Civil - Civil Engineering General | 1000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Step greater than 3mm between panels in Bay 23 North Lining Wall.
| 02SL - Stations (LUL) | Cxxx-NCR-000898 | NCR | Honeycomb in Bay 23 North Lining Wall next to Kicker |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2014-12-19 | 2014-12-19 10:02 | 0 | 2014-10-30 15:55 | Civil - Civil Engineering General | 1000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Honeycomb in Bay 23 North Lining wall next to the kicker and the construction joint with bay 24.
| 02SL - Stations (LUL) | Cxxx-NCR-000899 | NCR | Vertical Crack in Bay 15/16 Construction Joint, South Lining Wall |  | Crossrail | XRL | VID - Victoria Dock Portal (Central) |  | 2015-05-01 | 2015-05-01 19:10 | 0 | 2014-11-03 14:54 | Civil - Civil Engineering General | 1500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | After the casting of Bay 16 south lining wall and Bay 15 south U trough lining wall a vertical crack in the concrete has developed at the construction joint.
| 02SL - Stations (LUL) | Cxxx-NCR-000900 | NCR | Lining walls B29, B27 & B26 (South & North) & Median wall B29 plan position and Verticality are outside tolerance |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2014-11-25 | 2014-11-18 11:10 | -7 | 2014-11-11 13:49 | Civil - Structural Engineering | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The following Lining walls and Median wall Plan Position and Verticality are out of tolerance (As built Survey is attached). Cover meter survey was carried out on affected area. All affected area (Plan Position) cover between the reinforcement and face of wall is within the design limit of 40mm to 80mm. B 29 North Lining wall.......plan position - out of tolerance B 29 South Lining wall....... plan position & Verticality - out of tolerance B 27 South Lining wall ...... plan position & Verticality - out of tolerance B 26 North Lining wall .......Verticality- out of tolerance B 26 South Lining wall ...... plan position & Verticality - out of tolerance B 29 Median Wall - North face ..... Plan Position - Out of Tolerance
| 02SL - Stations (LUL) | Cxxx-NCR-000901 | NCR | Blowholes in Bay 23 Median concrete wall finish |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2014-12-12 | 2014-12-12 13:50 | 0 | 2014-11-19 11:27 | Civil - Civil Engineering General | 1000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Bay 23 Median concrete wall finish has Blowholes
| 02SL - Stations (LUL) | Cxxx-NCR-000902 | NCR | Lip & grout loss on B16 parapet infill wall - South face |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2015-01-16 | 2014-12-08 13:01 | -39 | 2014-11-18 09:06 | Civil - Civil Engineering General | 1500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | 1no lip and grout loss to both end of the Bay 16 infill Parapet wall
| 02SL - Stations (LUL) | Cxxx-NCR-000903 | NCR | Lip on Bay 12 South Parapet wall (south face) |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2015-01-16 | 2014-12-08 13:08 | -39 | 2014-11-20 10:00 | Civil - Civil Engineering General | 1000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | There is a Lip of up to 5mm on Bay 12 South Parapet wall (south face)
| 02SL - Stations (LUL) | Cxxx-NCR-000904 | NCR | Reduced cover to top Rebar at Roof Sab 1/2 construction joint |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2015-02-27 | 2015-02-19 16:40 | -8 | 2014-11-28 18:51 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | There is reduce cover of up to 5mm outside the allowed tolerance to top reinforcement at a section in Roof Slab 2, along the construction joint R1/R2
| 02SL - Stations (LUL) | Cxxx-NCR-000905 | NCR | Lip on Bay 10 South Parapet wall (south face) |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2015-01-30 | 2014-12-08 13:49 | -53 | 2014-11-24 09:37 | Civil - Civil Engineering General | 1500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | There is a Lip of more than 3mm on Bay 10 South Parapet wall (south face)
| 02SL - Stations (LUL) | Cxxx-NCR-000906 | NCR | Parapet Walls plan position out of tolerances. |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2014-12-15 | 2014-12-08 12:23 | -7 | 2014-12-01 17:21 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | In the following parapet walls plan positions are out of tolerance (see as built surveys attached). B 01 North Parapet Wall - First Pour B 03 North Parapet Wall - Second Pour B 03 South Parapet Wall - Second Pour B 05 North Parapet Wall - First and Second Pour B 07 North Parapet Wall - First and Second Pour B 08 North Parapet Wall - First and Second Pour B 09 South Parapet Wall - Second Pour B 10 North Parapet Wall - First and Second Pour B 10 South Parapet Wall - First and Second Pour B 11 South Parapet Wall - First and Second Pour B 12 North Parapet Wall - First Pour B 14 South Parapet Wall - First Pour B 15 North Parapet Wall - First Pour B 15 South Parapet Wall - First Pour
| 02SL - Stations (LUL) | Cxxx-NCR-000907 | NCR | Indentation on top of R2 North upstand. |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2015-02-06 | 2015-01-15 13:57 | -22 | 2014-12-08 09:52 | Civil - Civil Engineering General | 1000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Indentation on top of the R2 North upstand, see attached photos.
| 02SL - Stations (LUL) | Cxxx-NCR-000908 | NCR | Lips at top of West Parapet Wall |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2015-02-06 | 2015-02-06 10:50 | 0 | 2014-12-09 14:17 | Civil - Civil Engineering General | 1000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Steps of more than 3mm is on the West face of the West Parapet wall at the top.
| 02SL - Stations (LUL) | Cxxx-NCR-000909 | NCR | Blowholes on West Parapet Wall |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2015-02-06 | 2015-02-06 10:32 | 0 | 2014-12-09 14:27 | Civil - Civil Engineering General | 1000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Blowholes on West Parapet Wall West Face
| 02SL - Stations (LUL) | Cxxx-NCR-000910 | NCR | Lip of more than 3mm on Bay 7 South Parapet wall (south face) |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2015-02-27 | 2015-02-19 14:02 | -8 | 2014-12-16 12:26 | Civil - Civil Engineering General | 1000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | A Lip of more than 3mm is on Bay 7 South Parapet wall (south face)
| 02SL - Stations (LUL) | Cxxx-NCR-000911 | NCR | Exposed aggregate on vertical face of Bay 5 - South Parapet concrete wall (south face) |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2015-02-27 | 2015-02-19 14:11 | -8 | 2014-12-16 12:48 | Civil - Civil Engineering General | 1000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Exposed aggregate on vertical face of Bay 5 - South Parapet concrete wall (south face) adjacent to OHLE plinth
| 02SL - Stations (LUL) | Cxxx-NCR-000912 | NCR | No vertical chamfers on south face of OHLE plinth |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2015-01-30 | 2015-01-14 09:05 | -16 | 2014-12-18 13:11 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | No vertical chamfers were formed on south face of OHLE plinth
| 02SL - Stations (LUL) | Cxxx-NCR-000913 | NCR | Vertical step greater than 5mm in concrete - Bay 4 South Parapet Wall (south face) |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2015-05-29 | 2015-02-19 14:18 | -99 | 2014-12-18 13:31 | Civil - Civil Engineering General | 1000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | There is a Vertical step greater than 5mm in the finished concrete - Bay 4 South Parapet Wall (south face)
| 02SL - Stations (LUL) | Cxxx-NCR-000914 | NCR | Steps greater than 5mm in the top chamfer - Bay 4 south Parapet wall South face |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2015-05-29 | 2015-02-19 14:24 | -99 | 2014-12-18 13:38 | Civil - Civil Engineering General | 1000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Steps greater than 5mm is showing on top of chamfer - Bay 4 south Parapet wall South face
| 02SL - Stations (LUL) | Cxxx-NCR-000915 | NCR | Blowholes on B23 South Parapet wall |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2015-02-27 | 2015-02-19 15:22 | -8 | 2014-12-22 13:03 | Civil - Civil Engineering General | 1000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Blowholes are showing on B23 South Parapet wall
| 02SL - Stations (LUL) | Cxxx-NCR-000916 | NCR | Grout loss and Honeycombing on top of Bay 23 south Parapet wall |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2015-02-06 | 2015-02-06 10:39 | 0 | 2014-12-22 16:12 | Civil - Civil Engineering General | 1500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Top of Bay 23 south Parapet wall shows Grout loss and Honeycombing in the concrete finish
| 02SL - Stations (LUL) | Cxxx-NCR-000917 | NCR | Starter bars for HeadHouse ground floor wall out of position - Wall 13 |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2015-01-30 | 2015-01-28 10:03 | -2 | 2015-01-06 13:52 | Civil - Civil Engineering General | 2000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | 11no Starter bars on the south face of wall 13 (Head House ground floor) are 50mm out of position southwards. this will result in the south face of the wall falling almost directly on top of the bars
| 02SL - Stations (LUL) | Cxxx-NCR-000918 | NCR | Step greater than 3mm on Roof Slab soffit at construction joint between R3/R4 |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2015-02-27 | 2015-02-19 15:27 | -8 | 2015-01-08 17:46 | Civil - Civil Engineering General | 1000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | A step greater than 3mm is on Roof Slab soffit at construction joint between R3/R4
| 02SL - Stations (LUL) | Cxxx-NCR-000919 | NCR | Failure to carry out 28 days compressive test on concrete in the North side up-stand (Roof Slab R1) |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2015-02-27 | 2015-01-15 15:35 | -43 | 2015-01-13 10:05 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | There has been a failure to carry out 28 days compressive test on concrete in the North side up-stand (Roof Slab R1)
| 02SL - Stations (LUL) | Cxxx-NCR-000920 | NCR | Concrete finish to R1 Roof Slab not in compliant to works information |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2015-03-27 | 2015-03-02 10:16 | -25 | 2015-01-13 17:32 | Civil - Civil Engineering General | 1000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The concrete finish on roof slab R1, where the box-out is positioned for the median wall has a lip of more than 3mm and is not compliant with the works information and the specification for a plain finish ( (See section 8.6.2.3 in the NSCS). See attached photos
| 02SL - Stations (LUL) | Cxxx-NCR-000921 | NCR | Headhouse Concrete Works out of Tollerance |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2015-02-13 | 2015-01-22 16:01 | -22 | 2015-01-14 09:09 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The following headhouse concrete works are out of tolerance. - Headhouse infill, lean mix - Level too low - Headhouse Foundation wall A - Wall over poured These can be seen in the attached asbuilts.
| 02SL - Stations (LUL) | Cxxx-NCR-000922 | NCR | Easystrip installed at incorrect position from face of wall in Bay 18 - 19 North Parapet wall |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2015-02-27 | 2015-02-19 15:36 | -8 | 2015-01-14 17:27 | Civil - Civil Engineering General | 1000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | A number of Easystrips has been installed at incorrect position from face of wall in Bay 18 - 19 North Parapet wall giving rise to excess cover at a number of places in the nib along the North face.
| 02SL - Stations (LUL) | Cxxx-NCR-000923 | NCR | A lip of more than 3mm on concrete finish - Bay 23 North parapet wall (North face) |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2015-03-27 | 2015-02-19 15:46 | -36 | 2015-01-20 15:59 | Civil - Civil Engineering General | 1000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | A lip of more than 3mm on concrete finish - Bay 23 North parapet wall (North face)
| 02SL - Stations (LUL) | Cxxx-NCR-000924 | NCR | Lips greater than 3mm on North parapet wall extension.(North Face) |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2015-03-27 | 2015-02-19 15:52 | -36 | 2015-01-20 16:12 | Civil - Civil Engineering General | 1500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Lips greater than 3mm is on the North parapet wall extension concrete finish - (North Face)
| 02SL - Stations (LUL) | Cxxx-NCR-000925 | NCR | Bay 23 North and South Parapet Out of Tollerance |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2015-02-04 | 2015-01-30 16:25 | -5 | 2015-01-21 10:47 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Bay 23 North and South Parapet Walls positions are out of tolerance this is due to the capping beams position. Cxxx-FCD-836 proposed building the upstands and parapet walls inline with the capping beam, in order to avoid steps. Including mesh in areas of excess cover was encompassed in this FCD, so the cover to reinforcement is within tollerance. Please see the attached asbuilt for the positions of the walls.
| 02SL - Stations (LUL) | Cxxx-NCR-000926 | NCR | Grout loss to U17 median wall in-fill concrete finish - north and south side |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2015-03-27 | 2015-02-19 16:00 | -36 | 2015-01-27 09:11 | Civil - Civil Engineering General | 1500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | U17 median wall in-fill concrete finish shows grout loss at the lower section on both north and south faces
| 02SL - Stations (LUL) | Cxxx-NCR-000927 | NCR | Void at top of U17 north wall in-fill |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2015-03-27 | 2015-03-20 09:14 | -7 | 2015-01-27 14:40 | Civil - Civil Engineering General | 1500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | A void at the top of U17 north wall in-fill
| 02SL - Stations (LUL) | Cxxx-NCR-000928 | NCR | Void at top of U18 north wall in-fill |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2015-03-27 | 2015-03-20 09:21 | -7 | 2015-01-27 15:03 | Civil - Civil Engineering General | 1000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | A void is at the top of U18 north wall in-fill
| 02SL - Stations (LUL) | Cxxx-NCR-000929 | NCR | Cold Joint in Head House East Walls (1st Pour) |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2015-03-27 | 2015-02-27 11:22 | -28 | 2015-01-26 17:11 | Structural Engineering - Load Bearing Walls | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Due to problems with supply of concrete from plant, the concrete pour to the East walls of the Head House (Pour 1 - see marked up layout attached) was stopped, resulting in a cold joint within the AFS Logicwall permanent formwork wall panels.
| 02SL - Stations (LUL) | Cxxx-NCR-000930 | NCR | Step greater than 3mm on Bay 3 south Parapet wall concrete finish - south face |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2015-02-27 | 2015-02-19 14:31 | -8 | 2015-02-02 08:38 | Civil - Civil Engineering General | 1500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | A Step greater than 3mm is on Bay 3 south Parapet wall concrete finish - south face
| 02SL - Stations (LUL) | Cxxx-NCR-000931 | NCR | Voids within western half of Head House |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2016-02-12 | 2016-03-01 12:17 | 18 | 2015-02-04 09:39 | Civil - Civil Engineering General | 15000 |  | Workmanship | Repair | 2 (6-60k) | Complete | Management Problem - Other | Completed |  | Following the concrete pour on the western half of the head house it has been discovered that voids are present within the AFS panels. Final GPR Scan report is attached. Which illustrates the void locations and the extent.
| 02SL - Stations (LUL) | Cxxx-NCR-000933 | NCR | In the Western pour on the head house, It has been noted that the tops western sections of walls 5 and 13 are potentially up to 30mm low |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2015-03-27 | 2015-03-27 11:40 | 0 | 2015-02-13 17:45 | Structural Engineering - Structural Engineering - General | 1500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The Following western pour on the head house, it has been noted that the tops western sections of walls 5 and 13 are potentially up to 30mm low (see attached picture). This has occurred due to the panel being cut low when creating the slope on the wall prior to pouring concrete. To correct this fault the tops of the walls are to be grouted to the correct level.
| 02SL - Stations (LUL) | Cxxx-NCR-000934 | NCR | Excess cover to Rebar at top of Bay 27 platform (North of Median Wall) |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2015-04-24 | 2015-02-26 12:55 | -57 | 2015-02-19 15:53 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The west end of Bay 27 platform (North of Median Wall) shows excess cover of up to 10mm outside of the allowable tolerance of 40 - 80mm
| 02SL - Stations (LUL) | Cxxx-NCR-000935 | NCR | Vertical Crack in Bay 15/16 Construction Joint, North Lining Wall |  | Crossrail | XRL | VID - Victoria Dock Portal (Central) |  | 2015-05-01 | 2015-05-01 19:11 | 0 | 2015-02-25 14:42 | Civil - Civil Engineering General | 1500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | After the casting of Bay 16 north lining wall and Bay 15 north U trough wall a vertical crack in the concrete has developed at the construction joint.
| 02SL - Stations (LUL) | Cxxx-NCR-000936 | NCR | B25 South Platform poured without a suitably prepared construction joint |  | Crossrail | XRL | VID - Victoria Dock Portal (Central) |  | 2015-03-31 | 2015-03-31 15:36 | 0 | 2015-03-06 15:50 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The platform walkway at B25 south was offered up to Crossrail to inspect on 6 March 2015 without a suitably exposed aggregate finish evident on the top surface of base slab. The attached photograph demonstrates the situation at time of inspection. The Works Information states the top surface of the structural slab is to have an exposed aggregate finish. In addition the National Structural Concrete Specification Section 5.8.2 advises construction joint surfaces should be carefully prepared to expose the coarse aggregate. The platform walkway at B25 south was poured on 6 March 2015, without any remedial action being undertaken to achieve a compliant exposed aggregate finish at the construction joint with the underlying portal base slab.
| 02SL - Stations (LUL) | Cxxx-NCR-000937 | NCR | Failure to Notify CRL of a Witness point for the Collen frame grout repair |  | Crossrail | XRL | VID - Victoria Dock Portal (Central) |  | 2015-03-27 | 2015-03-26 12:20 | -1 | 2015-03-10 10:29 | Civil - Civil Engineering General | 500 |  | Planning | Repair | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | During the CRL inspection of the trial large void prior to grouting in the collen frame head house wall, CRL were not advised to inspect the trial medium size void which was filled with conbextra TS grout on 9 March 2015 in wall “H-H”. This is not in accordance with the SNC Cxxx-VIN-C-CCN-CR144_PT003-50607.
| 02SL - Stations (LUL) | Cxxx-NCR-000938 | NCR | Blowholes in Platform Bay 25 South |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2015-06-26 | 2015-06-17 13:15 | -9 | 2015-03-11 17:57 | Civil - Civil Engineering General | 1000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Bay 25 South Platform has a number of blowholes outside specification on the surface finish
| 02SL - Stations (LUL) | Cxxx-NCR-000940 | NCR | Defective Large void repair at Head House AFS Panel Wall |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2015-04-16 | 2015-04-16 17:20 | 0 | 2015-03-12 18:20 | Civil - Civil Engineering General | 1000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | At Head House AFS pannel Eastern Wall 2 (see marked up attached drawing 9005-00) External cement board on the outside face of Headhouse structure, split whilst pouring grout for a Large void (150mm width and greater than 500mm in height categorised in relevant SNC: Cxxx-VIN-C-CCN-CR144-PT003-50607). After poured the grout, it is identified that the internal wall has also bulged in the middle of the void up to 3-4mm. (Cement Board thickness 6mm).
| 02SL - Stations (LUL) | Cxxx-NCR-000941 | NCR | R1 South and R4 North Upstand Out of Tollerance |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2015-04-24 | 2015-04-20 13:28 | -4 | 2015-03-24 14:01 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | R1 South and R4 North Upstand plan positions are out of tolerance. R1 south upstand is out of tolerance as it follows the line of the capping beam as per Cxxx-FCD-000836.
| 02SL - Stations (LUL) | Cxxx-NCR-000942 | NCR | Voids within Eastern half of Head House- AFS Panel Wall |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2016-02-12 | 2016-03-01 12:16 | 18 | 2015-03-30 09:27 | Civil - Civil Engineering General | 10000 |  | Incorrect Installation | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Other | Completed |  | Following the concrete pours on the Eastern half of the head house, it has been discovered that voids are present within the AFS panels wall. Final GPR Scan report is attached. Which illustrates the void locations and the extent.
| 02SL - Stations (LUL) | Cxxx-NCR-000943 | NCR | Concrete cubes were kept in moulds for more than 72 hours after casting |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2015-06-05 | 2015-04-20 13:18 | -46 | 2015-04-13 11:20 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Platform Bay 18 Concrete cubes were kept in moulds for more than 72 hours after casting, the clause states that the concrete cubes must be removed from the moulds no later than 72 hours after casting.- ref; BS EN 1239-2 (Testing of Specimen) 5.5.1.
| 02SL - Stations (LUL) | Cxxx-NCR-000944 | NCR | Damage around Platform Drainage Outfall Bay 19 North |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2015-05-29 | 2015-06-02 08:20 | 4 | 2015-04-15 16:10 | Civil - Civil Engineering General | 600 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Concrete has cracked off around the outfall of the platform drainage in Bay 19 on the North face of the platform.
| 02SL - Stations (LUL) | Cxxx-NCR-000945 | NCR | Blowholes in Platform Bay 22 North Face |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2015-06-19 | 2015-06-19 15:16 | 0 | 2015-04-20 09:17 | Civil - Civil Engineering General | 600 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Bay 22 North Face has a number of blowholes outside specification on the surface finish. See attached photos.
| 02SL - Stations (LUL) | Cxxx-NCR-000946 | NCR | Blowholes on Horizontal Face of Track Slab Drainage Channel Bay 8S, 8N, 10N and 12S. |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2015-07-03 | 2015-06-16 17:12 | -17 | 2015-04-23 16:06 | Civil - Civil Engineering General | 600 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | A number of large blowholes have appeared on the horizontal faces of the drainage channel. This has occurred in Bay 8 South, 8 North, 10 North and 12 South.
| 02SL - Stations (LUL) | Cxxx-NCR-000947 | NCR | I & E Stair Goal Post – Paint damage to top coat and possibly galvanised coating. |  | Contr | LAO | VID - Victoria Dock Portal (Central) |  | 2015-08-26 | 2015-07-21 18:41 | -36 | 2015-04-23 08:45 | Civil - Structural Engineering | 1000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | A number of damaged areas have been identified to top coating, including one area of damage to the Galvanised coating of the I & E Stairs Goal Post on arrival to site (see damage survey and photos 2, 6, 10, 11, 12 attached)
| 02SL - Stations (LUL) | Cxxx-NCR-000948 | NCR | I & E Stair Goal Post – Repaired damaged paint work without approved repair procedure. |  | Contr | LAO | VID - Victoria Dock Portal (Central) |  | 2015-08-26 | 2015-07-21 18:39 | -36 | 2015-04-23 09:10 | Civil - Structural Engineering | 1000 |  | Supervision/Management | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The contractor repaired damaged areas on the back side of the vertical members of the I&E Goal Posts without an accepted repair method.
| 02SL - Stations (LUL) | Cxxx-NCR-000949 | NCR | Unapproved material used for I & E stair Goal Post repair work. |  | Contr | LAO | VID - Victoria Dock Portal (Central) |  | 2015-08-26 | 2015-07-21 18:41 | -36 | 2015-04-23 09:29 | Civil - Structural Engineering | 1000 |  | Supervision/Management | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The sub-contractor has used 3M __ coating 152LV to repair the damage on the back side of the vertical members of the Goal Posts (face against the parapet wall), however this material wasn’t accepted for repairs at the time.
| 02SL - Stations (LUL) | Cxxx-NCR-000950 | NCR | Blowholes and Honeycombing Drainage Channel Vertical Faces Track Slab Bay 14S and 10S |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2015-07-10 | 2015-06-16 17:18 | -24 | 2015-04-29 16:33 | Civil - Civil Engineering General | 750 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Blowholes and small areas of honeycombing can be seen on the vertical faces of the drainage channel in the track slab Bay 14S and 10S. See attached photos.
| 02SL - Stations (LUL) | Cxxx-NCR-000951 | NCR | Headhouse Wall Painting - Failing to follow hold point within ITP procedures correctly |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2015-05-29 | 2015-05-27 16:27 | -2 | 2015-04-29 18:25 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | During the painting of the Headhouse walls, painting had commenced on the first coat in rooms OHL-1 & OHL-2. CRL had not yet approved the 300mm x 300mm sample that is required as per item 4.20 'Sampling' in ITP: Cxxx-VIN-C-ITP-CR144_PT003-50104 which is a hold point.
| 02SL - Stations (LUL) | Cxxx-NCR-000952 | NCR | Hairline crack to Eastbound Tunnel Pre-Cast Segment |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2015-08-21 | 2015-07-17 10:55 | -35 | 2015-05-01 15:18 | Civil - Civil Engineering General | 500 |  | Damaged | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | A Hairline crack has developed on the Eastbound Tunnel Pre-Cast Segment as shown on the attached photos (IMG_8549, IMG_8766 and IMG_8768)
| 02SL - Stations (LUL) | Cxxx-NCR-000953 | NCR | Tensile Splitting Strength on Concrete not tested by a UKAS accredited body |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2015-08-28 | 2015-06-22 16:39 | -67 | 2015-04-30 18:04 | Civil - Civil Engineering General | 500 |  | Testing and Commissioning | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | The preliminary testing for track slab stage 1 concrete was tested by __. __ are not accredited to perform the Tensile Splitting Strength on Concrete to BS EN 12390-6: 2009.
| 02SL - Stations (LUL) | Cxxx-NCR-000954 | NCR | Blowholes in Track Slab Drainage Channel concrete finish - Bay 17N, 17S, 19S, 11N, 9N, 12N, 14N. |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2015-07-31 | 2015-06-22 16:36 | -39 | 2015-05-06 08:40 | Civil - Civil Engineering General | 750 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | A number of blowholes have formed at localised sections of the drainage channel in the following bays; North - 9, 11, 12, 14, 17. South - 17, 19.
| 02SL - Stations (LUL) | Cxxx-NCR-000955 | NCR | Exposed Rebar on Head House finish floor |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2015-07-31 | 2015-07-23 08:46 | -8 | 2015-05-05 18:25 | Civil - Civil Engineering General | 750 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Reinforcement bars are exposed on the Head House finish concrete floor at the entrance of the service riser and East end doorway
| 02SL - Stations (LUL) | Cxxx-NCR-000956 | NCR | Commencement of Tunnel Eye Ring works without ITP |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2015-06-12 | 2015-06-12 14:49 | 0 | 2015-05-08 11:36 | Civil - Demolition/Site Clearance | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | Work on the demolition of the last set of tunnel segments commenced with out the Tunnel Eye Ring Beams Construction ITP (Cxxx-VIN-C-ITP-CR144_PT003-50059 2.0) being accepted by Crossrail.
| 02SL - Stations (LUL) | Cxxx-NCR-000957 | NCR | Use of incorrect Permit to Penetrate Form |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2015-07-31 | 2015-07-08 09:56 | -23 | 2015-05-12 15:20 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Permit to Penetrate no 458 form for the road gully installation works has been completed on an old permit form and not the current Issue 3.0. Issue 3.0 has been available through the Health and Safety __ Intranet page since February 2015. Permit issuer and Construction Manager have not been made aware of this update by the site Health and Safety Manager.
| 02SL - Stations (LUL) | Cxxx-NCR-000958 | NCR | Work Commenced without Pre Start Construction Documentation |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2015-07-31 | 2015-06-29 13:01 | -32 | 2015-05-14 10:42 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | Construction work on the Road Gullies on Victoria Dock Road commenced without an accepted Code 1 or 2 ITP, MS or MCR's
| 02SL - Stations (LUL) | Cxxx-NCR-000959 | NCR | Poorly constructed Brickwork - Head House Foundation |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2015-07-31 | 2015-07-17 10:03 | -14 | 2015-05-19 14:28 | Civil - Civil Engineering General | 750 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The partly constructed Brickwork under the cantilevered floor to the Head House Foundation has voids and the mortar beds and joints not troweled flush. The work has not been cleaned down and excess mortar not been removed. This is in contrast to what is specified in Section 4.52 of !TP no. Cxxx-VIN-C-ITP-CR144_PT003-50024 Rev 5
| 02SL - Stations (LUL) | Cxxx-NCR-000960 | NCR | Blowholes in Drainage Channel - Bay 21 North, 16 and 19 South |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2015-10-30 | 2015-06-25 10:50 | -127 | 2015-05-21 08:35 | Civil - Civil Engineering General | 750 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Blowholes in Drainage Channel concrete finish - Bay 21 North, 19 and 16 South Please see attached photos
| 02SL - Stations (LUL) | Cxxx-NCR-000962 | NCR | Incorrect Drawing Revision on site |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2015-07-31 | 2015-06-22 16:38 | -39 | 2015-06-04 17:55 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Design Problem - Use of unapproved drawings | Completed |  | During a check by CRL and __ on drawing been used or intending to be used on site , it was observed that Drawing number Cxxx-VIN-E-DDD-CR144_PT003-30030 P04 was in the possession of __ site team. The current revision of this drawing is P05
| 02SL - Stations (LUL) | Cxxx-NCR-000963 | NCR | Step in lining wall - Bay 28/29 South |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2015-08-28 | 2015-08-28 08:53 | 0 | 2015-06-05 17:34 | Civil - Civil Engineering General | 750 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | There is a step in the lower level of Bay 28/29 South Lining Wall concrete finish (Please see attached photos)
| 02SL - Stations (LUL) | Cxxx-NCR-000964 | NCR | Blowholes on inner surface of Tunnel Eye Beam – Eastbound Pour 1 |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2015-07-31 | 2015-07-27 16:01 | -4 | 2015-06-11 11:16 | Civil - Civil Engineering General | 600 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The Eastbound Tunnel Eye Beam Pour 1 shows Blowholes on inner surface of the finished concrete
| 02SL - Stations (LUL) | Cxxx-NCR-000965 | NCR | Grout Loss and Blowholes in concrete finish – Bay 31 South 1st pour |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2015-07-31 | 2015-06-29 10:43 | -32 | 2015-06-11 12:04 | Civil - Civil Engineering General | 750 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | A section of Bay 31 South Ling wall (1st pour) has Blowholes Grout loss in the finish concrete.
| 02SL - Stations (LUL) | Cxxx-NCR-000966 | NCR | Tensile Splitting Strength Not Achieved |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2015-07-09 | 2015-07-09 14:41 | 0 | 2015-06-18 18:19 | Civil - Civil Engineering General | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | A number of Tensile Splitting Results have failed to reach the requirement of 3.4N/mm2 (Table KF11.A3 - Concrete Mixes). See NCR 966 - table 1 for all results currently received.
| 02SL - Stations (LUL) | Cxxx-NCR-000967 | NCR | Crack Base Slab Bay 11 |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2015-07-10 | 2015-06-25 10:51 | -15 | 2015-06-19 17:01 | Civil - Civil Engineering General | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Crack of greater than 3mm on base slab bay 11. Approximately 1.5m long. The crack appears only to be superficial max depth approximately 5mm. A feeler gauge would not penetrate deeper than this. See attached photos.
| 02SL - Stations (LUL) | Cxxx-NCR-000968 | NCR | Track Slab Level Out of Tollerance |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2015-07-03 | 2015-06-25 10:53 | -8 | 2015-06-19 17:36 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Track Slab Level Out of Tolerance. Cxxx Chainage EB16720, Bay 17 North Level is lower than the specified tolerance. See attached as-built.
| 02SL - Stations (LUL) | Cxxx-NCR-000969 | NCR | Honeycombing Eastbound Tunnel Ring Beam 2nd Pour |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2015-09-25 | 2015-08-04 09:28 | -52 | 2015-07-15 16:59 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The bottom of the Eastbound tunnel ring beam second pour (North Segment) has an area of Honeycombing. See attached photos.
| 02SL - Stations (LUL) | Cxxx-NCR-000970 | NCR | UPS Manufacture Commenced without Pre-Start Documentation |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2015-08-28 | 2015-08-27 15:46 | -1 | 2015-07-15 22:44 | Electrical - General | 0 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Lack of approval Code 1 procedures excessive | Completed |  | Manufacture of UPS Systems 1 (Emergency Lighting) and 2 (Comms) commenced without an accepted Code 1 or 2 ITP. __ has also commenced work without the submission or acceptance of a Project Specific Quality Plan.
| 02SL - Stations (LUL) | Cxxx-NCR-000971 | NCR | Failed 28 Days Cube results - Eastbound Tunnel Eye Beam (1st Pour) |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2015-09-30 | 2015-09-18 15:38 | -12 | 2015-08-26 16:47 | Civil - Civil Engineering General | 0 |  | Testing and Commissioning | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Improper handling of material | Completed |  | The 28 Days Cube results for Eastbound Tunnel Eye Beam (1st Pour), failed to meet the specified strength of 40N/mm2
| 02SL - Stations (LUL) | Cxxx-NCR-000972 | NCR | Failed 28 Days Cube results - Bay 32 North Wall, Westbound Tunnel Eye Beam (1st pour), Bay 32 Median Wall kicker |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2015-09-30 | 2015-09-18 15:43 | -12 | 2015-08-26 16:47 | Civil - Civil Engineering General | 0 |  | Testing and Commissioning | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Improper handling of material | Completed |  | The 28 Days Cube results for Bay 32 North Wall, Westbound Tunnel Eye Beam (1st pour), Bay 32 Median Wall kicker, failed to meet the specified strength of 40N/mm2
| 02SL - Stations (LUL) | Cxxx-NCR-000973 | NCR | Bay 30 North Lining Wall Plan Position Out of Tolerance |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2015-10-02 | 2015-09-17 10:16 | -15 | 2015-09-16 12:03 | Civil - Civil Engineering General | 0 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Plan position of Bay 30 North Lining Wall is 9mm maximum outside of the +/-10mm tolerance. See attached asbuilt.
| 02SL - Stations (LUL) | Cxxx-NCR-000974 | NCR | Failed 28 day Compressive Strength - Track Slab Bay 29 Plt North, 29 Plt South and 29 South |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2015-11-06 | 2015-11-03 10:10 | -3 | 2015-10-20 11:48 | Civil - Civil Engineering General | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | Bay 29 South, 29 Plt North and 29 Plt South, 28 day concrete compressive strength did not reach the required 35N/mm2.
| 02SL - Stations (LUL) | Cxxx-NCR-000983 | NCR | Reduced cover to Mesh Reinforcement in Protective concrete layer to Water Proofing - Roof Slab 10 |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2015-12-18 | 2015-12-16 13:38 | -2 | 2015-10-23 10:24 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Worker not correctly instructed | Completed |  | The Mesh Reinforcement in the Protective concrete layer to Water Proofing on Roof Slab R10 has a reduced cover from 50mm to 0mm on the protective board at approximately 400mm towards R9 Please see attached photos.
| 02SL - Stations (LUL) | Cxxx-NCR-000984 | NCR | Exposed Hydrophilic Strip in Sump and Shaft Walls |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2015-12-04 | 2015-11-25 08:32 | -9 | 2015-10-27 09:16 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Hydrophilic strip is exposed in the Westbound (South) Sump Lining Wall. Also a hydrophilic ring is showing through the shaft wall. See attached photos.
| 02SL - Stations (LUL) | Cxxx-NCR-000985 | NCR | Installation of unapproved Distribution Boards |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2015-12-17 | 2015-12-01 16:01 | -16 | 2015-10-23 10:37 | Electrical - Power Distribution | 500 |  | Material | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Worker not correctly instructed | Completed |  | The following unapproved Distribution Boards were installed SWITCH ROOM A __ SEA9BN12 DIST BOARD TP 12WAY SWITCH ROOM B __ SEA9BN12 DIST BOARD TP 12WAY CORRIDOR __ SEA9BN8 DIST BOARD TP 8WAY LOCATION CER __ SEA9BN16 DIST BOARD TP 16WAY __ SEA9BN16 DIST BOARD TP 16WAY __ SEA9BN8 DIST BOARD TP 8WAY
| 02SL - Stations (LUL) | Cxxx-NCR-000986 | NCR | Damaged Xylem N series (NP3171.09) Storm pump |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2015-12-18 | 2015-12-16 13:41 | -2 | 2015-10-23 10:37 | Mechanical - Pumps | 500 |  | Damaged | Reject | 4 (0.5-3k) | Complete | Personnel Error - Other human error | Completed |  | 1no Xylem N series (NP3171.09) Storm pump delivered to site shows considerable amount of paint damage, rust and had damaged cable. The site team rejected the pump based on the damages and was collected by the supplier. The pump has since been refurbished and returned to site. see attached - IMG_6634 and IMG_6636
| 02SL - Stations (LUL) | Cxxx-NCR-000987 | NCR | Placement of 6N fill material without an approved MCR - Roof Slab Waterproofing and Backfill |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2016-02-26 | 2016-01-14 16:04 | -43 | 2015-10-23 10:38 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Misunderstand the definition of the requirement | Completed |  | Backfilling works has commence on the placement of 6N fill material on the Roof Slab Waterproofing without an approved MCR
| 02SL - Stations (LUL) | Cxxx-NCR-000988 | NCR | PTRs not referenced on IFC/P status drawings |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2015-12-18 | 2015-12-16 15:20 | -2 | 2015-10-26 15:25 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Improper resource allocation | Completed |  | During a surveillance, it was observed that 6 of the 9 PTR’s reviewed has not been referenced on IFC or 'P' status drawings. The drawings in question are; 1. Cxxx-FCD-000927 was not marked on the current P status “P09” drawing Cxxx-VIN-E-DDA-CR144_PT003-30004 2. Cxxx-FCD-000916 was not marked on the current P status “P09” drawing Cxxx-VIN-E-DDA-CR144_PT003-30004 3. Cxxx-NCR-000973 was not on the correct IFC drawing number Cxxx-VIN-C-DDD-CR144_PT003-29157 4. Cxxx-RFI-000983 was not on the correct IFC drawing number Cxxx-HYD-C-DDA-CR144_PT003-20852 5. Cxxx-RFI-000981 was not on the correct IFC drawing number Cxxx-HYD-D-DDA-CR144_PT003-85611 6. Cxxx-RFI-000982 was not on the correct IFC drawing number Cxxx-HYD-D-DDA-CR144_PT003-85620
| 02SL - Stations (LUL) | Cxxx-NCR-000989 | NCR | Delivery note for two Flygt pumps missing |  | Crossrail | XRL | VID - Victoria Dock Portal (Central) |  | 2015-11-23 | 2015-11-23 15:11 | 0 | 2015-11-09 13:25 | Mechanical - Mechanical Engineering General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Personnel Error - Inattention to detail | Completed |  | NCR has been raised for the lack of a delivery note for two Flygt pumps that are to be installed at the portal as required by the procurement process outlined in WIv2B section 20.7. For details refer to surveillance report ref no.Cxxx-XRL-O4-RGN-CR001-50023
| 02SL - Stations (LUL) | Cxxx-NCR-000990 | NCR | 3D model maintenance |  | Crossrail | XRL | VID - Victoria Dock Portal (Central) |  | 2015-12-10 | 2015-12-16 10:32 | 6 | 2015-11-09 13:32 | Mechanical - Mechanical Engineering General | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Management Problem - Misunderstand the definition of the requirement | Completed |  | NCR has been raised to ensure that the 3D model is ‘maintained’ on regular basis as required by WIv2B part 7.7.7.1 and a clash detection report is in place.
| 02SL - Stations (LUL) | Cxxx-NCR-000991 | NCR | Installation of Dry rising Main Pipework without an approved MCR |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2016-01-29 | 2016-01-07 08:02 | -22 | 2015-11-16 08:26 | Mechanical - Public Health Engineering | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Misunderstand the definition of the requirement | Completed |  | A section of the Dry Rising Main Pipework has been install without an approved MCR
| 02SL - Stations (LUL) | Cxxx-NCR-000992 | NCR | Damage to Hydro Stormcell Units |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2016-01-29 | 2016-01-15 09:03 | -14 | 2015-11-20 17:30 | Civil - Civil Engineering General | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | After initially inspecting the installation of the Hydro Stormcell units for the Attenuation Tank, 15 no. instances approximately were found where the Stormcells' plastic sides had been damaged, varying in extent but up to 500mm x 50mm in size. (See attached photos). Further to this inspection, the filter membrane that is attached to the top and bottom faces of the Stormcells had been punctured in several places. This would have seemed to have occurred during the installation process, as well.
| 02SL - Stations (LUL) | Cxxx-NCR-000993 | NCR | PTRs not marked on 3no. IFC/P status drawings |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2016-01-29 | 2016-02-01 09:37 | 3 | 2015-11-26 16:07 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Information not detailed | Completed |  | PTRs were not marked on the following 3no. IFC/P status drawings Cxxx-HYD-C-DDA-CR144_PT003-85611 Cxxx-VIN-R3-DDA-CR144_PT003-55001 Cxxx-VIN-E-DDB-CR144_PT003-30029
| 02SL - Stations (LUL) | Cxxx-NCR-000994 | NCR | 6.1 Fabrication of Access Ladder for I&E Walkway. |  | Contr | LAO | VID - Victoria Dock Portal (Central) |  | 2016-01-20 | 2016-01-06 16:57 | -14 | 2015-11-27 17:04 | Architectural - General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | The sub-contractor has manufactured Access Ladder for I&E Walkway without an approved MCR by incorrectly assumed the ladder material were included in the Head House Internal Metalwork MCR as I&E walkway access ladder also to be made with same grade S275 steel as Architectural metalwork.
| 02SL - Stations (LUL) | Cxxx-NCR-000995 | NCR | Damage to Waterproofing Protective Slab Ch85890 |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2016-07-22 | 2016-06-02 07:44 | -50 | 2015-12-16 12:48 | Civil - Civil Engineering General | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Personnel Error - Inattention to detail | Completed |  | The roof slab waterproofing protective slab has a small area that has cracked away from the surrounding concrete (as per attached photos).
| 02SL - Stations (LUL) | Cxxx-NCR-000996 | NCR | Non compliance with specification |  | Contr | LAO | VID - Victoria Dock Portal (Central) |  | 2016-03-31 | 2016-02-22 11:14 | -38 | 2016-02-12 16:57 | Civil - Structural Engineering | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | As per civil & Structural specification (Spec No: Cxxx-HYD-Z-RSP-CR144_PT003-50004) clause KM10.1306; protective coating system shall be type N9 and __A Road and Bridge certificate. Steel contractor has used Sigmacover280 as intermediate coat for N9 Protective System which has test certificate to show this has been tested against __ specification NR /L3/CIV/039; however, Sigmarcover280 hasn’t got __A certification.
| 02SL - Stations (LUL) | Cxxx-NCR-000997 | NCR | Addition of water to Ready mix concrete delivered to site |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2016-04-29 | 2016-06-02 07:57 | 34 | 2016-03-03 18:45 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | Water was added to a C32/40 mix of concrete delivered to site for use on the Victoria Dock Road trench reinstatement. The water was added by the site team without the approval of the Engineer or supplier of the concrete (__).
| 02SL - Stations (LUL) | Cxxx-NCR-000998 | NCR | I&E Stairs |  | Contr | LAO | VID - Victoria Dock Portal (Central) |  | 2016-07-29 | 2016-06-10 08:17 | -49 | 2016-04-01 12:51 | Civil - Structural Engineering | 5000 |  | Incorrect Installation | Rework | 3 (3-6k) | Complete | Management Problem - Inadequate supervision | Completed |  | Eastern and Western I&E stairs are identical in terms of dimension; however, the Stair stringer & Sheeting rail connection positions are different. As the sub-contractor installed Eastern Stair at the location of Western Stair and Western Stair at the location of Eastern Stirs, the above mention stinger-sheeting rail connections are dislocated and unable to connect as per the current design.
| 02SL - Stations (LUL) | Cxxx-NCR-000999 | NCR | 3.2 - Incorrect hole position on Head House baguettes |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2016-07-22 | 2016-06-20 07:31 | -32 | 2016-05-16 09:36 | Civil - Civil Engineering General | 1500 |  | Design | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Inadequate/insufficient tooling. | Completed |  | 350 No. baguettes for the head house were manufactured and delivered to site with incorrect hole positions for fixings. Due to incorrect detailing by ICS (cladding sub-contractor) the second level of baguettes (from ground level) on the north and south face of the head house had one of two holes for fixings in the incorrect position.
| 02SL - Stations (LUL) | Cxxx-NCR-001000 | NCR | 7.3 - Incorrect disconnecting trap in SWMH01 |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2016-08-26 | 2016-09-02 10:49 | 7 | 2016-05-19 15:04 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The disconnecting trap installed in SWMH01 is right handed, with the vent pipe connected to the east side of the trap, however a left handed trap was required, with the vent pipe to be connected to the west side of the trap. In order to connect the vent pipe from the east side of the disconnecting trap to the vent pipe cast into the west side of the manhole rings the vent pipe would fall away from the trap, meaning that water could collect in the vent pipe. See attached photographs.
| 02SL - Stations (LUL) | Cxxx-NCR-001001 | NCR | Baguettes - Factory Documentation |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2016-09-12 | 2016-07-15 16:09 | -59 | 2016-06-14 08:00 | Architectural - Finishes | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Subcontractor Problems - Insufficient surveillance of subcontractors | Completed |  | As per current ITP Cxxx-VIN-A-ITP-CR144_PT003-50007 item 3.9 states that each pallet of baguettes should arrive on site with a checksheet (NBK Ceramic Baguette Manufacture). To date and during a surveillance carried out on 28-04-16 this information has not arrive on site.
| 02SL - Stations (LUL) | Cxxx-NCR-001002 | NCR | 3.2 - Head House Baguette Damage |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2017-06-01 | 2016-09-06 12:46 | -268 | 2016-06-02 12:56 | Architectural - General | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Improper handling of material | Completed |  | The NBK baguettes that have been installed on the Head House have a number of small chips in the glazed paintwork.
| 02SL - Stations (LUL) | Cxxx-NCR-001003 | NCR | Damage to Pipe Inlet SWMH02 |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2016-09-22 | 2017-02-21 13:23 | 152 | 2016-06-03 16:19 | Civil - Drainage | 1000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Not Defined | Completed |  | Whilst jetting a drainage line from manhole SWMH02, north twin wall 225mm dia plastic inlet pipe, coming from the Attenuation Tank, was damaged whilst retrieving the hose pipe. Pipe has been cracked at the crown back to the internal face of the manhole chamber ring.
| 02SL - Stations (LUL) | Cxxx-NCR-001004 | NCR | Pumped Drainage MDPE Pipe: Backfalling after CCTV survey |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2016-08-31 | 2016-08-02 11:10 | -29 | 2016-06-23 10:27 | Civil - Drainage | 1500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Review of CCTV survey for all underground drainage, identified sections of the pumped MDPE pipe (originating from the Headhouse and discharging at SWMH03) back falling. Water that had been jetted through the line, in preparation for the CCTV survey, was left sitting in the pipe - due to a rapid rise of invert level in the pipe at approx. an 82m distance away from SWMH03. The back fall on the pipe has caused water to sit in the pipe in the pipe upstream, from the 82m section identified in the CCTV survey.
| 02SL - Stations (LUL) | Cxxx-NCR-001005 | NCR | Head House Roof Leak - Noth West Corner |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2016-12-23 | 2017-01-03 11:25 | 11 | 2016-07-05 09:40 | Architectural - Roofing & Exterior Treatment | 1000 |  | System Defect | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | During recent heavy rainfall a leak has occurred in the North West corner of the head house. See attached photograph from the Head House toilet. Sky Green the roof installers have been out to investigate the issue and need to investigate further to complete a repair.
| 02SL - Stations (LUL) | Cxxx-NCR-001006 | NCR | Damaged Paint Finish on Site Fencing |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2016-12-02 | 2016-10-07 07:44 | -56 | 2016-08-04 15:00 | Civil - Landscaping | 600 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Improper handling of material | Completed |  | During Transport and Installation of Bow Top and SR3 fencing there has been varying degrees on damage to the painted surface. Damage extents as follows: Bow Top - Minor surface scratches and blemishes SR3 - Minor surface scratching sustained during transport - Cuts made to paint surface during installation of fittings SR3 Gates - Moderate paint damage as shown in photo attached sustained during transport
| 02SL - Stations (LUL) | Cxxx-NCR-001007 | NCR | 7.1 - Damage to Aco Channel at I&E Gates |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2016-10-14 | 2016-10-07 07:45 | -7 | 2016-08-10 10:16 | Civil - Civil Engineering General | 1000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | The Aco channel and Aco ‘Slimline’ channel to the north east of the head house shown on drawing Cxxx-VIN-L-DDA-CR144_PT003_1-10004 C01 has cracked due to forces on the sides of the channels. We have determined that this has been caused by thermal movements in the concrete/paving bedding mortar either side of the channels. See attached photos.
| 02SL - Stations (LUL) | Cxxx-NCR-001008 | NCR | Rain Water Bandseal Connection |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2016-12-23 | 2016-12-14 14:22 | -9 | 2016-08-12 11:24 | Civil - Drainage | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | At the connection between the I&E rain water and the sub surface drainage a band seal has been used. This band seal has been used in a location that has not been defined in the MCR. Because of the 30mm exposure above ground, it should have also been approved through an MEP MCR procedure. The band seal is cast in concrete and forms the connection between ductile iron rain water pipe and clay drainage pipe. See attached image for more detail.
| 02SL - Stations (LUL) | Cxxx-NCR-001009 | NCR | 4.2 Switchboard Front Access |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2017-08-31 | 2017-04-12 07:56 | -141 | 2016-08-23 14:05 | Electrical - Electrical Engineering General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | The LV switchboards are currently designed to be sited against the walls within the head house however the bus bars are located at the rear of the Burnell panels with solid sheet metal between the front of the panel and the bus bar therefore the bus bars cannot currently be accessed or viewed for inspection, maintenance and thermal imaging. This applied to the LV'A' and LV'B' switchboards, MCC Sump Pump Panel, UPS/MSB/1 and UPS/MSB/2.
| 02SL - Stations (LUL) | Cxxx-NCR-001010 | NCR | Broken Clay Pipe SWMH03 |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2016-11-24 | 2017-02-28 09:53 | 96 | 2016-09-01 09:25 | Civil - Drainage | 500 |  | Damaged | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | Damage has occurred to the 300mm VC pipe entering the southern side of SWMH03. The bottom section of the pipe penetrating the MH has been broken back to the MH ring, see attached photos. No damage is visible further along the pipe past the MH ring. There is no benching in SWMH03
| 02SL - Stations (LUL) | Cxxx-NCR-001011 | NCR | Backfall across benching in SWMH07 |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2018-08-31 | 2017-01-03 13:39 | -605 | 2016-09-01 10:15 | Civil - Drainage | 1000 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | There is 15mm backfall across the benching of SWMH07 between the 150mm diameter and the 300mm diameter pipes. Drawing Cxxx-VIN-P-DDA-CR144_PT003-35025 shows both pipes at an invert level of 101.007 See illustration attached.
| 02SL - Stations (LUL) | Cxxx-NCR-001012 | NCR | 4.5 Head House Lightning Protection Connections |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2016-12-31 | 2017-01-09 14:26 | 9 | 2016-10-05 10:04 | Electrical - General | 1000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Design Problem - Not Defined | Completed |  | The down conductor tapes at the 4 corners of the Head House (as shown on drawing Cxxx-VIN-E-DDA-CR144_PT003-30031) are connected to the rebar within the head house floor slab as shown on drawing Cxxx-VIN-E-DDB-CR144_PT003-30033 to form the portal earthing system. Currently each conductor tape runs down the outside of the head house cladding and is connected via square clamps on the architectural brickwork to 2No earth tapes which then travel a short distance up the inside of the cladding to the rebar connections (photographs 1 and 2 in the attached proposal document show this clearly). This arrangement means that the conductor tape does not follow 'the most direct route' in that it travels back up the inside of the cladding to the rebar.
| 02SL - Stations (LUL) | Cxxx-NCR-001013 | NCR | 7.1 Manhole Benching |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2017-03-16 | 2017-01-03 13:36 | -72 | 2016-11-25 13:34 | Civil - Civil Engineering General | 1000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Insufficient information made available to the worker. | Completed |  | Benching in surface water drainage manholes at Victoria Dock Portal does not comply with Sewers for Adoption 7th Edition. Aspects of non-compliance include the following: 1. Formation and shape of benching not sufficient enough to support pipes and form a smooth flow path 2. Granolithic screed not sufficiently applied to the surface of benching This was observed and agreed upon during CEG, CRL and __ works inspections 23/11/2016.
| 02SL - Stations (LUL) | Cxxx-NCR-001014 | NCR | 12.2 - LVB extractor fan grill alignment |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2018-08-31 | 2017-03-23 13:27 | -526 | 2017-01-18 10:18 | Mechanical - Heating Ventilation & Air Conditioning | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The duct for the extractor fan in the LV-B room of the head house does not align with the external grill. The external grill appears to have been installed on the Trespa cladding approx. 150mm out of position from the centre of the duct. The attached photograph taken from LV-B looking through the duct shows the back of the Trespa cladding with the edge of the external grill visible to one side of the duct.
| 02SL - Stations (LUL) | Cxxx-NCR-001015 | NCR | Head House roof leak |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2018-08-03 | 2018-07-31 12:07 | -3 | 2018-04-18 13:34 | Civil - Civil Engineering General | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | A leak has been identified in the Head House roof above the WC. Further investigation and testing carried out on 20/03/18 has identified that the water ingress originates from around the roof access hatch. It is intended to repair this leak using the same method as previously agreed in Cxxx-NCR-001005 - using Triflex Prodetail. The area of the intended repair is indicated on the attached photograph - inside the purple line and up to the first verge upstand flashing joint. Sky Green will treat the whole area including the upstand to the hatch. It is suspected that a cracked weld is the cause of the water ingress although this could not be pinpointed it was confirmed through the testing that the water ingress originates from within the area indicated (repair area). The technical data for Triflex Prodetail is provided in MCR - Cxxx-VIN-O4-ZFM-CR144_PT003-50433, this is intended to be applied to the external of the currently installed flashings. The Triflex will be painted to match the colour of the flashing once installed. Sky Green have confirmed that the above Triflex proposal does not affect the roof warranty in any way.
| 02SL - Stations (LUL) | Cxxx-NCR-001017 | NCR | Head House Roof Leak |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2019-11-29 | 2019-10-07 09:59 | -53 | 2019-06-26 09:22 | Architectural - Roofing & Exterior Treatment | 500 |  | System Defect | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Leaks in Head House roof. NW and SW corners: NW corner - In NW corner of Toilet, behind the access hatch. Appears to be a different location to previous repaired leaks. Initial investigation 03-04-2019 - further investigation required. SW corner - In SW corner of Air Heat Pump Room. Possibly from RWP connection to gutter. Initial investigation 03-12-2018 - further investigation required.
| 02SL - Stations (LUL) | Cxxx-NCR-001018 | NCR | Fire Alarm & Detection BS5839 Design Certificate |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2019-07-17 | 2019-07-15 11:37 | -2 | 2019-07-03 14:48 | Fire - Fire Systems & General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | A BS 5839 Fire Detection and Alarm Design Certificate was not issued at the design stage of the Victoria Dock Portal project, prior to installation of the Fire Detection and Alarm System.
| 02SL - Stations (LUL) | Cxxx-NCR-001019 | NCR | Head House Roof Leak |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2020-02-14 | 2020-02-03 15:43 | -11 | 2019-11-08 12:18 | Civil - Civil Engineering General | 10000 |  | System Defect | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Leak in Head House roof - NW corner. In the Head House Toilet, behind the access hatch. Appears to be a similar location to previous repaired leaks. Initial investigation 21-10-2019 - further investigation required.
| 02SL - Stations (LUL) | Cxxx-NCR-001020 | NCR | Eastbound platform water ingress via riser below Traction Switch Room A |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2020-02-28 | 2020-02-28 14:24 | 0 | 2019-12-18 15:43 | Civil - Civil Engineering General | 500 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Occassional water ingress has been identified via the tunnel soffit riser below Traction Switch Room A onto the Eastbound emergency platform. This riser is to be firestopped so there is concern that this water ingress may damage or build up behind the firestopping.
| 02SL - Stations (LUL) | Cxxx-NCR-001021 | NCR | Modifications to LVA and LVB main switch boards |  | Contr | VIN | VID - Victoria Dock Portal (Central) |  | 2020-03-31 | 2020-04-03 11:09 | 3 | 2020-01-22 19:15 | Electrical - General | 10 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Not Defined | Completed |  | Cxxx-PMI-00610 instructs modifications to LVA and LVB main switch boards in line with Cxxx-VIN-E-RGN-CR144_PT003-50014 - 'Technical Submittal Burnell - Connection Box Modification to Main LV Panels'. Due to the restricted space in the Cxxx Head House design the panels in LVA and LVB Switch Rooms could not be installed with rear access for busbar maintenance. Alternative means of busbar maintenance was agreed to allow front access for thermal imaging and maintenance (as per Cxxx-VIN-K2-GML-CR144_PT003-50010 - 'Burnell LV and Sump Pump Control Panel Busbar Maintenance'). The completed installation was tested, commissioned, maintenance demonstrated and signed off by CRL, CEG and RfL. Since Handover (Aug 2019), RfL have identified that access to the busbars was restricted. Cxxx-PMI-00604 instructed Burnell to attend site to demonstrate specific maintenance activities and subsequently provide a technical submittal on how new connection boxes could allow main incoming cables to be routed away to improve access to the busbar maintenance assess plate (Cxxx-VIN-E-RGN-CR144_PT003-50014 - 'Technical Submittal Burnell - Connection Box Modification to Main LV Panels').
| 03SR - Stations (RfL) | Cxxx-NCR-000073 | NCR | Piles constructed not to specified method. |  | Contr |  | PML - Pudding Mill Lane Portal (Central) |  | 2011-08-19 | 2011-10-10 17:47 | 52 | 2011-08-18 | Geotechnical Engineering - Concrete - Bored Pile | 500 |  | Design | Use As-Is |  | Complete |  | Completed |  | Piles constructed were re-bored after concrete was pumped, reinforcement cages were vibrated in.
| 03SR - Stations (RfL) | Cxxx-NCR-000105 | NCR | Pile PV27 |  | Contr |  | PML - Pudding Mill Lane Portal (Central) |  | 2011-09-16 | 2011-11-22 18:59 | 67 | 2011-09-13 | Structural Engineering - Reinforcement | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | The boring activities of the pile PV27 (Cxxx-SWN-S-DDA-CR094_PT0002_Z-21018-C01-A) stated at 14:30 and was completed at 15:15. 3 loads of concrete arrived at 13:40, 15:30, 16:20 and the slump test results were 190mm, 210mm and 190mm respectively. The cage was put into place from 16:15 to 16:30. The as built level of the top of the cage is currently 105.020 against the targeted level of 104.100, this means that the overall cage length is 420mm higher or 920mm including the staggered length. Several unsuccessful attempts were made to extract to cage but the operation was aborted due to safety reasons.
| 03SR - Stations (RfL) | Cxxx-NCR-000109 | NCR | Timely submittal for acceptance |  | Contr |  | PML - Pudding Mill Lane Portal (Central) |  | 2011-10-17 | 2011-10-04 18:47 | -13 | 2011-09-16 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | Submittals for Acceptance identified as Hold points were not implemented, the Hold points were bypassed and work proceeded without the required acceptances
| 03SR - Stations (RfL) | Cxxx-NCR-000110 | NCR | Testing concrete for consistence |  | Contr |  | PML - Pudding Mill Lane Portal (Central) |  | 2011-10-17 | 2011-10-04 18:54 | -13 | 2011-09-16 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | During surveillance visit observed sampling of fresh concrete which omitted testing for consistence
| 03SR - Stations (RfL) | Cxxx-NCR-000111 | NCR | Concrete test cube storage temperature |  | Contr |  | PML - Pudding Mill Lane Portal (Central) |  | 2011-10-17 | 2011-10-04 19:02 | -13 | 2011-09-16 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | No records or thermometer available to demonstrate the above requirement,
| 03SR - Stations (RfL) | Cxxx-NCR-000112 | NCR | 28 Day concrete test results |  | Contr |  | PML - Pudding Mill Lane Portal (Central) |  | 2011-10-17 | 2011-10-04 19:08 | -13 | 2011-09-16 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | 28 day concrete test cube results have not been submitted .
| 03SR - Stations (RfL) | Cxxx-NCR-000116 | NCR | DLR Viaduct Pile No. 12NPS |  | Contr |  | PML - Pudding Mill Lane Portal (Central) |  | 2011-09-23 | 2012-02-07 18:23 | 137 | 2011-09-16 | Geotechnical Engineering - Concrete - Bored Pile | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | The electronic depth guage on the CM120 piling rig malfunctioned during piling works. Pile construction continued and depth to toe of pile was measured manually
| 03SR - Stations (RfL) | Cxxx-NCR-000117 | NCR | DLR Station Pile No. PS32 |  | Contr |  | PML - Pudding Mill Lane Portal (Central) |  | 2013-02-28 | 2013-03-01 11:50 | 1 | 2011-09-16 | Geotechnical Engineering - Concrete - Bored Pile | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | The reinforcement cage of pile no. PS32 was installed 14mm out of the specified vertical tolerance. The specification states a vertical tolerance of +150mm / -50mm. The cage was installed at -64mm.
| 03SR - Stations (RfL) | Cxxx-NCR-000120 | NCR | CRL 1 Piles reinforcement |  | Contr |  | PML - Pudding Mill Lane Portal (Central) |  | 2011-09-23 | 2011-11-16 18:28 | 54 | 2011-09-19 | Structural Engineering - Reinforcement | 500 |  | Design | Use As-Is |  | Complete |  | Completed |  | The as built survey of the top of the cage is 104.183 instead of 104.400, this means that the cage was inserted 167mm lower its 50mm tolerance.
| 03SR - Stations (RfL) | Cxxx-NCR-000125 | NCR | Piles Reinforcement of CRL-RT1 |  | Contr |  | PML - Pudding Mill Lane Portal (Central) |  | 2011-09-30 | 2011-11-16 18:36 | 47 | 2011-09-21 | Structural Engineering - Reinforcement | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | The piles PR14, 16, 18, 22, 24, 25, 129 and 130 were installed staggered by 200mm prior to formal approval from designers.
| 03SR - Stations (RfL) | Cxxx-NCR-000139 | NCR | PR127 Pile out of tolerance |  | Contr |  | PML - Pudding Mill Lane Portal (Central) |  | 2011-10-07 | 2011-11-16 18:43 | 40 | 2011-09-28 | Structural Engineering - Structural Engineering - General | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | The pile PR127 as built survey is E:88215.923; N:38056.828 which is 1.028m West (centre to centre).
| 03SR - Stations (RfL) | Cxxx-NCR-000143 | NCR | 28 Days Cube Strength PWA6 |  | Contr |  | PML - Pudding Mill Lane Portal (Central) |  | 2011-10-07 | 2011-11-16 18:53 | 40 | 2011-10-03 | Structural Engineering - Structural Engineering - General | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | 28 Days concrete strength results are 37.5 and 32.8N/mm2 which is inferior to minimum requirement of 40N/mm2.
| 03SR - Stations (RfL) | Cxxx-NCR-000157 | NCR | Missing Calabration due date on certificate for Inclinometer system |  | Contr |  | PML - Pudding Mill Lane Portal (Central) |  | 2011-10-10 | 2011-10-18 14:36 | 8 | 2011-10-06 | Civil - Civil Engineering General | 500 |  | System Defect | Use As-Is |  | Complete |  | Completed |  | The certificate details that it was last calibrated 09/09/11 however dose not detail a next due date however this will obviously be prior to 09/09/12. Also there is no contingency plan covering the event of a break down of this equipment.
| 03SR - Stations (RfL) | Cxxx-NCR-000161 | NCR | 28 Days Cube Strength PWA4 |  | Contr |  | PML - Pudding Mill Lane Portal (Central) |  | 2011-10-21 | 2012-03-06 14:36 | 137 | 2011-10-12 | Structural Engineering - Structural Engineering - General | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | The 28 and 56 Day cube strength results are 37.0N/mm2 and 39.5N/mm2 which is inferior to the minimum requirement of 40N/mm2. 7, 28 and 56 cube certificates attached (Location PWA4). Also attached results taken from 2No of cores at 75 Day old (highest of 35N/mm2 for a minimum strength of 32N/mm2)
| 03SR - Stations (RfL) | Cxxx-NCR-000172 | NCR | use of Dip meter / inclinometer probe without a calibration cert |  | Contr |  | PML - Pudding Mill Lane Portal (Central) |  | 2011-10-18 | 2011-10-18 14:40 | 0 | 2011-10-17 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | The dip meter / inclinometer probe SN 1276 was found to be in use with no calibration cerififcate in place.
| 03SR - Stations (RfL) | Cxxx-NCR-000178 | NCR | Length of bars above cut off |  | Contr |  | PML - Pudding Mill Lane Portal (Central) |  | 2011-10-21 | 2012-03-06 14:41 | 137 | 2011-10-20 | Structural Engineering - Reinforcement | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | Please find attached existing condition.
| 03SR - Stations (RfL) | Cxxx-NCR-000179 | NCR | West Abutment Pile rebar bend |  | Contr |  | PML - Pudding Mill Lane Portal (Central) |  | 2011-10-24 | 2012-03-06 14:48 | 134 | 2011-10-21 | Structural Engineering - Reinforcement | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | 6 No of west abutment piles starter bars are bend as per follow: - PWA6: 6 No. - PWA8: 1 No. - PWA13: 1 No. - PWA15: 1 No. - PWA18: 1 No. - PWA23: 1 No. Please see attached pictures.
| 03SR - Stations (RfL) | Cxxx-NCR-000187 | NCR | Use of out-dated IFC drawing |  | Contr |  | PML - Pudding Mill Lane Portal (Central) |  | 2011-10-28 | 2011-12-14 18:36 | 47 | 2011-10-27 | Civil - Civil Engineering General | 500 |  | System Defect | Use As-Is |  | Complete |  | Completed |  | The steel fixing sub-contractor MPB was found in the Crossrail quality surveillance that MPB was not using the latest issued IFC drawing (i.e. Cxxx-SWN-S-DDD-CR094_PT002_A-21450 and 21451) during the steel fabrication of the DLR station west abutment pile cap on 25 Oct 2011.
| 03SR - Stations (RfL) | Cxxx-NCR-000188 | NCR | Bent starter bars to Pile No. 12NP2 on GL 12 of the new DLR Viaduct |  | Contr |  | PML - Pudding Mill Lane Portal (Central) |  | 2011-11-08 | 2012-03-06 14:52 | 119 | 2011-11-01 | Structural Engineering - Reinforcement | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | Pile No. 12NP2 was broken down initially using the pile cropper and then using the mini excavator. The starter bars during pile breakdown were bent over. See attached photo.
| 03SR - Stations (RfL) | Cxxx-NCR-000189 | NCR | Debonding foam removal to West Abutmebt piles for new DLR Station |  | Contr |  | PML - Pudding Mill Lane Portal (Central) |  | 2011-11-08 | 2012-03-06 15:59 | 119 | 2011-11-01 | Structural Engineering - Reinforcement | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | Debonding foam was located below pile cut off level and was required to be removed prior to pile cap construction works. An RFI was raised (RFI No. 180) and it was agreed that the debonding foam be removed from the starter bars by locally breaking out concrete surrounding the bars concerned. The area surrounding these bars would then be cleaned out and left until the pile cap was concreted. The piles affected are : PWA 4, 6, 18, 19 & 24.
| 03SR - Stations (RfL) | Cxxx-NCR-000217 | NCR | Use of incorrect IFC drawing |  | Contr |  | PML - Pudding Mill Lane Portal (Central) |  | 2011-11-15 | 2011-12-14 18:43 | 29 | 2011-11-14 | Geotechnical Engineering - Geotechnical Engineering - General | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | The steel work sub-contractor MPB was using an incorrect drawing for GL11 south pile cap steel fixing works on 10 Nov 2011 (Thursday afternoon). The drawing for GL8 pile cap (dwg no. Cxxx-SWN-S-DDD-CR094_PT002_2-14250). The right drawing should be Cxxx-SWN-S-DDD-CR094_PT002_2-14251.
| 03SR - Stations (RfL) | Cxxx-NCR-000226 | NCR | GL10 Pile No. 10NP2 Starter Bars |  | Contr |  | PML - Pudding Mill Lane Portal (Central) |  | 2011-11-28 | 2012-03-06 16:25 | 99 | 2011-11-21 | Structural Engineering - Reinforcement | 500 |  | Damaged | Repair |  | Complete |  | Completed |  | The lifting band of the pile reinforcefment cage was high. Site operatives were cutting off the lifting band using a stihl saw and cut into the 32mm diameter starter bars going into the pilecap thus causing damage to the bars.
| 03SR - Stations (RfL) | Cxxx-NCR-000227 | NCR | GL 11 Southern Pile Cap |  | Contr |  | PML - Pudding Mill Lane Portal (Central) |  | 2011-11-28 | 2011-12-01 16:32 | 3 | 2011-11-21 | Structural Engineering - Concrete Member | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | The northern face of GL11's southern pilecap was cast using a dented shutter. This caused the cover of the northern face to exceed the permitted tolerance. See attached as built survey.
| 03SR - Stations (RfL) | Cxxx-NCR-000240 | NCR | 2 No. 28 day cube strength results greater than 15% PR49 & 43 |  | Contr |  | PML - Pudding Mill Lane Portal (Central) |  | 2011-12-09 | 2012-03-06 16:51 | 88 | 2011-12-01 | Structural Engineering - Structural Engineering - General | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | The 28 day results for the pile number PR49 are 34 and 47.5 N/mm2 and the pile PR43 are 32.5 and 46.0 N/mm2.
| 03SR - Stations (RfL) | Cxxx-NCR-000244 | NCR | Diaphragm Wall steel reinforcement exposure |  | Contr |  | PML - Pudding Mill Lane Portal (Central) |  | 2011-12-16 | 2012-06-19 11:02 | 186 | 2011-12-06 | Civil - Structural Engineering | 500 |  | Damaged | Repair |  | Complete |  | Completed |  | During excavation works within the Cut & Cover, a section of overbreak was removed exposing the face of the steel reinforcement. The damaged area is approximately 300mm x 300mm, and is located on the south diaphragm wall adjacent to the 11kV box.
| 03SR - Stations (RfL) | Cxxx-NCR-000260 | NCR | PWA5 Cube strength results |  | Contr |  | PML - Pudding Mill Lane Portal (Central) |  | 2011-12-16 | 2012-03-06 16:56 | 81 | 2011-12-13 | Structural Engineering - Structural Engineering - General | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | 28 Days concrete strength results are 36.5 and 40.0N/mm2 which the average of 38.3N/mm2 is inferior to minimum requirement of 40N/mm2.
| 03SR - Stations (RfL) | Cxxx-NCR-000262 | NCR | Grid Line 8 Pile 8SP4 |  | Contr |  | PML - Pudding Mill Lane Portal (Central) |  | 2011-12-23 | 2012-03-06 17:16 | 74 | 2011-12-15 | Geotechnical Engineering - Concrete - Bored Pile | 500 |  | Damaged | Repair |  | Complete |  | Completed |  | During pile breakdown the southern face of pile no. 8SP4 was damaged by the excavator bucket thus exposing the rebar to the pile. On further inspection the concrete surrounding the pile was still "green".
| 03SR - Stations (RfL) | Cxxx-NCR-000263 | NCR | DLR Viaduct Grid Line 13 Pile Starter bars damaged |  | Contr |  | PML - Pudding Mill Lane Portal (Central) |  | 2011-12-23 | 2012-03-06 17:47 | 74 | 2011-12-16 | Geotechnical Engineering - Concrete - Bored Pile | 500 |  | Damaged | Repair |  | Complete |  | Completed |  | During pile installation, due to the limited working area at GL13 the service crane to the piling rig tracked across the newly constructed piles of GL 13 North pilecap thus bending the tops of the starter bars.
| 03SR - Stations (RfL) | Cxxx-NCR-000267 | NCR | Piles out of tolerance |  | Contr |  | PML - Pudding Mill Lane Portal (Central) |  | 2012-01-16 | 2012-03-06 17:54 | 50 | 2011-12-22 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | Pile S3P5 has been installed at 104.904m (+504mm), meaning it has been installed 354mm above its 150mm tolerance. Pile S3P16 is installed at 104.600m (+200mm), meaning it has been installed 50mm above its 150mm tolerance.
| 03SR - Stations (RfL) | Cxxx-NCR-000269 | NCR | Damaged reinforcement bars to column GL 11 North |  | Contr |  | PML - Pudding Mill Lane Portal (Central) |  | 2012-01-11 | 2012-03-06 19:00 | 55 | 2012-01-04 | Structural Engineering - Reinforcement | 500 |  | Workmanship | Rework |  | Complete |  | Completed |  | 1 No. starter bar damaged with disc cutter during installation of column reinforcement links. Reinforcement links also damaged by disc cutter during installation.
| 03SR - Stations (RfL) | Cxxx-NCR-000320 | NCR | load tranfer slab piles slab S1 |  | Contr |  | PML - Pudding Mill Lane Portal (Central) |  | 2012-01-16 | 2012-03-08 13:41 | 52 | 2012-01-13 | Civil - Civil Engineering General | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | As above.
| 03SR - Stations (RfL) | Cxxx-NCR-000341 | NCR | Pile PS54 DLR Station Stairs Slab |  | Contr |  | PML - Pudding Mill Lane Portal (Central) |  | 2012-01-27 | 2012-03-06 18:02 | 39 | 2012-01-18 | Geotechnical Engineering - Concrete - Bored Pile | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | Pile PS54 do not comply with the SPERW B3.4. Pile is currently set 530mm above target level and 380mm above the required tolerance. Several attempts were made to extract the cage and re-bore it but for safety reasons the operation was aborted.
| 03SR - Stations (RfL) | Cxxx-NCR-000362 | NCR | Blinding level in Cut and Cover phase 2A |  | Contr |  | PML - Pudding Mill Lane Portal (Central) |  | 2012-01-27 | 2012-01-31 09:50 | 4 | 2012-01-30 | Civil - Civil Engineering General | 500 |  | Workmanship | Rework |  | Complete |  | Completed |  | N / A
| 03SR - Stations (RfL) | Cxxx-NCR-000364 | NCR | Links BM25 GL3 & 5 North Elliptical columns |  | Contr |  | PML - Pudding Mill Lane Portal (Central) |  | 2012-01-31 | 2012-03-06 18:19 | 35 | 2012-01-30 | Structural Engineering - Reinforcement | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | The Links BM25 of the GL3 & 5 North has been placed curved by 90mm from the centre to the designed stright line.
| 03SR - Stations (RfL) | Cxxx-NCR-000366 | NCR | Damage to D-walls |  | Contr |  | PML - Pudding Mill Lane Portal (Central) |  | 2012-02-09 | 2012-06-11 15:55 | 123 | 2012-02-01 | Civil - Civil Engineering General | 500 |  | Damaged | Repair |  | Complete |  | Completed |  | built the walls
| 03SR - Stations (RfL) | Cxxx-NCR-000374 | NCR | Pile N1P60 Concrete Drop |  | Contr |  | PML - Pudding Mill Lane Portal (Central) |  | 2012-02-19 | 2012-05-22 09:32 | 93 | 2012-02-06 | Civil - Civil Engineering General | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | On 26/01/12 pile N1P60 was complated, then during the next pile (N1P40) the concrete level dropped by approximatly 7m. After N1P40 was completed N1P60 was re-filled to ground level using a tremmie pipe from the piling rig.
| 03SR - Stations (RfL) | Cxxx-NCR-000384 | NCR | Strain Guages Detached from Props |  | Contr |  | PML - Pudding Mill Lane Portal (Central) |  | 2012-02-10 | 2012-03-06 16:35 | 25 | 2012-02-09 | Geotechnical Engineering - Geotechnical Monitoring | 500 |  | Damaged | Repair |  | Complete |  | Completed |  | At least 4no strain guages at the top level props (103mL and 100mL) has been detached from the props. There are no reports being generated by these damaged / detached strain guages, hence not being read and uploaded to UCIMS.
| 03SR - Stations (RfL) | Cxxx-NCR-000388 | NCR | PWA 5, 9, 15 & 18 as built out of tolerance |  | Contr |  | PML - Pudding Mill Lane Portal (Central) |  | 2012-02-17 | 2012-02-14 11:08 | -3 | 2012-02-13 | Geotechnical Engineering - Concrete - Bored Pile | 500 |  | System Defect | Use As-Is |  | Complete |  | Completed |  | PWA5= 78mm PWA9= 86mm PWA15= 76mm PWA18= 103mm See attached as built survey
| 03SR - Stations (RfL) | Cxxx-NCR-000392 | NCR | V03N Column - Concrete Finishing Surface |  | Contr |  | PML - Pudding Mill Lane Portal (Central) |  | 2013-06-30 | 2013-07-05 14:00 | 5 | 2012-02-13 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete |  | Completed |  | A number of blow holes, stains and sand scouring are found on the concrete surface of the DLR station viaduct column V03 north column after de-shuttering.
| 03SR - Stations (RfL) | Cxxx-NCR-000394 | NCR | Pile S1P27 |  | Contr |  | PML - Pudding Mill Lane Portal (Central) |  | 2013-02-02 | 2012-12-20 15:11 | -44 | 2012-02-14 | Civil - Civil Engineering General | 500 |  | System Defect | Use As-Is |  | Complete |  | Completed |  | Immediatly after installation the concrete level dropped approximatly 1m. This was 'topped-up' to pile mat level and it continued to drop. 6m3 of concrete was used to finally hold the correct concrete level. This used 18.96m3 of concrete in total. This pile was installed on 10/02/12
| 03SR - Stations (RfL) | Cxxx-NCR-000395 | NCR | VO2 South F3 Finish |  | Contr |  | PML - Pudding Mill Lane Portal (Central) |  | 2013-06-30 | 2013-07-05 14:02 | 5 | 2012-02-15 | Structural Engineering - Finishes | 500 |  | Material | Repair | 4 (0.5-3k) | Complete |  | Completed |  | Several sand scouring, blow holes and concrete discoloration on the concrete finish of the DLR Station pier VO2 South.
| 03SR - Stations (RfL) | Cxxx-NCR-000396 | NCR | VO4 North F3 Finish |  | Contr |  | PML - Pudding Mill Lane Portal (Central) |  | 2013-06-30 | 2013-07-05 14:01 | 5 | 2012-02-15 | Structural Engineering - Finishes | 500 |  | Material | Repair | 4 (0.5-3k) | Complete |  | Completed |  | Several blow holes on the concrete finish of the DLR Station pier VO4 South.
| 03SR - Stations (RfL) | Cxxx-NCR-000399 | NCR | GL2 & 4 North BM25 links Arched |  | Contr |  | PML - Pudding Mill Lane Portal (Central) |  | 2012-02-15 | 2012-02-14 20:47 | -1 | 2012-02-14 | Structural Engineering - Reinforcement | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | 5 No of links (BM25) at each of the Piers VO2N and VO4N have been placed arched (40mm) to suit descrapencies between position of vertical bars and bar schedule.
| 03SR - Stations (RfL) | Cxxx-NCR-000400 | NCR | Piles PR54, 70 & 85 - 38days concrete testing results |  | Contr |  | PML - Pudding Mill Lane Portal (Central) |  | 2012-02-17 | 2012-02-20 18:23 | 3 | 2012-02-15 | Structural Engineering - Testing | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | The CRL Retaining Wall 1 piles PR54, 70 and 85 have been tested at 38 days instead of the required 28. See attached cube certificate.
| 03SR - Stations (RfL) | Cxxx-NCR-000401 | NCR | Cracks on top of stub column pour to GL 10N |  | Contr |  | PML - Pudding Mill Lane Portal (Central) |  | 2012-02-24 | 2012-02-20 18:41 | -4 | 2012-02-15 | Structural Engineering - Concrete Member | 500 |  | Workmanship | Rework |  | Complete |  | Completed |  | There is cracking visible on the top of the stub column at GL10N, extent unknown.
| 03SR - Stations (RfL) | Cxxx-NCR-000402 | NCR | GL 8N Kicker - Minimum curing temperature not maintained |  | Contr |  | PML - Pudding Mill Lane Portal (Central) |  | 2012-02-22 | 2012-02-20 18:29 | -2 | 2012-02-15 | Structural Engineering - Concrete Member | 500 |  | Planning | Reject |  | Complete |  | Completed |  | The concrete to GL 8N kicker was recorded as being less than the minimum 5 degrees centigrade as stated in the concrete specification.
| 03SR - Stations (RfL) | Cxxx-NCR-000403 | NCR | GL11S Timber to face of column |  | Contr |  | PML - Pudding Mill Lane Portal (Central) |  | 2012-02-24 | 2012-02-20 18:39 | -4 | 2012-02-15 | Structural Engineering - Concrete Member | 500 |  |  | Use As-Is |  | Complete |  | Completed |  | Upon removing the column shutter for GL11S column, a piece of plywood was evident on the surface.
| 03SR - Stations (RfL) | Cxxx-NCR-000405 | NCR | West Abutment Ballast Wall top face reinforcement cover |  | Contr |  | PML - Pudding Mill Lane Portal (Central) |  | 2012-02-16 | 2012-02-21 09:32 | 5 | 2012-02-15 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | Cover varies from 51mm up to 99mm
| 03SR - Stations (RfL) | Cxxx-NCR-000410 | NCR | West Abutment Ballast Wall - Concrete pour times and finish |  | Contr |  | PML - Pudding Mill Lane Portal (Central) |  | 2012-02-22 | 2012-02-28 09:59 | 6 | 2012-02-20 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | Concrete was poured out of time specification due to concrete becoming to stiff in skip and not coming. Therefore it was rejected. There is also a visual cold joint in the ballast wall. This joint does not appear to be significant enough to affect the structural nature of the wall.
| 03SR - Stations (RfL) | Cxxx-NCR-000411 | NCR | West Abument Plinths - Bent Reinforcement |  | Contr |  | PML - Pudding Mill Lane Portal (Central) |  | 2012-02-23 | 2012-03-07 10:30 | 13 | 2012-02-22 | Civil - Civil Engineering General | 500 |  | Damaged | Rework |  | Complete |  | Completed |  | B12 'U' Bars have been bent on site to make way for shutter formwork soldiers
| 03SR - Stations (RfL) | Cxxx-NCR-000412 | NCR | Pier VO4S bent reinforcement not as per IFC drawing |  | Contr |  | PML - Pudding Mill Lane Portal (Central) |  | 2012-04-17 | 2012-04-18 09:54 | 1 | 2012-04-11 | Civil - Civil Engineering General | 500 |  | Workmanship | Rework |  | Complete |  | Completed |  | Pre site bent link bars (Bar Mark 14) in pier VO4S bent on site to fit around B32 starter bars (Bar Marks 04 & 03). Bars should not have been bent.
| 03SR - Stations (RfL) | Cxxx-NCR-000462 | NCR | Defect in concrete - Cut and Cover base slab - CJ04 |  | Contr |  | PML - Pudding Mill Lane Portal (Central) |  | 2012-04-19 | 2012-04-11 17:33 | -8 | 2012-03-22 | Civil - Concrete Pavement | 500 |  | Damaged | Repair |  | Complete |  | Completed |  | As per attached photograph. For reference the isue with concrete cover over at the coupler location is to be raised on a seperate NCR.
| 03SR - Stations (RfL) | Cxxx-NCR-000464 | NCR | CRL1 Pile Cropping |  | Contr |  | PML - Pudding Mill Lane Portal (Central) |  | 2012-03-19 | 2012-04-26 17:02 | 38 | 2012-03-16 | Civil - Civil Engineering General | 500 |  | Damaged | Repair |  | Complete |  | Completed |  | CRL piles PR40, 48, 50, 51, 52, 55 and 64 have small impact damage to the inner radii of the bent bar, where it is suspected that the breaker used for the pile cropping has struck it.
| 03SR - Stations (RfL) | Cxxx-NCR-000465 | NCR | Damaged Concrete to GL10 North Column |  | Contr |  | PML - Pudding Mill Lane Portal (Central) |  | 2012-12-30 | 2012-12-20 17:02 | -10 | 2012-03-19 | Structural Engineering - Concrete Member | 500 |  | Damaged | Repair |  | Complete |  | Completed |  | The top corner of the column has been chipped off at the rainwater recess location and there is honeycombing evident at the joints between the ttop of the stub column and the base of the main column. See attached photos.
| 03SR - Stations (RfL) | Cxxx-NCR-000466 | NCR | CRL1 PR42 |  | Contr |  | PML - Pudding Mill Lane Portal (Central) |  | 2012-03-21 | 2012-04-26 16:52 | 36 | 2012-03-19 | Civil - Civil Engineering General | 500 |  | Damaged | Repair |  | Complete |  | Completed |  | CRL pile PR42 was partially cut with the grinder when the cut-off level was pre-cut prior to pile cropping. During an inspection with Andrew Parris this bar was snapped-off by hand leaving a small stub of reinforcement bar just above the concrete level.
| 03SR - Stations (RfL) | Cxxx-NCR-000471 | NCR | Cut and Cover base slab CJ04 |  | Contr |  | PML - Pudding Mill Lane Portal (Central) |  | 2012-03-28 | 2012-04-26 18:13 | 29 | 2012-03-22 | Civil - Concrete Pavement | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | There are 4 lines of couplers within the concrete pour. In certain loactions (6 out of 50) the cover is low to the revised PTR answer. In general and on the rest of the coupler location the cover is acceptable and within tolerance. The sketches are attached for reference to show the location of the areas which are out of tolerance.
| 03SR - Stations (RfL) | Cxxx-NCR-000485 | NCR | Out of tolerance cover meter |  | Contr |  | PML - Pudding Mill Lane Portal (Central) |  | 2012-04-02 | 2012-04-26 18:17 | 24 | 2012-03-26 | Civil - Concrete Pavement | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | Pile caps 9N, 9S, 10N, 10S and 13N have out of tolerance cover. See attached surveys
| 03SR - Stations (RfL) | Cxxx-NCR-000489 | NCR | Requirement of UKAS accreditation for Grouting Test |  | Contr |  | PML - Pudding Mill Lane Portal (Central) |  | 2012-03-28 | 2012-04-26 11:22 | 29 | 2012-03-27 | Civil - Civil Engineering General | 500 |  | Planning | Repair |  | Complete |  | Completed |  | The support testing laboratory does not meet the requirements of the Contract Vol 2B part 20.8. The UKAS accreditation is not in place, & there is no evidence of the Contractors submittal of an alternative testing proposal at this late stage when work was planned to commence on the day of the surveillance.
| 03SR - Stations (RfL) | Cxxx-NCR-000494 | NCR | Blinding to Transfer Slab S3 |  | Contr |  | PML - Pudding Mill Lane Portal (Central) |  | 2012-03-28 | 2012-04-11 16:12 | 14 | 2012-03-27 | Civil - Civil Engineering General | 500 |  | Workmanship | Rework |  | Complete |  | Completed |  | The areas shown on the attached sketch are high.
| 03SR - Stations (RfL) | Cxxx-NCR-000496 | NCR | Bentonite testing instrument - Fann Viscometer not available on site |  | Contr |  | PML - Pudding Mill Lane Portal (Central) |  | 2012-03-30 | 2012-04-05 12:19 | 6 | 2012-03-28 | Civil - Civil Engineering General | 500 |  | Planning | Repair |  | Complete |  | Completed |  | The Fann viscometer was not available to undertake the gel strength test of bentonite.
| 03SR - Stations (RfL) | Cxxx-NCR-000497 | NCR | Bentonite sampler not available on site |  | Contr |  | PML - Pudding Mill Lane Portal (Central) |  | 2012-03-30 | 2012-04-11 15:50 | 12 | 2012-03-28 | Civil - Civil Engineering General | 500 |  | Planning | Use As-Is |  | Complete |  | Completed |  | The D-wall subcontractor had only a home-made plastic bentonite sampler available on site to collect the bentonite sample from the base of excavation. However, it is not fully convinced that the sampler can seal the collected bentonite sample.
| 03SR - Stations (RfL) | Cxxx-NCR-000500 | NCR | D walling testing regime |  | Contr |  | PML - Pudding Mill Lane Portal (Central) |  | 2012-04-04 | 2012-04-24 18:11 | 20 | 2012-03-28 | Civil - Civil Engineering General | 500 |  | System Defect | Use As-Is |  | Complete |  | Completed |  | A flow table was not avaliable on the 28 March 2012 to test the workability of the concrete for panel N28. A slump test was carried out in-place of the flow table.
| 03SR - Stations (RfL) | Cxxx-NCR-000529 | NCR | NWR Gantry 3/4B screw pile location |  | Contr |  | PML - Pudding Mill Lane Portal (Central) |  | 2012-04-13 | 2012-05-03 10:10 | 20 | 2012-04-04 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | Southwest pile of the NWR Gantry 3/4B has been installed out of tolerence, see sketch SK.SW.4.4.12/003. The pile has been installed 90mm towards the centre of the cap and 85mm towards western face of the cap.
| 03SR - Stations (RfL) | Cxxx-NCR-000540 | NCR | Pile Cropping - Impact Damage |  | Contr |  | PML - Pudding Mill Lane Portal (Central) |  | 2012-04-15 | 2012-04-27 16:25 | 12 | 2012-04-12 | Civil - Civil Engineering General | 500 |  | Damaged | Repair |  | Complete |  | Completed |  | Piles PR21, 09, 12, 14. S3P14, 12, 5, 23, 24, 25, 28, 33, 21, 9, 35, 61, 60, 63, 64, 66, 75, 92, 90, 88, 87, 85, 99, 111, 126, 104 have suffered impact damage as covered initially by NCR-464.
| 03SR - Stations (RfL) | Cxxx-NCR-000541 | NCR | west abutment wing wall bag washing |  | Contr |  | PML - Pudding Mill Lane Portal (Central) |  | 2012-06-30 | 2012-07-12 16:05 | 12 | 2012-04-12 | Civil - Civil Engineering General | 500 |  | Workmanship | Rework |  | Complete |  | Completed |  | N/A
| 03SR - Stations (RfL) | Cxxx-NCR-000550 | NCR | barbers rd type one infill |  | Contr |  | PML - Pudding Mill Lane Portal (Central) |  | 2012-04-19 | 2012-06-09 11:16 | 51 | 2012-04-16 | Civil - Civil Engineering General | 500 |  | Planning | Use As-Is |  | Complete |  | Completed |  | n/a
| 03SR - Stations (RfL) | Cxxx-NCR-000571 | NCR | Diaphragm Walls Injectable Tube |  | Contr |  | PML - Pudding Mill Lane Portal (Central) |  | 2012-04-25 | 2012-05-03 09:25 | 8 | 2012-04-24 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | The following joints have been installed without re-injectible tube; N28 (E&W), C37 (E&W), N22 (E&W), S35 (W), N27 (E), N29 (W), N20 (E), C38 (W), N30 (W). This is 14No joints in total.
| 03SR - Stations (RfL) | Cxxx-NCR-000584 | NCR | Cut and Cover Roof Slab |  | Contr |  | PML - Pudding Mill Lane Portal (Central) |  | 2012-05-01 | 2012-05-09 14:20 | 8 | 2012-04-30 | Civil - Concrete Pavement | 500 |  | Workmanship | Rework |  | Complete |  | Completed |  | Due to a setting out error for the internal wall box outs, reinforcement has been cut incorrectly. The box outs have been repositioned in the correct location and previously cut reinforcement has to be extended.
| 03SR - Stations (RfL) | Cxxx-NCR-000589 | NCR | Storing Concrete Cubes |  | Contr |  | PML - Pudding Mill Lane Portal (Central) |  | 2012-05-04 | 2012-06-19 10:30 | 46 | 2012-05-02 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | Following surveillance on 26/04/12, 4nr concrete test cubes were immersed in water in a curing tank , the max min thermometer has a reading of 29 & 28 degrees Celsius this is higher than the specified 22 degrees Celsius Max. Record of the curing water temperature are not maintained, record of the air curing temperature is not maintained either
| 03SR - Stations (RfL) | Cxxx-NCR-000595 | NCR | Transfer Slab S2-P138 |  | Contr |  | PML - Pudding Mill Lane Portal (Central) |  | 2012-05-10 | 2012-06-12 13:56 | 33 | 2012-05-03 | Civil - Civil Engineering General | 500 |  | Damaged | Repair |  | Complete |  | Completed |  | Whilst breaking down pile S2P138 it became evident that the concrete was contaminated below the cut-off level.
| 03SR - Stations (RfL) | Cxxx-NCR-000597 | NCR | DLR NOS Bridge Northern Beam bent starter bars |  | Contr |  | PML - Pudding Mill Lane Portal (Central) |  | 2012-11-03 | 2012-11-02 12:18 | -1 | 2012-05-08 | Structural Engineering - Reinforcement | 500 |  | Damaged | Repair |  | Complete |  | Completed |  | Approximately 40No. starter bars have been damaged during transportation from __'s precast yard to Cxxx Pudding Mill Lane. The starter bars are protruding out of the precast beam at an angle of approximately 45 degrees as opposed to 90 degrees to the beam. See attached photo
| 03SR - Stations (RfL) | Cxxx-NCR-000598 | NCR | GL 13 - 14 South NOS Bridge Beam cut reinforcement starter bars to allow beam extension to be installed |  | Contr |  | PML - Pudding Mill Lane Portal (Central) |  | 2012-12-21 | 2012-12-21 13:01 | 0 | 2012-05-15 | Structural Engineering - Reinforcement | 500 |  | Design | Repair |  | Complete |  | Completed |  | Starter bars protruding from the beam into the deck slab were required to be cut so that the temporary beam extension could be installed.
| 03SR - Stations (RfL) | Cxxx-NCR-000602 | NCR | Sampling and Testing of Fresh Concrete |  | Contr |  | PML - Pudding Mill Lane Portal (Central) |  | 2012-05-13 | 2012-05-28 14:54 | 15 | 2012-05-10 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | Sampling and testing of fresh concrete was undertaken by the D wall Contractor’s personnel who had undergone training by the UKAS accredited laboratory Environmental Scientific Group (__). __ have issued certification with named individuals to document the training. The certification states that “All examinations and assessments were carried out in accordance with __ procedures which are audited by UKAS.”The __ training certificate does not meet the above requirement.
| 03SR - Stations (RfL) | Cxxx-NCR-000603 | NCR | Failure to comply |  | Contr |  | PML - Pudding Mill Lane Portal (Central) |  | 2012-09-17 | 2012-05-23 10:55 | -117 | 2012-05-10 | Logistics - Logistics - General | 500 |  | Planning | Use As-Is |  | Complete |  | Completed |  | 16 vehicles for Cut and Cover roof slab bay 1 not booked in. This was noted by site security as the vehicles attending site were not on the gate sheets. The Logistics Manager arranged with the TCC to have the day’s plan unlocked and this was amended after 7 loads had entered site. Therefore the remaining loads were entered on the gatesheet as planned bookings, however they were added after the deadline had passed.
| 03SR - Stations (RfL) | Cxxx-NCR-000604 | NCR | Marshgate Lane Soffit Concrete Pour |  | Contr |  | PML - Pudding Mill Lane Portal (Central) |  | 2012-11-21 | 2012-10-05 16:59 | -47 | 2012-06-11 | Civil - Civil Engineering General | 500 |  | Workmanship | Rework |  | Complete |  | Completed |  | F3 finish not achieved. exposed surface not acceptable
| 03SR - Stations (RfL) | Cxxx-NCR-000606 | NCR | CRL1 Piles cut too low |  | Contr |  | PML - Pudding Mill Lane Portal (Central) |  | 2013-03-01 | 2012-12-20 12:49 | -71 | 2012-05-11 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | Piles PR7 and 9 were saw-cut to the Transfer Slab cut-off level of 103.4m, which is 175mm low. PR9 has since been broken down to this level.
| 03SR - Stations (RfL) | Cxxx-NCR-000611 | NCR | DLR Station Bearing Incorrectly Installed |  | Contr |  | PML - Pudding Mill Lane Portal (Central) |  | 2012-05-13 | 2012-06-19 11:13 | 37 | 2012-05-11 | Civil - Structural Engineering | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | Bearing identification mark E on GL 01 E has been installed incorrectly. The orientation for bearing id E is 90 degrees out of direction.
| 03SR - Stations (RfL) | Cxxx-NCR-000614 | NCR | contemporaneous records |  | Contr |  | PML - Pudding Mill Lane Portal (Central) |  | 2012-06-14 | 2012-06-18 11:43 | 4 | 2012-05-14 | Civil - Civil Engineering General | 500 |  | System Defect | Use As-Is |  | Complete |  | Completed |  | ITP Cxxx-MRG-C-ITP-CR094_WS111-50022 rev 2.0 weld inspection records were not made available. D Wall Rig calibrations records that demonstrate traceability to national standards as required by Works Information Volume 2B part 20, clause 20.8 were also not made available during.
| 03SR - Stations (RfL) | Cxxx-NCR-000618 | NCR | Concrete placement - greater than 30 minutes between loads |  | Contr |  | PML - Pudding Mill Lane Portal (Central) |  | 2012-05-25 | 2012-06-15 10:05 | 21 | 2012-05-15 | Civil - Concrete Pavement | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | See attached pour record. NCR occured at 16:40 - 17:54 (highlighted on attachment). During this time concrete face was kept live by placing vibration poker along active face of concrete.
| 03SR - Stations (RfL) | Cxxx-NCR-000623 | NCR | Incorrect concrete placed in Cut and Cover roof slab |  | Contr |  | PML - Pudding Mill Lane Portal (Central) |  | 2012-05-21 | 2012-05-18 09:34 | -3 | 2012-05-17 | Civil - Concrete Pavement | 500 |  | Supervision/Management | Repair |  | Complete |  | Completed |  | Approximately 2m3 placed before pour was halted by __. Pour to be cleaned out. Classed as an NCR due to remedial work not fully complete within the shift.
| 03SR - Stations (RfL) | Cxxx-NCR-000624 | NCR | Pile Integrity Testing - S3 |  | Contr |  | PML - Pudding Mill Lane Portal (Central) |  | 2012-05-31 | 2012-07-09 11:37 | 39 | 2012-05-17 | Civil - Civil Engineering General | 500 |  | System Defect | Use As-Is |  | Complete |  | Completed |  | The following piles were not integrity tested; Pile Number / Installation Date S3P145 / 22 Feb S3P146 / 9 Mar S3P147 / 6 Mar S3P148 / 9 Mar S3P149 / 6 Mar S3P150 / 7 Mar S3P151 / 6 Mar S3P14 / 12 Dec
| 03SR - Stations (RfL) | Cxxx-NCR-000634 | NCR | Concrete poker lodged in 11KV internal wall pour |  | Contr |  | PML - Pudding Mill Lane Portal (Central) |  | 2012-05-31 | 2012-06-06 09:37 | 6 | 2012-05-23 | Civil - Concrete Pavement | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | When it became apparent that the poker could not be dislodged, the power cable was cut as low into the pour as possible, approxiimately 500mm of lead remaining. The location of the concrete poker is shown on the attached annotated drawing.
| 03SR - Stations (RfL) | Cxxx-NCR-000635 | NCR | Damage to Station & Viaduct Columns (Impact) |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2013-06-30 | 2013-07-05 11:38 | 5 | 2012-05-23 | Structural Engineering - Concrete Member | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete |  | Completed |  | Some column surfaces were damaged during removal of the column shutters. See attached photos.
| 03SR - Stations (RfL) | Cxxx-NCR-000636 | NCR | Honeycombing to concrete columns (DLR Station & Marshgate Lane Viaduct) |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2013-07-19 | 2013-07-22 12:19 | 3 | 2012-05-23 | Structural Engineering - Concrete Member | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete |  | Completed |  | Honeycombing is evident on some of the DLR Station / Marshgate Lane Viaduct RC columns.
| 03SR - Stations (RfL) | Cxxx-NCR-000637 | NCR | Uneven spacing of starter bars to precast beams for Marshgate Lane Viaduct |  | Contr |  | PML - Pudding Mill Lane Portal (Central) |  | 2012-12-21 | 2012-08-08 12:39 | -135 | 2012-05-23 | Structural Engineering - Reinforcement | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | Precast beams have starter bars that are unevenly spaced
| 03SR - Stations (RfL) | Cxxx-NCR-000638 | NCR | Bent starter bars to precast beams for Marshgate Lane Viaduct |  | Contr |  | PML - Pudding Mill Lane Portal (Central) |  | 2012-12-21 | 2012-12-20 16:09 | -1 | 2012-05-23 | Structural Engineering - Reinforcement | 500 |  | Damaged | Rework |  | Complete |  | Completed |  | A number of starter bars protruding out of the precast beams into the deck slab have been bent so are not perpendicular to the beams. See attached photos.
| 03SR - Stations (RfL) | Cxxx-NCR-000651 | NCR | Damage to S3-7 Transfer Slab |  | Contr |  | PML - Pudding Mill Lane Portal (Central) |  | 2012-11-30 | 2012-08-08 13:49 | -114 | 2012-05-30 | Civil - Civil Engineering General | 500 |  | Damaged | Repair |  | Complete |  | Completed |  | The corner of the latest concrete pour has been knocked-off. Approx size 50mm x 50mm x 100mm. This is on the construction joint to the next pour.
| 03SR - Stations (RfL) | Cxxx-NCR-000660 | NCR | Marshgate Lane Viaduct between GL9 & 10 |  | Contr |  | PML - Pudding Mill Lane Portal (Central) |  | 2013-04-15 | 2013-04-17 16:06 | 2 | 2012-06-01 | Civil - Civil Engineering General | 500 |  | Workmanship | Rework |  | Complete |  | Completed |  | 1. The concrete pour has not produced sound dense concrete; voids are apparent 2. The steel reinforcment have insufficient concrete cover; it is exposed on the deck soffit. 3. The method and sequence of pouring concrete has resulted in cold joints in several locations
| 03SR - Stations (RfL) | Cxxx-NCR-000663 | NCR | CRL1 Pile Cap (Pour 1) Concrete Testing |  | Contr |  | PML - Pudding Mill Lane Portal (Central) |  | 2012-08-15 | 2012-07-13 08:54 | -33 | 2012-06-06 | Civil - Civil Engineering General | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | The first pour on the CRL1 retaining wall pile cap, poured on the 29th March 2012, only obtained 38N/mm2.
| 03SR - Stations (RfL) | Cxxx-NCR-000664 | NCR | S2 Transfer Slab Pile Cropping |  | Contr |  | PML - Pudding Mill Lane Portal (Central) |  | 2012-07-15 | 2012-06-12 13:49 | -33 | 2012-06-06 | Civil - Civil Engineering General | 500 |  | Damaged | Repair |  | Complete |  | Completed |  | Piles S2P17, 34, 57, 70, 76, 85, 89, 94, 97, 123, 124, 140 & 155 were damaged during pile cropping operation.
| 03SR - Stations (RfL) | Cxxx-NCR-000674 | NCR | Bearing VO4S - paint finish |  | Contr |  | PML - Pudding Mill Lane Portal (Central) |  | 2012-10-31 | 2012-08-08 11:37 | -84 | 2012-06-19 | Structural Engineering - Structural Engineering - General | 500 |  | Damaged | Repair |  | Complete |  | Completed |  | During the placement of reinforcement to the station deck/beam pour 3 rebar was pulled through against the top plate edge of the bearing and has damaged the paint finish
| 03SR - Stations (RfL) | Cxxx-NCR-000682 | NCR | Slump test |  | Contr |  | PML - Pudding Mill Lane Portal (Central) |  | 2012-07-12 | 2012-06-26 10:12 | -16 | 2012-06-20 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Repair |  | Complete |  | Completed |  | Specified remixing did not take place during the CRL surveillance of 15th June 2012. The Contractor confirmed that the remixing was not undertaken as it was not included on the Contractors Inspection and Test Plan and stated that to date remixing had not taken place with the exception for Flow table tests.
| 03SR - Stations (RfL) | Cxxx-NCR-000683 | NCR | DLR station deck-Bay 1/Pour 1-Concrete surface |  | Contr |  | PML - Pudding Mill Lane Portal (Central) |  | 2012-10-31 | 2012-11-02 14:41 | 2 | 2012-06-20 | Structural Engineering - Concrete Member | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | During the concrete pour, long screed rails (steel tubes) were used and were not removed till the end of the pour. This required the concreting gang to revisit parts of the slab were concrete was in its initial setting (2-3 hours after placing) phase to remove the rails ,make good and finish the surface. This resulted in: -Movement, vibration and potential physical shock on immature concrete (workforce walking on concrete to finish, remove rails etc.) -Fresh concrete placed on top of the setting concrete to seal the voids left by the rails. -Wetting of the concrete surface to assist in finishing and amalgamating the fresh and set concrete -Poor ‘tamped’ finish ,the appearance of aggregates and ‘no fines’ concrete on the surface with potentially a weak concrete surface layer and shrinkage cracking. Refer to attached photos
| 03SR - Stations (RfL) | Cxxx-NCR-000686 | NCR | Station Deck Pour 2 |  | Contr |  | PML - Pudding Mill Lane Portal (Central) |  | 2012-10-25 | 2012-10-17 16:41 | -8 | 2012-06-25 | Civil - Civil Engineering General | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | There was a concern regarding the excessive rainwater mixed with the fresh concrete being placed on the station deck slab pour Bay2-Pour 1 (last 1m wide section) dated 15/06/2012. The impact of the rainwater remixing could have a potential adverse effects to the concrete's strength and durability.
| 03SR - Stations (RfL) | Cxxx-NCR-000694 | NCR | 220612 Concrete Drivers Untrained |  | Contr |  | PML - Pudding Mill Lane Portal (Central) |  | 2012-07-31 | 2012-06-26 10:09 | -35 | 2012-06-25 | Logistics - Logistics - General | 500 |  | System Defect | Rework |  | Complete |  | Completed |  | On 22 June 12 David Fuller (KH07 KNN) and Dumitru Stoian (KE56 GMX) driving __ concrete wagons were in breach of their 5 visits before attending a driver induction course. They were permitted to contunie as the 240m3 Transfer Slab pour was in-progress and without them would not have been able to continue.
| 03SR - Stations (RfL) | Cxxx-NCR-000695 | NCR | VMBS - Transfer Slab Concrete Pour |  | Contr |  | PML - Pudding Mill Lane Portal (Central) |  | 2012-07-31 | 2012-06-26 10:59 | -35 | 2012-06-26 | Logistics - Logistics - General | 500 |  | System Defect | Use As-Is |  | Complete |  | Completed |  | On 22/06/12 27 __ concrete wagons were booked on the VMBS system for that day, 24hrs later than required.
| 03SR - Stations (RfL) | Cxxx-NCR-000696 | NCR | Pile Cropping Transfer Slab S2 |  | Contr |  | PML - Pudding Mill Lane Portal (Central) |  | 2012-10-25 | 2012-10-24 18:02 | -1 | 2012-06-26 | Civil - Civil Engineering General | 500 |  | Damaged | Repair |  | Complete |  | Completed |  | Piles S2P38, 56, 69, 75, 87, 92 have small impact damage durung the pile cropping operation.
| 03SR - Stations (RfL) | Cxxx-NCR-000697 | NCR | Colouring of Curing Compound |  | Contr |  | PML - Pudding Mill Lane Portal (Central) |  | 2012-10-20 | 2012-10-15 10:49 | -5 | 2012-06-26 | Civil - Concrete Pavement | 500 |  | Material | Repair |  | Complete |  | Completed |  | The used curing compound is colourless after spraying onto the concrete surface.
| 03SR - Stations (RfL) | Cxxx-NCR-000699 | NCR | Transfer Slab S2 Splice Lengths |  | Contr |  | PML - Pudding Mill Lane Portal (Central) |  | 2012-07-31 | 2012-07-13 09:03 | -18 | 2012-06-27 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | Over pile S2P123 4No bars had a lap length of 1000mm. This was due to the position of the construction joint.
| 03SR - Stations (RfL) | Cxxx-NCR-000710 | NCR | FY06 JXU Trellis Works Vehicle |  | Contr |  | PML - Pudding Mill Lane Portal (Central) |  | 2012-07-31 | 2012-07-09 11:34 | -22 | 2012-07-02 | Logistics - Logistics - General | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | On 27/06/12 a Trellis Works truck mounted MEWP, vehicle registration FY06 JXU, entered site unplanned and not fitted with the required safety equipment. The vehicle was being used to carry out an 'aerial survey'.
| 03SR - Stations (RfL) | Cxxx-NCR-000718 | NCR | EIP Base Slab first pour, area of low cover |  | Contr |  | PML - Pudding Mill Lane Portal (Central) |  | 2012-07-31 | 2012-07-10 16:51 | -21 | 2012-07-04 | Civil - Concrete Pavement | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | An area of low cover has been discovered by cover meter survey carried out by MPB near the construction joint line between pours. Results vary from 36mm to 42mm.
| 03SR - Stations (RfL) | Cxxx-NCR-000732 | NCR | PSF resin |  | Contr |  | PML - Pudding Mill Lane Portal (Central) |  | 2012-07-19 | 2012-08-06 14:03 | 18 | 2012-07-11 | Civil - Civil Engineering General | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | The MCR has not been approved as the data sheet does not include shear value for 32mm diameter reinforcement bar. This has been used on the Cut and Cover base slab in bays 1 and 2 and for 12 number bars in the third base slab.
| 03SR - Stations (RfL) | Cxxx-NCR-000733 | NCR | D-wall panel N29 cube strength |  | Contr |  | PML - Pudding Mill Lane Portal (Central) |  | 2012-07-19 | 2012-08-07 10:24 | 19 | 2012-07-12 | Civil - Civil Engineering General | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | At 56 days the cube streghth only achieved 36N/mm2. See attached sheet
| 03SR - Stations (RfL) | Cxxx-NCR-000735 | NCR | Transfer slab S3 cover survey |  | Contr |  | PML - Pudding Mill Lane Portal (Central) |  | 2012-07-20 | 2012-08-08 11:23 | 19 | 2012-07-13 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | 4 No readings were slightly above the max. Seea attached survey
| 03SR - Stations (RfL) | Cxxx-NCR-000736 | NCR | Missing starter bars to cross wall 7 |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2015-03-31 | 2015-03-27 15:34 | -4 | 2012-07-13 | Civil - Concrete Pavement | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | 30 number, B25, 2 rows at 150mm centres missing from concrete pour.
| 03SR - Stations (RfL) | Cxxx-NCR-000748 | NCR | VO7N Pile Cap - Compressive Strength Statistical failure on the C40/50C mix |  | Contr |  | PML - Pudding Mill Lane Portal (Central) |  | 2012-08-20 | 2012-09-11 17:47 | 22 | 2012-07-19 | Civil - Civil Engineering General | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | Mean statistical compressive strength at 28 days for the second load of concrete is 43.0N/mm2.
| 03SR - Stations (RfL) | Cxxx-NCR-000749 | NCR | VO7S Pile Cap - Compressive Strength Statistical failure on the C40/50C mix |  | Contr |  | PML - Pudding Mill Lane Portal (Central) |  | 2012-08-20 | 2012-08-20 10:49 | 0 | 2012-07-19 | Civil - Civil Engineering General | 500 |  | Planning | Use As-Is |  | Complete |  | Completed |  | Mean statistical compressive strength at 28 days for the second load of concrete is 43.0N/mm2.
| 03SR - Stations (RfL) | Cxxx-NCR-000771 | NCR | Out of tolerance NWR gantry bolts |  | Contr |  | PML - Pudding Mill Lane Portal (Central) |  | 2012-08-15 | 2012-08-15 17:46 | 0 | 2012-08-08 | Civil - Civil Engineering General | 500 |  | Design | Use As-Is |  | Complete |  | Completed |  | As per attached as built survey. Bolts have been cast with cones for future adjustments, however due to reinforcement and plate design issues (previously documented) bolt positions were cast close to design position as physically allowed. Bolt clusters were checked and approved by __ contractor prior to pouring this structure and as-built records have since been taken.
| 03SR - Stations (RfL) | Cxxx-NCR-000796 | NCR | Load Transfer Slabs Concrete Failure |  | Contr |  | PML - Pudding Mill Lane Portal (Central) |  | 2012-10-15 | 2012-09-11 10:06 | -34 | 2012-08-20 | Civil - Civil Engineering General | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | Cast 27/04/12 (Transfer Slab S3-Pour 3) 2 of 5 samples failed the running average, achieving a low of 50.5N/mm². Cast 23/05/12 (Transfer Slab S3-Pour 5) 5 of 8 samples failed the individual strength, achieving a low of 39.3N/mm². 6 samples failed the running average, achieving a low of 42N/mm². Cast 28/05/12 (Transfer Slab S3-Pour 7) 4 of 6 samples failed the running average, achieving a low of 43N/mm².
| 03SR - Stations (RfL) | Cxxx-NCR-000838 | NCR | 11kV Central Wall Honeycombing |  | Contr |  | PML - Pudding Mill Lane Portal (Central) |  | 2012-10-19 | 2012-10-12 10:55 | -7 | 2012-09-17 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | Localised areas of honeycombing have been made apparent after removal of shuttering. These are located on walls A-B and B-C. See attached photographs.
| 03SR - Stations (RfL) | Cxxx-NCR-000870 | NCR | Slab N1 pile defects on completion of breakdown |  | Contr |  | PML - Pudding Mill Lane Portal (Central) |  | 2012-11-04 | 2012-10-25 14:19 | -10 | 2012-10-12 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | NCR details 1 Piles N1P2, NP145, N1P51, N1P36, N1P34 & N1P21 have had bars damaged by mechanical breakdown. 2 Pile N1P36 cage is positioned badly within the pile and offers little to no cover. 3 Pile N1P1 cage slumped 150mm & N1P60 cage slumped 270mm during construction.
| 03SR - Stations (RfL) | Cxxx-NCR-000874 | NCR | Slab S2 pour 5 surface finish |  | Contr |  | PML - Pudding Mill Lane Portal (Central) |  | 2012-12-06 | 2012-11-12 09:52 | -24 | 2012-10-13 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | During pouring / floating a part of the transfer slab S2 pour 5, we were experiencing very heavy and prolonged rain. It was suggested by CRL that we pull a plastic sheet over the finished section to protect from the rain. In doing this we have a rippled surface finish to this section of the pour.
| 03SR - Stations (RfL) | Cxxx-NCR-000875 | NCR | Slab S2 pour 5 concrete quality concern |  | Contr |  | PML - Pudding Mill Lane Portal (Central) |  | 2013-01-30 | 2013-01-17 15:07 | -13 | 2012-10-13 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | During pouring a section of slab S2 pour 5, we experienced very heavy and prolonged rain. Dispite efforts at the time to sheild the pour, rain water ran across the live face and ponded on the area to be floated. Excess water was then removed before floating off.
| 03SR - Stations (RfL) | Cxxx-NCR-000876 | NCR | 50mm foam joint between S2 / S3 ripped out |  | Contr |  | PML - Pudding Mill Lane Portal (Central) |  | 2012-11-07 | 2012-11-09 13:42 | 2 | 2012-10-13 | Civil - Civil Engineering General | 500 |  | Damaged | Repair |  | Complete |  | Completed |  | Due to trafficking the 50mm foam joint between slab S2 & S3 is partially ripped out and potentially can allow foreign objects in.
| 03SR - Stations (RfL) | Cxxx-NCR-000881 | NCR | Hy-Rib used without approval in Beam Vertical Construction Joint |  | Contr |  | PML - Pudding Mill Lane Portal (Central) |  | 2012-10-22 | 2012-10-18 18:05 | -4 | 2012-10-18 | Civil - Civil Engineering General | 500 |  | Material | Rework |  | Complete |  | Completed |  | Hy-rib used as a permanent formwork in the vertical construction joint of the beams in Bay 1-2 was not approved.
| 03SR - Stations (RfL) | Cxxx-NCR-000883 | NCR | Water ingress into fresh concrete |  | Contr |  | PML - Pudding Mill Lane Portal (Central) |  | 2013-05-30 | 2013-05-10 12:58 | -20 | 2012-10-18 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | Immature concrete at the construction joint between Pour 2-3 on Bay 1 has received some inadvertent rain during the curing process. The surface has been visible affected by water pooling and subsequent ingress. The finish is uneven and the strength of the concrete is compromised. Water ingress in the permanent structure may be a future problem at the joint.
| 03SR - Stations (RfL) | Cxxx-NCR-000885 | NCR | Surface Finish to Bay 1 - Pour 3 - South Platform |  | Contr |  | PML - Pudding Mill Lane Portal (Central) |  | 2012-10-23 | 2012-10-19 11:24 | -4 | 2012-10-18 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | Bay 1 – Pour 3 – South Platform has a large indent in the surface of the concrete due to a dropped timber barrier used to tent the fresh concrete from wet weather
| 03SR - Stations (RfL) | Cxxx-NCR-000920 | NCR | Slab N2 piles |  | Contr |  | PML - Pudding Mill Lane Portal (Central) |  | 2012-11-07 | 2012-11-09 13:33 | 2 | 2012-10-24 | Civil - Civil Engineering General | 500 |  | Damaged | Repair |  | Complete |  | Completed |  | Protruding steel for piles: N2P6, 20, 22, 27, 32, 35, 39, 40, 50, 52 & 58 have all had steel damaged by mechanical breakdown.
| 03SR - Stations (RfL) | Cxxx-NCR-000921 | NCR | Slab N2 piles |  | Contr |  | PML - Pudding Mill Lane Portal (Central) |  | 2012-11-07 | 2012-11-09 13:27 | 2 | 2012-10-24 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | Piles N2P20, 21, 28 & 39 all apprear to have low cover to the pile cage. It looks like the cage has fallen to one side during construction.
| 03SR - Stations (RfL) | Cxxx-NCR-000956 | NCR | Concrete Finish - Bay 2 - Pour 2 South Beam - Localised honeycombing and sand runs |  | Contr |  | PML - Pudding Mill Lane Portal (Central) |  | 2013-01-31 | 2012-12-20 16:01 | -42 | 2012-11-01 | Civil - Civil Engineering General | 500 |  | Material | Repair |  | Complete |  | Completed |  | When the shutter was struck the external face had a small area of localised honeycombing and sand runs, possibly due to a small portion of the concrete being insufficiently mixed before being placed in the pour.
| 03SR - Stations (RfL) | Cxxx-NCR-000965 | NCR | Concrete Finish - Bay 3 - Pour 2 South Beam - Localised honeycombing and sand runs |  | Contr |  | PML - Pudding Mill Lane Portal (Central) |  | 2013-01-07 | 2012-12-21 11:37 | -17 | 2012-11-07 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | When the beam shutter was struck the external face had a small area of localised honeycombing and sand runs.
| 03SR - Stations (RfL) | Cxxx-NCR-000984 | NCR | DLR NOS Bridge Beam Vent Cut |  | Contr |  | PML - Pudding Mill Lane Portal (Central) |  | 2013-01-31 | 2013-01-31 18:10 | 0 | 2012-11-12 | Civil - Civil Engineering General | 500 |  | Damaged | Repair |  | Complete |  | Completed |  | The vent pipes to the post-tensioning ducts in the precast edge beams have been cut flush. It is understood the pipes were cut because they were possibly in the way of temporary works – it is evident this was not the case for the central vents and if there was a clash at the end.
| 03SR - Stations (RfL) | Cxxx-NCR-000986 | NCR | Concrete Finish - Bay 1-3 - North & South Beam Kicker Construction Joint |  | Contr |  | PML - Pudding Mill Lane Portal (Central) |  | 2013-06-30 | 2013-07-11 16:22 | 11 | 2012-11-13 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete |  | Completed |  | When the internal track facing shutter was struck the face of the concrete at the line of the construction joint between the beam and deck had a small area of localised honeycombing. This was possibly due to grout loss at the kicker joint.
| 03SR - Stations (RfL) | Cxxx-NCR-000988 | NCR | DLR NOS Grout trial - grouting failure |  | Contr |  | PML - Pudding Mill Lane Portal (Central) |  | 2012-12-20 | 2012-12-21 13:18 | 1 | 2012-11-13 | Structural Engineering - Post Tensioning | 500 |  | Design | Rework |  | Complete |  | Completed |  | With reference to the grout trial in Site 1 car park. __ carried out the grouting of the tendon on 24th October. The beam was then cut at each end and in the middle. at the east end the grout demonstrated full penetration and no voids. At the west end the tendon illsutrated a 60% void. This exceeds the limit 5% limit for grouting. The reason for this void has been identified by __ as an air pocket caused by inusfficient venting at the end cap.
| 03SR - Stations (RfL) | Cxxx-NCR-000989 | NCR | Damage to expansion joint dowel bars |  | Contr |  | PML - Pudding Mill Lane Portal (Central) |  | 2012-12-21 | 2012-12-06 16:08 | -15 | 2012-11-14 | Civil - Civil Engineering General | 500 |  | Damaged | Repair |  | Complete |  | Completed |  | 5no dowel bars bent due to temporary works concrete infill to sheet pile cut-of wall, subsequently broken down for base slab construction. Waterbar has a tear in one section.
| 03SR - Stations (RfL) | Cxxx-NCR-000996 | NCR | CRL 1 wall Liberty finish |  | Contr |  | PML - Pudding Mill Lane Portal (Central) |  | 2013-03-15 | 2013-03-05 15:29 | -10 | 2012-11-15 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | Spacer blocks are visable in the Liberty finsih at the surface in the 1st 2 CRL 1 pours.
| 03SR - Stations (RfL) | Cxxx-NCR-001024 | NCR | Concrete Curing |  | Contr |  | PML - Pudding Mill Lane Portal (Central) |  | 2012-12-07 | 2012-12-06 16:14 | -1 | 2012-11-21 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | Due to prevailing weather conditions (strong drying wind) - the surface of the CRL1 retaining wall pour 3 was allowed to dry out before/during the installation of the plastic sheeting.
| 03SR - Stations (RfL) | Cxxx-NCR-001025 | NCR | Insufficient Cover to Reinforcement |  | Contr |  | PML - Pudding Mill Lane Portal (Central) |  | 2013-03-15 | 2013-03-06 12:02 | -9 | 2012-11-21 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Rework |  | Complete |  | Completed |  | Lack of cover to reinforcement - reinforcement exposed on surface of pour. 0mm cover.
| 03SR - Stations (RfL) | Cxxx-NCR-001030 | NCR | DLR NOS Bridge Deck Slab Damaged |  | Contr |  | PML - Pudding Mill Lane Portal (Central) |  | 2012-12-07 | 2012-12-04 13:18 | -3 | 2012-11-22 | Civil - Structural Engineering | 500 |  | Damaged | Repair |  | Complete |  | Completed |  | The DLR NOS Bridge Deck-slab-pour 1 (middle section) completed on 15/11/2012. Post drilled inserts (required for formwork stop ends) were fixed to the pour 1 deck slab using 200mm bolts without Crossrail's authorisation. One of the bolts was drilled directly above a post tensioning duct potentially damaging it.
| 03SR - Stations (RfL) | Cxxx-NCR-001031 | NCR | Wrong rebar shape code at DLR NOS Bridge |  | Contr |  | PML - Pudding Mill Lane Portal (Central) |  | 2012-12-10 | 2012-12-04 10:21 | -6 | 2012-11-22 | Civil - Structural Engineering | 500 |  | Workmanship | Rework |  | Complete |  | Completed |  | A wrong rebar shape code (i.e. 51) for BM16-23 was installed for the links around the post-tensioning end anchorages atthe DLR NOS Bridge Deck without an accepted FCD.
| 03SR - Stations (RfL) | Cxxx-NCR-001033 | NCR | CRL 1 wall base pour 21/11/12 |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2015-06-01 | 2015-03-30 15:43 | -63 | 2012-11-22 | Civil - Civil Engineering General | 4000 |  | Workmanship | Repair | 3 (3-6k) | Complete | Subcontractor Problems - Insufficient work planning by the subcontractors | Completed |  | During the most eastern (pre switch over) CRL 1 wall, base pour, dated 21/11/12, prolonged & excessive rain occoured during this pour and concern has been raised that best efforts were not made by MPB to remove water from the live face possibly weakening the mix design at the surface of the base.
| 03SR - Stations (RfL) | Cxxx-NCR-001036 | NCR | South Up-Stand Wall - Spacer Blocks Protruding from Face of Pour |  | Contr |  | PML - Pudding Mill Lane Portal (Central) |  | 2015-10-28 | 2015-11-11 15:45 | 14 | 2012-11-22 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Spacers Protruding on BOTH faces of the wall indicate low cover as well as poor quaility surface finish.
| 03SR - Stations (RfL) | Cxxx-NCR-001053 | NCR | Integrity Testing North Transfer Slabs |  | Contr |  | PML - Pudding Mill Lane Portal (Central) |  | 2012-12-21 | 2012-12-19 16:42 | -2 | 2012-11-27 | Civil - Civil Engineering General | 500 |  | System Defect | Use As-Is |  | Complete |  | Completed |  | Piles N2P56 & 58 are missing pile integrity test records.
| 03SR - Stations (RfL) | Cxxx-NCR-001076 | NCR | Lack of concrete cover to reinforcement - CJO6 - Cut and Cover base slab |  | Contr |  | PML - Pudding Mill Lane Portal (Central) |  | 2013-03-31 | 2012-12-20 16:35 | -101 | 2012-12-05 | Civil - Concrete Pavement | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | During the concrete pour, the stop end shutter failed and a small amount of concrete was lost through the underside of the shutter. This has led to an area of low cover on the line of the stop end and a few cracks. A cover meter survey of the stop end has been carried out and is attached to this NCR. This has been undertaken along the line of the stop end, where the reinforcement is exposed and 500mm back into the pour (which has proved to be in accordance with the specification).
| 03SR - Stations (RfL) | Cxxx-NCR-001084 | NCR | South upstand wall north face dividag bar cast in wall |  | Contr |  | PML - Pudding Mill Lane Portal (Central) |  | 2015-10-28 | 2015-12-14 15:37 | 47 | 2012-12-06 | Civil - Civil Engineering General | 1000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Panels 37 / 38 had several dividag bars left protruding from the wall. They should have been trimmed back 50mm beyond the surface and made good using the approved method. The divi bars were only cut back 10mm and a repair placed.
| 03SR - Stations (RfL) | Cxxx-NCR-001093 | NCR | Slab S1 damage to pile steel by pile break down |  | Contr |  | PML - Pudding Mill Lane Portal (Central) |  | 2012-12-21 | 2012-12-21 11:16 | 0 | 2012-12-12 | Civil - Civil Engineering General | 500 |  | Damaged | Repair |  | Complete |  | Completed |  | Pile rebar in piles S1P1, 2, 5, 6, 11, 16, 19, 20, 21, 23, 25, 34, 36, 40, 44, 47, 48, 49, 54, 55 & 56 have all sustained minor impact damage to pile steel during the pile breakdown process. Pile rebar in piles S1P3, 7, 8 & 22 have all sustained a bend greater than 30 deg during pile break down.
| 03SR - Stations (RfL) | Cxxx-NCR-001095 | NCR | South Up stand Wall Panel 43 North - Poor Reapir of Honey Combing |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2015-10-28 | 2016-01-13 16:24 | 77 | 2012-12-13 | Structural Engineering - Finishes | 2000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Supervision - Insufficient supervision | Completed |  | Area of honey combing had not been broken back to sound concrete - but had been skimmed over with poor quality repair mortar.
| 03SR - Stations (RfL) | Cxxx-NCR-001097 | NCR | DLR NOS concrete deck finish imperfections |  | Contr |  | PML - Pudding Mill Lane Portal (Central) |  | 2014-12-15 | 2013-04-29 12:12 | -595 | 2012-12-14 | Structural Engineering - Concrete Member | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | Depressed boot marks in concrete finish. Poor workmanship and potential reduced cover.
| 03SR - Stations (RfL) | Cxxx-NCR-001099 | NCR | CRL 1 - Pour 5 (4B) Retaining wall damaged/incorrect dowel bars. |  | Contr |  | PML - Pudding Mill Lane Portal (Central) |  | 2013-02-15 | 2013-02-15 13:23 | 0 | 2012-12-18 | Civil - Civil Engineering General | 500 |  | Workmanship | Rework |  | Complete |  | Completed |  | The movemnet joint dowel bars cast into the eastern end of the CRL 1 ret wall (Pour 5) are only 500mm long and are not installed not horizontal.
| 03SR - Stations (RfL) | Cxxx-NCR-001104 | NCR | South Upstand Wall Panel 45/46 - Poor constrcution joint |  | Contr |  | PML - Pudding Mill Lane Portal (Central) |  | 2013-02-28 | 2013-02-21 13:23 | -7 | 2012-12-20 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | A poor construction joint between panels 45 and 46 of the South Upstand Wall has left a nib of concrete (approx 100mm wide) protruding from the wall. This nib has been cut back level with the wall but has left exposed agrregate and signs of blow holes.
| 03SR - Stations (RfL) | Cxxx-NCR-001123 | NCR | S1 Transfer Slab Finishing |  | Contr |  | PML - Pudding Mill Lane Portal (Central) |  | 2013-06-30 | 2013-05-08 14:53 | -53 | 2013-01-08 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | The top face of the S1 transfer slab has numerous surface defects where frost protection was placed too early.
| 03SR - Stations (RfL) | Cxxx-NCR-001150 | NCR | Plant Room Piles - PS1,7,11,15 |  | Contr |  | PML - Pudding Mill Lane Portal (Central) |  | 2013-02-22 | 2013-02-22 13:23 | 0 | 2013-01-22 | Civil - Civil Engineering General | 500 |  | Damaged | Repair |  | Complete |  | Completed |  | During instllation of the piles (PS1,7,11,15) the head of the piles were damaged.
| 03SR - Stations (RfL) | Cxxx-NCR-001151 | NCR | South Upstand Wall Panels 47 to 50 - Spacer Blocks Protruding from Face of Pours |  | Contr |  | PML - Pudding Mill Lane Portal (Central) |  | 2013-03-15 | 2013-02-20 10:52 | -23 | 2013-01-22 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | Spacer blocks are protruding through the face of the concrete. This is similar to NCR 01036 which has not yet been closed. Post pour inspections are being signed without defects being identified and/or raised. This implies a failure in the self-certification process.
| 03SR - Stations (RfL) | Cxxx-NCR-001163 | NCR | Transfer Slab S1 Damage |  | Contr |  | PML - Pudding Mill Lane Portal (Central) |  | 2013-05-15 | 2013-05-14 10:43 | -1 | 2013-01-28 | Civil - Civil Engineering General | 500 |  | Damaged | Repair |  | Complete |  | Completed |  | Over the joint between transfer slabs S1 and S2 the corners of the transfer slabs have been damaged by traffiking plant as shown in the attached photos. There has also been some minor surface damage to the top of the S1 transfer slab where the crawler crane has left the slab via a temporary ramp.
| 03SR - Stations (RfL) | Cxxx-NCR-001195 | NCR | No fines concrete to the rear of West Abutment |  | Contr |  | PML - Pudding Mill Lane Portal (Central) |  | 2013-02-28 | 2013-02-20 08:57 | -8 | 2013-02-05 | Civil - Civil Engineering General | 500 |  | Material | Rework |  | Complete |  | Completed |  | The 1st load of no fines concrete used to bed the back of wall drainage to the rear of the west abutment appeared to have pockets of loose sand within when we crapped back a few area's.
| 03SR - Stations (RfL) | Cxxx-NCR-001198 | NCR | Plant Room Pile Cages |  | Contr |  | PML - Pudding Mill Lane Portal (Central) |  | 2013-02-27 | 2013-02-27 07:14 | 0 | 2013-02-21 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | Some of the the tapered and threaded tips of the vertical bars where damaged during installation of the piles in the plant room by plant having to drive over the top. This was due to the low top of pile mat level in relation to the cut off level (only 200mm difference).
| 03SR - Stations (RfL) | Cxxx-NCR-001205 | NCR | DLR Retaining Wall Reco Panels Fabricated to Unapproved ITP |  | Contr |  | PML - Pudding Mill Lane Portal (Central) |  | 2013-02-28 | 2013-02-27 19:06 | -1 | 2013-02-08 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | During a site visit to the __ pre-cast yard to inspect the fabrication of the DLR retaining wall Reco panels, the current approved ITP (Rev3.0) could not be produced. The manufacturers were working to Rev 4.0 that has not yet been submitted for review. Furthermore, the documents and checksheets being used to record the necessary data (as described in the ITP) were different to those submitted in any revision of the Inspection and Test Plan.
| 03SR - Stations (RfL) | Cxxx-NCR-001219 | NCR | Minor damage to station column pile caps during excavation |  | Contr |  | PML - Pudding Mill Lane Portal (Central) |  | 2013-04-26 | 2013-04-23 11:19 | -3 | 2013-03-04 | Civil - Civil Engineering General | 500 |  | Damaged | Repair |  | Complete |  | Completed |  | During excavation of the ground beams the already constructed column pile caps were damaged on the top corners.
| 03SR - Stations (RfL) | Cxxx-NCR-001236 | NCR | Damage to base of VO2S Column |  | Contr |  | PML - Pudding Mill Lane Portal (Central) |  | 2013-04-26 | 2013-04-24 16:25 | -2 | 2013-02-14 | Civil - Civil Engineering General | 500 |  | Damaged | Repair |  | Complete |  | Completed |  | During construction of the station viaduct falsework sleeper concrete was cast up against the base of the column. This could scar the surface of the column.
| 03SR - Stations (RfL) | Cxxx-NCR-001241 | NCR | DLR NOS pre-cast beams |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2013-07-23 | 2013-07-03 10:53 | -20 | 2013-04-23 | Civil - Structural Engineering | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - NCR excessive closure due to design issue | Completed |  | North beam – • The bearing is 93 mm out of position to north and the north edge of the beam is 78 mm too far north. • The clear gap to the CRL NOS is still a minimum of 202mm. • There is a 30mm difference between the Cxxx plinth centre line and the Cxxx(MM) plinth centre line • In a longitudinal direction the bearing is set 343mm from the end of the plinth whereas the design requires 315mm. South Beam • The bearing is 152mm out of position to the north and the edge of the inside face of the south beam is 143mm to far north. • The clear gap between the as-built position and the inner face of the south beam and the walkway is a minimum of 30mm. • There is a 31mm difference between the Cxxx plinth centre line and the Cxxx(MM) plinth centre line • In a longitudinal direction the bearing is set 338mm from the end of the plinth whereas the design requires 315mm.
| 03SR - Stations (RfL) | Cxxx-NCR-001245 | NCR | South Upstand S33 Roof Couplers |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2015-10-14 | 2015-10-14 17:32 | 0 | 2013-02-20 | Civil - Civil Engineering General | 2500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | All couplers have been installed the wrong side of the setting out and are all 850mm above the intended position. See attached survey. This error also slipped through the independant survey department check and an investigation into this is underway.
| 03SR - Stations (RfL) | Cxxx-NCR-001249 | NCR | Low Cover at CJ07 Roof Slab Cut and Cover Phase 2b |  | Contr |  | PML - Pudding Mill Lane Portal (Central) |  | 2013-03-21 | 2013-03-12 10:22 | -9 | 2013-02-21 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | See attached cover meter survey carried out on CJ07.
| 03SR - Stations (RfL) | Cxxx-NCR-001317 | NCR | CRL 1 wall Panel 1A |  | Contr |  | PML - Pudding Mill Lane Portal (Central) |  | 2013-05-05 | 2013-05-01 09:45 | -4 | 2013-03-07 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | Panel pour 1A has sand runs and slight honeycombing to the lower section of the wall.
| 03SR - Stations (RfL) | Cxxx-NCR-001329 | NCR | Incorrect compressible seperation layer used between structures. |  | Contr |  | PML - Pudding Mill Lane Portal (Central) |  | 2013-03-22 | 2013-03-20 17:33 | -2 | 2013-03-11 | Structural Engineering - Joints | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | Seperation membrane used was Miothene frost blanket as opposed to the approved material material (10mm flexcel)
| 03SR - Stations (RfL) | Cxxx-NCR-001351 | NCR | Concrete testing |  | Contr |  | PML - Pudding Mill Lane Portal (Central) |  | 2013-06-30 | 2013-04-19 09:43 | -72 | 2013-03-19 | Civil - Concrete Pavement | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | Cut and Cover Roof Pour - Half Width Roof Phase 2B - Pour date 11th February 2013 Due to the size of the pour and the number of cubes moulds available on the day of the pour, the number of early 7 day cubes and 56 days were reduced. The concrete was sampled at 1 set per 24m3 as per the specification but it was alternated making a set of 4 then a set of 2 cubes. It was the intention to crush 2 cubes at 28 days for each set, unfortunately the sample containing 2 cubes were labelled to be crushed at 56 days in error. The samples crushed at 28 days are compliant and I'm confident that the 56 day cube strengths will confirm that the concrete is acceptable. Please see attached summary for clarity and confirmation of strengths. A memo has been sent to the laboratory to remind that 2 cubes need to be tested at 28 days for compliance on the Deck mix and that it is only the base mix where there is a requirement for 2 to be crushed at 56 days.
| 03SR - Stations (RfL) | Cxxx-NCR-001352 | NCR | Concrete testing (1) |  | Contr |  | PML - Pudding Mill Lane Portal (Central) |  | 2013-06-30 | 2013-05-10 12:43 | -51 | 2013-03-19 | Civil - Concrete Pavement | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | Cut and Cover Roof Pour - Phase 2 B CJ07 - CJ10. Pour date 26th February 2013. The laboratory was instructed to crush 2 cubes from alternate sets at 15 days to confirm the strength of the roof slab for striking purposes. As a result there are now only 2 cubes in alternate sets to be crushed at 28 days, this means we only have 28 day cubes at a rate of 2 per 50m3 as opposed to 2 per 24m3 as required in the specification. The 15 day cube strengths achieved the 28 day characteristic strength and we don't anticipate there to be a problem with the 28 day strengths when they are crushed.
| 03SR - Stations (RfL) | Cxxx-NCR-001355 | NCR | Upstand Wall 2 Pour 5 Time between loads exceeded |  | Contr |  | PML - Pudding Mill Lane Portal (Central) |  | 2013-05-31 | 2013-04-23 12:55 | -38 | 2013-03-20 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | During the pour of upstand wall 2 pour 5, there was a 40minute delay between the first and second loads of concrete. Approximately 0.5m3 of concrete was retained. After 20minutes this was placed into the pour to freshen up the face. Once the second load had arrived onsite the face was visually inspected and was considered suitably fresh.
| 03SR - Stations (RfL) | Cxxx-NCR-001364 | NCR | DLR NOS deck drainage hoppers |  | Contr |  | PML - Pudding Mill Lane Portal (Central) |  | 2013-07-19 | 2013-07-19 09:05 | 0 | 2013-03-22 | Civil - Drainage | 1000 |  | Workmanship | Rework | 4 (0.5-3k) | Complete |  | Completed |  | 4no. Hoppers cast proud of DLR deck by approx 30-50mm.
| 03SR - Stations (RfL) | Cxxx-NCR-001383 | NCR | Cambridge Uni data cable in DLR embankment |  | Contr |  | PML - Pudding Mill Lane Portal (Central) |  | 2013-04-25 | 2013-04-13 16:01 | -12 | 2013-03-28 | Civil - Civil Engineering General | 500 |  | Damaged | Repair |  | Complete |  | Completed |  | The above data feed has been damaged during the fill operation by the dozer.
| 03SR - Stations (RfL) | Cxxx-NCR-001388 | NCR | Defective joint - Upstand wall 1 to Upstand wall 2 |  | Contr |  | PML - Pudding Mill Lane Portal (Central) |  | 2013-06-28 | 2013-04-23 12:29 | -66 | 2013-04-04 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | During the pour of upstand wall 1, the alignment of the shutter has slipped / moved. This has resulted in grout loss during the pour and a step (20mm maximum) in the line between upstand wall 1 and the stop end of upstand wall 2. A photograph has been atteched to this NCR for reference.
| 03SR - Stations (RfL) | Cxxx-NCR-001391 | NCR | Reco wall |  | Contr |  | PML - Pudding Mill Lane Portal (Central) |  | 2013-05-03 | 2013-05-03 16:16 | 0 | 2013-04-05 | Civil - Civil Engineering General | 500 |  | Workmanship | Rework |  | Complete |  | Completed |  | During construction of the reinforced earth wall some panels on the first layer of construction have moved beyond tolerance
| 03SR - Stations (RfL) | Cxxx-NCR-001392 | NCR | CRL 1 wall panel 3a |  | Contr |  | PML - Pudding Mill Lane Portal (Central) |  | 2013-05-31 | 2013-05-29 09:11 | -2 | 2013-04-05 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | Panel has light sand runs evident horizontally across the Reckli face, running in a band ~0.5m above the recess. There are also some spacer blocks protruding slightly (up to ~10mm) in an isolated area (at tie in to existing pour).
| 03SR - Stations (RfL) | Cxxx-NCR-001397 | NCR | Time Between Loads Exceeded Central Wall #13 |  | Contr |  | PML - Pudding Mill Lane Portal (Central) |  | 2013-07-08 | 2013-05-02 09:44 | -67 | 2013-04-08 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | During the pour of central wall pour #13, there was a 55minute delay between the first and second loads of concrete. The concrete was visually inspected prior to the second load being placed and was agreed to be suitably fresh to continue.
| 03SR - Stations (RfL) | Cxxx-NCR-001403 | NCR | Marshgate Lane Viaduct Bearing Issues |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2014-01-07 | 2014-01-07 16:46 | 0 | 2013-05-16 | Structural Engineering - Structural Engineering - General | 5000 |  | Workmanship | Rework | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Bearing sockets cast in to the recast beam are mis-aligned or not vertical.
| 03SR - Stations (RfL) | Cxxx-NCR-001420 | NCR | south upstand wall cover |  | Contr |  | PML - Pudding Mill Lane Portal (Central) |  | 2013-05-10 | 2013-04-30 12:24 | -10 | 2013-04-18 | Civil - Civil Engineering General | 500 |  | Design | Use As-Is |  | Complete |  | Completed |  | Now all cover surveys have been carried out, it is noted that all cover is on the excessive side ranging generally between 55mm - 85mm.
| 03SR - Stations (RfL) | Cxxx-NCR-001430 | NCR | Platform to Steel Frame Connections |  | Contr |  | PML - Pudding Mill Lane Portal (Central) |  | 2013-05-08 | 2013-05-08 11:45 | 0 | 2013-04-22 | Structural Engineering - Bolted Connections | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | The Couplers installed are not stainless steel but are zinc plated which could lead to bimetallic corrision problems in the future.
| 03SR - Stations (RfL) | Cxxx-NCR-001431 | NCR | Steel Frame Holding Down Bolts |  | Contr |  | PML - Pudding Mill Lane Portal (Central) |  | 2013-05-08 | 2013-05-08 11:49 | 0 | 2013-04-23 | Civil - Civil Engineering General | 500 |  |  | Rework |  | Complete |  | Completed |  | The Type A holding down bolt connection at the intersection of gridline F with S02 has dropped during construction. Although the bolt projects enough above the TOC there will be no thread sticking through the baseplate and therefore no nut can be fastened.
| 03SR - Stations (RfL) | Cxxx-NCR-001437 | NCR | CRL 1 rear guard damage |  | Contr |  | PML - Pudding Mill Lane Portal (Central) |  | 2013-05-23 | 2013-05-09 11:33 | -14 | 2013-04-23 | Civil - Civil Engineering General | 500 |  | Damaged | Repair |  | Complete |  | Completed |  | At 3 MJ locations the rearguard is damaged and will require repair.
| 03SR - Stations (RfL) | Cxxx-NCR-001445 | NCR | CMR DLR East Abutment Reinforcement Issue |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2013-06-30 | 2013-07-12 14:09 | 12 | 2013-05-08 | Civil - Civil Engineering General | 500 |  | Design | Repair | 4 (0.5-3k) | Complete |  | Completed |  | As above.
| 03SR - Stations (RfL) | Cxxx-NCR-001448 | NCR | Pitting to Structural Steelwork |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2013-08-02 | 2013-07-30 11:18 | -3 | 2013-04-24 | Structural Engineering - Steel Member | 4000 |  | Material | Repair | 3 (3-6k) | Complete |  | Completed |  | During the steelwork section rolling process, slag or other contaminants have been rolled into the web of the 1016x305x393 sections. Upon blasting for painting, __s have noted that on two of the beams there are indentations 1 to 3 mm deep which is outside the acceptable depth of BSEN 10025. Two further members may show similar defects once blasted. __s Report is attached along with a drawing showing their location in the completed station.
| 03SR - Stations (RfL) | Cxxx-NCR-001463 | NCR | CMR East abutment wall pour 1 - Concrete time lapse |  | Contr |  | PML - Pudding Mill Lane Portal (Central) |  | 2013-05-31 | 2013-06-07 13:51 | 7 | 2013-04-29 | Civil - Civil Engineering General | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | See attached pour record sheet, last (part load) placed 60 mins after previous load.
| 03SR - Stations (RfL) | Cxxx-NCR-001469 | NCR | End of Platform Couplers |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2013-07-10 | 2013-07-02 17:34 | -8 | 2013-04-30 | Civil - Structural Engineering | 1000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete |  | Completed |  | The design template did not fit inside the reinforcement layers of the platform and the designed coupler positions also clashed with the reinforcement (See DSCN3128). Therefore it was agreed with Cxxx that the template was to be to be removed and the couplers positioned as per the design above the T1 layer and beneath the B2 layer. The coupler and embedment B25 bar was then tied to the reinforcement to hold it in position. Although the couplers are in the right location they are on occasion not aligned correctly and therefore push the threaded bar insert out of alignment tolerance.
| 03SR - Stations (RfL) | Cxxx-NCR-001473 | NCR | CRL Pile cage damaged spacers |  | Contr |  | PML - Pudding Mill Lane Portal (Central) |  | 2013-05-20 | 2013-05-24 13:16 | 4 | 2013-04-30 | Civil - Civil Engineering General | 500 |  | Damaged | Repair |  | Complete |  | Completed |  | CRL pile cage sled spacers deformed, damaged and broken. This jeopardises design cover to the pile cage. See attached photo.
| 03SR - Stations (RfL) | Cxxx-NCR-001478 | NCR | Steel Columns on GLV01 - B & F |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2013-07-10 | 2013-07-10 09:46 | 0 | 2013-06-19 | Structural Engineering - Steel Member | 500 |  | Design | Rework | 4 (0.5-3k) | Complete |  | Completed |  | Columns do not fit as the incorrect design information for U/S baseplate was feed to the fabricators. This was not picked up before fabrication.
| 03SR - Stations (RfL) | Cxxx-NCR-001479 | NCR | Cracking in mortar bed of blockwork - Plant & Accomodation Rooms |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2013-07-10 | 2013-07-05 11:11 | -5 | 2013-06-19 | Architectural - Brickworks/Blockworks | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete |  | Completed |  | Various areas of localised shrinkage cracking in the mortar perts and bedding of the blockwork.
| 03SR - Stations (RfL) | Cxxx-NCR-001489 | NCR | Excess cover to precast beams - GL 07 -08 North and South and GL 12 - 13 South |  | Contr |  | PML - Pudding Mill Lane Portal (Central) |  | 2013-06-17 | 2013-06-24 10:01 | 7 | 2013-05-22 | Structural Engineering - Concrete Member | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | Areas of concrete cover to GL 7 -8 South and GL 12 - 13 South precast beams is in excess of 70mm.
| 03SR - Stations (RfL) | Cxxx-NCR-001490 | NCR | Damage to precast beams during tranportation - GL 12 - 13 N&S and GL 07 - 08 N&S |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2013-09-13 | 2013-08-20 11:30 | -24 | 2013-05-16 | Structural Engineering - Concrete Member | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete |  | Completed |  | Precast concrete beams to GL 07 - 08 & 12 - 13 North and South were damaged due to insufficient protection to the corners of the beams during transportation. See attached photos.
| 03SR - Stations (RfL) | Cxxx-NCR-001495 | NCR | Sand runs and Honeycombing |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2013-07-24 | 2013-07-19 09:32 | -5 | 2013-05-08 | Civil - Civil Engineering General | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete |  | Completed |  | Sand runs and small amounts of honeycombing
| 03SR - Stations (RfL) | Cxxx-NCR-001496 | NCR | DLR embankment |  | Contr |  | PML - Pudding Mill Lane Portal (Central) |  | 2013-06-14 | 2013-06-24 14:48 | 10 | 2013-05-08 | Civil - Civil Engineering General | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | On the 17th,18th, 19th, 23rd,24th and 25th April, 6 number of test samples have indicated that the moisture content of the 6I crushed Limestone material has been placed outside the ±2% limits stipulated in table 6/1 of the Section D Materials and workmanship specification for Groundwork. It should be noted that on the days in question 95% compaction has been achieved and that there are no concerns regarding the level of compaction. The non-compliant results have been caused by the dry weather and strong winds drying the material out very quickly. The material is sprayed by a water Bowser prior to rolling each layer to ensure that the material is within the moisture content tolerance. Greater effort is needed to co-ordinate compaction testing and sampling for bulk samples at the time the material is being placed and compacted. On the days stated testing has been performed a number of hours after compaction when the surface of the material has dried.
| 03SR - Stations (RfL) | Cxxx-NCR-001497 | NCR | Incorrect piling concrete. Pile No. N3P16 |  | Contr |  | PML - Pudding Mill Lane Portal (Central) |  | 2013-07-31 | 2013-06-24 17:25 | -37 | 2013-05-10 | Structural Engineering - Concrete Member | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | Mix Design used for N3P16 C32/40 10mm CIIIB+SR F5 Concrete batched at 0732hrs, completed placing at 1000hrs and completion of pile (cage inserted) at 1030hrs. This exceeds the requirements of BS8500 that states concrete shall be placed within 2hrs of being batched. Slump tests were carried out whilst the concrete was in the agitator. The __ technician deemed this concrete to be within the slump range of the specified mix before placement, therefore another slump test was not carried out during discharge. Attached slump test record.
| 03SR - Stations (RfL) | Cxxx-NCR-001501 | NCR | Main & Escape Stairs - Butt Weld Testing |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2013-08-01 | 2013-07-03 12:19 | -29 | 2013-06-17 | Civil - Structural Engineering | 750 |  | Planning | Repair | 4 (0.5-3k) | Complete |  | Completed |  | Test has not been carried out.
| 03SR - Stations (RfL) | Cxxx-NCR-001506 | NCR | CRL 1 phase 1 base cover surveys |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2013-07-19 | 2013-07-11 12:36 | -8 | 2013-05-16 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | cover is generally ok throughout, but some readings fall just outside tollerances down to 60mm and up to 90mm.
| 03SR - Stations (RfL) | Cxxx-NCR-001518 | NCR | Unforseen Ground Conditions at Load Transfer Slab N3 Pile no. N3P06 |  | Contr |  | PML - Pudding Mill Lane Portal (Central) |  | 2013-08-20 | 2013-06-19 11:29 | -62 | 2013-05-23 | Structural Engineering - Concrete Member | 500 |  | System Defect | Repair |  | Complete |  | Completed |  | Pile numbers N3P06 and N3P08 are deemed to be conjoined at approximately 5m below top of pile level. Whilst drilling pile N3P08 the concrete from pile N3P06 slumped by approximately 5m and whilst concreting N3P08, the concrete at N3P06 came back up at platform level. Piles were more than 3 x diameter distance away from each other (4m approximately, edge to edge), indicating that there is some kind of structure/void at 5m depth connecting the two piles, therefore unforeseen ground conditions are the underlying reasons contributing to this NCR.
| 03SR - Stations (RfL) | Cxxx-NCR-001519 | NCR | MGL Viaduct GL 12 - 13 Deck Soffit Honeycomb |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2013-06-28 | 2013-07-05 11:26 | 7 | 2013-05-22 | Structural Engineering - Concrete Member | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete |  | Completed |  | A small area of honeycombing is evident on the Western soffit of GL 12 - 13 deck slab
| 03SR - Stations (RfL) | Cxxx-NCR-001520 | NCR | Damage to 1 No. starter bar (BM29) GL 08 - 09 North Precast Beam (Infill location) |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2013-08-02 | 2013-08-02 15:08 | 0 | 2013-05-22 | Structural Engineering - Reinforcement | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | 1 No. starter bar (BM29) to the precast beam has been "nicked" with the Stihl saw.
| 03SR - Stations (RfL) | Cxxx-NCR-001521 | NCR | Retaining Wall Construction Joint Defect |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2013-07-19 | 2013-07-12 14:10 | -7 | 2013-06-03 | Civil - Civil Engineering General | 750 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Poorly Impacted concrete at construction joint
| 03SR - Stations (RfL) | Cxxx-NCR-001523 | NCR | Unapproved Concrete Mix |  | Contr |  | PML - Pudding Mill Lane Portal (Central) |  | 2013-06-05 | 2013-05-29 13:11 | -7 | 2013-05-28 | Civil - Civil Engineering General | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | For record purposes: S3 20mm Mix: Piles W5 & W9. S4 20mm Mix: Piles W2, W6, W18, W19, W22, & E4. S4 10mm Mix: Piles W1, W3, W11, W12, E1, E2, & E12.
| 03SR - Stations (RfL) | Cxxx-NCR-001526 | NCR | CMR - DLR Bridge pre-cast beam cover |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2013-07-19 | 2013-07-09 16:59 | -10 | 2013-05-24 | Civil - Structural Engineering | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | See attached example of cover meter survey which shows excessive cover to the DLR CMR pre-cast beams. The maximum cover measured is 63mm. Average cover for beam is 47mm.
| 03SR - Stations (RfL) | Cxxx-NCR-001533 | NCR | DLR station-Platform level pre-cast units |  | Contr |  | PML - Pudding Mill Lane Portal (Central) |  | 2013-06-21 | 2013-06-20 18:31 | -1 | 2013-05-28 | Structural Engineering - Pre-cast | 500 |  | Material | Reject |  | Complete |  | Completed |  | 1.The pre-cast units were manufactured and delivered to site (on May 21, 2013) while the MCR for the concrete mix design (ref. Cxxx-MRG-C-QAP-CR094_WS111-50189 rev 1.0) was still at code 3 and the structural calculations (submitted via RFI-01424) were rejected.This is a breach of the ITP hold points. 2.Further to a prelimenary inspection, defects were identified in 4 Nos units as follows: a) 1 No unit had significant cracks along the edges and inside the longitudinal voids. b)The edge of 1 No unit was cut longitudinally (during manufacturing) leaving a void across the unit (which modifies the edge profile) c)The edges of 2 Nos units were cut longitudinally (during manufacturing) exposing the pre-stressing tendon profiles Please refer to the attcahed photos. This is the notification of a Defect.
| 03SR - Stations (RfL) | Cxxx-NCR-001540 | NCR | CMR MH D1 E.Abutment drain inlet |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2013-07-19 | 2013-07-08 15:02 | -11 | 2013-05-30 | Civil - Drainage | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The inlet level of the perforated pipe from the east abutment is 105.025m. The sketch shows the majority of the pipe has been installed to the correct level along the back of the abutment. The last 1.1m of the pipe was installed incorrectly, resulting in a sharp fall in level.
| 03SR - Stations (RfL) | Cxxx-NCR-001554 | NCR | CRL 1 wall cover survey (north face) |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2013-08-02 | 2013-08-02 15:06 | 0 | 2013-06-04 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | In reviewing the cover surveys for the rear of the wall some cover readings are slightly higher than the upper limit reading as high as 60mm.
| 03SR - Stations (RfL) | Cxxx-NCR-001555 | NCR | CRL 1 wall base cover survey |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2013-08-02 | 2013-08-02 15:11 | 0 | 2013-06-04 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | In reviewing the cover surveys it is noted that some readings have come in as low 50mm.
| 03SR - Stations (RfL) | Cxxx-NCR-001558 | NCR | CRL 1 cover to front wall face |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2013-07-26 | 2013-08-02 15:12 | 7 | 2013-06-05 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | some readings are outside this range as low as 35mm and as high as 65mm.
| 03SR - Stations (RfL) | Cxxx-NCR-001567 | NCR | Structrual Steelwork Records |  | Crossrail | XRL | PML - Pudding Mill Lane Portal (Central) |  | 2013-07-19 | 2013-07-19 11:12 | 0 | 2013-06-06 | Civil - Structural Engineering | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete |  | Completed |  | There were no verifying Independent Inspection records for witnessing the checking of the tightness of bolts
| 03SR - Stations (RfL) | Cxxx-NCR-001568 | NCR | Structural Steelwork Records |  | Crossrail | XRL | PML - Pudding Mill Lane Portal (Central) |  | 2013-07-19 | 2013-07-19 11:14 | 0 | 2013-06-06 | Civil - Structural Engineering | 500 |  | Supervision/Management | Reject | 4 (0.5-3k) | Complete |  | Completed |  | 2. There were no delivery notes that verified the delivery details i.e. site address, who delivered, where from and who signed on receipt? Delivery notes form part of the traceability process for Self Certification as required in the contract.
| 03SR - Stations (RfL) | Cxxx-NCR-001569 | NCR | Structural Steelwork Records |  | Crossrail | XRL | PML - Pudding Mill Lane Portal (Central) |  | 2013-07-19 | 2013-07-19 11:15 | 0 | 2013-06-06 | Civil - Structural Engineering | 500 |  | Supervision/Management | Reject | 4 (0.5-3k) | Complete |  | Completed |  | There are no verifying records for inspections on delivery the steel sections as required in the contract
| 03SR - Stations (RfL) | Cxxx-NCR-001577 | NCR | Beam B415/3A end plate hole alignment |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2013-07-10 | 2013-07-10 09:49 | 0 | 2013-06-19 | Civil - Civil Engineering General | 500 |  | Design | Repair | 4 (0.5-3k) | Complete |  | Completed |  | During construction of the North Lift Shaft Cantilever Beam it was noted that the cast in sleeves were clashing with the reinfrocement of the beam and therefore had to be moved due to congestion of the rebar and requirements for minumum cover as per request by Cxxx on site designer representative. The steel beam had already been fabricated in order to meet the programme and could not be changed.
| 03SR - Stations (RfL) | Cxxx-NCR-001584 | NCR | STR-102 Works for BAL-110 |  | Contr |  | PML - Pudding Mill Lane Portal (Central) |  | 2013-06-28 | 2013-07-11 13:28 | 13 | 2013-06-14 | Architectural - General | 8000 |  | System Defect | Rework | 2 (6-60k) | Complete |  | Completed |  | STR-102 works for BAL-110 were fabricated at an edge distance off-set from grid line B and F at 225mm & from grid line S08 at 125mm.
| 03SR - Stations (RfL) | Cxxx-NCR-001597 | NCR | East Abutment North Ballast wall cover to rebar |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2013-07-19 | 2013-07-12 12:38 | -7 | 2013-06-19 | Civil - Structural Engineering | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete |  | Completed |  | Cover to the reinforcement is currently 110mm.
| 03SR - Stations (RfL) | Cxxx-NCR-001598 | NCR | Concrete supply to CMR |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2013-07-05 | 2013-07-03 12:41 | -2 | 2013-06-19 | Civil - Structural Engineering | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Subcontractor Problems - Other | Completed |  | See attached pour record sheet showing a 45 min delay between the first and second load. We asked for wagons to be batched 30 mins apart to provide consistent supply. The pour record sheet shows this was not the case.
| 03SR - Stations (RfL) | Cxxx-NCR-001603 | NCR | DLR Deck - Stray Current Collector |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2014-04-30 | 2014-04-16 13:59 | -14 | 2013-06-21 | Electrical - Electrical Engineering General | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | At GL12: - Mild steel flat bar was cut down to approximately half its width to facilitae the size of the u-bolt used. - Mild steel flat bar was not in contact with 4No. longitudinal bars. Witnessed as being in contact with 2No. possibly. - No evidence that contact surfaces were cleaned to bright metal and coated with contact grease prior to clamping.
| 03SR - Stations (RfL) | Cxxx-NCR-001604 | NCR | Missing __ Sockets in Viaduct Beams (GL07 and GL13) |  | Crossrail | XRL | PML - Pudding Mill Lane Portal (Central) |  | 2014-03-21 | 2014-03-21 14:54 | 0 | 2013-06-21 | Civil - Civil Engineering General | 3500 |  | System Defect | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The sockets were not included during the construction of the pre-cast slab. The omisison was not identified during the contractor's pre-pour inspections (deck slabs GL7-8 and GL12-13)
| 03SR - Stations (RfL) | Cxxx-NCR-001609 | NCR | Precast Brick Cladding panel - P22 |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2013-07-24 | 2013-07-10 09:59 | -14 | 2013-06-24 | Architectural - Brickworks/Blockworks | 500 |  | Workmanship | Reject | 4 (0.5-3k) | Complete |  | Completed |  | 1No panel (P22) on the North elevation between GLV05-S05 has had the brickettes cast into the panel 180 degrees in the wrong orientation (upside down). Therefore, the brickette courses do not match with the adjoining panels.
| 03SR - Stations (RfL) | Cxxx-NCR-001615 | NCR | CMR East abutment north ballast wall concrete grade |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2013-08-23 | 2013-07-10 11:07 | -44 | 2013-06-25 | Civil - Structural Engineering | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Use of unapproved materials | Completed |  | Concrete ordered to site to the correct standard/grade. Concrete arrived grade C35/45A as per approved mix for retaining walls. MS consulted CRL (__) and MS material engineer. Due to quantity of concrete (2.5m3) and location (north ballast wall, will be largely covered). A decision was made to utilise the concrete. __ informed MS that an NCR would need to be raised for the non conformance.
| 03SR - Stations (RfL) | Cxxx-NCR-001619 | NCR | ALIGNMENT FIXINGS OF BRICK CLADDING PANELS |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2013-11-15 | 2013-11-14 16:36 | -1 | 2013-06-27 12:07 | Civil - Civil Engineering General | 1500 |  | Planning | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | A cast in socket does not align with the hole in the steel work column stub. Therefore no alignment fixing can be made with the M20 stud in the back of the panel.
| 03SR - Stations (RfL) | Cxxx-NCR-001620 | NCR | Incorrect __ Socket Orientation in Viaduct Beam GL10-GL11 South |  | Crossrail | XRL | PML - Pudding Mill Lane Portal (Central) |  | 2014-02-07 | 2014-02-05 12:30 | -2 | 2013-06-27 11:49 | Civil - Civil Engineering General | 5000 |  | Supervision/Management | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The DLR viaduct pre-cast beam (GL10 to GL11 south) has 6No. halfen sockets cast into the underside (to aid future maintenance). Drawing number Cxxx-SWN-S-DDD-CR094_PT002_C-10409 rev C03 shows the sockets orientated in 3 rows of two. The as-manufacture beams have the sockets in two rows of 3 (rotated at 90 degrees).
| 03SR - Stations (RfL) | Cxxx-NCR-001622 | NCR | South upstand wall panel S35 surface cracking |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2013-07-26 | 2013-08-05 10:17 | 10 | 2013-07-08 11:29 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Not Defined | Completed |  | During snagging of the top surface of Panel S35, small surface cracking was noticed.
| 03SR - Stations (RfL) | Cxxx-NCR-001624 | NCR | Surface cracks on upstand Z shape wall |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2013-08-23 | 2013-08-08 09:28 | -15 | 2013-07-08 13:06 | Civil - Civil Engineering General | 1000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | As per NCR 1622 - Upstand wall. On inspection of the top level of the upstand Z shape wall, surface cracks on the top level have been found. These are predominately located on the central panel of the East - West wall, but others have been located on the North-South wall (wall 3) and the remaining section of East-West wall which is visible at present.
| 03SR - Stations (RfL) | Cxxx-NCR-001625 | NCR | Brick Cladding Panel - Darker Shade |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2013-12-01 | 2013-11-29 09:46 | -2 | 2013-07-10 09:31 | Architectural - Brickworks/Blockworks | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | panel P9 is a darker brick cladding panel than the adjacent panels
| 03SR - Stations (RfL) | Cxxx-NCR-001626 | NCR | Station Brick Cladding Panels - Damage during transportation & installation |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2013-12-01 | 2013-11-29 09:40 | -2 | 2013-07-10 11:24 | Civil - Civil Engineering General | 3000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Improper handling of material | Completed |  | During transportation and installation some minor damage to the brick panels was caused (pictures attached).
| 03SR - Stations (RfL) | Cxxx-NCR-001627 | NCR | EWS-102 [brick cladding] resin anchored connections not perpendicular |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2013-09-27 | 2013-09-30 17:05 | 3 | 2013-07-15 16:59 | Structural Engineering - Bolted Connections | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | the bolted connections which were resin anchored into the back of the brick cladding panel have not been fitted perpendicular in order to utilise the pre welded cleat on the main steel frame.
| 03SR - Stations (RfL) | Cxxx-NCR-001628 | NCR | Ret. Wall D Wall panel Concrete Supply - CMR |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2013-09-08 | 2013-08-23 15:18 | -16 | 2013-07-16 17:59 | Civil - Civil Engineering General | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Ret. Wall D wall panel D6 & D8 poured on the 08/07/13 failed to meet the specification with regard to time between loads (30 mins). See attached pour record sheet. Also see attached photos of wall panels which show no sign of a cold joint. Note, __ are fully aware of the mounting NCR's with regard to concrete supply. We have rigorously communicated the significance of concrete supply to our suppliers and have arranged a site meeting for them to justify their current performance failures.
| 03SR - Stations (RfL) | Cxxx-NCR-001629 | NCR | CRL Bridge Pile Concrete NCR - CMR |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2013-08-23 | 2013-08-23 08:05 | 0 | 2013-07-16 17:59 | Civil - Civil Engineering General | 500 |  | Material | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | With reference to pile E11 to the CRL bridge. The concrete specification dictates no longer than 2 hours from batch to placing concrete. The second load to the concreting operation exceeded the 2 hour specified limit. See attached concrete tickets for information and confirmation of times.
| 03SR - Stations (RfL) | Cxxx-NCR-001631 | NCR | EWS-102 Panel P5 Joints |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2013-12-01 | 2013-11-29 09:50 | -2 | 2013-07-19 14:08 | Architectural - Brickworks/Blockworks | 1500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Panel P5 has been fabricated to wide to fit between panel P4 & P6 and was fitted on site with no 10mm joint either side.
| 03SR - Stations (RfL) | Cxxx-NCR-001632 | NCR | DLR Deck elastomeric bearings |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2013-08-12 | 2013-08-19 15:31 | 7 | 2013-07-22 11:12 | Civil - Civil Engineering General | 750 |  | Material | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | With reference to the elastomeric bearings to the DLR deck at City Mil River and drawing Cxxx-MMD-C-EDR-CRG06-00129. __ completed the gouting phase of the bearing install and loaded the bearings after achieving the specified 28N/mm2 compressive strength. Once loaded 4no. bearings showed a crack in the 'over-pour' which surrounds the bearing (see attached photo). __s subcontractor (__), investigated the crack to establish if it propgated under the bearing (see attached pictures). The investigative works illustrated the crack terminated outside the loaded zone of the bearin grout. __ suspect the occurance of this crack is due to tension in the 'over-pour' section of the grout.
| 03SR - Stations (RfL) | Cxxx-NCR-001633 | NCR | CMR - Ret. Wall D5 base defect |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2013-08-31 | 2013-08-29 08:18 | -2 | 2013-07-30 16:03 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | With reference to the Retaining Wall panel D5 pile cap at City Mill River. See attached photos which show a defect to the top 100mm of the pile cap over a 1m stretch to the southern face.
| 03SR - Stations (RfL) | Cxxx-NCR-001634 | NCR | Retaining Wall diwydag hole repairs |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2013-08-31 | 2013-08-27 15:34 | -4 | 2013-07-30 16:16 | Civil - Civil Engineering General | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete |  | Completed |  | With reference to Retaining Wall panels D8 & D6 at City Mill River. __ witnessed 2no. diwydag holes which were incorrectly plugged/grouted. No rubber insert was present and insufficient grout witnessed within the sleeve.
| 03SR - Stations (RfL) | Cxxx-NCR-001635 | NCR | STR-102 Secondary Support Welded to Primary Steel Out of Position for EWS-101 Glazed Curtain Walling |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2013-10-31 | 2013-09-05 12:25 | -56 | 2013-08-06 13:44 | Archaeology - General | 1000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Following a survey we have assessed that a number of the STR-102 cleats are out of position verticaly, horizontaly and in plan.
| 03SR - Stations (RfL) | Cxxx-NCR-001636 | NCR | STR-102 Re-Work for Installation of Vent Pipe and Roof Drainage Downpipes |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2013-08-20 | 2013-08-19 11:01 | -1 | 2013-08-06 13:55 | Architectural - General | 750 |  | Design | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The STR-102 factory welded angle to the primary steel work roof beams clashes with the vent pipe and roof gutter downpipes at grid line 1 and grid line S05-V05.
| 03SR - Stations (RfL) | Cxxx-NCR-001637 | NCR | Low cover to Epoxy starter bars to MGL Viaduct Slab W54 |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2013-08-20 | 2013-08-21 11:12 | 1 | 2013-08-06 14:07 | Structural Engineering - Reinforcement | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | There is an area of low cover of 21mm - 24mm, to W54 track slab. Drawing attached.
| 03SR - Stations (RfL) | Cxxx-NCR-001638 | NCR | 'STR-102' for 'EWS-103 GRC Cladding' Clash with 'EWS-102 Brick Cladding' |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2013-11-30 | 2013-11-29 09:55 | -1 | 2013-08-06 14:14 | Archaeology - General | 1500 |  | Design | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The secondary support welded cleat to the main steel frame to support the GRC cladding clashes with the concrete boot for the brick cladding support.
| 03SR - Stations (RfL) | Cxxx-NCR-001639 | NCR | DLR deck bearing paint defects - CMR |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2013-10-15 | 2013-09-17 11:48 | -28 | 2013-08-08 14:39 | Civil - Civil Engineering General | 1000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | With reference to the DLR deck fixed and guided bearings at CMR. See attached photos which show chips to the finish paint work. These chips were caused as a result of tight tolerence during installation and more significantly due to the transit bolt removal. The bearings were free issue from CRL (from C248 works). The transit bolt sits vertically, to remove, the bolt had to be cut in 10mm sections at a time which caused inevitable clashes with the paint coating.
| 03SR - Stations (RfL) | Cxxx-NCR-001640 | NCR | Ret. Wall D3 & D5 Concrete pour |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2013-09-20 | 2013-09-23 11:45 | 3 | 2013-08-12 17:11 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | With referece to retaining wall pour D3 & D5 at CMR, see attached concrete pour record sheet. The final load to the concrete pour to panel D3 was placed 47 mins after the previous load. This does not conform to the 30 minute specification defined by the works information.
| 03SR - Stations (RfL) | Cxxx-NCR-001641 | NCR | Station Blockwork Mortar Results |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2013-08-27 | 2013-09-10 17:34 | 14 | 2013-08-13 13:10 | Architectural - Brickworks/Blockworks | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | The attached mortar prism results have not met the 28 day compressive strength requirement of class 'M4' as per clause F10.255, 256 & 257.
| 03SR - Stations (RfL) | Cxxx-NCR-001642 | NCR | HV Room Builders Hole |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2013-10-18 | 2013-09-16 16:35 | -32 | 2013-08-13 12:51 | Architectural - Brickworks/Blockworks | 750 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | The quality of the brickwork around the newly formed HV room builders hole was to a low standard. This work had not been accepted by __ and KN were asked to re-construct the builders hole to a better standard.
| 03SR - Stations (RfL) | Cxxx-NCR-001643 | NCR | Retail room roof screed - defects |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2013-08-27 | 2013-09-06 16:09 | 10 | 2013-08-13 12:58 | Architectural - Roofing & Exterior Treatment | 750 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Following the completion of the roof screeding to the retail room the access was taped-off with bunting at the top of the ladder access tower by KN. Sometime after this someone has entered the roof slab through the bunting and left footprints in the SW quarter of the screed (the later quarter to be screeded). The footprints do not exceed 5mm in depth.
| 03SR - Stations (RfL) | Cxxx-NCR-001644 | NCR | Incorrect opening size cast in Cable Riser 6 soffit |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2013-08-27 | 2013-09-10 17:29 | 14 | 2013-08-13 17:09 | Structural Engineering - Structural Engineering - General | 1500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Insufficient information made available to the worker. | Completed |  | Cable riser 6 has been cast with the opening at 900mm x 750mm, with a 150mm rebate around all four sides. (Please see attached marked up drawing) As detailed in RFI 1353, the opening should have been cast to 900mm x 900mm with a 100mm rebate around all four sides. The RFI also requests a ladder system with a suitable fall arrest system, complying with BS 4211 & BS EN 353, is required such as the Soll GlideLoc system or similar. Attached is the response from Soll Safety at Height detailing that the ladder and fall arrest system can be used in the 900mm x 750mm opening, and the ladder/fall arrest system can be fitted with an IKAR rescue set. (Also attached) Additionally, a D400 kite marked manhole cover can be supplied to fit over the opening. (Also attached)
| 03SR - Stations (RfL) | Cxxx-NCR-001645 | NCR | DLR Wall Reco panels shifting during mass concrete pour |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2013-09-27 | 2013-10-01 14:45 | 4 | 2013-08-21 11:17 | Civil - Civil Engineering General | 5000 |  | Workmanship | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | When pouring the mass concrete block to form the top of the wall detail against the top line of Reco panels, not enough care has been taken when placing concrete and it has been placed too fast shifting the top row of panels out of alignment across panel grid lines 50 - 57.Due to grout filling the Geomega sleeves the straps will not be able to be placed through these to secure the panels.
| 03SR - Stations (RfL) | Cxxx-NCR-001646 | NCR | Lack of Cover |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2013-08-31 | 2013-08-27 09:00 | -4 | 2013-08-17 09:23 | Structural Engineering - Reinforcement | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Lack of cover to Cable riser 6 upstands
| 03SR - Stations (RfL) | Cxxx-NCR-001647 | NCR | SCR-104 Plant Room Floor Screed Compaction |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2013-08-27 | 2013-09-06 16:06 | 10 | 2013-08-20 11:03 | Architectural - Flooring | 750 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | In the Plant Room's there are two patches of floor screed which have been poorly compacted. The screed is Keracol Keracem Eco.
| 03SR - Stations (RfL) | Cxxx-NCR-001648 | NCR | REN-104; Damage to Plant Room entrance render |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2013-09-03 | 2013-09-04 08:38 | 1 | 2013-08-20 15:09 | Architectural - Walls | 750 |  | Damaged | Rework | 4 (0.5-3k) | Complete |  | Completed |  | As shown in the attached photo a piece of render has spalled from the inside of the Plant Room doorway (eastern edge) at approximately 1.7m above FFL.
| 03SR - Stations (RfL) | Cxxx-NCR-001649 | NCR | Plant room blockwork - missing wall |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2014-02-07 | 2014-02-04 15:47 | -3 | 2013-08-21 16:07 | Architectural - Walls | 1500 |  | Supervision/Management | Repair | 4 (0.5-3k) | Complete | Supervision - Insufficient supervision | Completed |  | The blockwork wall which surrounds the column in the Combined Service Riser (in the left of the attached photo) has not yet been constructed.
| 03SR - Stations (RfL) | Cxxx-NCR-001651 | NCR | Track slab K starter bars from station deck |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2013-10-30 | 2013-09-16 12:25 | -44 | 2013-08-29 10:34 | Civil - Track | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Conflicting information on drawings | Completed |  | The epoxy coated starter bars from the station deck for track slab type K, have been cast at 300mm (edge) and 450mm (centres), the same dimensions as all other trackslabs along the station and viaduct deck. The drawing shows these should be at 150mm.
| 03SR - Stations (RfL) | Cxxx-NCR-001652 | NCR | CMR - Retaining Wall D7 & D9 Pile cap concrete |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2013-12-01 | 2013-10-24 13:52 | -38 | 2013-08-30 14:53 | Civil - Civil Engineering General | 3500 |  | Material | Use As-Is | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | With reference to Retaining wall pile caps D7 & D9 at City Mill River. Concrete Mix C35/45 C was used in the bases instead of C35/45 A. This oversight occurred despite the __ engineer, MS Clerk of Works and Crossrail Field Engineer being in attendance at the time of pour and checking the tickets prior to placing. Fortunately the C34/45 C mix complies with the requirements of the C35/45 A mix. The requirements are that the mix should have a design chemical class DC4 and a Chloride class 0.2. The cement content and blend of cements complies with the requirements of table 6 of BS8500 part 2 and the calculated chloride value for the mix is 0.18. See attached mix design certificate.
| 03SR - Stations (RfL) | Cxxx-NCR-001653 | NCR | Reco wall verticality |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2013-12-15 | 2013-10-31 12:29 | -45 | 2013-09-09 12:54 | Civil - Civil Engineering General | 10000 |  | Design | Use As-Is | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Further to a full verticality survey of the completed Reco wall it has been noted that areas of the wall are outside the specified tolerance given as guidance by Reco and noted on the drawings.
| 03SR - Stations (RfL) | Cxxx-NCR-001655 | NCR | SCR-103; Break-out around downpipes |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2014-03-30 | 2014-03-28 10:58 | -2 | 2013-09-12 11:42 | Architectural - Flooring | 650 |  | Planning | Rework | 4 (0.5-3k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | Where the downpipes penetrate the floor of the staff corridor the pipe embedded within the foundation is 100mm diameter, where the new pipe above ground level is 150mm diameter. In-order to fit a reducer piece the 150mm screed needs to be broken-out around 2 pipe locations, then reinstated. One of these locations has already been broken-out by the M&E contractor.
| 03SR - Stations (RfL) | Cxxx-NCR-001656 | NCR | CMR Retaining Wall As-built |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2013-10-24 | 2013-10-03 11:37 | -21 | 2013-09-12 13:38 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | See attached as-built of the east retaining wall at City Mill River. The as-built shows the plan location of the walls. Highlighted are the panels which do not conform to the setting out tolerence given on drawing Cxxx-MMD-C-EDR-CRG06-00070. Note, only retaining walls A and D2-D9 were constructed by __.
| 03SR - Stations (RfL) | Cxxx-NCR-001658 | NCR | CMR - DLR bridge foam concrete compressible filler board |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2013-10-02 | 2013-09-23 11:43 | -9 | 2013-09-12 14:09 | Civil - Civil Engineering General | 5000 |  | Supervision/Management | Rework | 3 (3-6k) | Complete | Management Problem - Misunderstand the definition of the requirement | Completed |  | With reference to the DLR bridge west abutment foam concrete to form the bearing shelf gallery. __ incorporated a 25mm flexcell movment joint which does not conform to the design intent. Following discussions with __, __ propose to break out a local section of the foam concrete to allow 40mm of compressible filler (miothene) to be placed. Foam concrete will then be placed to a maximum height of 1m. The remaining void will be filled with a deeper section of screed concrete. Please confirm this is acceptable. In addition, due to the nature of foam concrete the finished level is very difficult to control as screed rails were not able to be used. As a result the concrete has had to be trimmed to recieve the concrete capping layer. Confirm this is acceptable.
| 03SR - Stations (RfL) | Cxxx-NCR-001660 | NCR | 12mm Epoxy Coated Starter Bars Bent on Site in Bays E24-E26 |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2013-10-25 | 2013-10-29 10:14 | 4 | 2013-09-19 13:56 | Track - Track General | 1000 |  | Supervision/Management | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Central Epoxy coated starter bars on trackslab area bays E24, E25 and E26 were bent on site in attempt to solve an issue with starter heights. Once this was spotted by the management, an investigation found that a solution was found and executed at site level without consultation with any of the management teams.
| 03SR - Stations (RfL) | Cxxx-NCR-001661 | NCR | NCR for FCD 1657 (Bar cutting tolerances exceeded at supplier) |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2013-10-04 | 2013-10-03 09:56 | -1 | 2013-09-20 10:18 | Track - Track General | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | PLease refer to FCD 1657 (Due to the tollerance at the supplier reinforcement fabrication yard, MS have found upto 60mm of deviation in the longitudinal bars. For this reason the specified cover of 40mm is not achieveable in many places, and the station steel reinforcement has been delivered).
| 03SR - Stations (RfL) | Cxxx-NCR-001662 | NCR | CMR - DLR Bridge Slab Parapet Crack Report |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2014-04-30 | 2014-04-30 16:53 | 0 | 2013-10-01 08:11 | Civil - Civil Engineering General | 12000 |  | Material | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | With reference to the DLR Bridge slab cracks on the cantilever section at City Mill River and further to RFI 1768, see attached report covering __s findings.
| 03SR - Stations (RfL) | Cxxx-NCR-001663 | NCR | Coping Installation Not to an Approved FCD |  | Crossrail | XRL | PML - Pudding Mill Lane Portal (Central) |  | 2013-10-23 | 2013-10-23 10:57 | 0 | 2013-09-20 08:48 | Civil - Civil Engineering General | 5500 |  | Supervision/Management | Rework | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The ITP for coping installation (Cxxx-MRG-C-ITP-CR094_WS111-50048) states that the coping units are to be bedded on mortar as per FCD 1638. This FCD was not raised until after installation had begun.
| 03SR - Stations (RfL) | Cxxx-NCR-001664 | NCR | Low Cover to Piles Road Rail Vehicle Access Ramp |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2013-10-18 | 2013-10-03 15:31 | -15 | 2013-09-20 12:44 | Structural Engineering - Reinforcement | 3000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Reduced cover has been identified to Pile Numbers: P18, P19, P38, P39 and P62 of the Road Rail Vehicle Access Ramp.
| 03SR - Stations (RfL) | Cxxx-NCR-001665 | NCR | RRVAR Pile damaged reinforcement |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2013-10-18 | 2013-10-10 10:54 | -8 | 2013-09-20 12:56 | Structural Engineering - Reinforcement | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During the pile cropping operation two bars of Pile P27 were snapped. One 50mm above cut-off level and one 400mm.
| 03SR - Stations (RfL) | Cxxx-NCR-001666 | NCR | DLR coping units to be re-bedded |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2013-10-30 | 2013-10-23 11:00 | -7 | 2013-09-24 08:24 | Civil - Civil Engineering General | 5500 |  | Workmanship | Rework | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | __ have identified that a number of the DLR wall coping units need to be removed and re-bedded due to insufficient bedding contact being achieved across the unit.
| 03SR - Stations (RfL) | Cxxx-NCR-001667 | NCR | PT-50; Plant room floor paint finish |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2013-10-16 | 2013-10-03 11:52 | -13 | 2013-09-25 11:34 | Architectural - Flooring | 750 |  | Equipment Breakdown | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Inadequate/insufficient tooling. | Completed |  | During initial application of PT-50 to the plant room floor the subcontractor's spraying equipment broke-down and they opted to apply the paint by roller. This produced a poor finish with roller markings and the subcontractor was instructed to re-apply the paint by spray. It also became apparent that the manufacturers information only states brush or spray application methods. The rooms are now being re-sprayed to produce the desired finish.
| 03SR - Stations (RfL) | Cxxx-NCR-001668 | NCR | Reco Wall Strap and P-Way Drainage Clash |  | Crossrail | XRL | PML - Pudding Mill Lane Portal (Central) |  | 2014-01-31 | 2014-01-29 14:37 | -2 | 2013-12-05 16:56 | Civil - Civil Engineering General | 5000 |  | Supervision/Management | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During construction of the reinforced earth embankment, __ raised a PTR (Cxxx-RFI-001581) which highlighted a potential clash between the Reco wall straps and p-way undertrack drainage. The PTR response specifies the required arrangement and construction sequence of reinforcing straps and Geogrid membrane around the drainage pipes and catchpits. The sequence clearly indicates that the works should have been completed as part of the embankment construction. A further requirement to overcome this clash is shown on drawing Cxxx-SWN-R-DDL-CR094_PT002_Z-95620, which states that catchpits CPW3 and CPW4 should be “constructed at the same time as the placement of the reinforced earth wall structure.” Neither the information in the RFI response nor the drawing detail has been applied on site, resulting in the Geogrid and Reco wall straps (both structural elements in the retaining wall), interferring with the installation of drainage system. Refer to drawings: Cxxx-SWN-R-DDL-CR094_PT002_Z-95600 Cxxx-SWN-R-DDL-CR094_PT002_Z-95601 Cxxx-SWN-R-DDL-CR094_PT002_Z-95620
| 03SR - Stations (RfL) | Cxxx-NCR-001669 | NCR | Reco wall mass concrete block levels |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2013-11-15 | 2013-11-14 16:23 | -1 | 2013-09-30 15:38 | Civil - Civil Engineering General | 1000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The Reco mass concrete block levels have some high and low spots ranging from 30mm low to 20mm high
| 03SR - Stations (RfL) | Cxxx-NCR-001670 | NCR | CRL 1 surface cracking to top of wall bay 1 |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2014-10-31 | 2014-10-31 08:49 | 0 | 2013-10-02 13:36 | Civil - Civil Engineering General | 2000 |  | System Defect | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | There is several surface cracks to the top face of CRL 1 wall approx 1mm wide.
| 03SR - Stations (RfL) | Cxxx-NCR-001672 | NCR | CMR - D2 pile cap lost cubes |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2014-06-30 | 2014-06-02 15:34 | -28 | 2013-10-02 15:36 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | With reference to CMR retaining wall pile cap D2, cube set PML 712 is lost and as such the QA information will not be available for this cap.
| 03SR - Stations (RfL) | Cxxx-NCR-001673 | NCR | Drainage Pipework Grid line 06 to 09 |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2014-01-10 | 2014-01-20 11:01 | 10 | 2013-10-04 08:26 | Mechanical - Public Health Engineering | 1000 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Use of unapproved materials | Completed |  | The pipes installed where not in accordance with the specs/accepted MCR. The MCR for the proposed alternative pipes was not accepted before installation.
| 03SR - Stations (RfL) | Cxxx-NCR-001674 | NCR | TrackSlab bays E6-8, and E12-14, weep holes |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2014-01-31 | 2014-01-07 09:41 | -24 | 2013-10-08 09:22 | Track - Track General | 500 |  | Planning | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Weep holes on bays E6-8, and E12-14 have been cast above the track plinth. Please find attached asbuilt survey.
| 03SR - Stations (RfL) | Cxxx-NCR-001675 | NCR | Placement of Concrete around Bolt Clusters |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2014-02-20 | 2014-02-13 09:09 | -7 | 2013-10-08 09:20 | Track - Track General | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | 4no bolt clusters (please find attached pics) for the 3rd rail installation, have a lack of concrete surrounding them and the bolts are visibly exposed.
| 03SR - Stations (RfL) | Cxxx-NCR-001676 | NCR | Blow Holes in bays E6-8 and E12-14 |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2014-03-04 | 2014-02-27 09:42 | -5 | 2013-10-08 09:41 | Track - Track General | 1000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | A large number of blow holes on both Bays (E6-8, E12-14), on both 6' and Cess sides are apparent on the formed face.
| 03SR - Stations (RfL) | Cxxx-NCR-001677 | NCR | DLR coping unit PM13 |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2013-11-29 | 2013-12-09 11:33 | 10 | 2013-10-09 14:38 | Civil - Civil Engineering General | 1000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The most eastern coping unit to the DLR wall cannot be placed to the correct alignment. This is due to two factors. 1) The adjoining RC wall is 25mm wider than it should be. 2) The 1st few REco wall panels at the top are set back in a little. These two issues only allow the unit to butt up correctly at the east end (to the next unit).
| 03SR - Stations (RfL) | Cxxx-NCR-001680 | NCR | Cold joint - Track slab up-stand - Bay E6 |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2014-02-14 | 2014-02-13 09:20 | -1 | 2013-10-11 09:11 | Civil - Track | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | There is a small area on the North upstand of bay E6 where a cold joint has formed.
| 03SR - Stations (RfL) | Cxxx-NCR-001681 | NCR | Frit to Glazing EWS-101 |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2014-03-14 | 2014-03-10 11:09 | -4 | 2013-10-14 10:36 | Architectural - Glazing | 7500 |  | Material | Rework | 2 (6-60k) | Complete | Personnel Error - Verbal communication problem | Completed |  | Two number panes of glazing (out of six) have been delivered and installed on the station, but were found to not have the frit pattern as per the architects design intent. Drawings for the intended frit pattern were sent to __ and samples were procured and approved. __ submitted the drawings to CRL sent to them for the intended frit pattern under RFI 457 for confirmation and raised RFI 848 for approval of samples. During the design proccess for construction issue drawings a response from the architect to the sub-contractors design requested that six number glazed panels be fritted full height (see RFI 987 note 1). This response was seen as a change to the design intent and actioned by the sub-contractor. __ have not recieved any construction issue drawings for the required frit to date.
| 03SR - Stations (RfL) | Cxxx-NCR-001682 | NCR | Surface cracking to internal face of viaduct precast concrete beams GL7-8 |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2014-08-22 | 2014-08-16 09:49 | -6 | 2013-10-17 08:10 | Civil - Civil Engineering General | 2500 |  | System Defect | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Localised surface cracking is visible on the internal face of the precast concrete beams GL7-8 (north/ south).
| 03SR - Stations (RfL) | Cxxx-NCR-001683 | NCR | DLR wall - placed coping units |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2014-01-10 | 2014-01-06 17:56 | -4 | 2013-10-18 13:19 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | In order to best fit the DLR coping units along the REco wall alignment, butt them up to each other and tie in to existing structures, units have technically been placed out of tolerance. This has been confirmed in the as built survey.
| 03SR - Stations (RfL) | Cxxx-NCR-001684 | NCR | DLR wall stich pour at the back of copings |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2013-11-01 | 2013-10-29 11:04 | -3 | 2013-10-18 13:29 | Civil - Civil Engineering General | 750 |  | Equipment Breakdown | Use As-Is | 4 (0.5-3k) | Complete | Subcontractor Problems - Other | Completed |  | During the most western stich pour of the DLR embankment wall (25m long), the batching plant broke down. It was nearly an hour later when a backup plant sent out the 2nd and last load but this was rejected as it was 60mm over its upper slump limit. We could not then expsept concrete for a futher hour. This would cause a cold joint.
| 03SR - Stations (RfL) | Cxxx-NCR-001685 | NCR | CMR - CRL Bridge Pile Issues |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2014-01-15 | 2014-01-17 10:48 | 2 | 2013-10-23 14:06 | Civil - Civil Engineering General | 40000 |  | Workmanship | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | With reference to the Crossrail Bridge piling works at CMR, post excavation a number of piles have been installed outside of design tolerence in terms of installed height and 4no. have insufficient cover to one side. For clarity a schedule has been drawn up to capture the current as-built information along with proposals to rectify (see attached). Please confirm if these proposals are acceptable/appropriate.
| 03SR - Stations (RfL) | Cxxx-NCR-001686 | NCR | DLR Station Platform Drainage Channel / Missing Penetrations |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2013-11-13 | 2013-11-14 12:54 | 1 | 2013-10-30 12:40 | Civil - Drainage | 750 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | With reference to the marked up drawings attached that were issued under FCD 501 , The 2 No 150mm core holes that are required for the ACO drainage outlets located at GL 01 have not been completed.(highlighted in pink )
| 03SR - Stations (RfL) | Cxxx-NCR-001687 | NCR | DLR wall mass concrete block |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2013-11-14 | 2013-11-09 21:04 | -5 | 2013-10-31 08:55 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The buried mass concrete block under the coping stitch pour has not quite been poured to the actual face of the back of stitch pour in some areas.
| 03SR - Stations (RfL) | Cxxx-NCR-001688 | NCR | SCR-102 Concrete too high to accept Screed |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2013-11-22 | 2013-11-14 13:37 | -8 | 2013-11-01 10:50 | Civil - Civil Engineering General | 850 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Due to the concrete base of the Retail Unit being high there was insufficient room avaliable to install the floor insulation and screed and meet the required FFL of 104.675m and the screeding thickness tolerances required by the architectural spec and manufacturers data.
| 03SR - Stations (RfL) | Cxxx-NCR-001689 | NCR | DLR Station BAL 110 base plates pre drilled holes not alligned with pre drilled holes in steels |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2013-11-17 | 2013-11-15 09:57 | -2 | 2013-11-03 12:25 | Architectural - Balustrade | 750 |  | Design | Reject | 4 (0.5-3k) | Complete | Discipline/Workmanship - Error by manufacturer in shipping or marking | Completed |  | The pre drilled holes in base plates for BAL 110 station balustrade do not align with the pre drilled holes in station portal steels.This incident happens on 4 No location on the half posts at GL S08 The sub contractotr has re drilled the base plate on site as per attched photograph , the 2 No holes are to close together and this has weakend the fixing . Regards
| 03SR - Stations (RfL) | Cxxx-NCR-001690 | NCR | Permit to Load for RRVR Base Pour 1 |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2013-11-18 | 2013-11-15 13:29 | -3 | 2013-11-04 12:54 | Structural Engineering - Concrete Member | 500 |  | Supervision/Management | Reject | 4 (0.5-3k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | The RRVR base pour 1 was concreted without a signed Permit to Load being in place. The temporary works to this concrete pour was inspected progressively as it was being installed by a competent temporary works supervisor and was deemed adequate prior to concreting. The Permit to Load paperwork however had not been followed up and was not in place prior to concreting.
| 03SR - Stations (RfL) | Cxxx-NCR-001691 | NCR | RRVR Base Slab Pour 2 Starter Bars |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2013-11-19 | 2013-11-09 21:07 | -10 | 2013-11-05 09:27 | Structural Engineering - Reinforcement | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Approximately 80% of the starter bars (BM 24 & BM 77, Shape Code 13) have been installed with the "hooks" being re-bent to 45 deg angles to allow the reinforcement to be installed.
| 03SR - Stations (RfL) | Cxxx-NCR-001692 | NCR | DLR Track Slab Construction |  | Crossrail | XRL | PML - Pudding Mill Lane Portal (Central) |  | 2013-11-22 | 2013-11-22 13:47 | 0 | 2013-11-06 11:55 | Structural Engineering - Reinforcement | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | On the 08/10/2013 during a Crossrail led surveillance, held at the Pudding Mill Lane, the subject; the construction of the new DLR track slab and the verification records. The Contractor supplied the qualifications for the welding operative and they were found to be 10 years past their valid date.
| 03SR - Stations (RfL) | Cxxx-NCR-001693 | NCR | DLR Track Slab Construction |  | Crossrail | XRL | PML - Pudding Mill Lane Portal (Central) |  | 2014-01-31 | 2014-01-30 11:14 | -1 | 2013-11-06 12:05 | Structural Engineering - Reinforcement | 1000 |  | Supervision/Management | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | On the 24/10/2013 during a Crossrail led surveillance, held at the Pudding Mill Lane, the subject; the construction of the new DLR track slab and the verification records The Contractor raised PTR RFI-1774 asking the designers for confirmation of the welding specification to be used for the DLR permanent way stray current collection, highlighting the specific clauses which are to apply for preparation, the welding process and the consumables. The designer answered the RFI informing the Contractor that the welding requirements for the stray current bars in the DLR – Permanent Way are to be in accordance with BS EN 1011-1:2009 and BS EN 1090-2:2008. The Contractor has not complied with the requirements and omitted the welding procedure from the verifying documents
| 03SR - Stations (RfL) | Cxxx-NCR-001694 | NCR | P'way drainage levels - CMR (East End) |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2013-11-30 | 2013-11-25 17:00 | -5 | 2013-11-11 11:37 | Civil - Drainage | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | With reference to drawing number Cxxx-SWN-R-DDL-CR094_PT002_Z-95621, the drawing illustrates a table with the location and level information of manholes for the P'way drainage at CMR. Note: run D5-D4 complies with 1:200, MH D4-D3 complies with 1:150 fall. See attached excel file with as-built levels of the manholes constructed at CMR. Note the Cover levels of the manholes are governed by segment sizes and tokstrip settlement.
| 03SR - Stations (RfL) | Cxxx-NCR-001695 | NCR | Misaligned Frit Pattern |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2014-04-22 | 2014-03-28 17:23 | -25 | 2013-11-15 16:23 | Architectural - Glazing | 2000 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | On one pane of the SO6-S07 horizontal slope of the South elevation the frit pattern is not in alignment with the neighbouring panes due to it being printed on to the glass incorrectly
| 03SR - Stations (RfL) | Cxxx-NCR-001696 | NCR | CMR - Pile E11 shear collar extension |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2013-11-30 | 2013-11-29 14:48 | -1 | 2013-11-18 14:42 | Civil - Civil Engineering General | 1000 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | With reference to NCR 1685 (CRL Pile defects), pile E11 (shear collar) is required to be extended by approximately 160mm to accept shear studs as per the design intent. The shear collar was prepared to accept the full penetration butt weld in acccordance with an approved Weld Procedure Specification (WPS). The welding rods stated on the WPS indicated ESAB Filarc 56S (or equivelent). The rods used for the weld are ESAB Spezial, in 3.2mm and 4mm. The 3.2mm size was used for the root of the weld and the 4mm rods for the filler part of the weld. The 4mm rods were grade E42, the 3.2mm rods were E38. __ accept the use of Spezial E42 ,however, confirmed the E38 rods did not comply with the WPS.
| 03SR - Stations (RfL) | Cxxx-NCR-001697 | NCR | Permanent Way formation testing |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2014-01-20 | 2013-12-16 19:13 | -35 | 2013-11-21 13:46 | Civil - Track | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | __ have failed to adhere to clause 3.7.2 from the DLR Realignment specification in carrying out Light Weight Deflectometer (LWD’s) tests at the required level of 500mm below sub ballast on both the West and East embankments. In addition, the required CBR values were not taken on the West embankment at this level.
| 03SR - Stations (RfL) | Cxxx-NCR-001698 | NCR | Incorrect Concrete in Track Slab Bays W43-45 |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2014-04-27 | 2014-04-25 15:12 | -2 | 2014-01-23 10:50 | Track - Track General | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During the concrete pour to trackslab bays W43-45 between 1510hrs and 1810hrs on the 26/11/13, the following occurred; • __ mixer truck arrived on site and began discharge at 1513hrs and completed by 1528hrs. the next mixer truck did not arrive until 1620hrs • Following the slump test, discharge began and was quickly stopped when it became apparent that the __ mixer truck was due for __ and not for Galldris. • The area within the bay where concrete was discharged was mapped (please find attached), and calculated at being ≤1m³. • The wagon was sent away • The remaining concrete in the hopper and boom was discharged into a dumper and removed to the washout skip • Following the arrival of the correct mixer truck, the concrete pour was completed at 1810hrs. __ believe there may have been some contamination due the concrete entering the pipeline, however quick sums prove it is unlikely that any unapproved concrete entered the trackslab bay. A further set of cubes have been taken from the C32/40 CIIIA concrete which will be tested. This NCR is for both +30mins between loads, and cross-contamination of C32/40 CIIIA (unapproved), and C40/50 CIIIA (approved) concrete
| 03SR - Stations (RfL) | Cxxx-NCR-001700 | NCR | CMR CRL Bridge Permeation Grouting cube results |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2014-01-31 | 2014-01-29 15:50 | -2 | 2013-11-28 07:28 | Civil - Civil Engineering General | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | With reference to the permeation grouting works to bridge 53 at City Mill River and ITP Cxxx-MRG-C-ITP-CR094_WS111-50047. Please see attached register of cube results covering the works. The ITP references a minimum cube compressive strength of 2N/mm2 at 28 days (item 4.1). There are a number of examples of cube results not achieving the 2N/mm2 compressive strength. Consulting the specialist subcontractor, the results have to be viewed collectively. A single mix and thus a cube are not injected solely into a single TAM. Two mixes are specified and these are injected at odd/even locations along the TAM. One batch of a particular mix will be typically injected into multiple TAMS at different depths (sleeve positions). In the next phases the remaining TAM positions will be injected, creating a layered profile of grout around the TAM's to seal the ground. To ensure the ground is fully treated, sleeve positions were revisited and injected multiple times. If the cube results are considered collectively and averaged, the mean compressive strength is 2.01N/mm2. In addition a falling head test was completed on both abutments prior to de-mobilising. Both tests were successful. Note: The permeation grouting is temporary works and does not effect the integrity of the permanent works.
| 03SR - Stations (RfL) | Cxxx-NCR-001701 | NCR | Incorrect installation of type 'B' bearing at GL8 south |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2014-01-02 | 2013-12-17 10:09 | -16 | 2013-12-05 12:58 | Civil - Civil Engineering General | 1000 |  | System Defect | Rework | 4 (0.5-3k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | The type 'B' bearing at GL8 south has been installed incorrectly (PTFE disk is not in its correct position). The transit brackets for the type 'B' bearing are not capable of supporting the top/ base plate loads (500kg), having fixed the top plate to the precast beam soffit using structural adhesive. Due to this the PTFE disk comes out of its recess. To mitigate this, it was agreed with the bearing manufacturer, that prior to grouting the base sockets, steel shims (or equivalent) would be installed temporarily to provide the additional support required in order to ensure that the PTFE disk remains within its recess. The steel shims would then be removed prior to grouting to the underside of the bearing. This was done for the previous type 'B' bearings (2no), but was missed on the bearing in question.
| 03SR - Stations (RfL) | Cxxx-NCR-001702 | NCR | RRVAR Ramp Wall stop end position / clash with CRL NOS |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2014-01-31 | 2014-01-07 09:46 | -24 | 2013-12-05 12:11 | Civil - Civil Engineering General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The Eastern end of the Road Rail Vehicle Ramp (RRVR) front wall has been cast 30mm out of tolerance (See attached pre-pour survey). This is due to the Reckli being ordered as per RFI 1629 at 4.080m as a square section. However due to the angle of the face of Reckli and the angle of the wall end the Reckli dimension given should have accounted for the change in length over the height of the face.
| 03SR - Stations (RfL) | Cxxx-NCR-001703 | NCR | DLR track slab construction (2) |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2013-12-25 | 2013-12-19 13:58 | -6 | 2013-12-11 14:13 | Civil - Track | 1000 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | This NCR supersedes NCR 1692 which was raised by CRL and closed by CRL (incorrectly - following email information provided by Stephen Crummey not being uploaded). It was raised for the out of date welder qualifications, being found during CRL surveillance. To defend __, the welder qualifications required on the approved ITP were provided. Attached to this NCR is the original closed out NCR 1692 and email requesting this NCR to be raised.
| 03SR - Stations (RfL) | Cxxx-NCR-001705 | NCR | Duct entry to room C103 - Combined Service Riser |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2014-02-21 | 2014-02-20 12:31 | -1 | 2013-12-12 10:37 | Civil - Utilities Engineering | 750 |  | System Defect | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | During the time of plant room reinforced slab construction, the setting out details of the blockwork were not available to position the incoming ducts accurately against the wall. In addition to this the approximate duct location was in congested rebar U links, hence installed in the current location sitting 100-200mm from the walls. Isayas Tecleberhan
| 03SR - Stations (RfL) | Cxxx-NCR-001706 | NCR | IWS-103; Wall tiling to staff toilet out of plumb |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2014-02-28 | 2014-02-04 17:09 | -24 | 2013-12-16 10:38 | Architectural - Finishes | 2000 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The wall tiling to the southern wall of the Accomodation toilet (C109) was not built within specification tolerances for flatness (M40-550). The top corner at the eastern end of the wall protrudes ~30mm into the room.
| 03SR - Stations (RfL) | Cxxx-NCR-001707 | NCR | RFS-202. Damaged Panels |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2014-04-11 | 2014-04-10 16:09 | -1 | 2013-12-18 11:07 | Architectural - General | 2500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | 12 number RFS-202 panels are due to be replaced because the panels are damaged. See attached drawing for damaged panels.
| 03SR - Stations (RfL) | Cxxx-NCR-001709 | NCR | UTX cast too high |  | Crossrail | XRL | PML - Pudding Mill Lane Portal (Central) |  | 2014-02-14 | 2014-01-29 13:40 | -16 | 2013-12-19 12:25 | Civil - Civil Engineering General | 2000 |  | Supervision/Management | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The cable route ‘undertrack crossing’ (UTX), located at approx. Ch. 205 on the reinforced earth embankment has been cast too high. The ducts and concrete surround have been installed at the wrong level and they now clash with the undertrack drainage pipes that should pass over the crossing (between catchpits CP W4 and CP W5). Drawing number Cxxx-SWN-R-DDD-CR094_PT002_Z-95631 Rev C01, gives the invert level of the drainage carrier pipe (109.226m AOD). The same drawing also indicates that the “Actual design is dependant on cable sizes and required location.” The design of the UTX was the contractor’s responsibility and should have allowed for the drainage. It appears that the UTX concrete is approximately 300mm too high but this is not clear as no as-built records exist. Refer to drawings: Cxxx-SWN-R-DDL-CR094_PT002_Z-95602 Rev C02 Cxxx-SWN-R-DDD-CR094_PT002_Z-95631 Rev C01
| 03SR - Stations (RfL) | Cxxx-NCR-001710 | NCR | Failure to air test prior to backfilling - track slab drainage |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2014-02-15 | 2014-01-29 10:31 | -17 | 2014-01-13 11:39 | Civil - Track | 0 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Supervision - Insufficient supervision | Completed |  | Failure to follow checksheet 100 instructions: "air tests will be carried out prior to backfill to ensure the joints are not leaking"
| 03SR - Stations (RfL) | Cxxx-NCR-001711 | NCR | Track Slab E86-E88 - Slumped concrete beneath bolt clusters |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2014-02-14 | 2014-02-13 09:16 | -1 | 2014-01-17 09:02 | Civil - Track | 1000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | When pouring bays E86-88 on 10.01.2014, the concrete has slumped beneath 2 No. bolt clusters on the north up-stand of bay E87, exposing the cast in sleeves for the 3rd rail installation. On cutting out the defective concrete, the top lacers beneath the bolt cluster to the north west of bay E87 have also been partially cut. See attached sketch showing the location of these defects.
| 03SR - Stations (RfL) | Cxxx-NCR-001712 | NCR | Track Slab E66-E68 - Concrete levels |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2014-03-28 | 2014-03-27 18:01 | -1 | 2014-01-17 09:09 | Civil - Track | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The finished concrete level along the centre-line of track slab bays E66-E68 is low, and falls outside the specified design tolerances. This has resulted in a slight step between E65-E66 and E68-E69. These low levels will not affect track installation, cover is still adequate due to the proposed crown of the track slab and there is still a fall for drainage over the majority of the base.
| 03SR - Stations (RfL) | Cxxx-NCR-001713 | NCR | Unusable stray current sockets in the trackslab. |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2014-02-04 | 2014-01-30 11:17 | -5 | 2014-01-21 13:23 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | 2no bolt holes are located on the stray current collector bar and corresponding drawings, however only 1no bolt has been inserted during concreting, resulting in only one usable bolt for the stray current cable. Note the collector bar drawings show 2no bolt holes, yet the plan and section drawings only detail 1no cable/bolt This NCR has been raised as written confirmation from URS was not available at the time of initial survey.
| 03SR - Stations (RfL) | Cxxx-NCR-001714 | NCR | Pea shingle MCR |  | Crossrail | XRL | PML - Pudding Mill Lane Portal (Central) |  | 2014-02-28 | 2014-01-30 11:24 | -29 | 2014-01-17 10:43 | Civil - Drainage | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Procedure Problem - Other | Completed |  | The Contractor is working without an approved MCR Cxxx-MRG-R4-QAP-CR094_WS111-50008 for granular fill is at decal code 3 status “Not Accepted. Revise and resubmit. Work may not proceed. MCR reviewed and signed by the PFE 21/11/2013.
| 03SR - Stations (RfL) | Cxxx-NCR-001715 | NCR | CMR Crossrail Bridge Base Slab - Excess Cover |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2014-02-14 | 2014-02-13 18:10 | -1 | 2014-01-23 14:04 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | It has been identified that there is additional cover to reinforcement on the top face of the CMR base slab. Please refer to the cover survey of the T1 steel attached. It can be seen that the maximum cover on the top face of the slab is 91mm, this value is 21mm outside of the tolerance. The average cover on the top face of the base slab is 78mm.
| 03SR - Stations (RfL) | Cxxx-NCR-001717 | NCR | Blacktop / CBGM laid under the paved areas south of the DLR station |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2014-02-06 | 2014-02-04 12:52 | -2 | 2014-01-23 14:02 | Civil - Civil Engineering General | 2500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Supervision - Insufficient supervision | Completed |  | Where the blacktop & CBGM material was laid to the paved areas south of the new DLR station, we have identified a 50m2 area of AC32 binder course that has been laid approx 30mm low and an area of 10m2 laid approx 20mm high. Also 2 small areas of the CBGM which has been laid approx 30mm high.
| 03SR - Stations (RfL) | Cxxx-NCR-001718 | NCR | Track Slab Bays W84-W86 - Blown Shutter |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2014-03-21 | 2014-03-19 11:26 | -2 | 2014-01-27 10:26 | Civil - Track | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Whilst pouring track slab bays W84-W86, the inside shutter to the 6-foot upstand has deformed resulting in a non vertical face to the inside of the up-stand wall. Subsequently, the measurement between the inside faces of the up-stands falls outside the 2150mm (+/- 10mm) as shown on the relevant drawings. Colas have checked this against the Pway alignment and have advised that this will not impact on the position of the rail baseplates.
| 03SR - Stations (RfL) | Cxxx-NCR-001719 | NCR | CMR Crossrail Bridge - Reduced Reinforcement Splice Length in the Base Slab Construction Joint |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2014-04-04 | 2014-04-03 15:05 | -1 | 2014-01-27 14:09 | Civil - Civil Engineering General | 1000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The base slab of the CMR Crossrail Bridge has been cast with a construction joint on the north side to allow the existing NR Bridge 53 footing to be broken out in sections. After pouring the main section of the base slab it has been identified that the splice length of 4no. top mat reinforcement bars and 1no. bottom mat bars is not sufficient. The sketches attached detail the location of the issue and identify the bars that do not have the specified splice. The maximum available splice on each bar is detailed on the sketch.
| 03SR - Stations (RfL) | Cxxx-NCR-001720 | NCR | CMR Crossrail Bridge - Concrete Supply to East Abutment Pour 1 |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2014-03-06 | 2014-03-07 14:37 | 1 | 2014-02-20 17:28 | Civil - Civil Engineering General | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | During the concrete pour for the CMR Crossrail Bridge east abutment, the time between loads exceeded the duration detailed in clause E10.680 of the specification. As can be seen from the attached pour record sheet, the time between load 8 and 9 was 47 minutes. In addition, the delay between load 9 and 10 was 72 minutes.
| 03SR - Stations (RfL) | Cxxx-NCR-001721 | NCR | dmagaed drainage pipe north of the station |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2014-03-04 | 2014-03-05 11:53 | 1 | 2014-02-06 07:32 | Civil - Drainage | 750 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Drainage pipe DLRW8 on drawing 95224, where it comes out the Station base has suffered damage (this section of works had to be constructed in phases). A section of the pipe has cracked off, see attached photo, it is not possible to replace this section of pipe as it is cast into the station RC structure.
| 03SR - Stations (RfL) | Cxxx-NCR-001722 | NCR | RRVAR Walls - Tie Wire protruding from wall pours |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2014-04-04 | 2014-03-06 14:54 | -29 | 2014-02-07 11:36 | Structural Engineering - Concrete Member | 500 |  | System Defect | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | On the RRVAR Access Ramp Walls stainless steel tie wire has been cast in and is protruding from the joint between the kicker and the main body of the wall.
| 03SR - Stations (RfL) | Cxxx-NCR-001723 | NCR | Bottom ballast levels |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2014-04-23 | 2014-04-23 14:42 | 0 | 2014-02-10 15:17 | Civil - Track | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | MS note that following the installation of bottom ballast & prior to sleeper & rail install, the survey indicates a range of lifts between 24 & 71mm will be required compared to the tolerance stated in the Inspection & Test Plan of +0, -50mm. As the Schweerbau Tamper is capable of lifts in the range of 90mm in a single run this will not be a problem. Please note, the final data file which controls the tamping operations will be created from a top of rail survey in the hours immediately prior to tamping.
| 03SR - Stations (RfL) | Cxxx-NCR-001724 | NCR | Over 30 minutes between concrete loads |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2014-02-28 | 2014-02-21 19:11 | -7 | 2014-02-14 12:29 | Civil - Track | 0 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | Due to the nature of the track slab and the need to pour the slab as a whole the concrete needs to be placed slowly. This method of work combined with occasional issues with the supply of concrete (breakdowns, traffic etc.) has resulted in a number of occasions where the time between concrete loads on a number of track slab pours has exceeded 30 minutes. These bays are listed below: E33-E35 E39-E41 E45-E47 E51-E53 E54-E56 E60-E62 E66-E68 E69-E71 E83-E85 E86-E88 East End Eastbound Transition W02-W04 W05-W7B W31-W33 W37-W39 W43-W45 W52-W54 W55-W57 W58-W60 W61-W63 W67-W69 W72-W74 W75-W77 W84-W86 West End Eastbound Transition West End Westbound Transition
| 03SR - Stations (RfL) | Cxxx-NCR-001726 | NCR | DLR wall coping placing mortor cube failure |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2014-03-07 | 2014-03-05 11:30 | -2 | 2014-02-21 13:41 | Civil - Civil Engineering General | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Out of the 10 samples taken from the mortar used in placing the Coping stones on the DLR Retaining wall, 1 sample failed to comply with the compressive strength requirement of 5N/mm2. Sample reference number PML 922 achieved a strength of 3.7n/mm2. The sample was taken from material placed on the 19th September 2013 for Batch 9/08/13.09.00.
| 03SR - Stations (RfL) | Cxxx-NCR-001727 | NCR | DLR embankment fill - Missed Frequency for TRL Sulphates |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2014-03-07 | 2014-03-07 14:41 | 0 | 2014-02-21 13:47 | Civil - Civil Engineering General | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Personnel Error - Violation of requirement or procedure | Completed |  | When sampling the 6H material from __ and the Class 1A / 6N Crushed concrete from Cxxx’s Olympic Park site __ failed to achieve the specified sampling frequency for Water Soluble and Oxidisable sulphates. The frequency for these tests is not specified within table 1/5 of the Materials and workmanship specification – Earthworks, but is listed on the ITP with the frequency set at ‘5 per source to be confirmed’. We have 3 compliant results for the 6H from __ at Colchester and 2 compliant results from the Olympic material.
| 03SR - Stations (RfL) | Cxxx-NCR-001728 | NCR | RRVAR Wall B - Time between loads exceeded |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2014-03-26 | 2014-03-24 18:46 | -2 | 2014-02-26 11:49 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | During the pour of RRVAR Wall B there was a 58minute delay between the final two loads of concrete. Approximately 0.5m3 of concrete was retained in the pump and after 20minutes this was placed into the pour to freshen up the face. Once the final load had arrived onsite the face was visually inspected and was considered suitably fresh.
| 03SR - Stations (RfL) | Cxxx-NCR-001729 | NCR | DLR embankment - Missed Frequency for PH on the 6H Drainage Layer |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2014-03-13 | 2014-03-09 09:48 | -4 | 2014-02-27 07:59 | Civil - Civil Engineering General | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | When sampling the 6H material from __ Colchester site __ failed to achieve the specified sampling frequency for PH. We have 3 compliant results for the 6H from __ at Colchester out of a required 6. This equates to 1 result per 400t of material. Some weeks only 1 -2 loads have been imported and this in theory would require a sample taking. __ feel the sampling frequency achieved is more than adequate given that only a small proportion of 6H comes into contact with the reinforced earth straps and the small quantity imported. __ propose to leave both sources of material in the works. We feel there is no risk as the results are well within specification requirements.
| 03SR - Stations (RfL) | Cxxx-NCR-001730 | NCR | Out of tolerance levels - Track Slab Bay E32 |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2014-03-20 | 2014-03-13 15:06 | -7 | 2014-03-06 12:15 | Civil - Track | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The step in the track slab bases required for the change in baseplate type from Vipa to Vanguard has been cast between bays E32 and E33, as opposed to between E31 and E32 as required by the design. This has resulted in the main plinth of bay E32 being out of tolerance (maximum 32mm low, which is 7mm out of tolerance). Please see the attached as-built survey.
| 03SR - Stations (RfL) | Cxxx-NCR-001732 | NCR | Mesh / concrete used in the slabs at the base of the concourse stairs |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2014-04-30 | 2014-03-20 12:33 | -41 | 2014-03-11 08:59 | Civil - Civil Engineering General | 500 |  | Planning | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | With regard to the slabs required under the shackery corduroy tiles at the base of the stairs in the concourse area, the mesh used was doubled up 6mm in replace of the 10mm specified under RFI 2225 and the C40/50B concrete mix was used rather than the C40/50C mix specified.
| 03SR - Stations (RfL) | Cxxx-NCR-001733 | NCR | wrong mesh to the TVM / Esub base |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2014-04-27 | 2014-04-25 13:41 | -2 | 2014-03-11 09:11 | Civil - Civil Engineering General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The incorrect mesh was used in the conbined TVM / E-Sub base to the station concourse. In place of A393 mesh, 6mm mesh was used (doubled up)
| 03SR - Stations (RfL) | Cxxx-NCR-001734 | NCR | CMR Crossrail Bridge Base Slab Section 3 - Concrete Supply |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2014-04-01 | 2014-03-31 12:04 | -1 | 2014-03-18 15:23 | Civil - Civil Engineering General | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | During the concrete pour for the CMR Crossrail Bridge base slab section 3 on 15/03/14, the time between concrete deliveries exceeded the duration detailed in clause E10.680 of the specification. As can be seen from the attached pour record sheet, the time between loads 1 and 2 was 35 minutes.
| 03SR - Stations (RfL) | Cxxx-NCR-001735 | NCR | Damaged Mesh Cladding Panel EWS-105 |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2014-11-28 | 2014-11-05 16:04 | -23 | 2014-03-25 13:38 | Architectural - General | 3000 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Improper handling of material | Completed |  | EWS-105 Mesh cladding panel (M4006) was damaged on site. Panel is only aesthetically damaged and not structurally.
| 03SR - Stations (RfL) | Cxxx-NCR-001736 | NCR | joint sealant between CLR 1 wall and Station west abutment |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2014-04-26 | 2014-04-17 00:01 | -9 | 2014-03-25 15:06 | Civil - Civil Engineering General | 1000 |  | Planning | Repair | 4 (0.5-3k) | Complete | Management Problem - Improper resource allocation | Completed |  | The 2 part polysulphide joint spanning the joint between CRL 1 & Station west abutment was not installed before the north face cladding. This prevents us from installing the 2 part joint material as the installation method will not allow the gun in there.
| 03SR - Stations (RfL) | Cxxx-NCR-001737 | NCR | Main LV Switchboard |  | Crossrail | XRL | PML - Pudding Mill Lane Portal (Central) |  | 2014-04-11 | 2014-04-10 18:56 | -1 | 2014-03-25 18:23 | Electrical - Power Distribution | 10000 |  | Design | Rework | 2 (6-60k) | Complete | Design Problem - Error in equipment or material selection | Completed |  | Their is currently a confliction between the cable calculations that have been submitted under the latest AFC, that have been based upon __ release devices and the fact that their has been TM-D release devices Installed as part of the MCCB arrangement within the equipment currently in situ within the main Switch Room LV Switchboard. Despite the confliction being noted and highlighted by the DLR at/post the FAT it doesn’t appear to have been picked up and rectified and now required a modification at site level to rectify the confliction
| 03SR - Stations (RfL) | Cxxx-NCR-001738 | NCR | SER Distribution Board Arrangement |  | Crossrail | XRL | PML - Pudding Mill Lane Portal (Central) |  | 2014-04-30 | 2014-04-30 17:02 | 0 | 2014-03-25 18:41 | Electrical - Power Distribution | 1000 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Design Problem - Error in equipment or material selection | Completed |  | The current arrangement of protective devices within the SER distribution board does not reflect the information provided via PTR response which clearly set out the requirements, Post confirmation/clarification of the anomalies within the __ External Requirements Document. The Information and the change was instructed, but both the installation and the design has not been updated to reflect this, which will now require re-work/modification on site level
| 03SR - Stations (RfL) | Cxxx-NCR-001739 | NCR | Spalling of track slab concrete around conductor rail bolts |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2014-05-02 | 2014-04-25 15:50 | -7 | 2014-04-01 13:09 | Civil - Track | 5000 |  | Workmanship | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Brecknell Willis are currently installing the conductor rail through the DLR station and viaduct. Galvanised steel brackets are are being fixed to the inserts cast within the track slab upstand walls. In some areas a portion of concrete approximately 30mm deep (see attached photographs) has spalled away from the vertical face. This has happened in 9 locations through the station and viaduct. No steel reinforcement has been exposed.
| 03SR - Stations (RfL) | Cxxx-NCR-001740 | NCR | RRV wall D concrete void |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2014-05-09 | 2014-05-06 08:16 | -3 | 2014-03-26 17:07 | Civil - Civil Engineering General | 2000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | A void has been formed in the concrete to the top/rear face of RRV Wall D.
| 03SR - Stations (RfL) | Cxxx-NCR-001742 | NCR | Failure to apply protective coating to unistrut cut ends on ceiling grid |  | Crossrail | XRL | PML - Pudding Mill Lane Portal (Central) |  | 2014-05-08 | 2014-04-18 10:53 | -20 | 2014-03-27 12:59 | Architectural - Ceilings & Soffits | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | On the 27/01/2014 during a Crossrail led surveillance, held at Pudding Mill lane, on platform ceiling installation, it was found during the site inspection of the unistrut ceiling grid it appeared that the application of the zinc treatment to the cut ends had not been carried out in the correct manner. The zinc paint that was applied to the unistrut was seen from the brush marks to be applied after the cut ends were pushed against each other. The acceptable method that would ensure full coverage of the steel exposed due to cutting would have been to directly apply the zinc to the cuts prior to butting them together. No recorded checks had been carried out by the Contractor to verify that any of the cut ends have been treated
| 03SR - Stations (RfL) | Cxxx-NCR-001743 | NCR | Insufficient information on ceiling installation check sheets |  | Crossrail | XRL | PML - Pudding Mill Lane Portal (Central) |  | 2014-05-08 | 2014-04-19 10:31 | -19 | 2014-03-27 13:14 | Architectural - Ceilings & Soffits | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Verification Problems - Other | Completed |  | On the 31/01/2014 during a Crossrail led surveillance, held at the Pudding Mill Lane office, on platform installation verification records.The check sheets for the DLR platform ceiling installation number IS-08 do not contain sufficient information to demonstrate that the installation has been carried out to the specification, drawings i.e.There are no drawing numbers recorded on the Contractors check sheets IS-08 where stated as a requirement for carrying out the check, the checks undertaken for the grid and the ceiling panel fixings documented on IS-08 do not record the number of checks undertaken, both the check sheet and the ITP do not document the inspection frequency for any of the check items..
| 03SR - Stations (RfL) | Cxxx-NCR-001744 | NCR | DLR Station granite feature paving |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2014-04-10 | 2014-04-10 17:18 | 0 | 2014-03-27 13:33 | Civil - Civil Engineering General | 800 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Personnel Error - Inattention to detail | Completed |  | Feature granite paving laid between GL 1 – GL 4 to the south side of the station has been laid to the incorrect orientation. The band width should be 600mm wide not 420mm.
| 03SR - Stations (RfL) | Cxxx-NCR-001746 | NCR | RRV Ramp Wall D Cold Joint |  | Crossrail | XRL | PML - Pudding Mill Lane Portal (Central) |  | 2014-05-30 | 2014-05-30 16:05 | 0 | 2014-04-02 17:13 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Electrical or instrument noise | Completed |  | A cold joint is present in the RRV ramp wall D. It is approximately 3m long and displays 2 distinct areas. One where concrete is well compacted and an area above where the concrete is less well compacted.
| 03SR - Stations (RfL) | Cxxx-NCR-001747 | NCR | Cracking of grout pads under Pandrol base plates |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2015-01-30 | 2014-12-19 11:52 | -42 | 2014-04-04 10:42 | Civil - Track | 10000 |  | Material | Use As-Is | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The Parex Railfast grout that has been used beneath the Pandrol baseplates has cracked along the line of the hold down bolts. See attached photograph.
| 03SR - Stations (RfL) | Cxxx-NCR-001748 | NCR | 3rd rail support brackets |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2014-04-25 | 2014-04-18 10:50 | -7 | 2014-04-07 17:38 | Civil - Track | 500 |  | Manufacturing Defect | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | As part of the conductor rail design & installation process, the support brackets are fabricated by a 3rd party to the following standard details: M41898-01-FB and M41899-01-FB. As part of the First Article Inspections non confirmances were recorded in the dimensions & positioning of the bolt holes within the bracket bases. Attached is a full report from BW detailing the non conformances & why despite the non-conformances the support brackets are deemed fit for purpose.
| 03SR - Stations (RfL) | Cxxx-NCR-001749 | NCR | Expansion Switch Check Rail |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2014-04-24 | 2014-04-22 15:42 | -2 | 2014-04-10 16:59 | Civil - Track | 5000 |  | Design | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During the installation of the check rail on expansion switches 6, 7, 8 & 9, __ have had to notch out an approximate 20mm (maximum) square piece of steel iron from the check rail support bracket. This has occured to the centre support brackets on each leg of the expansion switch to facilitate the check rail check rail bracket installation over the two breather chairs. In some areas the top of the holding down bolt thread has been removed to avoid this clash. This clash was not picked up during the approval of the design and fabrication drawings.
| 03SR - Stations (RfL) | Cxxx-NCR-001750 | NCR | DLR Station TVM / E-Sub Base |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2014-04-28 | 2014-04-24 11:16 | -4 | 2014-04-10 12:47 | Civil - Civil Engineering General | 1200 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Personnel Error - Inattention to detail | Completed |  | The Combined TVM / E-sub base and cast in service pockets do not match the TVM/E-sub requirement. The 2 No eastern TVM cable pockets are 525mm too far west and the E-Sub duct ends also do not match the required location.
| 03SR - Stations (RfL) | Cxxx-NCR-001751 | NCR | Street Lighting Columns Southern Exterior of the Station |  | Crossrail | XRL | PML - Pudding Mill Lane Portal (Central) |  | 2014-06-16 | 2014-06-12 08:12 | -4 | 2014-04-15 12:38 | Electrical - Lighting | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Supervision - Insufficient supervision | Completed |  | __ have installed the incorrect heads on the 4mtr exterior lighting columns (approx NINE of to date) at the southern paved area of the station envelope
| 03SR - Stations (RfL) | Cxxx-NCR-001752 | NCR | Third Rail Anchor Installation |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2014-04-30 | 2014-04-25 15:04 | -5 | 2014-04-16 18:49 | Civil - Track | 2000 |  | Material | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During the thid rail bolt installation a number of bolts have not reached the required 20Nm torque setting. Attached to this NCR is how __s specialist sub-contractor are to overcome this issue - Document Number BW15628. A programme of works is included in this NCR.
| 03SR - Stations (RfL) | Cxxx-NCR-001753 | NCR | Incorrect Pandrol Clips at Expansion and Adjustment Switches |  | Crossrail | XRL | PML - Pudding Mill Lane Portal (Central) |  | 2014-05-06 | 2014-05-06 15:49 | 0 | 2014-04-22 18:02 | Track - Track General | 500 |  | Planning | Rework | 4 (0.5-3k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | ZLR clips (Zero Longitudinal Restraint clips), are required to be placed on the Pandrol VIPA baseplates at the free moving end of expansion switches and at both ends of adjustment switches. At the time of handing over the track to DLR (23rd April 2014), these clips had not been delivered to site and therefore were not installed as required.
| 03SR - Stations (RfL) | Cxxx-NCR-001754 | NCR | Edging Timber to Lineside Walkways |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2014-12-31 | 2014-12-19 12:08 | -12 | 2014-04-24 12:02 | Track - Walkways | 5000 |  | Incorrect Installation | Use As-Is | 3 (3-6k) | Complete | Design Problem - Other | Completed |  | Colas have inadvertently ordered the wrong grade of tanalised timber for the edging strips to the lineside walkways. Tanalising class UC2 timber, which is suitable for areas subject to occasional wetting, has been procured and installed as opposed to class UC4 which is the correct class for external use use.
| 03SR - Stations (RfL) | Cxxx-NCR-001755 | NCR | Non commissioning of BMU - PAE-102 |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2014-07-31 | 2014-07-25 13:05 | -6 | 2014-04-25 16:16 | Architectural - General | 5000 |  | Design | Rework | 3 (3-6k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | The BMU will not be commissioned for handover due to the hoist touching the glazing at the V04 North corner
| 03SR - Stations (RfL) | Cxxx-NCR-001756 | NCR | SCADA Field Wiring-Incorrect cable types |  | Crossrail | PDP | PML - Pudding Mill Lane Portal (Central) |  | 2014-07-31 | 2014-07-07 12:32 | -24 | 2014-04-25 16:20 | Communications and Control Systems - SCADA/Central Management System | 10000 |  | Incorrect Installation | Rework | 2 (6-60k) | Complete | Material/Preservation Problems - Use of unapproved materials | Completed |  | Number of cables (part of the SCADA Field Wiring) linking various services into the MDF were installed incorrectly.The cable types (shown on the attached list) were not in accordance with the SCADA Field Wiring Schedule (ref. Cxxx-MRG-R3-TSC-CR094_WS111-50045) and the Comms AfC design drawings. The MDF & SCADA Field Wiring ITP ref. Cxxx-MRG-R3-ITP-CR094_WS111-50003 places a Hold Point inspection (items 2.2 and 3.2) on both the S/C and the Contractor for the inspection of cables material delivery and installation.The defect was not identified or reported by the Contractor.
| 03SR - Stations (RfL) | Cxxx-NCR-001757 | NCR | Non approval of timber sleepers |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2014-05-13 | 2014-05-08 14:09 | -5 | 2014-04-29 15:37 | Civil - Track | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Use of unapproved materials | Completed |  | MCR Cxxx-MRG-R4-QAP-CR094_WS111-50019 for timber sleepers was not approved before the handover of the new DLR track.
| 03SR - Stations (RfL) | Cxxx-NCR-001758 | NCR | Concourse ACO drain cover levels |  | Crossrail | XRL | PML - Pudding Mill Lane Portal (Central) |  | 2014-08-29 | 2014-08-16 09:50 | -13 | 2014-05-01 16:49 | Civil - Drainage | 1500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The ACO drains in the DLR concourse which act as a rodding point for the column down pipes have been installed too low ~15mm. There has been an attempt to rasie the level by the addition of a stainless angle but this is unacceptable. This has been raised by CRL, DLR & Cxxx.
| 03SR - Stations (RfL) | Cxxx-NCR-001759 | NCR | Damage to DLR drain run DLRW 1.3 |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2014-08-29 | 2014-08-19 11:41 | -10 | 2014-05-02 15:59 | Civil - Drainage | 1500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Further to review of the CCTV survey of drain run DLRW1.3 we have indentified some damage. There is damage noted between the tank and Manhole DWS13 (the southern pipe) Please note: The CCTV was only carried out once __ had carried out the clean downstream. see attached photo.
| 03SR - Stations (RfL) | Cxxx-NCR-001760 | NCR | Damage to DLR drainage run (southside) |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2014-08-22 | 2014-08-18 09:54 | -4 | 2014-05-02 16:08 | Civil - Drainage | 2000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Further to review of the CCTV survey of drain run DLRW13.0 (south side of the DLR Station), we have identified some damage to the pipe approx 1m from the building. Please note: The CCTV was only carried out once __ had carried out the clean downstream.
| 03SR - Stations (RfL) | Cxxx-NCR-001762 | NCR | Photo Cell Wiring Associated With The Lighting Control System |  | Crossrail | XRL | PML - Pudding Mill Lane Portal (Central) |  | 2014-10-10 | 2014-09-10 17:21 | -30 | 2014-05-08 09:11 | Electrical - Lighting | 3000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | I discovered on Friday 02/05/2014 post an intrusive Inspection that __ES have wired some of the Photo Cells with the incorrect wiring and in some cases have used unspecified cables. This was known to __ES and was not shared with either CRL or the DLR. To overcome this problem they again made site changes in attempt to rectify the problem by adding additional Photocel Controllers (PC3) to try and bring down their now created resistance problem due to the incorrect wiring issue, again not discussed or agreed with CRL/DLR and not as per submitted design. The works will now require assessment to detail the extent of re-work and a report from __ES is pending
| 03SR - Stations (RfL) | Cxxx-NCR-001763 | NCR | Lighting Control System (Incorrect Functionality) |  | Crossrail | XRL | PML - Pudding Mill Lane Portal (Central) |  | 2014-10-10 | 2014-09-10 17:27 | -30 | 2014-05-08 09:26 | Electrical - Lighting | 3000 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | The Lighting Control System supplied and commissioned by __ and installed by __ES is currently not functioning correctly. The current design does not appear to work and the lighting system is switching lighting on and off intermittently, despite various setting alterations by the __ Commissioning Engineer. Factors do not appear to have been considered by the designer with locations of Photo Cell Controllers and as a for instance the lighting is currently coming on with the arrival of a train with the production of the train shadow influencing the photo cells and lighting going off upon its departure. Please note this is during daylight hours
| 03SR - Stations (RfL) | Cxxx-NCR-001764 | NCR | Unapproved Class 1A Backfill Material - RRV Ramp |  | Crossrail | XRL | PML - Pudding Mill Lane Portal (Central) |  | 2014-06-30 | 2014-06-03 10:59 | -27 | 2014-05-12 16:25 | Civil - Fill | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | Backfill material from a stockpile from Site 3 has been incorporated into the permanent works without being approved for use. The material (believed to be from Olympic Park), was transported from the stockpile and placed as a Class 1A product behind the CRL 2 retaining wall (north of the RRV ramp wall). At the time of placing this fill, there was no documentation (physical or chemical analysis) in place to suggest that it was suitable. An MCR for a similar material from the Olympic Park had been approved as Class 1A, but the grading for the stockpiled material was clearly very different. To avoid any delay to the works, Crossrail allowed the material to be left in place (at __’s risk), with the understanding that the necessary laboratory results were obtained as a matter of urgency (see email dated 2nd April 2014). Grading results were returned a week later and appeared to be compliant. However, the laboratory results of the chemical analysis have still not been received. Furthermore, __ have since stated that the required tests had not been carried out as of 9th May 2014 (over 5 weeks later).
| 03SR - Stations (RfL) | Cxxx-NCR-001765 | NCR | DLR Station Concourse - G/L 7 H/L Drainage |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2014-08-08 | 2014-08-08 10:55 | 0 | 2014-05-13 09:27 | Mechanical - Piping | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Insufficient information made available to the worker. | Completed |  | High Level Drainage requires supporting on DLR station concourse grid line 7 (north & south).
| 03SR - Stations (RfL) | Cxxx-NCR-001766 | NCR | DLR Station Emergency Lighting UPS System |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2014-08-20 | 2014-08-13 09:01 | -7 | 2014-05-13 14:10 | Electrical - Power Distribution | 2000 |  | Material | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Emergency Lighting UPS System control wiring (internal battery alarms) require re-wiring, this was identified during the SAT procedure.
| 03SR - Stations (RfL) | Cxxx-NCR-001767 | NCR | DLR Station - Installation of Luminaires |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2014-08-31 | 2014-08-14 08:52 | -17 | 2014-05-13 14:18 | Electrical - Lighting | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Some Luminaires have been omitted (not installed - Red Line drawing have reflected this).
| 03SR - Stations (RfL) | Cxxx-NCR-001768 | NCR | DLR Station - 110Volt Socket Outlet at Grid Line 1 |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2014-07-31 | 2014-08-04 11:23 | 4 | 2014-05-14 10:52 | Electrical - Power Distribution | 1000 |  | Design | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | 110Volt Sockets Outlets - required to be installed at Low Level on both platforms at Grid Line 1 (outlets currently installed above accessable ceiling panels).
| 03SR - Stations (RfL) | Cxxx-NCR-001769 | NCR | Inadequate splice length on the CRL Bridge phase 2 starter bars |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2014-07-31 | 2014-07-28 11:51 | -3 | 2014-06-02 15:27 | Civil - Civil Engineering General | 3000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | As stated in RFI 2364, the 1325mm splice length required for the phase 2 CRL bridge abutments has not been achieved in certain locations along the length of both east and west kickers. Refer to sketch attached for numbers and locations of the non conforming bars.
| 03SR - Stations (RfL) | Cxxx-NCR-001770 | NCR | DLR Retaining Wall - Security Fence Grout Strength |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2014-06-13 | 2014-06-09 16:24 | -4 | 2014-05-20 11:39 | Civil - Civil Engineering General | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Drawing Cxxx-MMD-C-EDR-CRG06-00172 revision 4 states that a thin layer of grout should be poured under the DLR Retaining Wall Security Fence posts. It is stated that the grout should have 28 day compressive strength of 50N/mm. As can be seen from the attached cube record form, sample 1151 has not reached the required strength. Sample 1151 has reached an average 28 day strength of 42.7N/mm. Results from the other batch of grout taken for the works, sample 1124 has reached a 28 day strength of 52.5N/mm and therefore satisfies the design intent.
| 03SR - Stations (RfL) | Cxxx-NCR-001771 | NCR | CRL bridge - Soffit concrete finish |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2014-06-06 | 2014-06-10 08:39 | 4 | 2014-05-20 17:40 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | After thorough making good on the phase 1 soffit the finish has not reached the F3 finish specified on drawing Cxxx-MMDC-EDR-CRG06-00108. Concrete spacer blocks are showing throughout the soffit despite bagging up. This is due to the extra weight placed on them by the additional deck reinforcement. MS raised a concern about the reinforcement congestion in RFI 2278 - to try and mitigate these issues the reinforcement was opened up in strategic locations to allow the concrete pump hose to reach through to the bottom mat, external shutter vibrators (screamers) were used during the pour and the concrete mix was altered from an S3 to an S4 to improve the flow. Despite these efforts the finish has still not reached the required F3.
| 03SR - Stations (RfL) | Cxxx-NCR-001772 | NCR | P'Way Drainage - CPE5 Outlet Stub |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2014-06-26 | 2014-06-24 14:37 | -2 | 2014-06-12 18:17 | Civil - Drainage | 3000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | With reference to P'Way drainage catchpit CPE5 on drawing Cxxx-SWN-R-DDL-CR094_PT002_Z-95621. The drawing contains a drainage plan along with an accompanying table highlighting each catchpit and manhole. The table illustrates location, levels, gradient and pipe diameter information. During construction of CPE5 __ installed the incorrect pipe diameter stub leading to CPE6 (225mm instead of 300mm). Note, CPE5 is the only catchpit called up twice at different locations on the table. The information refers to different pipe diameters, which has undoubtedly contributed to confusion when installing pipe stubs from the catchpit.
| 03SR - Stations (RfL) | Cxxx-NCR-001773 | NCR | Secant Piles - Low Piling Mat |  | Crossrail | XRL | PML - Pudding Mill Lane Portal (Central) |  | 2014-07-31 | 2014-07-08 17:59 | -23 | 2014-06-18 16:05 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Drawing No. Cxxx-SWN-S-DDD-CR094_PT002_Z-72440 rev C01 gives the pile cut off level of the secant piles as 109.500m. This is the level of the structural concrete after any potentially contaminated concrete has been broken down (a minimum of 300mm as per table B1.5 and cl. B1.10.3 of the ICE SPERW specification). The top of the as-constructed piling mat and guide walls for these works is 109.500m, lower than the min. 109.800mm required to meet the specs requirements.The contractor advised (after the issue below was raised) that the mat was placed at this level to adress the constraint of the rig drilling depth capacity. This is a process NCR.There is no Defect as the issue was identified and resolved (refer to Corrective Actions section) before the instalaltion of the Permanent Works.An advanced copy of the pile cage fabrication drawing (produced after the piling mat and guide wall were installed) confirms that that the top of steell cages is still ay +109.500 hence no allowance has been made for the contaminated concrete to be removed. No FCD or other forms of formal/informal communication was raised requesting a deviation from the design before the mat was installed. Therefore, the installed temporary works was not adequate for the Permanent Works.
| 03SR - Stations (RfL) | Cxxx-NCR-001775 | NCR | Four Span & CRL1 Base Slab Piling - Use of unapproved mix design |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2014-07-09 | 2014-07-11 13:03 | 2 | 2014-06-25 14:11 | Civil - Civil Engineering General | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Supervision - Insufficient supervision | Completed |  | During CFA piling operations on the CRL1 base slab and Pier 1 of the Four Span Underpass it was found that the mix being used was not approved under the Crossrail material approval process. A total of 24No piles were completed with the unapproved mixed. CRL1: PR90,93,97,101,105,109,117,118, 94,102,110,113,123,124,125. Four Span Underpass: P01Y,W,U,S,L,Z,K,I,G.
| 03SR - Stations (RfL) | Cxxx-NCR-001777 | NCR | Secant Piling |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2015-01-30 | 2015-01-28 15:51 | -2 | 2014-07-08 13:52 | Civil - Geotechnical Engineering | 500 |  | Incomplete Works | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Male Secant Pile Number P09 could not be plunged to its full depth. The cage was vibrated down to a depth of 94.3mATD before refusal. It was not possible to retract the pile cage. The pile was concreted to its full depth of 20.5m with a toe level of 89.0mATD. The steel reinforcement (5m) has been cut at PPL level.
| 03SR - Stations (RfL) | Cxxx-NCR-001778 | NCR | P18 female pile cage out of tolerance |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2014-07-30 | 2014-07-29 17:11 | -1 | 2014-07-16 12:00 | Civil - Geotechnical Engineering | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Female pile P18 is out of tolerance by 23mm. The cage was installed 73mm low at a level of 109.127mATD. The prescribed top of cage level is 109.200mATD
| 03SR - Stations (RfL) | Cxxx-NCR-001779 | NCR | Removal of Base slab and Roof slab coupler shear key box-outs from secant pile cages |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2014-07-24 | 2014-07-21 13:37 | -3 | 2014-07-10 17:20 | Civil - Geotechnical Engineering | 15000 |  | Incomplete Works | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Due to unforeseen conditions the secant pile shear key coupler box outs for the cut and cover base and roof slabs have been reduced in diameter/size in 3no piles and removed completely in a further 5no pile cages. This was done as the subcontractor was unable to plunge the cages to the prescribed depth/level due to the conditions, using the self-weight of the cage. The box-outs were examined closely to ensure they were the correct diameter and size before any piles were driven into the ground and therefore not causing the cage to become wedged against the side of the bore. The cages refused plunging through the concrete beyond the base slab box-out level, and were then vibrated down using the cage vibrator. Once the cage reached the roof slab box-out, the cage almost refused getting down to depth. With some considerable vibration time and force was applied, the cages were plunged to the correct depth. It was then trialled to reduce the diameter/size of the box-out, which still did not prove workable. Lastly we trialled the cages without the box-out – significantly wrapping the couplers in denzo tape, which is proving to be more successful than the other two trials in installation. This NCR covers the removal of the shear key box-outs from the secant piles wall base and roof slab connection detail, Piles-to-date; P08, 12, 16, 20 - With Full Design Box-out P10, 14, 17 - With Reduced Diameter Box-out (Diameter reduced on site) P06, P15, P18, P19 - Without Box-out) Please refer to FCD 1778 to eliminate the use of the shear key box-outs
| 03SR - Stations (RfL) | Cxxx-NCR-001780 | NCR | Station drainage pipe DLRW1.5 laid 30mm high at MH DWS17 |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2014-07-24 | 2014-07-15 13:24 | -9 | 2014-07-10 13:44 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Drain run DLRW1.5 has been constructed 30mm too high at the MH DWS17. With the Attenuation tank to the service yard now in place this creates a small backfall between the Attenuation and DES17.
| 03SR - Stations (RfL) | Cxxx-NCR-001781 | NCR | 4 Span Underpass - Obstruction encountered whilst undertaking P03K (1050 dia pile) |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2014-08-29 | 2014-08-26 11:00 | -3 | 2014-07-11 15:36 | Civil - Civil Engineering General | 10000 |  | Incomplete Works | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Obstruction encountered whilst undertaking P03K (1050dia) at approximately 80.000m. Piling rig attempted to auger through obstruction numerous times but to no avail. Pile concreted at 80.000m - 6m above that of design toe level (74.000m). P03J and P03L (also 1050dia) completed with design toe level achieved.
| 03SR - Stations (RfL) | Cxxx-NCR-001782 | NCR | CMR - Position range couplers in the CRL base slab finger pour 3 |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2014-07-30 | 2014-07-31 12:20 | 1 | 2014-07-16 14:49 | Civil - Civil Engineering General | 1000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Further to RFI 2291, the 2nd pour of the CRL bridge base underpinning works included the provision of position range couplers. The couplers were to allow for the "L" bars in the 3rd pour to be installed and torqued. The male section of the couplers was not removed from the female prior to pouring the concrete for the 2nd finger of the underpinning. The male section of coupler was therefore cast in to the pour. This resulted in it being impossible to screw the "L" bars that made up the side of the 3rd pour into the 2nd pour couplers.
| 03SR - Stations (RfL) | Cxxx-NCR-001783 | NCR | CMR CRL - East Abutment Phase 1 Cantilever BM33 |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2014-07-31 | 2014-07-30 16:26 | -1 | 2014-07-17 08:53 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Repair | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Referring to drawing Cxxx-MMD-C-EDR-CRG06-00120, 1no. BM33 in the near face of the CMR CRL Bridge east abutment was not installed prior to the phase 1b concrete pour. The attached photograph shows the location of the omitted bar. The 20mm vertical bar was not installed during the fix of the near face of steel, as access was required in to the abutment to pour concrete. It was intended that the bar was installed immediately prior to the concrete pour when no further access was required. This was not completed.
| 03SR - Stations (RfL) | Cxxx-NCR-001784 | NCR | CMR CRL Bridge - Cranked Reinforcment Starter Bar |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2014-08-29 | 2014-08-15 14:12 | -14 | 2014-07-17 15:36 | Civil - Civil Engineering General | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During the concrete pour for the CMR Crossrail Bridge phase 1B west abutment, a B16 starter bar in the T5 mat of the deck steel was cranked at the phase 1 construction joint to allow the concrete pump boom to be lowered in to the pour. The BM152, detailed on drawing Cxxx-MMD-C-DDJ-CRG06-50005 was bent to approximately 45 degrees as shown on the attached photograph.
| 03SR - Stations (RfL) | Cxxx-NCR-001785 | NCR | DLR removable bollard (small peice of wood has come off) |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2014-11-14 | 2014-11-07 16:03 | -7 | 2014-07-18 08:29 | Civil - Civil Engineering General | 2000 |  | Material | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | 1 No removable DLR concourse bollard (4th from the west side) has shed a small section of wood from the corner during the bedding in process (crazing). The supplier "Woodscape" has confirmed this can sometimes happen. Bollards as detailed on Drw: DDD-96144.
| 03SR - Stations (RfL) | Cxxx-NCR-001786 | NCR | Unapproved Sand Backfill Material |  | Crossrail | XRL | PML - Pudding Mill Lane Portal (Central) |  | 2014-08-04 | 2014-07-30 10:13 | -5 | 2014-07-21 11:20 | Civil - Fill | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Sand backfill material was used during the installtion of the attenuation tanks. No approval was sought for use of the material at the time of use (the tanks were installed between June 2013 and March 2014). An MCR for the matrial was submitted in July 2014 (MCR 50312).
| 03SR - Stations (RfL) | Cxxx-NCR-001787 | NCR | Secant wall pile cages - couplers wrong levels |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2014-08-05 | 2014-07-31 10:41 | -5 | 2014-07-22 10:04 | Civil - Civil Engineering General | 2000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Secant pile cages No’s 4, 23 & 40 have all been delivered to site with the couplers set to incorrect levels ranging between 190mm and 380mm wrong. These errors were picked up via the cage delivery inspections.
| 03SR - Stations (RfL) | Cxxx-NCR-001788 | NCR | Structural Expansion Switch |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2015-06-15 | 2015-06-09 12:16 | -6 | 2014-07-28 10:39 | Civil - Track | 75000 |  | Incorrect Installation | Rework | 1 (>60k) | Complete | Design Problem - Not Defined | Completed |  | The four number structural expansion switches at either end of the new DLR station structure were installed without construction baseplate pads (drawing ref: __-190-12339).
| 03SR - Stations (RfL) | Cxxx-NCR-001789 | NCR | Secant wall pile No 5 - Failure to produce full pile log data from the rig |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2014-08-11 | 2014-08-04 16:41 | -7 | 2014-07-28 10:00 | Civil - Civil Engineering General | 500 |  | Software | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The rig operator accidently did not activate the rig data recording computer for Secant pile No 5. This has resulted in limited pile log date for this pile.
| 03SR - Stations (RfL) | Cxxx-NCR-001790 | NCR | Records |  | Crossrail | XRL | PML - Pudding Mill Lane Portal (Central) |  | 2014-08-11 | 2014-08-11 12:46 | 0 | 2014-07-28 13:33 | Geotechnical Engineering - Concrete - Bored Pile | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Verification Problems - Not Defined | Completed |  | During a planned CRL surveillance, a review of the secant piling records found section 5 CSP/female piles it was found that only concrete delivery tickets and reinforcement check sheet for piles 8, 10(type P3),12 and 20 were in the file. The __ pile auguring-pile records / __ instrumentation print outs and the placement of concrete /concrete check sheets were missing
| 03SR - Stations (RfL) | Cxxx-NCR-001793 | NCR | CMR Crossrail Bridge - West Abutment Phase 1B Low Cover To Reinforcement |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2014-10-31 | 2014-10-29 18:12 | -2 | 2014-08-13 18:14 | Civil - Civil Engineering General | 2000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | In reference to notes drawing Cxxx-MMD-C-EDR-CRG06-00070 Rev 8.0, the specified cover to reinforcement for the CMR Crossrail Bridge abutments is 55mm ± 15mm fixing tolerance. The attached cover meter survey shows that the minimum allowable cover of 40mm has not been achieved on a section of the west abutment near face adjacent to the drainage recess (see photograph 1). In the worst location, the cover to the reinforcement is 15mm. Drawing Cxxx-MMD-C-EDR-CRG06-00130 details the reinforcement in this phase of the abutment. The cover has been taken to the lacing reinforcement, BM9 and BM10, which are on the outer face of the vertical bars.
| 03SR - Stations (RfL) | Cxxx-NCR-001795 | NCR | Secant wall pile 8 - Failure to capture pile log data via rig computer |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2014-08-12 | 2014-08-04 16:45 | -8 | 2014-07-29 16:19 | Civil - Civil Engineering General | 500 |  | Software | Use As-Is | 4 (0.5-3k) | Complete | External Phenomenon - Power failure or transient | Completed |  | The rigs computer crashed during P8, resulting in limited rig data being captured by the rigs computer.
| 03SR - Stations (RfL) | Cxxx-NCR-001796 | NCR | CRL Bridge - West Abutment Alignment |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2014-09-26 | 2014-09-15 16:23 | -11 | 2014-08-29 12:21 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The north end of the raised section of kicker on the west abutment has been cast outside of its positional tolerance. It is 29mm west of its design alignment and takes 1.5M to taper back in to tolerance as you come further south (see sketch for clarity).
| 03SR - Stations (RfL) | Cxxx-NCR-001797 | NCR | Secant Pile No P64 5mm out of tollerance |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2014-08-14 | 2014-08-04 16:43 | -10 | 2014-07-31 14:41 | Civil - Geotechnical Engineering | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Supervision - Not Defined | Completed |  | Pile P64 is out of tolerance by 5mm. The cage was installed 55mm low at a level of 109.145mATD. The prescribed top of cage level is 109.200mATD
| 03SR - Stations (RfL) | Cxxx-NCR-001798 | NCR | CRL 1 - Pile 118 LUTZ Record |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2014-12-23 | 2014-12-11 11:50 | -12 | 2014-08-05 15:13 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Whist concreting pile PR118 for the CRL 1 Pile Cap the depth gauge cable snapped on the piling rig. Due to this the LUTZ report for this pile is missing information above 18.5m depth. See attached LUTZ and Concrete pumping records.
| 03SR - Stations (RfL) | Cxxx-NCR-001800 | NCR | Secant wall P70 cage couplers too low |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2015-10-16 | 2015-10-10 08:23 | -6 | 2014-08-08 09:13 | Civil - Civil Engineering General | 3000 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The cage to Female pile No 70 has been plunged 46mm below coupler tolerance.
| 03SR - Stations (RfL) | Cxxx-NCR-001801 | NCR | CMR Crossrail Bridge Phase 2 West Abutment - Aborted Concrete Pour |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2014-10-10 | 2014-09-29 18:36 | -11 | 2014-08-11 16:24 | Civil - Civil Engineering General | 10000 |  | Material | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | __ aborted the CMR Crossrail Bridge Phase 2 west abutment concrete pour after discharging one load, approximately 6m of concrete. The pour, carried out on 08/08/14, was aborted due to the discharged concrete not being workable at the time of the second load being ready to discharge, approximately 25 minutes after the completion of the first load. The concrete had cured to a state that an emergency wash-out of the pump was required to prevent blockage and the vibrating pokers were not able to fully penetrate the poured concrete. Due to the industry shortage of PFA, a CEMII B-V mix has been approved for the C35/45A CMR abutment concrete. The approved mix is an S4 consistency due to the high cement content of the concrete. The initial load arriving on site during the 08/08/14 concrete pour, stated an S3 consistency on the ticket. This load was rejected and not discharged on site. The second load arriving on site, although had the correct consistency stated on the ticket, was not within tolerance when slump tested. This load was rejected from site. The third load had the correct S4 consistency stated on the ticket and the consistency was within specification so the pour commenced. After completing the discharge of the load, it was identified that the concrete was becoming unworkable despite the ticket stating it had only been batched 42minutes before finishing the discharge. The next concrete load arrived on site 18 minutes after the completion of the previous discharge. At this point the poured concrete was assessed and a decision made that a cold joint would be formed if the pour continued. The pour was aborted at this point. The pour record sheets are attached for information and photographs to show the current condition of the abutment.
| 03SR - Stations (RfL) | Cxxx-NCR-001802 | NCR | Secant wall pile No 198 cage too low |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2015-11-27 | 2015-11-04 11:37 | -23 | 2014-08-14 08:15 | Civil - Civil Engineering General | 2000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | When plunging the last 2m of female Secant pile cage 206, when the machine pushed it down, it plunged too low. The crane was unable to hook back on and the cage remains 194mm too low.
| 03SR - Stations (RfL) | Cxxx-NCR-001803 | NCR | Secant wall piles P11, P35 & P47 (with inclinometers) |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2014-09-12 | 2014-09-12 11:13 | 0 | 2014-08-14 08:23 | Civil - Civil Engineering General | 1000 |  | Incomplete Works | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | In order to plunge the cages for male Secant piles P11, P35 & P47, the inclinometer tubes were cut down to 50mm below the top of cage and plated over.
| 03SR - Stations (RfL) | Cxxx-NCR-001804 | NCR | Secant pile 198 cage too low |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2015-12-30 | 2015-11-05 20:18 | -55 | 2014-08-14 10:41 | Civil - Civil Engineering General | 2000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | When vibrating down Secant pile female cage 198 the cage settled 129mm too low.
| 03SR - Stations (RfL) | Cxxx-NCR-001805 | NCR | Secant pile cage 204 too low |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2015-11-27 | 2015-11-11 15:53 | -16 | 2014-08-15 15:38 | Civil - Civil Engineering General | 2000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | When plunging the last 2m of female Secant pile cage 204, when the machine pushed it down, it plunged too low. The crane was unable to hook back on and the cage remains 244mm too low.
| 03SR - Stations (RfL) | Cxxx-NCR-001806 | NCR | SU Wall - Lack of Cover to Piles |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2014-08-28 | 2014-09-01 13:49 | 4 | 2014-08-21 10:39 | Civil - Civil Engineering General | 1000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Discrete pile 508 has 35mm cover to one side as the cage is not central to the pile. Pile 514 has 65mm cover. Minimum cover to these piles should be 80mm.
| 03SR - Stations (RfL) | Cxxx-NCR-001807 | NCR | SU Wall – Clash with Pile Cap |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2014-09-12 | 2014-09-12 11:16 | 0 | 2014-08-21 11:56 | Civil - Civil Engineering General | 5000 |  | Incorrect Installation | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Having excavated discrete piles 500 and 501 it is apparent that they have been displaced 115mm north and 40mm east as CRL1 pile cap (which was not visible during piling) has forced the auger in this direction. Having reviewed the CRL1 drawings and PTR’s, it would appear that the CRL1 Pile cap is required to have a 250mm step to receive the wider pile cap for the discrete piles. The requirement was missed and the step was not constructed. The piles have now been broken down but are hard against the CRL1 pile cap.
| 03SR - Stations (RfL) | Cxxx-NCR-001808 | NCR | Four Span Underpass - pile reinforcement de-bonding foam beneath cut off level |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2014-10-26 | 2014-10-01 09:06 | -25 | 2014-08-27 15:49 | Civil - Civil Engineering General | 5000 |  | Incorrect Installation | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Other | Completed |  | During cropping of piles in the Pier 5 pile cap 10No piles were found to contain de-bonding foam beneath the design cut-off level. The piles affected were the 10 most southern piles installed pre-switchover of the DLR tracks (P05E-I & P05N-R) in phase 1 of the piling works.
| 03SR - Stations (RfL) | Cxxx-NCR-001809 | NCR | Secant wall - P205 - failure to record pile log data |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2014-09-11 | 2014-09-09 09:43 | -2 | 2014-08-28 08:47 | Civil - Civil Engineering General | 500 |  | Equipment Breakdown | Use As-Is | 4 (0.5-3k) | Complete | External Phenomenon - Other | Completed |  | During drilling of pile P205 the rig suffered a hydraulic hose burst resulting in the rig needing to be shut off to facilitate repair. This has prevented the full collection of pile log data via the rigs computer.
| 03SR - Stations (RfL) | Cxxx-NCR-001810 | NCR | DLR station paving to south side slot drain |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2016-12-31 | 2016-12-14 09:34 | -17 | 2014-08-28 09:43 | Civil - Civil Engineering General | 10000 |  | Workmanship | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | For the paved area south of the DLR station (typically against the slot drain) the paving slabs immediately against the slot drain have suffered some rotation / differential settlement. Actual cause of settlement is not currently known and maybe related to design not allowing the water to escape, excess water in bedding sand and adverse weather during installation.
| 03SR - Stations (RfL) | Cxxx-NCR-001811 | NCR | Secant wall - P188 cage too low |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2015-11-27 | 2015-11-11 16:00 | -16 | 2014-08-28 13:39 | Civil - Civil Engineering General | 5000 |  | Workmanship | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During cage vibration of P188 the cage suddenly self-plunged the last meter or so and is now 269mm too low. It could not be lifted with the crane.
| 03SR - Stations (RfL) | Cxxx-NCR-001812 | NCR | Four Span Underpass – Piles in Pier 5 installed outside of positional tolerance |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2014-09-17 | 2014-09-12 15:57 | -5 | 2014-09-03 10:35 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Piles P05A, P05E, P05O, P05H, P05I in pile cap 5 of the Four Span Underpass have been installed outside of the positional tolerance of +/-75mm. See attached As-Built drawing for confirmation.
| 03SR - Stations (RfL) | Cxxx-NCR-001813 | NCR | SU Wall – Pile P504 Out of Tolerance |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2014-09-29 | 2014-09-25 16:13 | -4 | 2014-09-01 12:36 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Please see the attached as-built survey. Pile P504 is 121mm out of position and is 55mm from the tunnel face of the pile cap. Piling positional tolerances are +/-75mm.
| 03SR - Stations (RfL) | Cxxx-NCR-001814 | NCR | SU Wall – Pile P515 Out of Tolerance |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2014-09-29 | 2014-09-11 08:51 | -18 | 2014-09-01 12:39 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Please see the attached as-built survey. Pile P515 is 147mm out of position and is 44mm from the soil face of the pile cap. Piling positional tolerances are +/-75mm.
| 03SR - Stations (RfL) | Cxxx-NCR-001815 | NCR | Delays to Secant Pile Concrete |  | Crossrail | XRL | PML - Pudding Mill Lane Portal (Central) |  | 2014-10-31 | 2014-11-04 16:07 | 4 | 2014-09-10 10:57 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | The QA records for the secant pile installation show that concrete is being brought to site and kept in the agitator for extended periods of time. In some cases the concrete is not being placed for up to 4 hours after being batched. The approved ITP for these works state that concrete will be used within 2 hours of being batched.
| 03SR - Stations (RfL) | Cxxx-NCR-001816 | NCR | Blow-out of 4 Span Underpass pile P02R |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2014-10-17 | 2014-10-10 02:17 | -7 | 2014-09-08 08:34 | Civil - Civil Engineering General | 15000 |  | Damaged | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Following the excavation of 4SU Pier 2 to blinding level, it would seem that there has been a blow-out of pile P02R. With no discrepancies found on the LUTZ report, it would suggest that the blow-out was caused by a localised soft spot at a depth of 3.5m on the south eastern side of the pile. The defect is a result of the high density concrete blowing through and displacing the localised low density soft material. It is thought having plunged the cage increasing the pressure within the bore, that the concrete was displaced outwards. The displaced soft material has then found its way back into the void left by the concrete resulting in the pile core being compromised.
| 03SR - Stations (RfL) | Cxxx-NCR-001817 | NCR | 4SU GL5 Pile Cap BM132&BM147 Fabrication Error |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2014-10-17 | 2014-10-13 13:12 | -4 | 2014-09-12 17:01 | Civil - Civil Engineering General | 1000 |  | Manufacturing Defect | Reject | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | BM132 and BM147 on the reinforcement drawing for Pile Cap #5 have been delivered to site as the wrong shape code – Shape Code 00 rather than Shape Code 11.
| 03SR - Stations (RfL) | Cxxx-NCR-001818 | NCR | Pier 2 - Pile P02F blow out |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2014-10-15 | 2014-10-14 08:21 | -1 | 2014-09-16 16:19 | Civil - Civil Engineering General | 15000 |  | Workmanship | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Following the excavation of 4SU Pier 2 to blinding level, it would seem that there has been a blow-out of pile P02F. With no discrepancies found on the LUTZ report, it would suggest that the blow-out was caused by a localised soft spot at a depth of 3.5m on the South Eastern side of the pile. The defect is a result of the high density concrete blowing through and displacing the localised low density soft material surrounding it. It is thought having plunged the cage increasing the pressure within the bore, that the concrete was displaced outwards. The displaced soft material has then found its way back into the void left by the concrete resulting in the pile core being compromised.
| 03SR - Stations (RfL) | Cxxx-NCR-001819 | NCR | CRL 1 Base Slab Patch Repair |  | Contr | TWC | PML - Pudding Mill Lane Portal (Central) |  | 2014-10-01 | 2014-10-08 12:14 | 7 | 2014-09-17 13:41 | Civil - Civil Engineering General | 2000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The CRL 1 base slab was previously poured 300 mm too wide, for a 5m section at the Eastern end of Upstand Wall 1.1. As a result, the pile capping beam for the Upstand Wall 1.2 has insufficient room to be cast against the adjacent pile cap. To remove the superfluous concrete slab section, wire sawing was undertaken. In an effort to miss the reinforcement when cutting, a section of the base slab was broken back to expose the reinforcement locations. However, excess concrete was removed during this investigative works, and this needs to be ameliorated prior to the casting of the pile cap beam alongside.
| 03SR - Stations (RfL) | Cxxx-NCR-001820 | NCR | CRL NOS west abutment - Out of tolerance piles |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2014-11-07 | 2014-11-03 16:40 | -4 | 2014-09-25 10:31 | Civil - Civil Engineering General | 5000 |  | Incorrect Installation | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | As-builts of 4No CRL NOS west abutment piles (P2, P5, P12 & P17) show that the piles exceed the +/- 75mm positional tolerance stated under the 'ICE specification for piling and embedded retaining walls'.
| 03SR - Stations (RfL) | Cxxx-NCR-001821 | NCR | Track Support Slab - Pile PR333 |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2014-10-24 | 2014-10-30 12:21 | 6 | 2014-09-24 16:14 | Civil - Civil Engineering General | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The 28 day strength results for cube references 7857 and 7859 have failed to meet the individual strength requirements for a C32/40 mix of 36N/mm². The cubes relate to concrete placed in TSS pile PR333. Cube reference 7857 achieved 32N/mm² whilst cube reference 7859 achieved 34.5N/mm² at 28 days. 56 day results have achieved 36N/mm² and 40N/mm² respectively, which are compliant with the minimum strength requirements for a 40N mix. It is difficult to say why the failures have occurred, the attached autographic records from the batching plant show that the load has been batched within tolerances and in accordance with the mix design. The statistical analysis of the mix strengths is compliant and there are no signs of a downward trend. The densities of both sets of cubes are low which would indicate poor cube manufacture. __ propose to ‘leave as is’ as the concrete has achieved strength requirements prior to the piles being loaded. The concrete mix contains a high proportion of GGBS which results in a slower rate of strength gain. The concrete will continue to gain strength upwards of 90 days and will be in excess of 40N prior to loading.
| 03SR - Stations (RfL) | Cxxx-NCR-001822 | NCR | Secant wall Pile 231 |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2014-10-09 | 2014-10-08 10:39 | -1 | 2014-09-25 08:20 | Civil - Civil Engineering General | 500 |  | Equipment Breakdown | Use As-Is | 4 (0.5-3k) | Complete | Verification Problems - Other | Completed |  | During concreting of Secant Pile 231 the rig data computer crashed and had to be restarted loosing the last 9m of data.
| 03SR - Stations (RfL) | Cxxx-NCR-001823 | NCR | Secant Pile Concrete Delivery Tickets |  | Crossrail | XRL | PML - Pudding Mill Lane Portal (Central) |  | 2014-10-09 | 2014-10-07 16:13 | -2 | 2014-09-25 16:06 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Lack or improper material identification and traceability | Completed |  | There have been many instances of the secant pile concrete being delivered to site without the batching time being displayed on the delivery ticket. At the least, this has occurred every day of piling since 26th August to 22nd September (5 consecutive weeks). This, together with the concrete being held for several hours on site (NCR 1815), does not give much assurance of the concrete’s usability.
| 03SR - Stations (RfL) | Cxxx-NCR-001825 | NCR | CRL 1 wall CJ cracks |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2015-01-30 | 2015-01-29 11:11 | -1 | 2014-09-29 08:14 | Civil - Civil Engineering General | 5000 |  | Workmanship | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | 3 No CJ’s to the top of CRL 1 wall have been identified as potentially cracked. See attached sketch for locations.
| 03SR - Stations (RfL) | Cxxx-NCR-001826 | NCR | Secant Pile not bored to depth (P251) |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2014-10-24 | 2014-10-30 13:35 | 6 | 2014-10-03 16:53 | Civil - Geotechnical Engineering | 500 |  | Incomplete Works | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Secant Pile Number 251 could not be bored to full depth. The casing met refusal at 20.1m, however the auger was able to continue boring a further 300mm. The top of the pile cage was levelled at 109.419mATD, therefore we suspect the cage may be settled on the ground.
| 03SR - Stations (RfL) | Cxxx-NCR-001827 | NCR | CRL MGL - Pile reinforcement de-bonding foam beneath cut off level |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2014-10-30 | 2014-10-17 15:55 | -13 | 2014-10-16 13:04 | Civil - Civil Engineering General | 2000 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | With reference to PTR 1787, pile reinforcement debonding foam beneath cut off level has been encountered. The piles concerned are those installed pre DLR switchover (12No).
| 03SR - Stations (RfL) | Cxxx-NCR-001828 | NCR | RRV Ramp QA Documents |  | Crossrail | XRL | PML - Pudding Mill Lane Portal (Central) |  | 2014-10-20 | 2014-10-17 16:43 | -3 | 2014-10-06 17:00 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Repair | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | During a review of the documentation for the RRV ramp, it is apparent that QA documents have not been produced contemporaneously. There appears to be no pre-pour or post pour sheets for walls B, C, D or the NR gantry. __ were unable to explain if the records existed when asked. These works were carried out in February and March 2014 (9 months ago).
| 03SR - Stations (RfL) | Cxxx-NCR-001829 | NCR | Four Span Underpass - Pier 2 - Low Cover to pile cage reinforcement |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2014-10-22 | 2014-10-21 14:08 | -1 | 2014-10-08 17:36 | Civil - Civil Engineering General | 2000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During cropping of piles in Pier 2, 3No piles (P02EE, P02G & P02O) – see attached survey of cover to reinforcement) were found to have low cover the outside face of the pile cage reinforcement. Design requires 90mm but a minimum cover of 75mm will be accepted.
| 03SR - Stations (RfL) | Cxxx-NCR-001830 | NCR | Secant wall - P70 low cube strength |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2014-10-30 | 2014-10-30 12:36 | 0 | 2014-10-09 15:04 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Not Defined | Completed |  | The 28 day strengths for Cube references 7993 have failed to meet the individual strength requirements for a C35/40 mix of 36N/mm2. The cubes relate to concrete placed in pile number P70 Reference 7993 achieved 34.1N/mm2 at 28 days. 56 day cube has been crushed for this sample and has achieved 38.3N/mm2. The 56 day result is compliant with the minimum strength requirements for a 40N mix. It is difficult to say why the failures have occurred, the autographic records from the batching plant show the load has been batched within tolerances and in accordance with the mix design. The statistical analysis of the mix strengths is compliant and there are no signs of a downward trend. The densities of the set of cubes are low which would indicate poor cube manufacture.
| 03SR - Stations (RfL) | Cxxx-NCR-001831 | NCR | Secant wall pile 160 - couplers too low |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2015-10-30 | 2015-10-27 10:06 | -3 | 2014-10-09 15:11 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Pile 160 cage was accidently installed despite __ pointing out that the cage couplers were 180mm out (too high). Cage was checked by __ the day before and the defect relayed to __. __ then subsequently arranged for it to be collected. However, due to miss-communication within __, Pile 160 was piled and the cage used.
| 03SR - Stations (RfL) | Cxxx-NCR-001832 | NCR | Four Span Underpass - Pier Kicker F3 finish not achieved |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2014-11-05 | 2014-11-03 11:29 | -2 | 2014-10-22 07:54 | Civil - Civil Engineering General | 750 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Upon striking the pier kicker shutter the specified F3 finish face was found to have localised areas of honeycombing and entrained air bubbles.
| 03SR - Stations (RfL) | Cxxx-NCR-001833 | NCR | CRL NOS West Abutment - Low Pile Reinforcement |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2014-11-07 | 2014-10-29 11:37 | -9 | 2014-10-21 14:44 | Civil - Civil Engineering General | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | In reference to drawing Cxxx-SWN-S-DDD-CR094_PT002_1-41431, the pile reinforcement is shown at a level of 107.325. After uncovering the piles, it has been identified that a number of piles have been tracked over by the rig causing the reinforcement to be bent. The bent reinforcement bars have been cut down resulting in some of the pile reinforcement being lower than designed. The attached sketch details the number of bars lower than the 107.325 on each pile and the worst case level for each pile. The piles have all passed an integrity test.
| 03SR - Stations (RfL) | Cxxx-NCR-001834 | NCR | CRL MGL - Out of tolerance piles |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2014-11-03 | 2014-10-29 16:07 | -5 | 2014-10-20 17:16 | Civil - Civil Engineering General | 1500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | As-builts of 5No CRL MGL east abutment piles (P2, P3, P4 P11 & P18) show that the piles exceed the +/- 75mm positional tolerance stated under the 'ICE specification for piling and embedded retaining walls'. Following discussions with __ (URS) only P2 & P4 are a concern, having moved further towards the face of the pile cap (refer to the attached)
| 03SR - Stations (RfL) | Cxxx-NCR-001835 | NCR | Use of Type C bars in lieu of Type B prior to FCD in place |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2014-11-05 | 2014-10-22 17:37 | -14 | 2014-10-22 13:52 | Civil - Civil Engineering General | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Specification E – Cxxx-SWN-S-RSP-CR094_PT002-00002_Rev5 - Clause E30.150 specifically states that reinforcement used must be strength grade ‘B500B’. On areas of the Four Span Underpass, Marshgate Lane Abutment and NOS CRL Abutment Type C reinforcement has been fixed.
| 03SR - Stations (RfL) | Cxxx-NCR-001836 | NCR | SUW 1.2 - U-Bars with couplers bent incorrectly |  | Contr | TWC | PML - Pudding Mill Lane Portal (Central) |  | 2015-01-22 | 2014-12-08 08:23 | -45 | 2014-11-27 10:03 | Civil - Civil Engineering General | 500 |  | Manufacturing Defect | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Drawing Cxxx-SWN-S-DDD-CR094_PT002_Z-60404 and schedule Cxxx-SWN-S-DDJ-CR094_PT002_Z-60404 show U - Bars (BM 159 and BM 170) with couplers to be installed in the South Upstand Wall 1.2 to provide a connection to the steel in the base & roof slab. After several checks on the schedule and what has been delivered to site, we believe the steel has been bent and supplied incorrectly by MPB’s supplier (Thames Reinforcement). As a result, leg lengths are different and coupler faces do not line up, meaning there will be differing amounts of cover to the coupler face when concrete is poured, requiring additional scabbling works to establish the shear key. In some instances in the roof slab, the top coupler protrudes past the vertical steel by 30mm, whereas the bottom coupler face is behind the vertical steel, which is different to that designed on drawing No. Cxxx-SWN-S-DDD-CR094_PT002_Z-71321 and deemed unacceptable by Cxxx.
| 03SR - Stations (RfL) | Cxxx-NCR-001837 | NCR | Secant pile 138 - cage did not fully plunge |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2015-06-26 | 2014-11-26 15:13 | -212 | 2014-10-24 12:43 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Female pile 138 cage was inserted to a depth of 15.325m where it met refusal with the vibrator and the cage could not be removed. The top 5m of the cage has been cut off.
| 03SR - Stations (RfL) | Cxxx-NCR-001838 | NCR | Secant piles installed to unapproved revison of fab drawings |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2014-11-07 | 2014-11-03 16:09 | -4 | 2014-10-24 14:03 | Civil - Civil Engineering General | 5000 |  | Documentation and Records | Use As-Is | 3 (3-6k) | Complete | Management Problem - Other management problem | Completed |  | Secant pile cage fab drawings 50120 & 50122 for pile types 5 & 6 are currently code 3 with very basic comments. The comments have been addressed some 2 weeks ago in a further revision and have been issued informally to URS. We are unable to formally issue the revised drawings as we are still waiting for the decal sheet to be returned despite repeated requests. Technically, piles are now being installed without formal approval of these fab drawings. Note: all piles are being installed to the drawings awaiting to be formally issued. An EWN was raised relating to this.
| 03SR - Stations (RfL) | Cxxx-NCR-001840 | NCR | Secant pile cage 281 fabricated with couplers wrong |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2015-12-04 | 2015-11-11 16:09 | -23 | 2014-10-30 14:10 | Civil - Civil Engineering General | 2000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Secant pile male cage 281 has been fabricated with the couplers 170mm too high.
| 03SR - Stations (RfL) | Cxxx-NCR-001841 | NCR | 4SU - Pile P03A reinforcement cage installed 300mm high |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2014-11-28 | 2014-11-04 08:30 | -24 | 2014-10-31 12:04 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | P03A was undertaken/ completed with design toe level achieved (87.000m). Following boring of the pile, the reinforcement cage was installed 300mm high (refer to the attached).
| 03SR - Stations (RfL) | Cxxx-NCR-001842 | NCR | SUW 1.2 - Honeycombing on Panel 3 |  | Contr | TWC | PML - Pudding Mill Lane Portal (Central) |  | 2015-02-28 | 2015-02-28 08:23 | 0 | 2014-11-06 10:00 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | South Upstand Wall 1.2, Panel 3, has patches of honey combed concrete on both the North and South faces, as shown in the pictures attached. During the course of the concrete pour, one number load of concrete was rejected due to exceeding slump, which lead to more than 30min delay between loads & may have contributed to the issue.
| 03SR - Stations (RfL) | Cxxx-NCR-001843 | NCR | Four Span Underpass - Pier 3 Pile P03A - Low Reinforcement Cover |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2014-11-24 | 2014-11-17 14:11 | -7 | 2014-11-10 15:38 | Civil - Civil Engineering General | 1000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Pile PO3A in Pier 3 of the Four Span Underpass has low concrete cover to pile cage reinforcement in an isolated area.
| 03SR - Stations (RfL) | Cxxx-NCR-001845 | NCR | Secant wall pile P83 - cage delivered without inclinometer tube |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2014-11-27 | 2014-11-26 10:03 | -1 | 2014-11-13 08:55 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Cage P83 was delivered to site without the inclinometer tube.
| 03SR - Stations (RfL) | Cxxx-NCR-001846 | NCR | CRL CMR Deck - Misalignment of Eastern Face of Deck and Corbel |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2014-11-26 | 2014-11-17 13:10 | -9 | 2014-11-14 18:36 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | In reference to the CMR Deck setting out point drawing Cxxx-MMD-C-EDR-CRG06-00097. The setting out points 'K' and 'Y' detailing the break point in the eastern face and corbel have been incorrectly set out. The location of the break point is located 200mm too far north as detailed in the attached sketches.
| 03SR - Stations (RfL) | Cxxx-NCR-001847 | NCR | NOS WA - Incorrect Settitng out of Jacking Plinth Starter Bars |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2014-12-12 | 2014-12-11 08:15 | -1 | 2014-11-17 17:45 | Civil - Civil Engineering General | 1000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | In reference to the latest P05 revision of drawing Cxxx-SWN-S-DD-CR094_PT002_A-41601 detailing the new jacking plinths on the CRL NOS Bridge West abutment. The location of the northern plinth was incorrectly set out when installing the starter bars prior to pouring the abutment pile cap. The cast in starter bars are therefore approximately 1m south of the design location.
| 03SR - Stations (RfL) | Cxxx-NCR-001848 | NCR | Four Span Underpass - GL3 Pile Cap - Piles out of position tolerance |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2014-12-01 | 2014-11-28 08:09 | -3 | 2014-11-17 15:45 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Ref. Drg. Cxxx-SWN-S-DDD-CR094_PT002_Z-69470 - Piles P03A/B/J/O/P/Q have been installed outside of the specification positional tolerance of +/-75mm. See attached As-Built drawing for confirmation.
| 03SR - Stations (RfL) | Cxxx-NCR-001849 | NCR | CMR Phase 2 Deck - East Abutment 'L' Bar Levels |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2014-12-08 | 2014-11-25 17:59 | -13 | 2014-11-18 17:07 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The CRL CMR Bridge east abutment 'L' Bars, BM01 and BM02 have been cast in to the abutment pour approximately 80mm low. The 'L' bars are designed to tie in to the T2 mat of the deck reinforcement. As the 'L' bars are low, the remaining northern face splay 'U' bars will fit correctly.
| 03SR - Stations (RfL) | Cxxx-NCR-001851 | NCR | Secant wall pile 251 - concrete placed outside spec |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2015-01-10 | 2015-01-16 10:59 | 6 | 2014-11-19 09:18 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Due to boring difficulties on secant pile P251, the time between batching and placing the 1st load of concrete was 6 hours. This will have effected approximately the first 4m3 placed in the bottom of the pile.
| 03SR - Stations (RfL) | Cxxx-NCR-001852 | NCR | Proposal to introduce M__ couplers for steel reinforcement incorrectly cut in emergency doorway location at pier 4 wall |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2014-12-03 | 2014-11-26 15:30 | -7 | 2014-11-19 11:40 | Structural Engineering - Reinforcement | 1500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The steel reinforcement pile cap projection bars in the four span underpass pier 4 wall have been cut at the incorrect location for the emergency access doorway, refer drawings Cxxx-SWN-S-DDD-CR094_PT002_Z-68443, Cxxx-SWN-S-DDB-CR094_PT002_Z-69201, bending schedule Cxxx-SWN-S-DDJ-CR094_PT002_Z-68443 and the marked up drawing. As per discussions with __ (URS), __ propose to install M__ couplers onto the cut down steel reinforcing pile cap protection bars (6 no. 25mm bars (BM107) and 6no. 32mm bars (BM 105)). The horizontal lacer bars (BM35,BM36,BM37,BM38) are spaced at 150mm centres. One number 20mm diameter horizontal lacer bar shall be cut immediately north and south of the M__ couplers (maximum M__ coupler length 312mm, see attached specification sheet) refer marked up sketch. The lacer bars above and below shall be displaced slightly to just above and just below the couplers. M__ couplers shall be installed in accordance with the manufactures recommendations 1No. end capping bar, BM35/BM36 shall be cut down on the return leg (i.e. not on the 'B' leg of the bar) so the two corners of the bar remain intact. Cxxx to confirm the length of steel reinforcing bar required to be fixed into the M__ coupler onto which the wall Capping 'U' bar shall be fixed (BM 58/59)
| 03SR - Stations (RfL) | Cxxx-NCR-001853 | NCR | Secant Guide Wall Out of Tolerance |  | Crossrail | XRL | PML - Pudding Mill Lane Portal (Central) |  | 2014-12-11 | 2014-12-11 16:49 | 0 | 2014-11-20 13:45 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | This NCR superceeds Cxxx-NCR-1850. There appears to be numerous sections of the secant guide wall have been cast out of tolerance. In the worst case, (Pile P254) the inside face of the wall is 40mm beyond the allowed position (55mm from design position). See the attached Excel sheet.
| 03SR - Stations (RfL) | Cxxx-NCR-001854 | NCR | Secant wall plan location as-built P281-P155 |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2015-09-01 | 2015-08-03 11:39 | -29 | 2014-11-20 13:57 | Civil - Civil Engineering General | 0 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Secant wall as-built plan location SK-10593 (piles 255 – 281) details several piles out of tolerance for plan location with the worst being 15mm out of tolerance (away from track) and 2mm out of tolerance (towards the track). See attached survey.
| 03SR - Stations (RfL) | Cxxx-NCR-001855 | NCR | Secant wall Pile 102 cage too low |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2015-10-30 | 2015-10-27 10:22 | -3 | 2014-11-20 14:00 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Secant pile cage 102 was pushed into position using the machine bucket. The chains were then removed but the cage began to self-plunge further. The cage is now 150mm low.
| 03SR - Stations (RfL) | Cxxx-NCR-001857 | NCR | Four Span Underpass - Unapproved cast in items (Conical Cones for Alsipercha System) |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2014-12-11 | 2014-12-05 14:42 | -6 | 2014-11-27 12:33 | Civil - Civil Engineering General | 750 |  | Planning | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Refer to the following documents: Ref Drg - Cxxx-SWN-S-DDA-CR094_PT002_A-69101 Ref Spec - Cxxx-SWN-S-RSP-CR094_PT002-00002 Clause E20.145 During the GL5 Abutment pour 3No. 850mm conical steel tubes were cast into pour 1 at shelf level without prior approval. The cones are for the purpose of providing a footing for a future Alsipercha fall arrest system.
| 03SR - Stations (RfL) | Cxxx-NCR-001858 | NCR | Propping Works Ongoing Without an Approved ITP |  | Crossrail | XRL | PML - Pudding Mill Lane Portal (Central) |  | 2015-01-23 | 2015-01-21 12:59 | -2 | 2014-11-24 14:43 | Civil - Excavation | 500 |  | Documentation and Records | Repair | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | The Works Information states that an ITP is to be produced and accepted prior to works beginning on site. Although the Cut and Cover temporary propping ITP (Cxxx-MRG-C-ITP-CR094_WS111-50019) was accepted for the first phase of works in 2011, it is lacking the required information for phase 3 (currently ongoing). Despite numerous requests, __ have not yet updated this ITP is updated but continue to preceed with the works.
| 03SR - Stations (RfL) | Cxxx-NCR-001859 | NCR | Four Span Underpass - GL 5 Abutment - Concrete Finish |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2016-04-30 | 2016-01-11 11:56 | -110 | 2014-11-27 17:14 | Civil - Civil Engineering General | 2000 |  | Planning | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Please refer to documents: Ref Drg - Cxxx-SWN-S-DDC-CR094_PT002_Z-69222 Ref Spec - Cxxx-SWN-S-RSP-CR094_PT002-00002 Ref - E41.201 & E41.201 The contract specified U3 finish (finish shall be steel-trowelled under firm pressure to produce a dense, smooth uniform surface free from trowel marks) was not achieved on the GL5 Abutment East shelf. The contract specified F3 finish (smooth and uniform in texture and appearance, no formwork staining or blemishes) was not achieved on the seen vertical faces of GL5 Abutment wall and due to the embedded ties. Additionally, as the as per request of Cxxx-FCD-1826 a F4 trial panel was not poured, prepared and offered for inspection prior to pouring the abutment.
| 03SR - Stations (RfL) | Cxxx-NCR-001861 | NCR | CMR CRL Bridge - Phase 2 West Abutment Miothene Compression |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2015-02-16 | 2015-02-13 15:13 | -3 | 2014-12-08 14:23 | Civil - Civil Engineering General | 1000 |  | Design | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Drawing Cxxx-MMD-C-EDR-CRG06-00088 details 100mm of compressible filler on the B53 west abutment brickwork. __ used approved compressible filler board with a layer of 18mm of plywood on top of the filler due to the loading concerns raised in RFI 2739. Prior to the west abutment bearing shelf concrete pour, all levels were checked and no issues identified. On completion of the post pour as-built surveys of the west abutment bearing shelf, it has been identified that the level of the reinforcement has dropped by approximately 60mm. A level survey of both the concrete and reinforcement is attached to this NCR. In addition, a cover meter survey has been carried out on the bearing shelf showing that all areas are within the 40mm – 70mm tolerance. The level survey however shows the following issues have resulted from the fall in reinforcement level: 1) The northern end of the drainage channel has fallen causing the channel to backfall. 2) The level of B1 plinth reinforcement has fallen resulting in additional cover to the top. The position of plinth B1 has been disturbed as can be seen in the atatched plinth position survey. 3) The reinforcement on the west end of the deck has fallen resulting in excess cover to the T1 mat. This will only be an issue north of the robust kerb where the T5 and T6 layers of reinforcement are not specified. In addition to the above, following a plinth pre-pour survey, the reinforcement for plinth B5 is 30mm low.
| 03SR - Stations (RfL) | Cxxx-NCR-001862 | NCR | EIP - Couplers for Vent Wall |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2015-01-11 | 2014-12-11 08:24 | -31 | 2014-11-27 16:40 | Civil - Civil Engineering General | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | B25 couplers have been installed in the base slab of the EIP for the Ventilation Wall, instead of the B16 couplers as shown on drawing Cxxx-SWN-S-DDD-CR094_PT002_Z-80414 (C03). Significant delays from the supplier (__) in delivering the B16 couplers meant that B25 couplers (already on site for other works) were the only viable option to meet critical programme.
| 03SR - Stations (RfL) | Cxxx-NCR-001863 | NCR | NOS West Abutment out of position piles |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2014-12-25 | 2014-12-11 12:02 | -14 | 2014-11-27 14:27 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | This NCR is raised further to NCR 1820 - out of position piles at NOS West Abutment which identified piles P2, P5, P12 and P17 as being out of tolerance. As-Built Records taken at cut-off level show that pile numbers P8, P11, P13 and P15 are 90mm, 147mm, 147mm and 91mm out of position respectively. These piles were not identified as being out of tolerance on NCR 1820
| 03SR - Stations (RfL) | Cxxx-NCR-001864 | NCR | Secant wall as built pile location out of tolerance |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2015-08-15 | 2015-08-03 11:20 | -12 | 2014-11-28 08:57 | Civil - Civil Engineering General | 0 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Secant wall as built drawing SK-10597 (attached for piles P173 to P214 showing face of pile at ground level) details some pile locations outside the target tolerance with the worst case being 28mm out of tolerance (note all out of tolerances are away from the future Crossrail track alignment).
| 03SR - Stations (RfL) | Cxxx-NCR-001865 | NCR | EIP - Cross Wall 4 Starters |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2015-01-12 | 2015-01-06 17:55 | -6 | 2014-11-28 13:21 | Civil - Civil Engineering General | 500 |  | Design | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The couplers in the southern half of Crosswall 4 have been installed with minimal spacing, as a result of steel congestion in the base slab. This provides cover to the starter bars of 100mm in both faces.
| 03SR - Stations (RfL) | Cxxx-NCR-001866 | NCR | EIP - Lift Shaft Southern Wall starters |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2015-01-17 | 2014-12-11 09:32 | -37 | 2014-11-28 13:37 | Civil - Civil Engineering General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The southern wall of the lift shaft at base slab level has a row of B25 couplers that were displaced from the designed position, due to the TBM launching blocks (for Cxxx operations) being designed in a location that conflicted with the lift shaft wall. These displaced coupler positions give reduced cover to the northern couplers (circa 35mm) and increased cover to the southern couplers (circa 135mm).
| 03SR - Stations (RfL) | Cxxx-NCR-001867 | NCR | Secant wall Pile P125 cage fabricated wrong |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2015-10-29 | 2015-10-27 10:51 | -2 | 2014-11-28 13:31 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Secant wall pile cage P125 has arrived to site with the roof slab couplers 2m out of position.
| 03SR - Stations (RfL) | Cxxx-NCR-001868 | NCR | CRL - Retaining Wall 1 Base - Pile Issues |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2015-01-30 | 2014-12-19 14:43 | -42 | 2014-12-01 17:30 | Civil - Civil Engineering General | 2000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Please refer to: Drg: Cxxx-SWN-S-DDA-CR094_PT002_1-30150 Spec: Cxxx-SWN-S-RSP-CR094_PT002-00004 Please also refer to attached sketch. PR116 - 1No bent B25 vertical reinforcement bar above cut off level. PR92, PR113 & PR117 - Piles have not achieved the minimum specified cover. PR90, PR93 & PR101 - All had reduced cover. PR96 - A small piece of concrete sheared off the face of the pile during breakdown works leading to reduced cover.
| 03SR - Stations (RfL) | Cxxx-NCR-001869 | NCR | EIP - Missing Couplers for Cross Wall 3 |  | Contr | TWC | PML - Pudding Mill Lane Portal (Central) |  | 2015-02-20 | 2015-01-15 10:45 | -36 | 2014-12-01 10:24 | Civil - Civil Engineering General | 2000 |  | Design | Repair | 4 (0.5-3k) | Complete | Previous Construction - Problems based on previous construction errors | Completed |  | Cross Wall 3 has no couplers installed in the base slab due to the TBM launching blocks (for Cxxx operations) being designed in a location that conflicted with the wall.
| 03SR - Stations (RfL) | Cxxx-NCR-001870 | NCR | C&C2 - Roof Infill Cxxx Waterbar Damage |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2015-02-20 | 2015-01-15 10:43 | -36 | 2014-12-03 13:31 | Civil - Civil Engineering General | 1000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | RFI-2827 was raised to cover the issue of the waterbar in the Cut and Cover roof infills being damaged by Cxxx. The welded corners of the waterbar have been torn apart during the occupation of the site by Cxxx, a resolution is required.
| 03SR - Stations (RfL) | Cxxx-NCR-001871 | NCR | Records not being produced contemporaneously |  | Crossrail | XRL | PML - Pudding Mill Lane Portal (Central) |  | 2015-01-23 | 2015-01-23 11:05 | 0 | 2014-12-01 13:21 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Repair | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | The Cut and Cover temporary propping works have been ongoing for approx 6 weeks. During this time __ have been working to revision 2.0 of ITP Cxxx-MRG-C-ITP-CR094_WS111-50019. However, after numerous requests for the QA documentation sheets to be provided for review, many documents required under the ITP have not yet been produced. This lack of contemporaneously produced documentation contradicts section 20.8 and 20.9 of the works information. Although rev 2.0 the ITP has been accepted Code 1, it is now over 3 years old and deemed unsuitable for the current works, as it does not reference the relevent drawings or controls specific to the props equipment being installed. Numerous requests to update this ITP have been made.
| 03SR - Stations (RfL) | Cxxx-NCR-001872 | NCR | Non- Conformance with FCD 0861 |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2015-01-20 | 2015-01-19 14:05 | -1 | 2014-12-01 16:17 | Structural Engineering - Joints | 1000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The MJ in the constructed CRL 1 retaining wall and base slab at the interface between the phase 1 and phase 2 construction works has not been constructed in accordance with FCD 0861. The MJ in the CRL 1 retaining wall and base slab are not coincidental and the 250mm back of wall water bar has not been installed in the constructed section of the base slab. FCD 0861 stated that it 'appears that this will coincide with the fifth joint from the returned surface of the wall from the west abutment end’, this wasn’t the case. The set out co-ordinates shown on drawing Cxxx-SWN-S-DDA-CR094_PT002_1-30150 for the end of the base slab did not line up with the end of the 12m wall CRL1 wall panel section, there was a 400mm step. The 250mm water bar was missed during the installation.
| 03SR - Stations (RfL) | Cxxx-NCR-001873 | NCR | Compressive strength test failure of 1 set of cubes taken from the CRL bridge west abutment kicker - CMR |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2015-01-20 | 2015-01-22 14:13 | 2 | 2014-12-03 16:21 | Civil - Civil Engineering General | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | 1 set of the cubes taken from the CRL bridge west abutment phase 2 kicker pour reached only 37.9N/mm2, failing the 28 day requirement of 41N/mm2.
| 03SR - Stations (RfL) | Cxxx-NCR-001874 | NCR | Four Span Underpass - GL 5 Abutment - Approved Construction Joint Level |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2015-05-05 | 2015-05-04 07:58 | -1 | 2014-12-03 13:20 | Civil - Civil Engineering General | 2500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Please refer to: Drg: Cxxx-SWN-S-DDC-CR094_PT002_Z-69222 Spec: Cxxx-SWN-S-RSP-CR094_PT002-00002 Ref E10.640 PTR: Cxxx-RFI-2616 & Cxxx-RFI-2638 The approved construction joint level of the GL5 Abutment Pour 1 was not met on the __ Up Electric end. Please see attached sketch detailing the post pour level survey of the Abutment.
| 03SR - Stations (RfL) | Cxxx-NCR-001875 | NCR | EIP - Varying cover in the base of the EIP walls |  | Contr | TWC | PML - Pudding Mill Lane Portal (Central) |  | 2015-07-31 | 2015-05-29 14:26 | -63 | 2014-12-08 10:50 | Civil - Civil Engineering General | 2000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Cover to the reinforcement in the lower section of the EIP walls is outside of tolerance in several locations.
| 03SR - Stations (RfL) | Cxxx-NCR-001876 | NCR | CRL - Retaining Wall 1 Base - Piles out of tolerance |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2014-12-19 | 2014-12-19 14:55 | 0 | 2014-12-05 17:01 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Please refer to: Drg: Cxxx-SWN-S-DDA-CR094_PT002_1-30150 Spec: Cxxx-SWN-S-RSP-CR094_PT002-00004 KP10.3210 Please see attached highlighted sketch showing five piles that have been installed outside of positional tolerance (75mm) within the final section of the CRL - Retaining Wall 1 Base. The pile numbers are PR104/105/113/117 & 126.
| 03SR - Stations (RfL) | Cxxx-NCR-001877 | NCR | CMR CRL Bridge - Phase 2 Deck Pour 1 |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2015-01-22 | 2015-01-22 14:18 | 0 | 2014-12-08 14:50 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Error by manufacturer in shipping or marking | Completed |  | During the concrete pour for the CMR Crossrail Bridge Deck phase 2 pour 1 on 14/11/14, the time between concrete deliveries exceeded the duration detailed in clause E10.680 of the specification. As can be seen from the attached pour record sheet, the time between loads 7 and 8 and loads 9 and 10 was 40 minutes.
| 03SR - Stations (RfL) | Cxxx-NCR-001878 | NCR | South upstand wall panel S50 dowel bars |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2015-04-10 | 2015-03-23 08:18 | -18 | 2014-12-11 15:39 | Civil - Civil Engineering General | 1200 |  | Planning | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | THIS NCR SUPERSEDES NCR 1089 (To be cancelled) The dowel bars on South Upstand Wall panel S50 have not been installed. See NCR 1089 for history.
| 03SR - Stations (RfL) | Cxxx-NCR-001879 | NCR | CRL - Retaining Wall 1 Base - Low Blinding |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2015-01-26 | 2015-01-14 10:07 | -12 | 2014-12-17 11:03 | Civil - Base Course | 1000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Please refer to: Ref Drg - Cxxx-SWN-S-DDC-CR094_PT002_Z-69222 & Cxxx-SWN-S-DDD-CR094_PT002_Z-31423 & Cxxx-SWN-S-DDB-CR094_PT002_Z-30250 Ref Spec - Cxxx-SWN-S-RSP-CR094_PT002-00002 The blinding in the lower/thicker section of the CRL base slab (see attached marked up sketch) was poured in worse case 20mm low. This may cause the base slab reinforcement cage to sit low and have excess cover to the top mat reinforcement layer. The specified Nominal concrete cover to outermost layer of reinforcement including links to be 75mm.
| 03SR - Stations (RfL) | Cxxx-NCR-001881 | NCR | Finished Concrete to capping beam pour 2 |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2015-02-06 | 2015-02-06 16:12 | 0 | 2015-01-10 08:45 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The shutter to the capping beam pour 2 (covered ramp) kicked in and has left an indentation on the finished concrete both north and south faces (please see attached photographs)
| 03SR - Stations (RfL) | Cxxx-NCR-001882 | NCR | Secant Pile P126 installed too low |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2015-11-20 | 2015-11-04 11:27 | -16 | 2015-01-10 09:36 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | P126 was installed 79mm low. The cage was fabricated incorrectly with the couplers out of dimension. __ adjusted this cage so that the couplers would be at the correct level thus leaving the cage 29mm out of tolerance
| 03SR - Stations (RfL) | Cxxx-NCR-001883 | NCR | 4SU GL2 Piles out of position tolerance |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2015-03-05 | 2015-02-04 13:54 | -29 | 2015-01-19 07:46 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Similar to NCR 1848, piles within GL2 of the four span underpass have been constructed out of positional tolerance. Please see attached As-Built of piles showing direction of the delta and degree of error.
| 03SR - Stations (RfL) | Cxxx-NCR-001884 | NCR | Four Span Underpass - GL2 Pier - Pile Cap Bent Starter Bars |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2015-02-27 | 2015-01-26 11:49 | -32 | 2015-01-20 16:18 | Civil - Civil Engineering General | 3500 |  | Damaged | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Please refer to: Drg: Cxxx-SWN-S-DDD-CR094_PT002_Z-68421/68424 Spec: Cxxx-SWN-S-RSP-CR094_PT002-00002 Clause E30.320 PROTECTION OF REINFORCEMENT · Dropping from height, mechanical damage and shock loading: Prevent. After construction of GL2 Pile Cap the reinforcement was protected and buried to maintain access to the Cut & Cover Phase 3 works. However, during excavation of the area 18No starter bars have been bent during the excavation works of the GL2 Pier starter bars.
| 03SR - Stations (RfL) | Cxxx-NCR-001885 | NCR | 4SU - Pier 3 starter bar clash with doorway |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2015-03-05 | 2015-01-26 12:01 | -38 | 2015-01-19 08:36 | Civil - Civil Engineering General | 750 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | See attached RFI 2908: On the south side of the doorway at Pier 3 there is less than 20mm cover between the edge of the doorway and the starter bar. There is also a U-Bar to be installed.
| 03SR - Stations (RfL) | Cxxx-NCR-001886 | NCR | TSS Pile Reinforcement Low |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2015-03-27 | 2015-01-30 10:31 | -56 | 2015-01-20 16:18 | Civil - Civil Engineering General | 2000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Pile numbers PR300, PR301, PR307, PR313 and PR352 of the Track Support Slab structure have been installed with low reinforcement ranging between -223mm and -349mm.
| 03SR - Stations (RfL) | Cxxx-NCR-001888 | NCR | Secant wall FULL pile as-built shown as centre of pile |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2016-04-30 | 2016-02-11 14:36 | -79 | 2015-01-22 10:02 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Please find attached the Secant wall pile as built. This is the full Secant wall, detailing the as built location along the centre line as requested. The survey shows numerous piles out of plan tollerance. This NCR now supersedes NCR's 1854 & 1864.
| 03SR - Stations (RfL) | Cxxx-NCR-001889 | NCR | C&C Phase 2a - Hydrophilic strip in the cable risers |  | Contr | TWC | PML - Pudding Mill Lane Portal (Central) |  | 2015-03-27 | 2015-03-16 18:23 | -11 | 2015-01-22 18:19 | Civil - Civil Engineering General | 1500 |  | Incomplete Works | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Cable risers 1& 2 in Cut & Cover phase 2a have had their kicker poured without hydrophilic strip placed at the base. The hydrophilic strip was not shown on the drawing, but was required in the response to RFI’s 1218 and 2866. The pour was inspected by __ and Crossrail engineers but the omission of the hydrophilic strip was missed, as it was not shown on the drawings.
| 03SR - Stations (RfL) | Cxxx-NCR-001890 | NCR | Excess Cover to capping beam (secant piles) |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2015-02-09 | 2015-02-02 13:53 | -7 | 2015-01-26 13:43 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Capping beam pours 1-5 have been found to have excess cover ranging from 1-8mm over the specified tolerance. This can be seen in both the pre-pour surveys and the cover meter surveys.
| 03SR - Stations (RfL) | Cxxx-NCR-001891 | NCR | Damage to Gallows Bracket |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2015-02-16 | 2015-02-19 17:06 | 3 | 2015-01-26 10:07 | Civil - Civil Engineering General | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Supervision - Other | Completed |  | During excavation in the narrow width (cut and cover phase 3), a gallows bracket for the temporary propping frame has been bent
| 03SR - Stations (RfL) | Cxxx-NCR-001894 | NCR | CRL NOS Bridge - Bearing 2 Bottom Plate Orientation |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2015-02-27 | 2015-02-16 12:06 | -11 | 2015-01-28 15:56 | Civil - Civil Engineering General | 500 |  | Manufacturing Defect | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During the installation of the CRL NOS Bridge during the 24 January possession, it was noted that the 60mm this bottom plate from bearing 2, highlighted on the attached drawing, had been fixed to the rocker section of bearing in the incorrect orientation. The plate has been installed with the 40mm dimension, highlighted, on the outside face and the 50mm dimension on the inside. Bearing 3 has been fabricated correctly. The fabrication error resulted in the southern girder being incorrectly positioned, although survey checks during the possession highlighted the issue and the girder was relocated to the design alignment.
| 03SR - Stations (RfL) | Cxxx-NCR-001896 | NCR | Covered ramp capping beam link BM 09 |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2015-05-15 | 2015-05-11 14:12 | -4 | 2015-01-28 08:40 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | When placing the capping beam main link bars, the vertical dimension of this bar has been consistently 1110mm and this has been set with 75mm cover to the bottom and 65mm cover to the top. BM09 (main link) changes to a vertical dim of 1150mm. This bar should have been set with note 2 in mind with 50mm to the bottom and top. Instead it was fixed with the same 75mm cover to the bottom. Although there is a scheduling error in changing the dim of the same bar, this should have been picked up and note 2 applied for. See Drw DDD-60405.
| 03SR - Stations (RfL) | Cxxx-NCR-001897 | NCR | CMR CRL Bridge - Phase 2 Soffit Concrete Finish |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2015-03-17 | 2015-02-18 13:51 | -27 | 2015-02-05 18:19 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | In reference to drawing Cxxx-MMD-C-EDR-CRG06-00109 the soffit of the CMR Crossrail Bridge is shown as having an F3 finish. Specification Cxxx-MMD-C-TSC-CRG06-00001 clause 80.030 states that an F3 finish should be 'smooth and of uniform texture and appearance'. As can be seen from the attached photographs of the soffit, the concrete finish does not satisfy this requirement.
| 03SR - Stations (RfL) | Cxxx-NCR-001898 | NCR | CRL NOS west abutment pile cap - misalignment |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2015-02-27 | 2015-02-16 17:41 | -11 | 2015-02-13 07:44 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The CRL NOS west abutment pile cap was poured outside of its plan positional tolerances. The pile cap was set out incorrectly by the MPB enigineer, refer to the attached survey. All the reinforcement and shuttering were installed before the issue was identified by the MS engineering and survey departments.
| 03SR - Stations (RfL) | Cxxx-NCR-001899 | NCR | Incorrect reporting of cube concrete cube test results and a marginal failure on the running mean of 6 average for concrete mix C35/45C |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2015-04-13 | 2015-03-27 17:48 | -17 | 2015-03-06 12:22 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Personnel Error - Not Defined | Completed |  | The results on the recent submission of the test reports for sample numbers PML 1147 and PML 1148 were incorrect due to a typographical error caused when transposing numbers onto the report sheet at Heathrow. The reports previously sent through to Mark Wilson (MS Senior Engineering Technician – Materials) back in September contain the correct compliant results. As a separate issue due to a dip in strengths during the period when these cubes were crushed there has been a statistical running mean of 6 non-conformance. The running average of 6 no 28 day results marginally fell below the 47 N/mm2 requirement for a C35/45 mix. See the attached graph illustrating the failure.
| 03SR - Stations (RfL) | Cxxx-NCR-001900 | NCR | Disregard for Quality Procedure |  | Crossrail | XRL | PML - Pudding Mill Lane Portal (Central) |  | 2015-03-13 | 2015-02-20 09:36 | -21 | 2015-02-04 08:15 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Verification Problems - Inspection points not adequate | Completed |  | Despite numerous verbal and written requests, __ are failing to invite Crossrail to witness various construction activities as specified in the ITPs. This is in contradiction to Parts 20.8 and 20.9 of the Works Information.
| 03SR - Stations (RfL) | Cxxx-NCR-001901 | NCR | Lack of cover survey prior to backfilling C&C Capping Beam |  | Crossrail | XRL | PML - Pudding Mill Lane Portal (Central) |  | 2015-02-18 | 2015-02-20 09:11 | 2 | 2015-02-04 12:37 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | Pour 5 of the C&C phase 3 capping beam was cast on 22nd January 2015. Despite numerous requests for a cover survey to be conducted of this structure, as of 4th February no survey has been produced. Furthermore, the area to the north of the capping beam has now had permanent backfill placed, preventing a survey from being conducted.
| 03SR - Stations (RfL) | Cxxx-NCR-001902 | NCR | EIP Southern wall lift shaft kicker |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2015-02-27 | 2015-02-23 14:14 | -4 | 2015-02-06 14:05 | Civil - Civil Engineering General | 3000 |  | Design | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Couplers in the base slab were displaced due to the late design clash with Cxxx thrust plinth requirements. As a result of this, there was a discontinuity between starter bars and lacers on the south side of the lift shaft wall, i.e. excessive concrete cover.
| 03SR - Stations (RfL) | Cxxx-NCR-001903 | NCR | TSS - Pile extensions concreted to incorrect level |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2015-06-19 | 2015-06-11 09:02 | -8 | 2015-02-09 10:43 | Civil - Civil Engineering General | 1000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Pile extensions PR 302, 303, 304, 349 & 351 were cast with the concrete to low, it ranges from 35-112mm, see attached sketch and table.
| 03SR - Stations (RfL) | Cxxx-NCR-001904 | NCR | EIP - Builders Hole in Crosswall 2 installed at wrong level |  | Contr | TWC | PML - Pudding Mill Lane Portal (Central) |  | 2015-03-13 | 2015-03-03 14:46 | -10 | 2015-02-07 12:30 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The builders hole box out detailed in RFI 2771 was installed in Crosswall 2 at 91.74 (300mm below design invert level) due to a setting out error. As a result, the steel altered in Crosswall 2 to suit the standard builders hole detail in RFI 2939 is incorrect.
| 03SR - Stations (RfL) | Cxxx-NCR-001905 | NCR | Excess cover to Capping Beam Pour 5 |  | Crossrail | XRL | PML - Pudding Mill Lane Portal (Central) |  | 2015-02-23 | 2015-02-27 11:35 | 4 | 2015-02-09 11:31 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Further to Cxxx-NCR-001901 and Cxxx-NCR-001890 There are some areas of excess cover to the C&C north capping beam (Pour 5). (Note that the area has now been backfilled).
| 03SR - Stations (RfL) | Cxxx-NCR-001906 | NCR | EIP - Coupler alignment in the head wall |  | Contr | TWC | PML - Pudding Mill Lane Portal (Central) |  | 2015-05-22 | 2015-05-20 11:11 | -2 | 2015-02-10 10:15 | Civil - Civil Engineering General | 1000 |  | Design | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The L bars with couplers (BM 07) have been cast into the head wall as designed on drawing Cxxx-SWN-S-DDD-CR094_PT002_Z-80410 (C03). The threaded starter bars that connect into the these couplers in the head wall (BM 06) have not been designed to take into consideration the angle of the head wall, and hence couplers, relative to that of the Western facing core walls.
| 03SR - Stations (RfL) | Cxxx-NCR-001907 | NCR | South upstand waterbar MCR not code 1 when used |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2015-07-31 | 2015-07-29 16:46 | -2 | 2015-02-10 11:08 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | MCR 50081 for the water bar used in the south up-stand wall was not code 1 approved at the time of use
| 03SR - Stations (RfL) | Cxxx-NCR-001908 | NCR | DLR wall coping repair system MCR not code 1 approved when used |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2015-11-13 | 2016-02-08 12:01 | 87 | 2015-02-10 11:15 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | MCR 50263 for the repair mortar system to DLR copings was not code 1 approved at the time of use.
| 03SR - Stations (RfL) | Cxxx-NCR-001911 | NCR | MGL - Collision Beam Bolts installed out of tolerance |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2015-02-26 | 2015-02-27 09:53 | 1 | 2015-02-12 14:07 | Structural Engineering - Inserts | 2500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | MGL Collision Beam Bolts have been installed out of tolerance, drawing Cxxx-SWN-S-DDD-CR094_PT002_Z-51374 states the bolts shall have 100mm protrusion above the concrete level, i.e. a design top of bolt level at 107.847m (not allowing for the 1:100 concrete fall over the length of the base plate). Please refer the attached sketch showing the as built levels taken on the bolts on the Four Span Underpass Pier 5. The concrete level on the top of Pier 5 abutment is also provided on the marked up sketch and varies from the design level of 107.747m (with a 1:100 crossfall excluded for the purpose of analysis of the top of bolts), this is covered under a separate NCR specific to the concrete works on Pier 5 abutment. A cover meter survey has been undertaken at each bolt location to ensure there is sufficient cover to the steel reinforcement in the bearing shelf, refer attached marked up sketch. To resolve the issue with reduced bolt projection length, Cxxx propose to scabble around the bolt set for the area of the Collision Beam base plate to a level of 107.708. This will provide a minimum 100mm bolt protrusion to the worst case scenario bolt (top of bolt 107.808) whilst reducing the cover to the abutment shelf steel reinforcement to 23mm (worst case scenario). The Collision Beam base plate is designed with a nominal 25mm thickness grout bed, therefore increasing the minimum cover to 48mm. The grout bed will be cast using __ EP Epoxy Resin free flow grout (MCR approved) in accordance with RFI 3006. Please confirm this rectification proposal is acceptable.
| 03SR - Stations (RfL) | Cxxx-NCR-001912 | NCR | Missing Grout records |  | Crossrail | XRL | PML - Pudding Mill Lane Portal (Central) |  | 2015-03-16 | 2015-03-09 13:41 | -7 | 2015-02-16 11:35 | Civil - Excavation | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Verification Problems - Other | Completed |  | During a planned Crossrail led surveillance of temporary propping, the Contractor stated that cubes had been taken for grout strength as per the ITP Cxxx-MRG-C-ITP-CR094_WS111-50019 rev 6.0 item 4.7; 25 N/mm2. Cubes to be taken and tested by a UKAS approved test house. The Contractor was unable to provide records to confirm this had been carried out.
| 03SR - Stations (RfL) | Cxxx-NCR-001913 | NCR | Four Span Underpass - GL1 Abutment - Pile Issues |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2015-03-04 | 2015-02-27 14:39 | -5 | 2015-02-18 14:40 | Civil - Civil Engineering General | 2000 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Please refer to: Drg: Cxxx-SWN-S-DDD-CR094_PT002_Z-69470 Spec: Cxxx-SWN-S-RSP-CR094_PT002-00004 P01F - 1No bent B25 vertical reinforcement bar above at cut off level during cropping. P01F & P01H - Piles have not achieved the minimum specified cover to the reinforcement cage
| 03SR - Stations (RfL) | Cxxx-NCR-001914 | NCR | C&C2 - Central Wall Head Starters |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2015-04-19 | 2015-03-16 18:21 | -34 | 2015-02-18 13:21 | Civil - Civil Engineering General | 1500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | There is an issue with misaligned couplers in the C&C central wall. As result of this, some of the vertical bars cannot be connected to the couplers cast into the C&C roof or the spacing is excessive. Please note each situation is generally duplicated for both faces. 1) A vertical run of steel has no corresponding coupler in the roof. 2) Across the roof joints couplers would have fouled the waterbar, hence no couplers installed over ~550mm. 3) In panel 3 a bar is misaligned and has been deemed as too excessively bent. 4) In panel 2 there is a bar as per situation 1 but the gap between coupled bars is 330mm (>250mm). Cause – The cause is believed to be a mis-placement of the roof couplers due to steel congestion.
| 03SR - Stations (RfL) | Cxxx-NCR-001915 | NCR | Four Span Underpass - Pile P01V |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2015-03-09 | 2015-02-27 08:22 | -10 | 2015-02-23 17:26 | Civil - Civil Engineering General | 2000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Contamination | Completed |  | Please refer to: Drg: Cxxx-SWN-S-DDD-CR094_PT002_Z-69470 During excavation of the pile P01V the head of the pile was found to contain soft concrete due to the effects of the surrounding contaminated soil. Further investigation has found the soft concrete to extend as far as 1m beneath the design cut off level (102.250m). Additional temporary works was installed to confirm the extent of the soft concrete, confirming the extent is localised within 1.5m.
| 03SR - Stations (RfL) | Cxxx-NCR-001916 | NCR | NOS Bridge - Rotation of London End Trimmer Beam |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2015-03-27 | 2015-03-10 10:50 | -17 | 2015-02-24 13:01 | Civil - Civil Engineering General | 3000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | In reference to CBUK marking plan drawing 665/10001 attached, the London end trimmer beam 08101 has been site welded to deck plates 08102 & 08103. In the process of completing the butt weld on the eastern side of the trimmer beam, the beam has distorted and rotated around the welded joint. The trimmer beam has rotated out of vertical alignment, the top flange has moved towards the centre of the bridge and the bottom flange has moved away from the centre. The rotation of the trimmer has introduced a slope in the bottom flange of the trimmer beam of 25-0mm around the location of bearing 6. This has resulted in bearing number 6, which is welded to the bottom flange of the trimmer beam, to rotate out of vertical alignment as shown on the attached photographs. The bearing is not currently grouted so is free to rotate within the dowel pockets.
| 03SR - Stations (RfL) | Cxxx-NCR-001917 | NCR | Material Approval Schedule not updated and regularly submitted as required by Works Information Vol 2B Part 20 |  | Crossrail | XRL | PML - Pudding Mill Lane Portal (Central) |  | 2015-04-30 | 2015-04-27 17:02 | -3 | 2015-02-24 15:42 | Materials - Approval | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Misunderstand the definition of the requirement | Completed |  | During a planned Crossrail surveillance at Cxxx dated 04th February 2015, it was highlighted on review of the Materials Approval Schedule (MAP), Cxxx-MRG-O-TSC-CR094_WS111-50001, which is functioning as the Materials Proposal Schedule (MPS), that the ‘current’ version on eB, Revision 5, has been at a Code 2 Decal since July 2012 with Revision 6 submitted January 2015 being ‘draft’ and ‘not approved’, which is currently with Crossrail for review. This meant that there was a 28 month time lapse between MAP (MPS) submissions. The requirements of Works Information Vol 2B Part 20.7 states “The Contractor shall regularly submit the Material Proposal Schedule and a matrix of approvers for all materials and products….” and “The preliminary schedule shall be submitted for the Project Manager’s acceptance within 6 weeks of the starting date, and shall subsequently be regularly updated and resubmitted to incorporate changes and updates”.
| 03SR - Stations (RfL) | Cxxx-NCR-001918 | NCR | Code 3 MCRs used in permanent works and information not provided for 6 MCRs at Code 3 decal as requested during planned CRL surveillance |  | Crossrail | XRL | PML - Pudding Mill Lane Portal (Central) |  | 2015-06-30 | 2015-06-30 17:38 | 0 | 2015-02-24 15:47 | Materials - Approval | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate resources | Completed |  | During a planned Crossrail surveillance at Cxxx dated 04th February 2015, it was highlighted on review of the Materials Approval Schedule (MAP) that 16 Materials Compliance Records (MCRs) were still at a Code 3 decal, with some dating back to 2012. Of the 16 MCRs, information was made available for 10; 6 of which had not been used in the works (not noted on MAP as being cancelled) and 4 which had been used at a Code 3 decal (see below). Following multiple requests for information on the remaining 6 (see below), nothing was provided as such the surveillance could not verify that the remaining 6 materials had not been used (see below). Under Document management Procedure Rev 2, CRL1-XRL-Z3-GPD-CR001-50001, a Code 3 decal stands for “Not Accepted. Revise and resubmit. Work may not proceed”, as such this NCR was raised as Code 3 MCRs had been used in the permanent works and information could not be provided for 6 others. Code 3 MCRs – Cxxx-MRG-C-QAP-CR094_WS111-* 50087 22/05/2012 (Civil) Anchon Bars and Couplers (used - required updating) 50124 05/03/2013 (MEP) DLR Speakers (used - required updating) 50081 25/04/2012 (Civil) Wall Waterbar (Cxxx-NCR-001907 already raised by Contractor) 50263 16/10/2013 (Civil) Repair Mortar (Cxxx-NCR-001908 already raised by Contractor) 50171 24/09/2013 (MEP) Mechanical Pipework (no information provided) 50016 16/09/2013 (MEP) Trunking and Acc (no information provided) 50002 18/07/2013 (MEP) Ventilation Fan (no information provided) 50226 20/06/2013 (Civil) Foam Concrete (no information provided) 50019 30/08/2013 (Civil) CT Chamber (no information provided) 50328 15/09/2014 (Civil) Osmose Naturewood (no information provided)
| 03SR - Stations (RfL) | Cxxx-NCR-001919 | NCR | 12 MCRs were found to be at a Code 2 decal for periods longer than 3 months during a CRL planned surveillance |  | Crossrail | XRL | PML - Pudding Mill Lane Portal (Central) |  | 2015-06-30 | 2015-06-30 17:45 | 0 | 2015-02-24 16:02 | Materials - Approval | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate resources | Completed |  | During a planned Crossrail surveillance at Cxxx dated 04th February 2015, it was highlighted on review of the Materials Approval Schedule (MAP) that 12 MCRs were at a Code 2 decal status for periods longer than 3 months, with some dating back to 2012. Under Document management Procedure Rev 2, CRL1-XRL-Z3-GPD-CR001-50001, a Code 2 decal stands for “Not accepted, revise and resubmit work may proceed subject to incorporation of changes indicated”. The 12 MCRs were therefore not current at the time of the surveillance as the required changes were not incorporated. Works Information Vol 2B 13.2 details the provision of contemporaneous records; to ensure compliance this NCR was raised. Code 2 MCRs – Cxxx-MRG-C-QAP-CR094_WS111-* 50041, 50113, 50131, 50137, 50152, 50191, 50192, 50193, 50195, 50199, 50238, 50339
| 03SR - Stations (RfL) | Cxxx-NCR-001920 | NCR | TSS - Damaged pile reinforcement bars |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2015-03-26 | 2015-03-20 14:58 | -6 | 2015-02-26 10:30 | Geotechnical Engineering - Concrete - Bored Pile | 2500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During the excavation works for the central third of the TSS, 8no piles with damaged reinforcement bars where uncovered. It appears that following the pouring of the piles, the concrete settled from above pile reinforcement to 50mm – 300mm below on the 8no. piles. This then left the reinforcement unprotected from the Class A granular fill and plant movement above the piles. This has resulted in reinforcement being bent, the bent sections of reinforcement have now been trimmed off and the top of the remaining pile reinforcement has been surveyed. See attached survey data
| 03SR - Stations (RfL) | Cxxx-NCR-001921 | NCR | FSU - Inaccurate casting of the Marshgate Lane U Deck Hold Down Bolt void former locations at Pier 5 |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2015-05-05 | 2015-05-05 12:08 | 0 | 2015-02-26 16:46 | Structural Engineering - Concrete Member | 2000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The void formers for the Marshgate Lane U Deck bridge girder Hold Down Bolts to pier 5 abutment have been installed out of alignment, both vertically and horizontally. An attempt to centralise the void formers at their design location by locally scabbling around the voids has proved unsuccessful. To rectify the issue __ propose to break out concrete around up to the perimeter of each bearing plinth (approximately 50mm from the steel reinforcement), refer marked up plan drawing Cxxx-SWN-S-DDD-CR094_PT002_Z-51071 and photograph appended with this NCR. Concrete shall be broken out to between 50mm and 70mm below the design level of the Holding Down Bolts, see attached spreadsheet for proposed levels. If steel reinforcement is visible at the proposed break out level additional concrete shall be broken out to expose 50mm below the reinforcing bar. The exposed surface shall be treated as a construction joint and prepared in accordance with the Concrete Specification Cxxx-SWN-S-RSP-CR094_PT002-00002 E40.230 The bearing plinth shall then be re-cast up to the design finished level as per drawing Cxxx-SWN-S-DDD-CR094_PT002_Z-51071 with 120mm diameter void formers set vertical about the centre of the Hold Down Bolt design location. Please confirm the rectification proposal is acceptable
| 03SR - Stations (RfL) | Cxxx-NCR-001922 | NCR | Four Span Underpass - GL3 Pier - failure to pour to the approved Construction Joint |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2015-05-29 | 2015-03-03 13:20 | -87 | 2015-03-02 10:29 | Civil - Civil Engineering General | 1000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Please refer to: Drg: Cxxx-SWN-S-DDB-CR094_PT002_Z-69201 Spec: Cxxx-SWN-S-RSP-CR094_PT002-00002 Clause E10.680 & E40.132 Concrete was locally not poured to the approved construction joint (see attached photo).
| 03SR - Stations (RfL) | Cxxx-NCR-001923 | NCR | MGL east abutment ballast wall kicker |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2015-03-16 | 2015-03-03 10:30 | -13 | 2015-03-02 13:02 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The lower section of the Marshgate Lane east abutment kicker was poured with a C40/50/B mix as per spec, but the concrete was delivered with fire resistant monofilament polypropylene fibres. The specification requires this C40/50/B fire resistance on all Cut & Cover Tunnel, Cover Ramp and four span underpass, but not within the Marshgate Lane east abutment. See attached sketch The unrequested addition of the monofilament polypropylene fibres was discovered during the pre-pour testing of the concrete. Discussions were then held between __ and MPB, the conclusion was that the use of the concrete fulfils the specification requirements and that the fibre would not have any detrimental effect. The concrete pour then progressed as discussion were being held with CRL representative.
| 03SR - Stations (RfL) | Cxxx-NCR-001924 | NCR | Track Support Slab - Pile Issues PR320 & PR325 |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2015-03-17 | 2015-03-05 17:11 | -12 | 2015-03-03 13:33 | Civil - Civil Engineering General | 2000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | 2no piles PR320 and PR325 were excavated and have been discovered with cracks approx 300mm below cut off level.
| 03SR - Stations (RfL) | Cxxx-NCR-001925 | NCR | Cut & Cover Phase 2a - Honeycombing on 11kV Column West |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2015-06-05 | 2015-06-01 12:42 | -4 | 2015-03-06 16:19 | Civil - Civil Engineering General | 2000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The shutters on the Western 11kV column (drawing Cxxx-SWN-S-DDD-CR094_PT002_Z-71474 C01) have been struck and show honeycombing around the base (see attached photos and drawing mark up).
| 03SR - Stations (RfL) | Cxxx-NCR-001926 | NCR | EIP- Insufficient cover to the trackside face on Western facing walls |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2015-05-08 | 2015-03-31 20:12 | -38 | 2015-03-09 08:17 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The cover to BM 32 in the Western facing walls of the EIP (Eastern half) is out of tolerance, with insufficient cover on the track facing side (35mm ) and excessive on the internal side (85mm). The area affected is 1.5m x 1m to the underside of the platform walkway slabs (see attached).
| 03SR - Stations (RfL) | Cxxx-NCR-001927 | NCR | EIP - Concrete Infill to Emergency Stairs |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2015-04-28 | 2015-04-27 16:01 | -1 | 2015-03-09 13:31 | Civil - Civil Engineering General | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | It was approved to replace the polystyrene fill beneath the emergency staircase with a mass concrete fill. Seperately to this RFI-2684 asking for what mix to use as 'C20 Concrete' as concrete mass-fill already shown in the design was answered as requiring an ST4 mix. On the day of the pour a Gen1 mix was placed. Also no FCD was raised to cover the change completely to concrete from polystyrene as this had been agreed verbally since the response to RFI-2626 was recieved.
| 03SR - Stations (RfL) | Cxxx-NCR-001928 | NCR | C&C Phase 2a - Cable riser 3 exceeding concrete placement times |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2015-04-14 | 2015-03-16 18:19 | -29 | 2015-03-09 16:27 | Civil - Civil Engineering General | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | Cable riser 3 walls were poured with concrete placement times exceeding the 30 minutes specified in Section E10.680 of the concrete specification (Cxxx-SWN-S-RSP-CR094_PT002-00002).
| 03SR - Stations (RfL) | Cxxx-NCR-001929 | NCR | Four Span Underpass - GL 1 Pile Cap (North Section) |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2015-04-10 | 2015-03-19 08:37 | -22 | 2015-03-12 17:28 | Civil - Civil Engineering General | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Improper resource allocation | Completed |  | Please refer to: Drg: Cxxx-SWN-S-DDA-CR094_PT002_1-69100 Spec: Cxxx-SWN-S-RSP-CR094_PT002-00002 Clause E10.680 Fresh concrete was placed against in situ concrete outside of the specified 30 minute time window (between the 5th & 6th loads). Concrete was placed at 34 minutes and face was still live at the time of placement.
| 03SR - Stations (RfL) | Cxxx-NCR-001930 | NCR | CRL - Retaining Wall 1 - Rear wall waterproofing |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2015-06-25 | 2015-03-30 10:40 | -87 | 2015-03-17 08:07 | Civil - Civil Engineering General | 1500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Please refer to: Drg: Cxxx-SWN-S-DDD-CR094_PT002_Z-31400 PTR: Cxxx-RFI-1494 For approximate 7m length of CRL 1 retaining wall, the Back of wall waterproofing (Nufins NuProof) has been applied to the full height of the wall rather than terminated 400mm below the proposed finished surface level (see attached photo).
| 03SR - Stations (RfL) | Cxxx-NCR-001931 | NCR | Cut & Cover Phase 2a - Roof Infill No.1 cracking |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2015-06-15 | 2015-06-10 16:24 | -5 | 2015-03-16 17:35 | Civil - Civil Engineering General | 1500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Not Defined | Completed |  | The roof infill No.1 in the Cut & Cover Phase 2a section has cracking on the soffit in each corner of the roof slab.
| 03SR - Stations (RfL) | Cxxx-NCR-001932 | NCR | Gallows Bracket Pocket Excavation |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2015-04-14 | 2015-04-15 10:58 | 1 | 2015-03-18 12:09 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Repair | 4 (0.5-3k) | Complete | Personnel Error - Violation of requirement or procedure | Completed |  | The pocket excavations for the gallows brackets on the lower propping frames exceeded the dimensions given in FCD's 1872-1874. This was done to maintain safe access and egress into the pockets for drilling welding and grouting.
| 03SR - Stations (RfL) | Cxxx-NCR-001933 | NCR | SUW - Localised Honeycombing |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2015-05-07 | 2015-04-14 08:28 | -23 | 2015-03-19 11:43 | Civil - Civil Engineering General | 1000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Please refer to: Drg: Cxxx-SWN-S-DDB-CR094_PT002_Z-61202 Spec: Cxxx-SWN-S-RSP-CR094_PT002-00002 Clause E10.690 Upon striking of the South Upstand Wall half shutters from Panel 5, in fills 1 & 2, localised honeycombing was found at the construction joints (see attached photos).
| 03SR - Stations (RfL) | Cxxx-NCR-001934 | NCR | ETS piling: Reinforcement cages out of level tolerance |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2015-05-08 | 2015-05-01 09:34 | -7 | 2015-04-24 16:05 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During the installation of the ETS piles three reinforcement cages were installed high of their design level. Section R6 of the General Notes drawing “Cxxx-MMD-C-DDL-CRG06_Z-00002” P01 states that the maximum tolerance in its vertical location is +/- 50mm from its design level. The cage in pile P36: was installed 50mm high of maximum tolerance – this was due to the design of cage vibrating tool being unable to push the cage below ground level. Top of steel for all the cages was approximately 100mm below pile mat level. The cage in pile P32: was installed 52mm high of its maximum tolerance – this was due to the design of cage vibrating tool being unable to push the cage below ground level. The cage in pile P21: was installed 1100mm high of its maximum tolerance – the pile was bored to the correct depth and received the correct theoretical volume of concrete. Reason for refusal is unknown.
| 03SR - Stations (RfL) | Cxxx-NCR-001935 | NCR | Four Span Underpass - GL1 Pile P01V - cage out of positional tolerance |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2015-04-03 | 2015-03-24 15:05 | -10 | 2015-03-20 14:18 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Please refer to: Drg: Cxxx-SWN-S-DDD-CR094_PT002_Z-69470 Spec: Cxxx-SWN-S-RSP-CR094_PT002-00004 Pile P01V is 118mm out of position, an additional 43mm out of positional tolerance.
| 03SR - Stations (RfL) | Cxxx-NCR-001936 | NCR | Cut & Cover Phase 2a - Roof slab box out incorrect reinforcement |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2015-04-18 | 2015-04-13 12:01 | -5 | 2015-03-21 08:01 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | One of the 500mm sq. box outs cast into the cut & cover roof slab for pouring the centre wall below has reinforcement running through the opening, impeding the concrete tremie from being inserted down into the centre wall to deliver concrete from the appropriate height.
| 03SR - Stations (RfL) | Cxxx-NCR-001937 | NCR | Low concrete cover to the reinforcement on the CRL NOS bridge deck |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2015-06-10 | 2015-05-15 08:33 | -26 | 2015-04-01 15:44 | Civil - Civil Engineering General | 1000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | This NCR relates to two isolated areas of low cover the reinforcement on the CRL NOS bridge deck; The design requires 40mm of concrete cover to the reinforcement (+ 0/ - 10mm) 1. There is a 2000mm long x 100mm wide section in the south east corner of the CRL NOS bridge RC deck that has between 26 - 29mm of concrete cover to the reinforcement, refer to locations 27 and 28 on the attached cover metre survey. 2. A bootprint has been left in the finish in north west corner of the deck. This was left by one of the concrete gang whilst trying to cover the pour with frost blanket; cover to the reinforcement within the bootprint is 20mm, refer to location 29 in the attached cover metre survey.
| 03SR - Stations (RfL) | Cxxx-NCR-001938 | NCR | RRVAR - Positional Tolerance to RC structure |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2015-07-10 | 2015-06-15 11:03 | -25 | 2015-03-27 11:29 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | As previous
| 03SR - Stations (RfL) | Cxxx-NCR-001940 | NCR | Four Span Underpass - CRL Deck Pour 2 |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2015-05-01 | 2015-04-14 12:39 | -17 | 2015-03-26 17:56 | Civil - Civil Engineering General | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Please refer to: Drg: Cxxx-SWN-S-DDA-CR094_PT002_C-69103 Spec: Cxxx-SWN-S-RSP-CR094_PT002-00002 Clause E10.680 Fresh concrete was placed against in situ concrete outside of the specified 30 minute time window (between the 17th & 18th loads). Concrete was placed at 54 minutes and the face was still live at the time of placement.
| 03SR - Stations (RfL) | Cxxx-NCR-001941 | NCR | C&C Phase 2a - Exceeding pour times for cable riser 3 throat pour |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2015-04-24 | 2015-04-07 15:58 | -17 | 2015-03-27 17:07 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | Cable riser 3 throat sections were poured with concrete placement times exceeding the 30 minutes specified in Section E10.680 of the concrete specification (Cxxx-SWN-S-RSP-CR094_PT002-00002).
| 03SR - Stations (RfL) | Cxxx-NCR-001942 | NCR | C&C Phase 2a - Exceeding concrete pour times for Centre Wall Panel 2 |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2015-04-24 | 2015-04-20 11:23 | -4 | 2015-03-27 17:17 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | External Phenomenon - Other | Completed |  | The Centre Wall panel 2 were poured with concrete placement times exceeding the 30 minutes specified in Section E10.680 of the concrete specification (Cxxx-SWN-S-RSP-CR094_PT002-00002).
| 03SR - Stations (RfL) | Cxxx-NCR-001943 | NCR | Greenway Piles - P19 |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2015-05-15 | 2015-04-28 15:56 | -17 | 2015-03-31 13:07 | Civil - Structural Engineering | 2500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Greenway ramp pile P19 has been excavated and found to have only 5mm cover to one side. ~70mm cover has been found 1.4m below cut-off level.
| 03SR - Stations (RfL) | Cxxx-NCR-001944 | NCR | Greenway Ramp - Pile issues |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2015-05-28 | 2015-04-28 16:09 | -30 | 2015-04-09 10:51 | Civil - Civil Engineering General | 2000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Pile P24 - A shard of concrete has broken off the face of the pile during excavation works. Pile P21 - During excavation of the pile, a lump of soft concrete came away, this is below cut-off level.
| 03SR - Stations (RfL) | Cxxx-NCR-001945 | NCR | Four Span Underpass - GL3-4 Deck - Deck Pour 2 - U4 Finish |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2015-06-19 | 2015-04-17 16:06 | -63 | 2015-04-01 12:32 | Civil - Civil Engineering General | 1500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Please refer to: Drg: Cxxx-SWN-S-DDA-CR094_PT002_C-69103 Spec: Cxxx-SWN-S-RSP-CR094_PT002-00002 Clause E41.201 The specified U4 finish was not achieved. In the process of covering the finish face the frost blanket and holding down timbers came into contact with the finished horizontal face on the South section of the Westbound deck (see attached photos) prior to the concrete sufficiently hardening. This caused depressions in the top of the concrete. There is also the presence of laitance on the surface of the deck.
| 03SR - Stations (RfL) | Cxxx-NCR-001946 | NCR | South Upstand Wall – Surface Crack – South Face Panel 49 |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2015-04-15 | 2015-04-14 08:46 | -1 | 2015-04-01 12:09 | Civil - Civil Engineering General | 1000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Please refer to: Drg: Cxxx-SWN-S-DDD-CR094_PT002_Z-72485 Spec: Cxxx-SWN-S-RSP-CR094_PT002-00002 Clause E05.430 In the South face of panel S48 in the South Upstand Wall there is a small 1.5m long surface crack measuring 0.3-0.35mm wide.
| 03SR - Stations (RfL) | Cxxx-NCR-001947 | NCR | Greenway Ramp Tre Bale Lack of Approved ITP |  | Crossrail | XRL | PML - Pudding Mill Lane Portal (Central) |  | 2015-06-17 | 2015-06-15 17:43 | -2 | 2015-04-01 15:17 | Civil - Fill | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Procedure Problem - Other | Completed |  | Starting work on the excavation and fill of the Greenway Ramp without an approved ITP. ITP informally review by CRL FE and verbally approved - but still lacking a of formally approved copy after several days after starting works.
| 03SR - Stations (RfL) | Cxxx-NCR-001948 | NCR | Lack of Approved MCR for Greenway Ramp Fill |  | Crossrail | XRL | PML - Pudding Mill Lane Portal (Central) |  | 2015-06-17 | 2015-06-15 17:40 | -2 | 2015-04-01 15:30 | Civil - Fill | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Procedure Problem - Other | Completed |  | Incorporation of the following materials into the permenant works without an approved MCR: - Leca LWA Fill 10-20mm - Cxxx-MRG-C-QAP-CR094_WS111-50366 - Tyre Bales – Anglo Environmental - Cxxx-MRG-C-QAP-CR094_WS111-50365
| 03SR - Stations (RfL) | Cxxx-NCR-001949 | NCR | C&C D wall leaks Panels N19 to N32 (north wall) |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2015-06-30 | 2015-05-20 15:11 | -41 | 2015-04-07 11:49 | Civil - Civil Engineering General | 5000 |  | System Defect | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Further to the excavation and construction of phase 2a C&C (specifically panels N19-N32). There remains some minor leaks to these D-walls. The full report containing details of these leaks have been issued via RFI 3124. The report is also attached in this NCR.
| 03SR - Stations (RfL) | Cxxx-NCR-001950 | NCR | C&C D wall leaks to all CSJV walls (excluding phase 3) |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2015-09-25 | 2015-08-20 14:22 | -36 | 2015-04-07 12:00 | Civil - Civil Engineering General | 5000 |  | System Defect | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Error by manufacturer in shipping or marking | Completed |  | Further to the verbal request from CRL (__) to carry out a full review of leaks in the D-walls constructed by -C248. We have submitted our full leak report via RFI 3123. The report is also attached to this NCR. This details various leaks ranging from joints, mid panel and at the MJ.
| 03SR - Stations (RfL) | Cxxx-NCR-001951 | NCR | MGL - Reckli Wall out of Position |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2015-05-21 | 2015-05-19 16:15 | -2 | 2015-04-20 12:56 | Structural Engineering - Structural Engineering - General | 3000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Marshgate Lane Abutment South Reckli Wall has been constructed out of position by 27mm at the south east base of the wall and also on the wrong vertical slope meaning top of the South East face of the MGL Reckli Wall is leaning approx 75mm north from design. The back face of the stopend is also leaning approx 35mm north from design which in turn has meant the wall is narrow by 30mm at the top. (Refer to drawing no. Cxxx-NCR-CR094-1951TG) The south west end of the Reckli wall is approx 30mm south from design at the top and the bottom of the wall which has meant the incorrect bearing of the reckli face has been exaggerated even further. (Refer to drawing no. Cxxx-NCR-CR094-1951TG)
| 03SR - Stations (RfL) | Cxxx-NCR-001952 | NCR | C&C phase 3 prop install with un approved weld documentaion pack |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2015-07-31 | 2015-07-15 11:29 | -16 | 2015-04-09 16:25 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | C&C ph3 temp works propping is proceeding without an unapproved welding documentation pack while CRL’s ongoing comments are being addressed. Rev 2.0 has been returned with basic comments relating to the __s covering review letter.
| 03SR - Stations (RfL) | Cxxx-NCR-001953 | NCR | ETS Pile 33 - Inclusions at Cut-Off Level |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2015-05-14 | 2015-05-13 09:53 | -1 | 2015-04-14 08:27 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | In reference to drawing Cxxx-MMD-C-DDA-CRG06_Z-00004 detailing the East Track Slab piles. When excavating and cropping the piles it has been noted that there are inclusions in the pile at cut off level. The photos attached show the condition of the pile after it has been cropped. The inclusions do not impact on the cover to reinforcement on the pile.
| 03SR - Stations (RfL) | Cxxx-NCR-001954 | NCR | ETS Excavation - Commencing Works Prior to WPP Approval |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2015-05-15 | 2015-04-17 13:17 | -28 | 2015-04-15 08:53 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Procedure Problem - Failure to follow status stamp | Completed |  | Excavation for the East Track Slab (ETS) construction commenced prior to the approval of the Works Package Plan (WPP) for the ETS Superstructure (Cxxx-MRG-C-GMS-CR094_WS111-50154). Revision 1 of the WPP was issued to Crossrail for approval on 23/03/15. __ were attempting to confirm the requirements for Japanese Knotweed muck-away and membrane with Crossrail (RFI 3115 and RFI 3121) prior to submitting the WPP, hence the short timescale for approval. To-date, __ still have not received an instruction for the installation of Japanese Knotweed membrane with the response to RFI 3115 not providing a definitive answer. Informal comments on revision 1 of the ETS Superstructure WPP were received from both DLR and NR by 01/04/15. Formal comments to revision 1 of the WPP were delayed in the DLR document control process so __ were unable to issue revision 2 of the document until 09/04/15 when the code 3 Decal sheet was returned. The revision 2 of the ETS Superstructure WPP was immediately issued but to-date has not been approved. After discussions with Crossrail, __ understood that the excavation of the piling platform could be carried out under the approved WPP for the ETS piling (Cxxx-MRG-C-GMS-CR094_WS111-50153) as the plant and risks involved in the works were identical. __ were informed on 10/04/15 at 1400 that Crossrail did not believe that the works were covered under the ETS Piling WPP. At this point all works were suspended immediately. No further works have been completed on the ETS since this date. __ are keen to proceed with the ETS works as they are critical to the hand-over to Contract 610 on the key date of 04/12/2015.
| 03SR - Stations (RfL) | Cxxx-NCR-001955 | NCR | Four Span Underpas - __ Ballast Wall Reinforcement Level |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2015-04-30 | 2015-04-21 15:45 | -9 | 2015-04-16 12:52 | Civil - Civil Engineering General | 750 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Please refer to: Drg: Cxxx-SWN-S-DDC-CR094_PT002_Z-69222 & Cxxx-SWN-S-DDD-CR094_PT002_Z-68442 PTR: Cxxx-RFI-2770 The reinforcement U-bars for the __ Ballast wall (South side only - see attached sketch) has been cast into the GL5 Abutment too high on the 12/11/14. This has come to light after review of RFI-2770 when setting the formwork for the Ballast wall pour. RFI-2770 provides a different level to the contract drawing Cxxx-69222 for the South section compared to the North but this was not picked by Cxxx. The U-bars (BM17 from Cxxx-68442) cannot now be moved down.
| 03SR - Stations (RfL) | Cxxx-NCR-001956 | NCR | Secant wall leaks piles 1 - 65 only. |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2016-01-29 | 2016-01-06 14:49 | -23 | 2015-04-17 08:33 | Civil - Civil Engineering General | 10000 |  | Workmanship | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Now that a substantial amount of the secant wall is exposed in C&C phase 3. We have carried out a leak review and attach the report for piles 1 - 65. All leaks on the report are of the running water nature and require sealing.
| 03SR - Stations (RfL) | Cxxx-NCR-001957 | NCR | Four Span Undepass - Central Wall Unapproved Cast In Items |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2015-05-01 | 2015-04-24 12:38 | -7 | 2015-04-17 16:37 | Civil - Civil Engineering General | 750 |  | Planning | Repair | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | Please refer to: Drg: Cxxx-SWN-S-DDA-CR094_PT002_C-69103 Ref Spec - Cxxx-SWN-S-RSP-CR094_PT002-00002 Clause E20.145 Cxxx has cast in 2No 850mm steel conical tubes for an Alsipercha fall arrest system into the permanent works in the locations shown on the attached location sketch without prior permission of Cxxx. The cones are for the purpose of providing a footing for a future Alsipercha fall arrest system used when installing the soffit CRL roof deck formwork. The cones are in Pour 1 in the centre of the Central wall which is a 500mm thick section. Cones are positioned so that they do not come into contact with the permanent works reinforcement within the body of the wall.
| 03SR - Stations (RfL) | Cxxx-NCR-001958 | NCR | C&C Phase 2a - Missing Water stop in 500 sq box outs in roof slab |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2015-07-17 | 2015-06-03 09:08 | -44 | 2015-04-18 12:42 | Civil - Civil Engineering General | 1000 |  | Design | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | No waterstop has been installed in the 500mm sq box outs in the cut & cover phase 2a roof slab.
| 03SR - Stations (RfL) | Cxxx-NCR-001959 | NCR | EIP - Lack of cover to Reinforcement in Crosswall 5 |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2015-06-26 | 2015-06-08 13:01 | -18 | 2015-04-18 13:15 | Civil - Civil Engineering General | 1500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | There is insufficient cover to the internal reinforcement at intersection with Crosswall 5 and the core walls ( Western and Eastern running tunnels).
| 03SR - Stations (RfL) | Cxxx-NCR-001960 | NCR | Removal of Attenuation Tank NBC 1.1 |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2015-12-28 | 2015-11-17 16:18 | -41 | 2015-04-20 17:07 | Civil - Civil Engineering General | 60000 |  | Planning | Rework | 2 (6-60k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | Upon receipt of the lift plan co-ordinates for the MGL bridge lift, it was discovered that the outrigger of the LG1550 crane clashes with the previously installed attenuation tank NBC 1.1. In order to achieve the possession date and satisfy ourselves that the outrigger loadings were not imposed onto this tank, __ have removed the section of tank which was impacted by the outrigger and its load path. For information purposes, 15m of the 28m tank has been removed.
| 03SR - Stations (RfL) | Cxxx-NCR-001961 | NCR | Failure of re-injectable tubes to C&C and D walls |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2015-09-30 | 2015-08-20 14:24 | -41 | 2015-04-21 08:41 | Civil - Civil Engineering General | 500 |  | System Defect | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Further to the request by CRL to inject resin in to all base slab and roof slab re-injectable tubes as well as all available D-wall joint re-injectable tubes within the EIP and Cut & Cover structures. We have carried out an extensive exercise to do the injecting works and have been unable to successfully inject into these tubes. Upon investigation it would appear that the tubes have collapsed. Please note that the product suppliers representative visited site several times during installation of the base slab / roof slab tubes and has visited again on the 16/4/15 to witness / confirm the failure of the tubes to take injection resin. This relates to EIP, 11KV, C&C phase 2A, C&C phase 2B and Diaphragm wall joints. Refer to MCR Cxxx-MRG-C-QAP-CR094_WS111-50018 for the MCR details. Attached is E-mail correspondence from the product suppliers representative detailing his site visits at construction stage and a recent one to review the failure. Also attached are some picyures taken by the rep at the time of install.
| 03SR - Stations (RfL) | Cxxx-NCR-001962 | NCR | Four Span Underpass - __ Ballast Wall Pour - Concrete Finish |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2015-06-26 | 2015-05-22 14:49 | -35 | 2015-04-27 17:29 | Civil - Civil Engineering General | 2000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Please refer to: Cxxx-SWN-S-DDC-CR094_PT002_Z-69222 Spec: Cxxx-SWN-S-RSP-CR094_PT002-00002 Clause E41.200 Upon striking of the shutter from the __ Ballast wall pour there was the following defects: 1) Incomplete pour of the North Upstand Corner 2) Honeycombing to the South face in line with the South CRL wall 3) Honeycombing/incomplete pour to the central lip section of the ballast wall 4) Honeycombing/incomplete pour to the NWR deck section of the pour 5) Bulge in the South CRL Wall stub – line out of tolerance
| 03SR - Stations (RfL) | Cxxx-NCR-001963 | NCR | Insufficient cover to reinforcement within ETS piles |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2015-05-22 | 2015-05-22 08:40 | 0 | 2015-04-24 14:38 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Section C4 of General Notes drawing Cxxx-MMD-C-DDL-CRG06_Z-00002 P01 states that the nominal cover to the reinforcement within the ETS piles is 75mm (+/- 15mm) After cropping pile number P24 to cut off level it was found to have an area of low cover on one side, a minimum of 45mm was recorded. During cropping P26 it was found to have an area of soil inclusions, once it was thoroughly cleaned out one side of the pile was left 150mm below cut off level. Refer to attached sketch "Sk001/LM/23.4.15"
| 03SR - Stations (RfL) | Cxxx-NCR-001964 | NCR | Cxxx - MGL Abutment missing cover plate recess on __ Upstand Wall |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2015-09-11 | 2015-08-26 09:11 | -16 | 2015-04-23 13:21 | Structural Engineering - Concrete Member | 1000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The 120mm x 25mm cover plate recess on top of the __ upstand wall at MGL Abutment, refer drawing Cxxx-SWN-S-DDB-CR094_PT002_Z-51200 and attached photograph, has been missed during the construction of the wall.
| 03SR - Stations (RfL) | Cxxx-NCR-001965 | NCR | Greenway Ramp - Time between loads exceeded |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2015-06-26 | 2015-05-22 11:40 | -35 | 2015-05-01 09:01 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | During the pile cap pour there was an issue with concrete supply. This resulted in 45mins between the first and second load of concrete and 1hr 10minutes between the second and third load. Thereafter concrete supply improved and was considered compliant with specification.
| 03SR - Stations (RfL) | Cxxx-NCR-001966 | NCR | Shop Painting, Marsh Gate Lane Bridges |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2015-07-10 | 2015-07-04 13:06 | -6 | 2015-05-01 09:53 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Subcontractor Problems - Insufficient surveillance of subcontractors | Completed |  | During an audit of __'s shop painting process (08/04/15), it was noted that an ICORR Level 2 coatings inspector had not been appointed to carry out inspections, as required by the Works Information and approved ITP (Cxxx-MRG-C-ITP-CR094_WS111-50066). See attached NCR raised by __ for this and Cxxx-RSK-W-RGN-CRG03-50013, the Crossrail Inspection Report.
| 03SR - Stations (RfL) | Cxxx-NCR-001967 | NCR | Greenway Ramp - Time between loads exceeded #2 |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2015-06-25 | 2015-05-22 10:18 | -34 | 2015-05-21 09:05 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | During the second pile cap step pour the second load of concrete went to the wrong site entry, the delay in getting the delivery to the pump has caused a 52minute wait between the first two loads.
| 03SR - Stations (RfL) | Cxxx-NCR-001968 | NCR | Greenway Ramp - Excess cover to pile cap |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2015-06-05 | 2015-05-22 10:47 | -14 | 2015-05-01 10:47 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Following a cover meter survey it has come to our attention that the first pour to the Greenway Ramp has cover out of tolerance. Cover ranges from 53mm to 72mm. Required cover is 50mm +/- 10mm.
| 03SR - Stations (RfL) | Cxxx-NCR-001969 | NCR | Damage to existing dowel bars in the phase 2b/3 base slab |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2015-07-10 | 2015-07-06 09:38 | -4 | 2015-05-05 16:27 | Civil - Civil Engineering General | 1000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During breakout of the concrete infill between the sheet piles of phase 2b and the 2b baseslab, the dowel bars cast into the slab were bent.
| 03SR - Stations (RfL) | Cxxx-NCR-001970 | NCR | MGL EB and Network rRil Up Electric U decks - clevis plates welded onto the wrong ends of the bridges |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2015-08-07 | 2015-06-09 12:35 | -59 | 2015-05-05 13:12 | Structural Engineering - Steel Member | 7500 |  | Workmanship | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Please refer the attached marked up fabrication drawings 665-21102 Rev 01 and 665-23101 Rev 01. The clevis plates (components 21F142, 21F165, 23F367 & 23F368) as highlight on the attached drawings have been installed at the wrong ends of the bridge decks. This has caused the bridge not to sit on its bearings, but sit down on the pins in the clevis, leaving a 20mm gap (EB U deck) & 10mm gap (__ U deck) between bearing block and bearing pad at the higher end of the bridge (country) and a birds mouth gap between under side of the bearing plate and bearing at the lower end (London). The clevis plates have approximately 24mm (EB U deck) & 7mm (__ U deck) difference in dimension. Note - This NCR is raised based on __ NCR 665-25
| 03SR - Stations (RfL) | Cxxx-NCR-001971 | NCR | Blinding concrete placed without an IRF submission |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2015-06-30 | 2015-06-02 11:01 | -28 | 2015-05-06 09:22 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | When there was concrete left over from a 4SU wall pour Monday 27th April, the decision was made to use it to blind the under the north wall capping beam down turn (4m2) drw Cxxx-SWN-S-DDD-CR094_PT002_Z-60405. No IRF was issued to CRL to invite them to view this.
| 03SR - Stations (RfL) | Cxxx-NCR-001973 | NCR | C&C phase 3 centre D wall couplers too low to bays 1 & 2 |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2015-07-31 | 2015-07-20 15:08 | -11 | 2015-05-07 14:53 | Civil - Civil Engineering General | 0 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Some of the central D wall couplers are set too low and will clash with the bottom base slab mat in bays 1 & 2. The couplers are outside of the tolerance of -50mm +150mm. See attached report. Also see drw DDD-72461.
| 03SR - Stations (RfL) | Cxxx-NCR-001974 | NCR | Cxxx - MGL __ Up Electric 'U' deck bearing taper plates welded out of position |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2015-06-26 | 2015-06-03 14:00 | -23 | 2015-05-08 13:39 | Structural Engineering - Steel Member | 3000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The bearing taper plates welded to the __ Up Electric U deck, refer items 2No 23F111 & 2No 23F117 on attached drawing Cxxx-MRG-S-DWG-CR094_WS111-50486, have been welded 10mm and 14mm out of position respectively. An asbuilt is attached for the __ Up Electric Bridge. Note - This NCR is raised against __ NCR 665-24
| 03SR - Stations (RfL) | Cxxx-NCR-001975 | NCR | Cut & Cover Phase 2a & 11kv - Walkway column position |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2015-09-25 | 2015-05-22 10:58 | -126 | 2015-05-09 08:39 | Civil - Civil Engineering General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Inadequate/insufficient tooling. | Completed |  | The position of several platform walkway columns in the 11kV and Cut & Cover areas are outside of tolerance.
| 03SR - Stations (RfL) | Cxxx-NCR-001976 | NCR | Cxxx - MGL U decks missing lindapator clips on emergency walkway panels |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2016-03-31 | 2016-03-01 11:55 | -30 | 2015-05-11 16:31 | Structural Engineering - Bolted Connections | 5000 |  | Workmanship | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | lindapter fixings securing the walkway panels onto the stringer beams can not be located correctly due to a summation of the tolerances between the drilling of the holes and the fabrication of the walkway frames. The affected locations are as per the following __s fabrication drawing numbers included below; Eastbound Bridge Cxxx-MRG-S-DWG-CR094_WS111-50398 (x1 plate), 50409 (x12 plates), 50409 (x1 plate), 50404 (x1 plate), 50403 (x1 plate), 50400 (x1 plate), 50399 (x1 plate) Westbound 50379 (x1 plate), 50472 (x13 plates), 50384 (x1 plate), 50470 (x1 plate), 50472 (x1 plate), 50471 (x1 plate) __ Up Electric 50513 (x1 plate), 50514 (x1 plate), 50517 (x1 plate), 50511 (x14 plates), 50519 (x1 plate), 50518 (x1 plate), 50516 (x1 plate), 50517 (x1 plate)
| 03SR - Stations (RfL) | Cxxx-NCR-001977 | NCR | Over-removal of overbreak to pile 57 |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2015-07-31 | 2015-07-31 12:39 | 0 | 2015-05-13 13:35 | Civil - Civil Engineering General | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Whilst removing overbreak to pile 57, additional concrete into the pile was accidentally removed
| 03SR - Stations (RfL) | Cxxx-NCR-001978 | NCR | Marshgate Lane East Abutment - Upstand Wall Concrete to Reinforcement Cover Issues |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2015-05-27 | 2015-05-19 09:00 | -8 | 2015-05-13 12:20 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Please refer to: Drg: Cxxx-SWN-S-DDD-CR094_PT002_2-51433 Spec: Cxxx-SWN-S-RSP-CR094_PT002-00002 Clause E30.470 PTR: Cxxx-FCD-1957 Upon carrying out a cover meter survey on Marsh Gate Lane East abutment ballast walls (GL6), high and low cover was found at various localised points (See attached cover meter survey for reference).
| 03SR - Stations (RfL) | Cxxx-NCR-001979 | NCR | Four Span Underpass - CRL South Wall |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2015-05-27 | 2015-05-28 14:33 | 1 | 2015-05-13 15:40 | Civil - Civil Engineering General | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | Drg: Cxxx-SWN-S-DDD-CR094_PT002_Z-68428 Spec: Cxxx-SWN-S-RSP-CR094_PT002-00002 Clause E10.680 Fresh concrete was placed against in situ concrete outside of the specified 30 minute time window (between the 3rd & 4th loads). Concrete was placed at 46 minutes and face was still live at the time of placement.
| 03SR - Stations (RfL) | Cxxx-NCR-001980 | NCR | Failed weld on East Bound (RH leg) ch 9110 |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2015-07-03 | 2015-07-06 11:59 | 3 | 2015-05-18 14:15 | Track - Welding | 1000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During the first of the May possessions (3-5th May 2015) 1no weld was deemed as a failure by the welder (self-certification) during the Resillient Pad install of the __ 13. The weld failure is on the Eastbound (RH leg) at ch 9110
| 03SR - Stations (RfL) | Cxxx-NCR-001981 | NCR | Exposed D wall rebar during overbreak removal |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2015-08-31 | 2015-08-20 14:29 | -11 | 2015-05-20 08:49 | Civil - Civil Engineering General | 5000 |  | Damaged | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Inadequate/insufficient tooling. | Completed |  | During large overbreak removal to centre D wall panel C35 in C&C phase 3, an area 0.3m x 0.3m sheared back exposing rebar. This is similar to NCR 1977 where overbreak has been removed from a secant pile. see attached pic.
| 03SR - Stations (RfL) | Cxxx-NCR-001982 | NCR | Four Span Underpass - Back of Pier 1 Rearguard Waterstop |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2016-09-29 | 2016-07-28 11:41 | -63 | 2015-05-22 09:47 | Civil - Civil Engineering General | 1000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Please refer to: Drg: Cxxx-SWN-S-DDB-CR094_PT002_Z-69201 Spec: Cxxx-SWN-S-RSP-CR094_PT002-00002 E40.310 PTR: Cxxx-FCD-1863 The Rearguard waterstop installed as part of FCD-1863 to the West face of Pier 1 has been damaged. See attached photo of the 3No holes.
| 03SR - Stations (RfL) | Cxxx-NCR-001984 | NCR | C&C ph 3 key hydrodem between Secant wall / base slab |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2015-08-31 | 2015-09-14 14:15 | 14 | 2015-05-22 09:32 | Civil - Civil Engineering General | 5000 |  | Supervision/Management | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During C&C base slab key forming between Secant piles and base slab using hydrodem, too much concrete has been removed in both height and depth. This has created difficulties in placing the hydrophilic strips to the correct locations without being in contact with pile rebar.
| 03SR - Stations (RfL) | Cxxx-NCR-001985 | NCR | Damage to Southern D walls by Cxxx |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2015-10-09 | 2015-09-07 14:20 | -32 | 2015-05-22 09:43 | Civil - Civil Engineering General | 5000 |  | Damaged | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During breaking back of overbreak concrete to southern D walls by Cxxx to facilitate the tunnel drive works, there are various areas of exposed rebar with some of them quite large. We are soon to be starting the fire lining works and these repairs will be need to be considered / repaired prior to starting. See attached photo survey.
| 03SR - Stations (RfL) | Cxxx-NCR-001986 | NCR | Damage to water bar |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2015-05-27 | 2015-05-28 13:29 | 1 | 2015-05-22 16:14 | Civil - Civil Engineering General | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The base slab waterbar between Phase 2b and Phase 3 was damaged whilst removing the sheetpile concrete plug
| 03SR - Stations (RfL) | Cxxx-NCR-001987 | NCR | CMR - Fabrication of Cover Plate Prior to Acceptance of MCR |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2016-01-29 | 2016-01-06 09:50 | -23 | 2015-06-02 09:36 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | In reference to drawing Cxxx-MMD-C-EDR-CRG06-00124 detailing the City Mill River Crossrail to DLR bridge cover plate. The plate is detailed as a 300 x 10mm thick S275J0 plate. The plate has been fabricated in accordance with the drawing details prior to the MCR or the fabrication drawings for the plate being approved by Crossrail. The plate has been delivered to site and is currently partially fixed in its permanent location, to prevent damage, awaiting approval of the ITP for the CMR Finishing Works. The plate will correctly installed and offered for inspection when the MCR and ITPs for the works have been approved.
| 03SR - Stations (RfL) | Cxxx-NCR-001988 | NCR | D-wall overbreak to phase 2 & 2a |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2015-08-28 | 2015-08-20 14:23 | -8 | 2015-05-23 08:57 | Civil - Civil Engineering General | 5000 |  | Workmanship | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Further to formal D-wall overbreak survey for phase 2 / 2a via RFI 3050, this highlighted various areas of overbreak outside the allowable tolerance of 140mm.
| 03SR - Stations (RfL) | Cxxx-NCR-001989 | NCR | Secant wall leaks |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2016-01-22 | 2016-01-06 14:50 | -16 | 2015-05-26 14:39 | Civil - Civil Engineering General | 10000 |  | Workmanship | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Following further C&C excavation works more leaks have been noted to the Secant wall between piles 66 - 132. Some of which have already had one round of sealing to slow down the flow. See attached report.
| 03SR - Stations (RfL) | Cxxx-NCR-001990 | NCR | 4SU CRL Central South Wall Honeycombing |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2015-09-04 | 2015-09-01 11:33 | -3 | 2015-05-28 11:50 | Civil - Structural Engineering | 1000 |  | Supervision/Management | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The first 300mm wide CRL wall was poured on Friday 22nd May. It was the Central South Wall close to gridline 3. Given that the gap between the reinforcement, and between the reinforcement and the forms was too small (approximately 80mm) to fit the standard size concrete vibration pokers through, shutter vibrators (screamers) and thinner pokers (50mm) were utilised for concrete compaction. After stripping this morning, it was noticed that honeycombing had occured in the vicinity, generally beneath, of where the Reinforced Continuity System was placed for the walkway slab connection. In addition to this location, but not as severely, honeycombing also occured along the base construction joint. See attached photos.
| 03SR - Stations (RfL) | Cxxx-NCR-001991 | NCR | RRAR CRL2 Wall - Minor Honeycombing on Reckli Face |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2015-07-03 | 2015-07-01 11:47 | -2 | 2015-05-28 12:28 | Civil - Civil Engineering General | 1000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Please refer to: Cxxx-SWN-S-DDB-CR094_PT002_Z-35271 Spec: Cxxx-SWN-S-RSP-CR094_PT002-00002 Clause E41.200 There is minor Honeycombing to the South face of the RRAR CRL2 wall east of MGL Abutment, this has not comprimised the cover to the reinforcement and only affects the comestics of the wall.
| 03SR - Stations (RfL) | Cxxx-NCR-001992 | NCR | Secant Pile Slab Connection Details |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2016-08-10 | 2016-07-29 15:48 | -12 | 2016-07-27 08:33 | Civil - Civil Engineering General | 100000 |  | Documentation and Records | Repair | 1 (>60k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | Following FCD 1746, a non standard secant pile coupler bar was requested by Cxxx, and the detail for this coupler bar was produced and approved under FCD 1760. The non standard bar was based on a Shape Code 34, with one of the radii detailed at 175mm, instead of the British Standard 112mm radius bend. Drawing Cxxx-MRG-C-DWG-CR094_WS111-50104 refers. This detail was prior to the pile cage fabrication drawings being submitted and approved. With the submission and acceptance of the various male pile cage drawings the coupler bar detail was included on these drawings, but detailed as a standard Shape Code 34 and was produced in accordance with BS 8666:2005 Table 2. All the male secant pile cages were fabricated and installed in accordance with the following drawings: Cxxx-MRG-C-DWG-CR094_WS111-50109 Rev 3 Cxxx-MRG-C-DWG-CR094_WS111-50110 Rev 2 Cxxx-MRG-C-DWG-CR094_WS111-50112 Rev 2 Cxxx-MRG-C-DWG-CR094_WS111-50113 Rev 2 Cxxx-MRG-C-DWG-CR094_WS111-50115 Rev 2 Cxxx-MRG-C-DWG-CR094_WS111-50120 Rev 2 Cxxx-MRG-C-DWG-CR094_WS111-50121 Rev 2 Cut and Cover Phase 3 Base Slab Bay 1 has been constructed in accordance with the Code 1 approved fabrication drawings, but the pile coupler bars are not as detailed in FCD 1760, i.e. they have the British Standard radius of 112mm instead of the non standard 175mm radius.
| 03SR - Stations (RfL) | Cxxx-NCR-001993 | NCR | C&C base slab level step between ph3 and 2b |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2016-02-28 | 2016-01-27 08:51 | -32 | 2015-05-29 14:28 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | When casting bay 1 of the C&C phase 3 base slab it appears we have a level step between bay 1 in phase 3 and the last base cast for phase 2b.
| 03SR - Stations (RfL) | Cxxx-NCR-001994 | NCR | ETS - Piles cropped below the design cut off level |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2015-07-17 | 2015-07-15 10:16 | -2 | 2015-06-05 16:03 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | 5 no piles within the East Track slab have been partially cropped below the design cut off level. This was due to poor workmanship and inadequate supervision. The maximum a section of pile has been cropped below cut off level is 30mm and no pile is completely low of its design level, refer to the attached sketch for clarity.
| 03SR - Stations (RfL) | Cxxx-NCR-001995 | NCR | ETS - Piles constructed with lifting straps cast within them |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2015-06-26 | 2015-06-24 14:42 | -2 | 2015-06-05 16:05 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | 3 no piles within the East Track Slab have been constructed with lifting strops cast within them. The strops were used by piling subcontractor UPAC to suspend the cages at the correct level during the pouring of the concrete. The general practise was to remove the strop once the concrete was poured to the correct level. The three affected piles are P64, P67 and P72. After investigation by __ (__) it was decided the integrity of P72, an E type pile, would not be affected and could be left as-is. Piles P64 and P67, D type piles, would need to have the strops removed before the East Track Slab is cast across the top.
| 03SR - Stations (RfL) | Cxxx-NCR-001996 | NCR | Marshgate Lane - Bearing Plinths low Concrete Strength |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2015-07-31 | 2015-06-22 15:47 | -39 | 2015-06-03 10:51 | Civil - Structural Engineering | 1000 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Please refer to: Drg: Cxxx-SWN-S-DDD-CR094_PT002_Z-51071 Spec: Cxxx-SWN-S-RSP-CR094_PT002-00002 Rev 5 clause E10.132 With regards to the 2no MGL West abutment NWR Up-electric bearing plinths, sample number: PML1461 has only achieved 44N/mm2 strength at 28 days. This sample was taken from concrete placed on the 10th April 2015.
| 03SR - Stations (RfL) | Cxxx-NCR-001997 | NCR | NR Embankment Drainage - Access chamber NRT8.0 constructed without C status drawings |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2015-07-09 | 2015-07-01 15:18 | -8 | 2015-06-03 14:24 | Civil - Drainage | 1000 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Change to drawings not provided on time | Completed |  | NR Embankment Drainage access chamber NRT8.0 was partially constructed without construction status drawings issued.
| 03SR - Stations (RfL) | Cxxx-NCR-001998 | NCR | Additional leak in North CSJV D wall |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2015-07-31 | 2015-07-29 16:59 | -2 | 2015-06-03 16:34 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Further to leak sealing the North D-wall an additional leak has now apeared in joint N17 / N18. It is of a running water nature. see attached picture.
| 03SR - Stations (RfL) | Cxxx-NCR-001999 | NCR | CMR Bull Head Rail - Cast in Socket Issues |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2015-09-30 | 2015-09-25 12:13 | -5 | 2015-06-05 16:05 | Civil - Civil Engineering General | 1000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | In reference to drawing Cxxx-MMD-C-EDR-CRG06-00086 & Cxxx-MMD-C-EDR-CRG06-00115 , detailing the CMR rubbing strip, there are two issues with the sockets cast in to the abutments on to which the bull head rail is to be fixed. 1) The misalignment of the cast in sockets on the CMR DLR Bridge. The attached survey ‘Bull Head Rail’ shows that on the 3645mm section of wall there is a variance of 35mm on the upper rail and 65mm on the lower rail. The tolerance within the flanges of the rail will be 18mm for the 24mm bolt. There also are a few centres of greater than 400mm between sockets. 2) In reference to RFI 1130, the anchors for the Bull Head Rail in CMR Bridge are M20s at approximately 400mm centres, the greatest being 445mm. A survey of the anchor location is attached ‘CMR CRL Bull Head Survey’. The anchors are 75mm in length as detailed on the attached data sheet so do not comply with the drawing detail which shows 150mm embedment. These sockets are however suitably aligned
| 03SR - Stations (RfL) | Cxxx-NCR-002000 | NCR | Secant pile P36 base slab box out has come loose during plunging |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2015-11-11 | 2015-10-13 13:39 | -29 | 2015-06-10 14:31 | Civil - Civil Engineering General | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | It would appear that during cage plunging of Secant pile P36, the base slab box out has broken loose and floated approx. 1100mm. See attached.
| 03SR - Stations (RfL) | Cxxx-NCR-002001 | NCR | Secant pile P58 base slab box out has broken loose during plunging |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2015-07-06 | 2015-07-06 09:44 | 0 | 2015-06-10 14:35 | Civil - Civil Engineering General | 1000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | It would appear that during cage plunging of Secant pile P58, the base slab box out has broken loose and floated approx. 500mm. See attached.
| 03SR - Stations (RfL) | Cxxx-NCR-002002 | NCR | Greenway Ramp - Piles out of positional tolerance |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2015-07-16 | 2015-06-23 11:32 | -23 | 2015-06-11 13:38 | Civil - Civil Engineering General | 1500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Please see attached as-built survey of the Greenway Ramp Piles. 3no Piles are out of position by: P14: 84mm, P11: 90mm and P19: 124mm
| 03SR - Stations (RfL) | Cxxx-NCR-002003 | NCR | Secant wall further leaks eveident due to additional downturn dig |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2015-07-03 | 2015-07-03 16:27 | 0 | 2015-06-15 08:27 | Civil - Civil Engineering General | 5000 |  | Design | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Other | Completed |  | Now there is a requirement to excavate below original base slab for the downturn beam to C&C ph 3 bays 3 & 4, we have identified more leaks in secant pile joints. These leaks could prevent sound casting of the down stand against the Secant wall. The leaks are at joints 50/51, 58/59 & 64/65. Leak sealing by injection is not practicable in this down stand area due to physical space and the restriction on over digging. The lower hydrophilic strip as shown on the Cxxx drawing will be installed (along with any additional hydrophilic strips detailed with the down turn detail) this will ensure that the discovery of these lower leaks can have no impact, in the permanent state, on the Cxxx waterproofing detail or function.
| 03SR - Stations (RfL) | Cxxx-NCR-002004 | NCR | Track Support Slab - Piles out of positional tolerance |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2015-07-25 | 2015-07-01 15:35 | -24 | 2015-06-19 14:10 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Please see attached as-built survey of the Track Support Slab Piles. 12no Piles are out of position by: PR304 : 94mm PR310 : 89mm PR312 : 84mm PR317 : 83mm PR319 : 97mm PR326 : 85mm PR327 : 87mm PR329 : 89mm PR332 : 92mm PR340 : 100mm PR341 : 149mm PR346 : 104mm
| 03SR - Stations (RfL) | Cxxx-NCR-002005 | NCR | EIP - Cranking of reinforcement bars in the intermediate to ground slab walls |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2015-07-17 | 2015-07-15 16:27 | -2 | 2015-06-17 16:39 | Civil - Civil Engineering General | 2000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | A section of the lift shaft wall and Crosswall 4 has had B16 starter bars cranked (BM’s 95, 224 and 614).
| 03SR - Stations (RfL) | Cxxx-NCR-002006 | NCR | Secant wall pile 61 base slab box out has broken loose during plunging |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2015-07-31 | 2015-07-09 13:30 | -22 | 2015-06-18 13:42 | Civil - Civil Engineering General | 1000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | It appears that the base slab box out has come loose during plunging and floated up 600mm.
| 03SR - Stations (RfL) | Cxxx-NCR-002007 | NCR | Secant pile 68 base slab box has broken loose during plunging |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2015-07-17 | 2015-07-09 13:31 | -8 | 2015-06-18 13:50 | Civil - Civil Engineering General | 1000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | It appears that the base slab box out has come loose during plunging and floated up 550mm.
| 03SR - Stations (RfL) | Cxxx-NCR-002008 | NCR | Secant pile 64 base slab box out has broken loose during plunging |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2015-07-10 | 2015-07-06 09:51 | -4 | 2015-06-18 13:56 | Civil - Civil Engineering General | 1000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | It appears that the base slab box out has come loose during plunging and floated up 500mm.
| 03SR - Stations (RfL) | Cxxx-NCR-002009 | NCR | Secant wall, further low level leaks discovered in the 500mm downturn dig |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2015-07-06 | 2015-07-06 10:16 | 0 | 2015-06-18 14:25 | Civil - Civil Engineering General | 500 |  | Design | Repair | 4 (0.5-3k) | Complete | Previous Construction - Other | Completed |  | during further excavation below for base slab for the downturn beam for C&C ph 3 bays 5, we have identified more low level leaks in secant pile joints. These leaks could prevent sound casting of the down stand against the Secant wall. The leaks are at joints 84/85 & 96/97.
| 03SR - Stations (RfL) | Cxxx-NCR-002010 | NCR | EIP - Incorrect doorway widths intermediate slab level |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2015-09-04 | 2015-07-20 10:15 | -46 | 2015-06-18 17:12 | Civil - Civil Engineering General | 750 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | The kickers for two double doorways on the EIP Intermediate slab have been cast too narrow (2140mm instead of 2160mm)
| 03SR - Stations (RfL) | Cxxx-NCR-002011 | NCR | C&C ph 3 bay 2 / 3 upstand coupler bars used instead of splice |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2015-06-24 | 2015-06-26 09:48 | 2 | 2015-06-19 11:52 | Civil - Civil Engineering General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | With regard the additional upstand beam to C&C ph 3, bay 2, where it adjoins bay 3. On informally issued sketch Cxxx-PML-47059718 rev A (rebar detail layout). The B20 & B16 bars were detailed protruding into bay 3. These prodruding bars would have clashed with bay 3 downturn dig preventing construction.
| 03SR - Stations (RfL) | Cxxx-NCR-002012 | NCR | 4SU - CRL Central Wall Honeycombing |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2015-11-25 | 2015-11-19 14:45 | -6 | 2015-06-23 13:21 | Civil - Civil Engineering General | 1000 |  | Design | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Central Wall pour 6N was poured 18th June 2015. After stripping the pour section on Saturday it was evident that honeycombing of the concrete had occurred just above the kicker connection. This problem has previously occurred on other pours such as described in NCR#1990, but this case is not as severe. In addition to concrete supply and slump being within specfication, all actions we were taken as part of the preventative recurrence actions of the previous NCR including using S4 concrete, toolbox to concreters on correct compaction techniques, use of shutter vibrators as per submitted plan, full supervision of the concrete pour by __, wetting of the Construction Joint and steady rate of rise of concrete. However, due to the area of reinforcement congestion where the reinforced continuity system (RCS) attaches to the wall, the thinner pokers (50mm) could not fit through this section of pour. The area beneath the RCS is relied on the shutter vibrators only for concrete vibration, and it is this section where the honeycombing occured. Note, shutter vibrators were moved progressively up the wall from starting 500mm from the ground.
| 03SR - Stations (RfL) | Cxxx-NCR-002014 | NCR | East Track Slab - Out of Tolerance piles |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2016-01-08 | 2015-12-03 12:38 | -36 | 2015-07-07 13:33 | Civil - Civil Engineering General | 1000 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Please see the attached as-built for the East Track Slab piles. The allowable setting out tolerance for the piling works is +/- 75mm. There are 10No. piles that are out of positional tolerance. Pile 8: 124mm, Pile 21: 112mm, Pile 27: 87mm, Pile 38: 112mm, Pile 40: 93mm Pile 41: 77mm, Pile 42: 101mm, Pile 51: 79mm, Pile 55: 98mm, Pile 72: 78mm, The __ Engineer checked the rig for positional and plumb tolerances before each pile was drilled. While the casings were being removed from the pile, the concrete expanded into the void that was left by the casings causing the overbreak to appear out of position.
| 03SR - Stations (RfL) | Cxxx-NCR-002015 | NCR | Incomplete Welding the Cut and Cover P3 105.5 level props (last 11no) |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2015-07-15 | 2015-07-14 11:10 | -1 | 2015-06-24 13:35 | Civil - Civil Engineering General | 1000 |  | Incomplete Works | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Welding to the gallows brackets was found to be incomplete. The TW design requires a 12mm CFW to all sides of the gallows bracket. Please see attached photograph and survey of missing welds. The survey should be read as; The three numbers is the length of the backing place with the missing welds highlighted Eg, 35-45-80 BL Is 35mm of weld, 45mm gap, 80mm weld (over the 160mm plate) Bottom Left
| 03SR - Stations (RfL) | Cxxx-NCR-002016 | NCR | Cxxx - MGL Collision Beam weld testing |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2016-02-29 | 2015-12-02 15:43 | -89 | 2015-06-24 | Structural Engineering - Welding | 5000 |  | Testing and Commissioning | Use As-Is | 3 (3-6k) | Complete | Discipline/Workmanship - Other | Completed |  | The transverse welds between the collision beam and base plate (part pen weld 001 and 002, 8mm fillet weld 005 and 006) can not be N__ inspected due to the gap between the underside of the collision beam and the top of the abutment not being sufficient to fit the weld testing equipment. __ NCR 665-26 including supplementary weld log and N__ test reports is enclosed with this NCR
| 03SR - Stations (RfL) | Cxxx-NCR-002017 | NCR | Excess concrete cover to reinforcement within the ETS western slab |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2015-07-17 | 2015-07-15 10:08 | -2 | 2015-06-25 12:57 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The blinding on the west end of the ETS was poured lower than its design level and the requirement for the top of concrete is for it to tie in with the existing CMR CRL bridge level (that was 10mm higher than its design), this resulted in maximum of 130mm of cover to the reinforcement in this area. Refer to the attached sketch showing the areas of excessive cover.
| 03SR - Stations (RfL) | Cxxx-NCR-002018 | NCR | ETS: M__ headed anchors fixed at the wrong level |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2015-07-17 | 2015-07-15 09:50 | -2 | 2015-06-26 07:18 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Piles P1 to P8 within ETS required M__ headed anchors to be fitted. The anchors on piles P1, P3 and P6 were fitted approximately 100mm higher than their design level. This resulted in the top of the anchor sitting between the layers of T1 and T2 reinforcement (refer to the attached photo).
| 03SR - Stations (RfL) | Cxxx-NCR-002019 | NCR | 4SU - CRL Box Concrete Times out of Specification |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2015-09-18 | 2015-09-04 17:03 | -14 | 2015-06-26 14:51 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | Drg: Cxxx-SWN-S-DDD-CR094_PT002_Z-68428 Spec: Cxxx-SWN-S-RSP-CR094_PT002-00002 Clause E10.680 On Wednesday 24th June 2015 during Pour 6 of the North Wall, fresh concrete was placed against in situ concrete outside of the specified 30 minute time window (between the 4th &37th loads). Concrete was placed at 37 minutes and face was still live at the time of placement. RevA by Ciaran Beirne 16/7/15 The concrete record sheet provides the details of the pour including times of truck arrivals, discharging, slumps etc. I have added our QA checksheets, photos (images 1-4) of area after "cleaning", and an email from __'s concrete representative Mark Wilson confirming the unlikeliness of a cold joint.
| 03SR - Stations (RfL) | Cxxx-NCR-002020 | NCR | 4SU - Honeycombing on Emergency Walkways Column W142 |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2015-08-31 | 2015-08-25 13:19 | -6 | 2015-07-03 14:44 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Drawing Cxxx-SWN-S-DDD-CR094_PT002_Z-68448. Emergency Walkway column W142 was poured on 25/6/15. The concrete used for the column pour was taken from the third truck from the EIP Core Walls Pour 1. See attached docket. After striking the column, honeycombing was shown on one corner of the column.
| 03SR - Stations (RfL) | Cxxx-NCR-002021 | NCR | 4SU - Box Walls Gridline 3-5 As-Built positional non-conformance |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2015-11-30 | 2015-09-28 17:57 | -63 | 2015-07-13 16:03 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Drawing: Cxxx-SWN-S-DDD-CR094_PT002_Z-68428 & Cxxx-SWN-S-DDD-CR094_PT002_Z-68430 See attached drawing of the as built of the Four Span North, Central and South Walls on gridlines 3-5. Note that there are two points out of tolerance. They are the following: North Wall on Gridline 5 - 15mm to the west Central Wall on gridline 3-4 - 11mm to the south
| 03SR - Stations (RfL) | Cxxx-NCR-002022 | NCR | ETS - Central slab section cold joint |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2015-09-08 | 2015-08-14 09:13 | -25 | 2015-07-10 08:06 | Civil - Civil Engineering General | 5000 |  | Material | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The central section of the ETS slab was poured on Monday the 6th July. 6 loads (48 M3) had been poured in to the slab before the seventh load was backed up to the mobile pump and a slump test was carried out. The slump value for the seventh load was recorded at 50mm. The concrete mix being used was the C35/45A which is specified as having an S3 slump range (between 80 - 180 mm). The load was rejected. The eighth load was not on site waiting to take the place of the failed seventh and took 35 minutes to arrive. By the time it was backed on to the pump the concrete in the line had cured sufficiently to block it, the line could not be cleared in time to resume the pour and a cold joint formed in the ETS central slab. The MS management advised that the pour had to be stopped and the cold joint would have to be assessed and prepared before the pour could be completed. The cold joint was formed approximately 3.5 linear metres from the CJ of the previous pour (refer to the attached sketch LM/6.7.15/SK01)
| 03SR - Stations (RfL) | Cxxx-NCR-002023 | NCR | 4SU - End Beam BM91 incorrect installation Proposal |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2015-08-14 | 2015-08-06 10:04 | -8 | 2015-07-10 17:11 | Civil - Civil Engineering General | 500 |  | Planning | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Drawing: Cxxx-SWN-S-DDD-CR094_PT002_Z-68428 and Cxxx-SWN-S-DDD-CR094_PT002_Z-68454. The North Wall was cast with Bar Marks 124 (U-Bars), and 107 and 108 (L-Bars) installed as per drawing Cxxx-SWN-S-DDD-CR094_PT002_Z-68454. Note, this drawing refers to sketch in FCD#1964. These bars have 150mm spacings and are locked in place with the cast concrete. Due to this, it was too difficult to install Bar Marks 91 in its design location so BM91, with dimensions of 2135mm and 1800mm, was cut on site and installed, for which a 16mm splice bar (L-Bar) with 500mm leg splice was installed. See attached photo.
| 03SR - Stations (RfL) | Cxxx-NCR-002024 | NCR | ETS - Eastern Slab Pour: 30 minute between loads time lapse |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2015-08-14 | 2015-07-22 10:23 | -23 | 2015-07-15 11:10 | Civil - Civil Engineering General | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During the concrete pour to the eastern slab section of the ETS there was a 50 minute gap between the first load completing its discharge and the second load starting. This was caused due to __ leaving 75 minutes between batching the first and second loads
| 03SR - Stations (RfL) | Cxxx-NCR-002025 | NCR | Secant pile P71 - foreign object cast into pile face |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2015-08-31 | 2015-08-24 16:57 | -7 | 2015-07-15 15:03 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | There appears to be a foreign object cast into the face of Secant P71.
| 03SR - Stations (RfL) | Cxxx-NCR-002026 | NCR | 4SU - Central T-Piece Non-Flush Finish on Joint between adjacent Concrete Pour |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2015-10-21 | 2015-10-20 15:11 | -1 | 2015-07-23 15:31 | Civil - Civil Engineering General | 1500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Drawing: Cxxx-SWN-S-DDD-CR094_PT002_Z-68429 After stripping the Central Wall (T-Piece) section last week it was noticed that the eastern face of the wall did not finish flush will the adjacent Central (North) Wall section. There is a drop of 15mm between the two walls. These walls in this area are 300mm wide, and the adjacent wall that was poured on 18/6/15, which had a 200mm 'return' on the end of the wall where it abuts against the T-piece, did not have a pre-pour survey carried out on the return section only. An as-built survey was carried out on the East face of the T-section, along with the 'return' on the adjacent wall pour, and the results are attached. The T-piece section is all within tolerance, however, the adjacent Central (North) Wall is up to 5mm outside tolerance.
| 03SR - Stations (RfL) | Cxxx-NCR-002028 | NCR | gallow bracket clash with covered ramp base slab 14 |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2015-11-16 | 2015-10-13 15:07 | -34 | 2015-07-16 16:39 | Civil - Civil Engineering General | 500 |  | Design | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The northern end gallow bracket clashes with the top of base slab 14 by 140mm. See attached picture and drawing.
| 03SR - Stations (RfL) | Cxxx-NCR-002029 | NCR | Secant wall pile couplers at incorrect angle |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2015-07-31 | 2015-07-30 11:53 | -1 | 2015-07-16 16:52 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Secant Pile cages 239, 237 & 229 have twisted during plunging and the couplers are angled out of tolerance with the worst at approx 22 deg. See attached pictures.
| 03SR - Stations (RfL) | Cxxx-NCR-002030 | NCR | EIP - trimming of starter bars (BM224) for door nib next to headwall (East facing walls) |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2015-08-28 | 2015-07-23 10:43 | -36 | 2015-07-17 16:29 | Civil - Civil Engineering General | 750 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The starter bars (BM224) for the column next to the headwall in the East facing wall are too short to splice onto.
| 03SR - Stations (RfL) | Cxxx-NCR-002031 | NCR | C&C bay 14 base slab excessive cover |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2015-11-28 | 2015-10-09 11:35 | -50 | 2015-07-20 09:51 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | As Above
| 03SR - Stations (RfL) | Cxxx-NCR-002032 | NCR | 3D model Clash Detection report overdue |  | Crossrail | XRL | PML - Pudding Mill Lane Portal (Central) |  | 2015-11-30 | 2015-11-30 15:49 | 0 | 2015-07-20 13:52 | Mechanical - Mechanical Engineering General | 1500 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | The ‘__ES Gate Recovery Programme’ identifies a revised 3D model Clash Detection report based on coordination between Cxxx-Cxxx to be issued on 12 June 2015. This was not done. The3D model Clash Detection report was not available at the time of surveillance 23 June 2015
| 03SR - Stations (RfL) | Cxxx-NCR-002033 | NCR | No evidence that the interface meetings are taking place with Cxxx |  | Crossrail | XRL | PML - Pudding Mill Lane Portal (Central) |  | 2016-01-23 | 2016-01-06 14:04 | -17 | 2015-07-20 14:13 | Mechanical - Mechanical Engineering General | 1000 |  | Design | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Minutes of interface meetings between Cxxx and Cxxx were not available to demonstrate implementation as required by Works Information 2B part 7.7.7.3
| 03SR - Stations (RfL) | Cxxx-NCR-002034 | NCR | Necking of concrete on Lutz report – RRV Ramp pile P01, P02, P03, P21 and P25 |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2015-12-04 | 2015-11-16 14:00 | -18 | 2015-07-21 09:37 | Civil - Civil Engineering General | 500 |  | Software | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | From the Lutz reports taken from the above pile reports, necking is shown between -16m / -17m. __ have confirmed that this is a glitch in the software. As the CFA auger is being extracted the operation is stopped and the rotary table is lowered down the kelly bar extension, it is at this point the computer thinks the extraction operation is still taking place and therefore appears as necking on the Lutz print out.
| 03SR - Stations (RfL) | Cxxx-NCR-002035 | NCR | 4SU - CRL Centre Box Wall Reinfocement installed incorrectly |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2015-08-23 | 2015-08-18 09:43 | -5 | 2015-07-22 15:49 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Cxxx-SWN-S-DDD-CR094_PT002_Z-68446 Referencing FCD#2072, during the deck concrete pour in the vicinty of gridline 1, BM77 that falls within Central Wall Pour 13 was not installed on the the required skew angle that Gridine 1 follows. A total of 4 bars were installed. Exact spacing of the these bars were not possible to achieve due to the width of the proposed M__ couplers.
| 03SR - Stations (RfL) | Cxxx-NCR-002036 | NCR | Covered ramp base slab bay 14 poor concrete supply & failed slump test concrete used |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2015-11-28 | 2015-10-02 16:54 | -57 | 2015-07-22 16:08 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During covered ramp base slab bay 14 concrete pour, we suffered poor supply of concrete with 2No wagons exceeding their 30min time between loads. See attached. The 1st of the two, where 50 mins had already passed, the wagon arriving late then failed its slump with a reading 200 (range should be 80-180). In an attempt to avoid a cold joint issue this concrete was placed.
| 03SR - Stations (RfL) | Cxxx-NCR-002037 | NCR | EIP - Core walls out of tolerance platform to Intermediate level |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2015-09-25 | 2015-09-17 15:24 | -8 | 2015-07-22 17:25 | Civil - Civil Engineering General | 750 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | There are two locations where the EIP core wall is out tolerance in plan position.
| 03SR - Stations (RfL) | Cxxx-NCR-002038 | NCR | 4SU - Grout Loss in section of Central Wall Pour 12 |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2015-09-08 | 2015-09-03 17:30 | -5 | 2015-07-28 11:34 | Civil - Civil Engineering General | 1000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Central Wall Pour 12 was poured on 11th July 2015. After stripping this the wall, it was notified that there a small section of honeycombing and concrete surface void on the North face of the wall where it abuts against the previously poured Central Wall Pour 11 (west of Pour 12). This void appears to be 23mm deep at the deepest point.
| 03SR - Stations (RfL) | Cxxx-NCR-002039 | NCR | Concrete Finish to Greenway Ramp |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2015-10-26 | 2015-10-05 13:37 | -21 | 2015-07-28 11:12 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | See dwg Cxxx-SWN-S-DDL-CR094_PT002_Z-95010 & Spec: Cxxx-SWN-S-RSP-CR094_PT002-00002 Following a post pour inspection of wall 6 on the Greenway ramp the following defects were observed in localised areas of the wall: -Areas of inconsistent finish -'Bugholes' or blemishes approx 20mm (see attached photos)
| 03SR - Stations (RfL) | Cxxx-NCR-002040 | NCR | Secant Leaks P133-P281 |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2016-01-29 | 2016-01-06 14:04 | -23 | 2015-07-27 10:26 | Civil - Civil Engineering General | 20000 |  | Workmanship | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Following further C&C excavation works more leaks have been noted to the Secant wall between piles 133 - 281. See attached report.
| 03SR - Stations (RfL) | Cxxx-NCR-002041 | NCR | EIP - Crosswall 7 out of position |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2015-09-18 | 2015-09-11 10:42 | -7 | 2015-07-27 17:25 | Civil - Civil Engineering General | 1000 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Crosswall 7 is out of tolerance in plan position
| 03SR - Stations (RfL) | Cxxx-NCR-002042 | NCR | 4SU - Roof Bars cut prior to Crossrail Acceptance |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2015-08-25 | 2015-08-21 10:51 | -4 | 2015-07-28 09:07 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Procedure Problem - Other | Completed |  | FCD#2094 works were carried out, as discussed Cxxx, however, a PMI was not issued from Crossrail (new procedure under PMC 1033). It was just possible to install the BM04a in the north wall with the temporary working platform with a C-dimension of 1990mm. However, due to the location of the existing __ line on the north wall, the 'L-Bar' BM107 and BM108, with a C-dimension of 3535mm, it was not possible to install the BM05a. A total number of 12 BM05a had to be cut and then spliced. These had the C-dimension cut to 1500mm to enable safe installation, and additional splice bars added with minimum splice lengths achieved. This was inspected by Crossrail FE and Cxxx designer.
| 03SR - Stations (RfL) | Cxxx-NCR-002043 | NCR | EIP - Crosswall 3 kicker out of tolerance |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2015-09-25 | 2015-09-21 12:56 | -4 | 2015-07-29 11:22 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The kicker for Crosswall 3 is out of tolerance in plan position by 20 mm.
| 03SR - Stations (RfL) | Cxxx-NCR-002044 | NCR | Uneven level over section of Greenway Ramp Parapet |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2015-12-25 | 2015-11-13 13:35 | -42 | 2015-07-29 16:20 | Civil - Civil Engineering General | 1000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Over a length of approx 1.4m there is an uneven surface ontop of the parapet. The approx level discrepancy between the outside and the inside of the parapet is 25mm.
| 03SR - Stations (RfL) | Cxxx-NCR-002045 | NCR | MGL Abutment South Wall-Wrong Width of Plain Band on Reckli Face |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2016-01-29 | 2015-12-07 08:09 | -53 | 2015-07-31 10:04 | Civil - Civil Engineering General | 1500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | This NCR is refering to the comment raised in the answer to RFI3313 about the 'plain band' width on the South Reckli Wall of the MGL Abutment being 380mm instead of 431mm. The 431mm is not stated on any drawings apart from a sketch in RFI2718. The width being incorrect is due to miscommunication between MPB and __.
| 03SR - Stations (RfL) | Cxxx-NCR-002046 | NCR | FSU – North Wall pour 9. BMs 105 and 121 incorrect placement |  | Crossrail | XRL | PML - Pudding Mill Lane Portal (Central) |  | 2015-10-23 | 2015-10-01 10:59 | -22 | 2015-07-31 19:46 | Civil - Structural Engineering | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Not all the already fixed reinforcement U-bars BM 105 and 121 fitted correctly on the Western extreme of the wall, being their shape and position as described in Cxxx-RFI-003345, Contractor’s Propose Answer. As Cxxx’s response for the RFI mentioned above was that those bars are scheduled correctly, BMs 105 and 121 do not match the original design. Refer to NCR-002046 (1).jpg, NCR-002046 (2).jpg, and Cxxx-RFI-003345.
| 03SR - Stations (RfL) | Cxxx-NCR-002047 | NCR | Concrete Finish Subway Wall 6 |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2015-11-04 | 2015-10-28 17:48 | -7 | 2015-08-05 07:24 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | A localised section of the Greenway subway wall 6 has evidence of surface honeycombing (see attached photo)
| 03SR - Stations (RfL) | Cxxx-NCR-002048 | NCR | MGL East Abutment - South infill end wall out of tolerance |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2015-12-23 | 2015-11-19 15:00 | -34 | 2015-08-05 14:57 | Civil - Civil Engineering General | 1500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The south infill end wall (see attached sketch) has been poured 33mm out of position at the top south east corner. Please see attached additional attachments showing the as built position of the wall. These show that the wall is not plumb and is outside the tolerance at the top east corner and within tolerance at the bottom and top north east corner. There is no step at kicker level. The out of plumb alignment cannot be identified visually. A cover meter survey has also been carried out - See attached
| 03SR - Stations (RfL) | Cxxx-NCR-002049 | NCR | Cut and Cover Tunnel - Missed 100mm Dia UTX Box Out Bay 6 |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2015-12-31 | 2015-12-05 12:02 | -26 | 2015-08-05 14:26 | Civil - Civil Engineering General | 3000 |  | Supervision/Management | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Within the Cut and Cover Tunnel design a 100mm diameter UTX has been specified at a 30m frequency as per attached design drawing (Cxxx-SWN-S-DDA-CR094_PT002_Z-81104) to service the Contract 610 works. The required void forming box out at Bay 6 has not been installed when casting the slab.
| 03SR - Stations (RfL) | Cxxx-NCR-002050 | NCR | North D wall panel N32 waterbar damage |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2015-11-27 | 2015-11-19 15:30 | -8 | 2015-08-05 10:58 | Civil - Civil Engineering General | 2000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | When removing the "waterbar holding channel" from the end face of North D wall panel N32 a fair amount of damage has been encountered to the waterbar. See attached pictures. This is due to the angle in which it had to be removed as P1 didn’t allow it to be removed straight off.
| 03SR - Stations (RfL) | Cxxx-NCR-002051 | NCR | 4SU - North Wall Pour 9A |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2016-08-19 | 2016-02-12 13:03 | -189 | 2015-08-13 10:37 | Civil - Civil Engineering General | 5000 |  | Workmanship | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Please refer to: Drg: Cxxx-SWN-S-DDA-CR094_PT002_C-69103 & Cxxx-SWN-S-DDB-CR094_PT002_Z-69141 & Cxxx-SWN-S-DDD-CR094_PT002_Z-68430 Spec: Cxxx-SWN-S-RSP-CR094_PT002-00002 Clause E20.316 & E30.451 & E30.470 PTR: Cxxx-FCD-1957/2055 & 2199 Upon striking of the shutter and survey the Four Span Underpass North Wall Panel Pour 9A was found to have the following defects: a) Out of positional tolerance b) Excess cover – South face c) Lack of cover – North face d) Not pouring to the centre ridge of the back of concrete wall PVC waterguard Please see attached the As Built survey of the wall, cover meter survey and photo survey of the pour.
| 03SR - Stations (RfL) | Cxxx-NCR-002052 | NCR | CMR Tow Path - MHC4 inlet level |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2015-10-30 | 2015-10-26 13:54 | -4 | 2015-08-11 18:12 | Civil - Civil Engineering General | 1000 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | When the CMR CRL bridge east abutment was constructed a 300mm diameter UPVC pipe was cast within to allow for a cast iron drain pipe to pass through – refer to RFI 2122. Although the level of the cast in UPVC pipe is within 35mm of the design level the steep pitch of the cast in drainage pipe has resulted in the invert level for the inlet to MHC4 being 170mm lower than design – refer to “CRL bridge - East abutment outlet; Photo 1”.
| 03SR - Stations (RfL) | Cxxx-NCR-002053 | NCR | Secant Piles base slab box-out has broken loose during plunging |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2015-10-25 | 2015-10-10 16:44 | -15 | 2015-08-17 14:19 | Civil - Civil Engineering General | 500 |  | Manufacturing Defect | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | It appears that the base slab box out foam has come loose and floated up the pile during plunging. This has been found on the piles detailed below; Pile 31 @ an approximate level of 100.200 Pile 39 @ an approximate level of 100.170 Pile 54 @ an approximate level of 100.520 Pile 60 @ an approximate level of 100.680
| 03SR - Stations (RfL) | Cxxx-NCR-002054 | NCR | Kwikastrip bar out of tolerance |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2015-11-16 | 2015-10-03 14:36 | -44 | 2015-08-18 07:54 | Civil - Structural Engineering | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | At the first landing platform on the greenway ramp the level of the top bar of kwikastrip is out of tolerance with regards to cover. The worst case being approx 20mm between top of bar and top of concrete.
| 03SR - Stations (RfL) | Cxxx-NCR-002055 | NCR | Water control when mixing Aqualite |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2015-11-16 | 2015-10-12 15:19 | -35 | 2015-08-20 13:20 | Civil - Civil Engineering General | 3000 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Defective or inadequate procedure | Completed |  | It was detailed within the Fre lining ITP that 9.5L would be used to mix each 25kg of Aqualite. The precise control of water dosing is not possible. A water feed is tapped in direct and the precise mixing ration controlled at the nozzle.
| 03SR - Stations (RfL) | Cxxx-NCR-002056 | NCR | Repair proceedure detailied in NCR 1985 |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2015-09-30 | 2015-09-24 16:35 | -6 | 2015-08-20 13:25 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Other | Completed |  | In NCR 1985, the repair proceedure states that the D98 mesh is to be fixed to the D wall using promat anchors. The repairs commenced without formal capture of an amendment to this detail. The D98 mesh is now pused (unfixed) into the 4th layer of wet Aqualite.
| 03SR - Stations (RfL) | Cxxx-NCR-002057 | NCR | RRV Attenuation Tank - Crack in unit 22 invertvert |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2016-07-29 | 2016-06-02 11:23 | -57 | 2015-08-24 08:25 | Civil - Civil Engineering General | 1000 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | A small crack in the bottom of the 22nd segment of the Attenuation Tank was discovered post installation. See attached photos The width of the crack was monitor measured at 0.1mm and the length is approx 0.9m, on the 12/08/15.
| 03SR - Stations (RfL) | Cxxx-NCR-002058 | NCR | RRV Attenuation Tank - Bitumen Strip between joints |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2016-02-26 | 2016-01-25 16:26 | -32 | 2015-08-24 08:28 | Civil - Civil Engineering General | 3000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The bitumen sealing strip detailled on McCanns standard detail (see attached) was placed between the attenuation tank units in the incorrect position, this occured on an unknown number of units but can be seen clearly between the access open units.
| 03SR - Stations (RfL) | Cxxx-NCR-002060 | NCR | RRVR Attenuation Tank - Bedding layer |  | Crossrail | XRL | PML - Pudding Mill Lane Portal (Central) |  | 2015-11-27 | 2015-10-23 14:49 | -35 | 2015-08-21 17:07 | Civil - Drainage | 2000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Use of unapproved materials | Completed |  | CRL is aware that the bedding for the RRVR Attenuation Tank has not been carried out in one single layer as per the design detail shown in drawing Cxxx-SWN-R4-DDD-CR094_PT002_Z-95034. Additionally, the tank is not currently resting on a hard surface that should be provided by the ST3 concrete specified in the design for the blinding layer but on a dry concrete mix, present as loose material (see photos attached).
| 03SR - Stations (RfL) | Cxxx-NCR-002061 | NCR | Covered Ramp Damaged Couplers at Bay 12 |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2015-09-07 | 2015-09-04 09:52 | -3 | 2015-08-24 17:01 | Civil - Civil Engineering General | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | __ identified 5 number damaged Diaphragm Wall B32 dowel couplers under Cxxx-FCD-002116. These couplers were installed as part of the wall construction undertaken by Contract 248. 4 of the damaged couplers were simply due to damaged threads and 1 coupler was orientated upwards so that an installed dowel would be aligned outside of the slab pour. This prevented installation of the male coupler mounted Bar Mark 15 1300mm straight dowel bars at the locations shown in the attached sketch.
| 03SR - Stations (RfL) | Cxxx-NCR-002062 | NCR | ETS - Pour 2; 28 day cube strength non-conformance |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2015-10-30 | 2015-09-15 09:30 | -45 | 2015-09-08 08:50 | Civil - Civil Engineering General | 1000 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | A set of cubes taken during the “ETS - Pour 2: Central Section” has failed its 28 day characteristic strength requirement. The concrete reference is C35/45A and the cube reference PML 1631. This was the first set of cubes taken during the pour and the corresponding concrete would have been placed on the east end of the central section –refer to the attached sketch for clarity. The 28 day characteristic strength requirement for a C45 concrete is a minimum of 41 N/mm2. Set PML 1631 reached an average of 38.2 N/mm2 at 28 days. As a result this has led to a marginal non-conformance on the running mean of 6 compliance. The following 28 day results achieved minimum strength criteria but there has been a further dip and marginal non-conformance by 0.6 and 0.9N’ - refer to the attached schedule.
| 03SR - Stations (RfL) | Cxxx-NCR-002063 | NCR | Stray Current Collector System - Drawing Approval |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2015-10-30 | 2015-09-02 11:53 | -58 | 2015-08-27 13:08 | Civil - Civil Engineering General | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | __'s specialist Sub-Contractor Antagrade (through Colas), have installed the Stray Current Collector Cable, with Diode Unit and Fabricated Cover without an approved Design. The Stray Current Collector Cable Installation Design Ref. Cxxx-MRG-R4-RSP-CR094_WS111-50002 was not officially approved until 25/08/2015.
| 03SR - Stations (RfL) | Cxxx-NCR-002064 | NCR | 4SU - South Wall Pour 3 Honeycombing |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2015-11-14 | 2015-11-09 10:43 | -5 | 2015-09-03 16:44 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Drawing: Cxxx-SWN-S-DDD-CR094_PT002_Z-68428 Specification: Cxxx-SWN-S-RSP-CR094_PT002-00002 As previously discussed with Crossrail and Cxxx, it was noticed that there is some concrete honeycombing located on the south face of the south wall of pour 3, see attached photo. This does not achieve F2 finish.
| 03SR - Stations (RfL) | Cxxx-NCR-002065 | NCR | Necking of Piles - Track Support Slab |  | Crossrail | XRL | PML - Pudding Mill Lane Portal (Central) |  | 2015-11-17 | 2015-11-13 13:45 | -4 | 2015-09-03 14:08 | Civil - Civil Engineering General | 2000 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | After reviewing __’s construction records for Phase 1 of the Track Support Slab piling works, it would appear that a number the CFA piles show signs of ‘necking’. The Lutz profiles for piles P302, 303, 304, 305, 311, 318, 322, 351 all display this narrowing between approximately 16 to 16.5m from the top of the pile. Pile P310 shows narrowing at approximately 25m and P351 also appears to suggest that the pile concrete finishes at 26m (the design depth of the pile is 28.75m).
| 03SR - Stations (RfL) | Cxxx-NCR-002066 | NCR | 4SU - BM122,112 and BM10,28 North & South Walls incorrectly installed |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2015-10-09 | 2015-09-17 13:45 | -22 | 2015-09-07 08:01 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Drawing: Cxxx-SWN-S-DDD-CR094_PT002_Z-68429 & Cxxx-SWN-S-DDD-CR094_PT002_Z-68430 BM122 and BM112 in the north wall, and BM10 and BM28 in the south wall have been incorrectly installed in the B2 position as opposed to the T2.
| 03SR - Stations (RfL) | Cxxx-NCR-002067 | NCR | NR Drainage-150 drainage pipe from CRL2 Wall to NRE8.1 |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2016-01-29 | 2015-12-11 08:40 | -49 | 2015-09-07 07:31 | Civil - Drainage | 600 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | This NCR relates to the drainage run between NRTE8.0 and NRTE8.1. The straight alignment shown on all the drainage plans between the two manholes was difficult to achieve through the 32mm starter bars of the wall. A much larger gap was left between the starter bars than the design of 150mm spacing but with the outside diameter of the pipe being 180mm and also the extra slope distance of the pipe when the pipe is projected through the wall at a 49 degree angle instead of 90 degrees. See attached sketch from 150914. This issue should have been highlighted prior to the construction of the wall and pile cap.
| 03SR - Stations (RfL) | Cxxx-NCR-002068 | NCR | Greenway Ramp Wall 5 - Reduced concrete cover |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2015-12-18 | 2015-12-04 09:17 | -14 | 2015-09-09 12:41 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Following a cover meter survey we have found that a localised section of wall 5 (west of wall 2) has reduced cover. Cover ranges from 35 to 39mm. The design nominal cover is 50mm with a tolerance of +/-10mm
| 03SR - Stations (RfL) | Cxxx-NCR-002069 | NCR | Greenway Wall 6 |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2015-10-30 | 2015-10-26 10:36 | -4 | 2015-09-15 06:51 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | Spec: Cxxx-SWN-S-RSP-CR094_PT002-00002 Clause E10.680 On the 14/07/15 38 minutes elapsed between the 2nd and 3rd load of concrete. Please find attached - Concrete Pour sheet - Photographs post pour.
| 03SR - Stations (RfL) | Cxxx-NCR-002070 | NCR | Greenway Western Transition Slab |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2015-10-30 | 2015-10-07 13:57 | -23 | 2015-09-15 06:52 | Civil - Civil Engineering General | 500 |  | Planning | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | Spec: Cxxx-SWN-S-RSP-CR094_PT002-00002 Clause E10.680 On the 15/7/15 45 minutes elapsed until the last load. Please find attached: - Concrete Pour sheet - Post pour photographs
| 03SR - Stations (RfL) | Cxxx-NCR-002071 | NCR | Greenway Western Deck |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2015-10-30 | 2015-10-10 11:06 | -20 | 2015-09-15 06:53 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | Spec: Cxxx-SWN-S-RSP-CR094_PT002-00002 Clause E10.680 On the 19/8/15 53 minutes elapsed between 4th and 5th delivery of concrete. Please find attached: - Pour sheet records - Photographs post pour
| 03SR - Stations (RfL) | Cxxx-NCR-002072 | NCR | EIP - Concrete Cube strength for 10mm aggregate |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2016-01-08 | 2015-12-16 08:23 | -23 | 2015-09-14 08:12 | Civil - Civil Engineering General | 2000 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | 1 sample of C50/50B and 1 sample of sample of C40/50B FR have marginally failed to meet the minimum strength requirements of BS 8500 of 46 N the samples achieved 43.8 and 44.5 N/mm2 respectively.
| 03SR - Stations (RfL) | Cxxx-NCR-002073 | NCR | Urban Realm GWY Reduced Cover to Subway Wall 6 |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2016-04-13 | 2016-03-23 11:38 | -21 | 2015-10-01 13:43 | Civil - Civil Engineering General | 2000 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | This NCR relates to an area of reduced cover which is out of tolerance on Subway Wall 6 Greenway Ramp. The area has since been resurveyed using __ 331 and drilled at three locations to determine depths (please find attached NCR 2073 dip survey and __ cover survey). The previous survey was conducted using a __ Micro Covermeter 7000 this was found to be inaccurate (see attached cover survey photos). Whilst the __ was found to accurate there are still sections of the Subway Wall that are out of tolerance.
| 03SR - Stations (RfL) | Cxxx-NCR-002074 | NCR | Four Span Underpass - GL5 Roof Parapet Pour |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2015-10-23 | 2015-10-13 10:52 | -10 | 2015-09-16 16:11 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | Please refer to: Drg: Cxxx-SWN-S-DDA-CR094_PT002_C-69103 Spec: Cxxx-SWN-S-RSP-CR094_PT002-00002 Clause E10.680 Fresh concrete was placed against in situ concrete outside of the specified 30 minute time window (between the 2nd & 3rd loads). Concrete was placed at 46 minutes and the face was still live at the time of placement.
| 03SR - Stations (RfL) | Cxxx-NCR-002075 | NCR | C&C2 - Fire Lining Level |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2015-12-27 | 2015-11-02 14:51 | -55 | 2015-09-28 17:48 | Civil - Civil Engineering General | 1500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Previous Construction - Problems based on previous construction errors | Completed |  | In reference to Cxxx-SWN-S-DDD-CR094_PT002_Z-81132 detail 18 showing the diaphragm wall fireproofing penetrating 50mm below the first stage concrete. An as-built survey has been carried out on the bottom of the completed fireproofing in the C&C2 east bound tunnel. The attached spreadsheet shows that the 50mm penetration isn't achieved in a number of locations. In the worst case, the fireproofing is 32mm above the first stage concrete design level.
| 03SR - Stations (RfL) | Cxxx-NCR-002077 | NCR | Cut & Cover Tunnel Phase 3 Central Wall Panels 7A / 7B Cover Issues |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2015-10-30 | 2015-10-22 14:52 | -8 | 2015-09-24 13:16 | Civil - Civil Engineering General | 1000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | During the pre-pour inspection of Central Wall Panel 7 B it was found that the cover on both faces of the West end were out of the specified tolerance (45mm +/- 10mm). On the South face it was found that 80mm cover available at the West end of the pour which came back to maximum cover (55mm) at a distance of 1.9m, and extending down to the top of the Emergency Walkway pull out connection bars. On the North face it was found to be 30mm and minimum cover (35mm) was achieved at a distance of 450mm, and that this extended from the top of the wall 3.1m.
| 03SR - Stations (RfL) | Cxxx-NCR-002078 | NCR | Covered Ramp - North Upstand Panel 5 / 6 Wall Alignment |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2015-10-30 | 2015-10-07 16:38 | -23 | 2015-09-24 13:09 | Civil - Civil Engineering General | 500 |  | System Defect | Use As-Is | 4 (0.5-3k) | Complete | Previous Construction - Other | Completed |  | After reviewing the North Upstand kicker for Pour 5 / 6 where the Secant Piles and Capping Beam East return in Bay 15, it has been found that the upstand wall position has a difference of 17 – 26mm towards the track alignment. Monitoring records from the Secant pile Inclinometers in this area show lean of 7mm at top of piles. The worst case (26mm) position on the corner of the return aligns with Ch 14.519 of the running track. The offset from central alignment of Eastbound running track is 2.992m and 2.275m from centre of nearest track. At this Chainage the track cant/superelevation is 32mm towards the central wall / away from North wall.
| 03SR - Stations (RfL) | Cxxx-NCR-002079 | NCR | Greenway East box walls 28 day strength result PML1565 |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2015-12-30 | 2015-10-27 11:41 | -64 | 2015-10-01 13:58 | Civil - Civil Engineering General | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | Concrete sample PML1565 returned a failed 28 day strength result. The sample was taken for the Greenway East Box pour (walls 3, 4, 5 & 6) on the 8/6/15. The C40/50A mix returned a cube strength result of 40.3N/mm2
| 03SR - Stations (RfL) | Cxxx-NCR-002080 | NCR | Fire lining - Aqualite cube testing |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2016-05-27 | 2016-05-26 09:30 | -1 | 2015-09-25 16:27 | Civil - Civil Engineering General | 10000 |  | Supervision/Management | Repair | 2 (6-60k) | Complete | Management Problem - Other management problem | Completed |  | As the fire lining aqualite machines were not able to demonstrate a measured mix ratio, it was suggested that cubes could be taken to verify 40N. Taking cubes has not been practicle as the material is not suitable for placing in moulds. As a result the cubes are all falling well short of the suggetsed 40N on __s data sheet.
| 03SR - Stations (RfL) | Cxxx-NCR-002081 | NCR | EIP - Insufficient cube strength on Vent Wall Pour 2 |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2015-12-18 | 2015-09-30 13:54 | -79 | 2015-09-28 13:34 | Civil - Civil Engineering General | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | 1 sample of C50/50B has marginally failed to meet the minimum strength requirements of BS 8500 of 46 N, with the samples achieving an average 28 day strength of 45.5 N/mm2.
| 03SR - Stations (RfL) | Cxxx-NCR-002082 | NCR | Greenway East Box walls 28 day strength result PML1566 |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2016-01-04 | 2015-10-27 11:43 | -69 | 2015-10-01 13:57 | Civil - Civil Engineering General | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | Concrete sample PML1566 returned a failed 28 day strength result. The sample was taken for the Greenway East Box pour (walls 3, 4, 5 & 6) on the 8/6/15. The C40/50A mix returned a cube strength result of 38.9N/mm2
| 03SR - Stations (RfL) | Cxxx-NCR-002083 | NCR | Covered Ramp and 4SU Interface - North Wall Dowel Bars incorrectly installed |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2015-12-11 | 2015-10-22 19:08 | -50 | 2015-10-05 11:31 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Supervision - Insufficient supervision | Completed |  | Drawings: Cxxx-SWN-S-DDD-CR094_PT002_Z-68430 and Cxxx-SWN-S-DDD-CR094_PT002_Z-60405 Specifications: Cxxx-SWN-S-RSP-CR094_PT002-00002 revison 8 Clause E30.451 BM92 on the drawing Cxxx-SWN-S-DDD-CR094_PT002_Z-68430 was installed in the incorrect location in the 4SU North Wall pour (pour 9B). These dowel bars were installed centrally in the 4SU North Wall (800mm wide wall) as opposed to centrally for the Covered Ramp North Wall pour (500mm wide wall). These bars do not fit within the reinforcement cage of the Covered Ramp north wall.
| 03SR - Stations (RfL) | Cxxx-NCR-002084 | NCR | EIP - C1 columns at Ground level |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2015-12-18 | 2015-12-11 08:25 | -7 | 2015-10-02 09:05 | Civil - Civil Engineering General | 1000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Three C1 columns on the North side of the EIP have been cast outside of tolerance.
| 03SR - Stations (RfL) | Cxxx-NCR-002085 | NCR | 4SU - Reinforcement in Roof upstands not adjusted for Handrail Anchors |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2015-12-18 | 2015-12-05 12:20 | -13 | 2015-10-31 11:29 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | Drawings: Cxxx-SWN-S-DDD-CR094_PT002_Z-68430 Cxxx-SWN-S-DDD-CR094_PT002_Z-68428 Cxxx-SWN-S-DDB-CR094_PT002_Z-69141 Specifications: Cxxx-SWN-S-RSP-CR094_PT002-00002 Clause E05.235 PTRs: FCD#2183 and FCD#2198 The centres of the handrail posts and holding down (HD) bolts were not marked out prior to tying the reinforcement in the upstands. Although the longitudinal reinforcement was adjusted in order to miss the bolts, the transverse capping bars were overlooked.
| 03SR - Stations (RfL) | Cxxx-NCR-002086 | NCR | EIP - Eastern Core Wall with non-specified finish |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2016-01-15 | 2016-01-11 12:17 | -4 | 2015-10-09 15:46 | Civil - Structural Engineering | 1500 |  | Supervision/Management | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Drawings: Cxxx-SWN-S-DDD-CR094_PT002_Z-80411 Specifications: Cxxx-SWN-S-RSP-CR094_PT002-00002 The Eastern Core Wall was poured 01/10/15. Upon striking the shutters, it was noticed there was a surface defect on both faces of the wall as per attached photo. Also see attached plan for location.
| 03SR - Stations (RfL) | Cxxx-NCR-002087 | NCR | Covered Ramp - Honey Combing Found at Central Wall Panel 16A |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2015-12-25 | 2015-12-16 11:14 | -9 | 2015-10-06 09:11 | Civil - Civil Engineering General | 1000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Some 'honey combing' has been identified during post pour inspection of the Covered Ramp Central Wall Panel 16A. The area identified is just above the kicker in the South East corner of the wall panel pour.
| 03SR - Stations (RfL) | Cxxx-NCR-002088 | NCR | Four Span Underpass - Westbound Tunnel - Platform to Track Stairs - missing step |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2015-11-13 | 2015-10-21 08:15 | -23 | 2015-10-06 15:26 | Civil - Civil Engineering General | 500 |  | Incomplete Works | Repair | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | Please refer to: Drg: Cxxx-SWN-S-DDD-CR094_PT002_Z-69191 PTR: RFI-3444 & 3492 The Westbound tunnel platform to track mass fill stairs has been constructed with 6No steps instead of the now required 7No steps (see attached photo). The steps constructed are to the correct dimensions as detailed in RFI-3444 but is 1No short at the base when compared to the sketch issued in RFI-3492.
| 03SR - Stations (RfL) | Cxxx-NCR-002089 | NCR | Four Span Underpass - Failure of 2No handrail anchor fixings |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2015-11-15 | 2015-11-10 12:20 | -5 | 2015-10-08 10:44 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Repair | 4 (0.5-3k) | Complete | Management Problem - Misunderstand the definition of the requirement | Completed |  | Please refer to: Drg: Cxxx-SWN-S-DDB-CR094_PT002_Z-69141 & Cxxx-MRG-C-DWG-CR094_WS111-50047 PTR: Cxxx-RFI-1902 2No handrail anchor fixings failed during tension load testing on the Four Span Roof South Upstand due to over loading (see attached photos).
| 03SR - Stations (RfL) | Cxxx-NCR-002090 | NCR | EIP - Doorway width at Platform Level |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2016-03-29 | 2016-02-24 09:04 | -34 | 2015-10-14 14:46 | Civil - Civil Engineering General | 1500 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Conflicting information on drawings | Completed |  | The kicker for the door opening at platform level in the East Facing Wall has been cast with the dimension width as per drawing no. Cxxx-SWN-S-DDA-CR094_PT002_3-80101-C01 Platform Level. As a result the doorway width at kicker level has the dimension of 2100mm. However, drawing no Cxxx-SWN-S-DDB-CR094_PT002_Z-80201-C01 Sections B&E shows the door width as 2160mm. This discrepancy in the GA drawings, between Cxxx-SWN-S-DDA-CR094_PT002_3-80101 C01 and Cxxx-SWN-S-DDB-CR094_PT002_Z-80201 C01 lead to kicker being cast protruding 60mm inside the door opening. The doorway was constructed to the plan dimensions as we thought correct at the time of construction.
| 03SR - Stations (RfL) | Cxxx-NCR-002091 | NCR | Cut and Cover Phase 2B Emergency Walkway Column Out of Position |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2015-11-27 | 2015-11-05 20:27 | -22 | 2015-10-09 14:21 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Verification Problems - Other | Completed |  | It has been identified during the pre-pour survey that the Emergency Walkway Stub Column WB62 is out of position (please see attached sketch for location and asbuilt). All movement is towards the Central Diaphragm Wall and away from the running track. The worst case being the North East corner with a difference of 24mm from design. As the reason for the misalignment is the cast slab coupler position, this cannot be adjusted without significant re-work.
| 03SR - Stations (RfL) | Cxxx-NCR-002092 | NCR | EIP - South Lift Shaft Wall Honeycombing |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2016-01-14 | 2016-01-11 12:27 | -3 | 2015-10-16 11:25 | Civil - Civil Engineering General | 3000 |  | Supervision/Management | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Drawings: Cxxx-SWN-S-DDD-CR094_PT002_Z-80411 Specifications: Cxxx-SWN-S-RSP-CR094_PT002-00002 The South Lift Shaft walls for the ground to first floor were poured on 16/9/15. After striking the falsework, it was noticed there was localised honeycombing in a section of the wall. Please see attachments for the locations and photos.
| 03SR - Stations (RfL) | Cxxx-NCR-002094 | NCR | EIP - Intermediate Concrete Slab Levels |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2016-07-08 | 2016-06-30 14:51 | -8 | 2016-05-03 14:36 | Civil - Civil Engineering General | 2000 |  | Planning | Use As-Is | 4 (0.5-3k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | Drawing: Cxxx-SWN-S-DDA-CR094_PT002_2-80102 After pouring the Intermediate level slab, it was picked up on an as-built survey that the levels of the floor were out of tolerance as per attached drawing. A survey on soffit shows the levels have dropped in a localised area.
| 03SR - Stations (RfL) | Cxxx-NCR-002095 | NCR | A number of Re-injecto tubes in the Cut and Cover/Covered Ramp base slabs have failed to pass water through post-concreting |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2016-04-29 | 2016-04-29 17:22 | 0 | 2015-10-14 14:28 | Civil - Civil Engineering General | 6000 |  | Damaged | Use As-Is | 3 (3-6k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | With regards to the request from Cxxx to test inject the Re- injecto tubes with water in NCR 1961, a number of Re-injecto tubes in the Cut and Cover Ph3/Covered Ramp base slabs have failed to pass water through, post slab construction. (See attached sketch). All re-injecto tubes were tested prior to concreting and all passed water through. Further to this NCR __ have investigated where the blockage has occured inside the injecto tubes as per Cxxx's request. This was done by inserting a length of tying wire inside the tube until it stopped and the lengths recorded. (See attached drawing)
| 03SR - Stations (RfL) | Cxxx-NCR-002096 | NCR | Connection detail at roof slab in CnC Ph3 not as per design |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2015-11-27 | 2015-11-20 16:46 | -7 | 2015-10-12 15:46 | Civil - Civil Engineering General | 500 |  | System Defect | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | The roof slab connection detail at secant piles in Cut and Cover Phase 3 is not constructed as per Detail 1 in drawing Cxxx-SWN-S-DDD-CR094_PT002_Z-71321. The shear key has been cut 50mm down from the top of the slab and 50mm up from the soffit. (See attached sketch)
| 03SR - Stations (RfL) | Cxxx-NCR-002097 | NCR | Covered ramp coupler levels bays 10-15 south wall |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2015-11-27 | 2015-11-16 13:17 | -11 | 2015-10-13 16:17 | Civil - Civil Engineering General | 3000 |  | Supervision/Management | Repair | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | Due to a combination of design scheduling and fabrication errors of the south wall roof deck U-bar couplers to covered ramp bays 10 – 15 we have large areas of reduced cover to the top and bottom of the 500mm roof deck.
| 03SR - Stations (RfL) | Cxxx-NCR-002098 | NCR | CRL - Retaining Wall 1 - Unable to achieve handrail anchor embedment depth |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2015-11-30 | 2015-11-10 12:12 | -20 | 2015-10-14 17:16 | Civil - Civil Engineering General | 500 |  | Planning | Repair | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Please refer to: Drg: Cxxx-MRG-C-DWG-CR094_WS111-50047 & Cxxx-SWN-S-DDC-CR094_PT002_Z-31200 & Cxxx-SWN-S-DDD-CR094_PT002_Z-31400 One number hole drilled for a __ S/S sleeve handrail anchor in the CRL 1 Retaining wall failed to reach the correct depth due to the presence of vertical reinforcement. A depth of 140mm was achieved.
| 03SR - Stations (RfL) | Cxxx-NCR-002099 | NCR | Cxxx - Water leaking through interface between 11KV plunge column and structural slab |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2015-11-30 | 2015-11-16 10:12 | -14 | 2015-10-21 17:25 | Civil - Civil Engineering General | 5000 |  | Damaged | Repair | 3 (3-6k) | Complete | Supervision - Insufficient supervision | Completed |  | It has been observed water is seeping up through the interface between one of the plunge columns in the 11KV Box (westbound) and the structural base slab. This interface detail shows waterbar connection detail, refer drawing Cxxx-SWN-S-DDD-CR094_PT002_Z-71323.
| 03SR - Stations (RfL) | Cxxx-NCR-002100 | NCR | Low concrete strengths |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2016-02-01 | 2016-01-21 11:25 | -11 | 2015-10-16 08:08 | Civil - Civil Engineering General | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | __ are currently experiencing a dip in strengths with the following structural concrete mixes MPB are receiving from __’s Canning town Plant C34/45A 10mm DLR Bridge Abutment Walls and Pile Caps C40/50AFR 10mm Deck and Slab mix C40/50B 10mm Piers, Walls and Abutments C40/50B 10mm FR Piers walls and Abutments This dip in strengths has resulted in a Statistical running mean of 6 failures on 4 mixes and 3 marginal individual 28 day cube failures on 2 mixes. The 4 individual failures relate to the following pours EIP – headwall 10th July 2015 achieved 43.8N/mm2 at 28 days but achieved 52.7N/mm2 at 56 days 4 Span - columns w135,136 poured on the 14th July 2015. The 28 day cubes achieved 43.5N/mm2 and the 56 day achieved 58.9N/mm2. 4 span - north wall pour 8 poured 11th July 2015. The 28 day cube achieved 45.1N/mm2 and the 56 day cube achieved 52.6N/mm2 4 span - section wall poured on the 11th July 2015. The 28 day cube achieved 44.5N/mm2 and the 56 day cube achieved 48.6N/mm2. The 4 sets failed to achieve the minimum 28 day strength of 46 N/mm2 but achieved compliance at 56 days. All other mixes are currently demonstrating compliance with the specification but only marginally. Based on current 7 day strengths and current rate of strength gain there is still potential for there to be the occasional marginal 28 day failures.
| 03SR - Stations (RfL) | Cxxx-NCR-002101 | NCR | EIP - Ground Floor Slab cracking on soffit |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2016-11-15 | 2016-09-26 09:21 | -50 | 2015-10-29 09:22 | Civil - Civil Engineering General | 3000 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | External Phenomenon - Not Defined | Completed |  | Drawings: Cxxx-SWN-S-DDA-CR094_PT002_1-80103 Specifications: Cxxx-SWN-S-RSP-CR094_PT002-00002 revison 8 During an inspection after stripping the soffit of the EIP ground floor, it was noticed that there was excessive cracking ( > 0.3mm). The largest width crack was measured as 0.45mm. A crack map has been created to record the locations and is attached.
| 03SR - Stations (RfL) | Cxxx-NCR-002102 | NCR | Marshgate Lane Bridges - Fabrication error in clearance between flange plates |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2016-01-29 | 2016-01-20 14:49 | -9 | 2015-10-20 08:42 | Civil - Civil Engineering General | 500 |  | Manufacturing Defect | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Please refer to: Drg: Cxxx-SWN-S-DDB-CR094_PT002_Z-51200 & Cxxx-MRG-S-DWG-CR094_WS111-50486 Survey Drg: Cxxx-MRG-SRV-SK-CR094-10995-03 The Marshgate Lane Bridges (Crossrail Eastbound, Westbound & __ Up Electric) have been fabricated out of tolerance when working to a line deviation of +/-10mm standard for each beam. Please see attached Cxxx as built survey of the three bridges. This may impact the proposed design gauge clearance which varies according to each bridge (Ref: Cxxx-SWN-S-DDB-CR094_PT002_Z-51200).
| 03SR - Stations (RfL) | Cxxx-NCR-002103 | NCR | Procedure for the inspection of remedial works |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2015-12-04 | 2015-12-02 20:45 | -2 | 2015-10-23 13:32 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Supervision - Insufficient supervision | Completed |  | This NCR is being raised to cover the procedural failure in relation to NCRs 1036, 1084 and 1095, raised in 2012. These NCRs were raised were raised to record minor defects in the South Upstand Wall RC works. The remedial works were carried out, but there is no records of the actual remedial work done or any inspections carried out by the Crossrail Field Engineers. Further inspections carried out week commencing 19/010/15 by Crossrail and __, but these repair works were not able to be identified, as they have been buried since 2012 under backfill.
| 03SR - Stations (RfL) | Cxxx-NCR-002104 | NCR | Pressurisation fan flow rates |  | Crossrail | XRL | PML - Pudding Mill Lane Portal (Central) |  | 2015-12-04 | 2015-11-30 16:09 | -4 | 2015-10-26 11:48 | Mechanical - Heating Ventilation & Air Conditioning | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | NCR has been raised to highlight the discrepancy between pressurisation fan flow rates and to ensure that the issue has been corrected. For details refer to document ref. no. Cxxx-XRL-O4-RGN-CR001-50074.
| 03SR - Stations (RfL) | Cxxx-NCR-002105 | NCR | attenuators casing thickness |  | Crossrail | XRL | PML - Pudding Mill Lane Portal (Central) |  | 2015-12-03 | 2015-11-30 15:59 | -3 | 2015-10-26 11:53 | Mechanical - Heating Ventilation & Air Conditioning | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | NCR has been raised to ensure that this alteration to the attenuators casing thickness is formally captured through the MCR process. For details refer to document ref. no. Cxxx-XRL-O4-RGN-CR001-50074.
| 03SR - Stations (RfL) | Cxxx-NCR-002106 | NCR | Four Span Underpass - North CRL Wall/Deck Concrete Finish GL4-5 |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2016-04-30 | 2016-04-23 11:05 | -7 | 2015-10-28 17:01 | Civil - Civil Engineering General | 5000 |  | Workmanship | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Please refer to: Drg: Cxxx-SWN-S-DDA-CR094_PT002_A-69101 & Cxxx-SWN-S-DDB-CR094_PT002_Z-69201 Spec: Cxxx-SWN-S-RSP-CR094_PT002-00002 Clause E41.200 On the North face of the CRL Deck pour 2 an F2 finish was not achieved due to a visible step and overspill of concrete. Attached photo IMG_0956 shows finish of the deck.
| 03SR - Stations (RfL) | Cxxx-NCR-002107 | NCR | OPLC - Community Heating Concrete Sleeve (West) Air Pressure Test Failure |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2015-11-11 | 2015-11-02 13:10 | -9 | 2015-10-28 14:46 | Civil - Utilities Engineering | 1000 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | Please refer to: Drg: Cxxx-SWN-U-DDA-CR094_PT002_Z-95005 Spec: __ 024000 PTR: Cxxx-FCD-1912 When air pressure tested as a complete 55m run the West length of 525mm concrete sleeve for the OPLC Community Heating fails (see attached sketch).
| 03SR - Stations (RfL) | Cxxx-NCR-002108 | NCR | Secant pile couplers out of tollerance but used as is |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2015-12-11 | 2015-10-29 15:59 | -43 | 2015-10-27 15:12 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Upon review of the as-built location drawings for Secant wall couplers to roof slab it has been noted that piles P59 & P92 are 5mm & 7mm out of tollerance. They are just outside the -50mm tollerance. However, these fitted on site with no issues.
| 03SR - Stations (RfL) | Cxxx-NCR-002109 | NCR | Damaged coupler in bay 7 roof slab south wall |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2015-11-27 | 2015-11-04 18:32 | -23 | 2015-10-27 16:40 | Civil - Civil Engineering General | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | In C&C bay 7 south wall roof slab we have identified a coupler that has been damaged. see attached picture.
| 03SR - Stations (RfL) | Cxxx-NCR-002111 | NCR | RRVR Attenuation Tank- Spigot pipe connection to attenuation tank end unit |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2016-01-01 | 2015-12-10 13:58 | -22 | 2015-11-02 17:08 | Civil - Drainage | 1000 |  | Manufacturing Defect | Repair | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | When trying to insert a spigot stub pipe into the RRV attenuation tanks end units opening, it was found that the concrete pipe (450mm internal dia) would not fit inside the 600mm opening. The external dimension of the pipe was found to be 4mm greater than that of the precast units open. The sub-contractor decided without consulting __ to chip 10mm off the top and sides of the pipe to make it fit, this pipe was removed within 24 hours. __ have discussed with __s who confirmed the opening should be cut on the bottom and one side by 10-15mm to allow the pipe to be inserted. McCanns guaranteed this would not compromise the structural integrity or design lift of the unit.
| 03SR - Stations (RfL) | Cxxx-NCR-002112 | NCR | C&C2a - Roof Slab back fill |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2016-01-11 | 2015-12-01 10:53 | -41 | 2015-10-29 12:44 | Civil - Civil Engineering General | 1000 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Misunderstand the definition of the requirement | Completed |  | The C&C2a roof slab has been back filled with class 1a material and compacted to requirement of Series 600 to compaction method as prescribed in Table 6/4 method 2. However, a typo error was recorded on number of passes whilst completing earthwork check sheets, which is amended and noted.
| 03SR - Stations (RfL) | Cxxx-NCR-002113 | NCR | C&C roof slab bay 12 - missing coupler in north wall |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2015-11-13 | 2015-11-04 11:17 | -9 | 2015-10-30 14:41 | Civil - Civil Engineering General | 1000 |  | Incomplete Works | Repair | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | We have itentified 3 No couplers missing for the roof slab to bay 12 in the north wall. see attached plan location.
| 03SR - Stations (RfL) | Cxxx-NCR-002114 | NCR | Four Span Underpass - Stair Core - Missing RCS from stair riser |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2016-01-08 | 2015-12-01 13:37 | -38 | 2015-10-30 14:38 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Please refer to: Drg: Cxxx-SWN-S-DDD-CR094_PT002_Z-68425 & Cxxx-SWN-S-DDD-CR094_PT002_Z-69191 PTR: Cxxx-FCD-1914 The proposed reinforcement continuity system in FCD-1914 for the stair riser (see attached sketch) was not installed as part of the wall pours leaving no pull out bars available.
| 03SR - Stations (RfL) | Cxxx-NCR-002115 | NCR | Continuing with construction before closing Cxxx-NCR-002097 - C+C3 roof |  | Crossrail | XRL | PML - Pudding Mill Lane Portal (Central) |  | 2015-12-04 | 2015-11-26 19:26 | -8 | 2015-11-02 14:49 | Structural Engineering - Concrete Member | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Personnel Error - Violation of requirement or procedure | Completed |  | Pouring concrete into C+C3 roof slab bay 12 without closing Cxxx-NCR-002097. No verbal approval from Field Engineering or written agreement with FDC.
| 03SR - Stations (RfL) | Cxxx-NCR-002116 | NCR | MGL East Abutment - Reckli finish to south face |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2016-06-03 | 2016-06-02 12:13 | -1 | 2015-11-02 17:02 | Archaeology - General | 2000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The south face of the Marshgate Lane East Abutment has been constructed without continuity between the reckli finish on the abutment section and the top curtain/ballast wall section of the structure.
| 03SR - Stations (RfL) | Cxxx-NCR-002117 | NCR | Missing couplers in bay 11 roof slab at SUW |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2015-12-11 | 2015-12-05 13:43 | -6 | 2015-11-03 15:28 | Civil - Civil Engineering General | 2000 |  | Supervision/Management | Repair | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | 4no couplers have not been installed during SUW construction in roof bay 11. The location is as attached (8.1m west from the bay 12 CJ)
| 03SR - Stations (RfL) | Cxxx-NCR-002118 | NCR | Couplers clashing with top mat in capping beam |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2015-12-17 | 2015-12-05 13:57 | -12 | 2015-11-05 09:25 | Civil - Civil Engineering General | 2000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | With reference to FCD 1902 and more recently FCD 2225, the couplers in the north upstand wall for the roof slab were clashing with the top mat in the capping beam. This situation occured in two areas (Bay 10 & 11), however FCD 1902 only mentioned Bay 10. A solution was given for Bay 10 (see FCD 1902) and the contractor assumed this would be the solution for Bay 11 as well. However, in Bay 11 the holes could not be drilled 600mm deep as the wall is 500mm, hence FCD 2225 was raised to address this issue. Cxxx believe this is an NCR as the contractor should have notified Cxxx of the problem in the first instance and before progressing works without installing couplers.
| 03SR - Stations (RfL) | Cxxx-NCR-002119 | NCR | Footsteps found in bay 2 roof slab |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2016-03-18 | 2016-02-23 14:00 | -24 | 2015-11-04 13:26 | Civil - Civil Engineering General | 1000 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | There have been footprints identified in a localised area of the roof slab in the cut and cover phase 3 bay 2. These were first found once the curing protection was removed.
| 03SR - Stations (RfL) | Cxxx-NCR-002120 | NCR | Cxxx - Damaged concrete in structural base slab EIP/11KV Box interface |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2015-12-19 | 2015-11-25 16:29 | -24 | 2015-11-05 07:40 | Structural Engineering - Concrete Member | 3000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Previous Construction - Problems based on previous construction errors | Completed |  | The concrete slab has been damaged exposing the steel reinforcement in the structural base slab at the interface between the EIP and 11KV Box in the WB portal. The location of the damaged concrete lays directly on the expansion joint and pressure relief drainage area of the Stage 1 concrete. In recent times this area has been covered over by materials so the damage has not been obvious. In preparation for the Stage 1 concrete pour materials have been relocated and the area cleaned, the exposed reinforcement was the identified
| 03SR - Stations (RfL) | Cxxx-NCR-002122 | NCR | C&C Base Slab Construction Records |  | Crossrail | XRL | PML - Pudding Mill Lane Portal (Central) |  | 2015-11-19 | 2015-12-09 09:40 | 20 | 2015-11-05 13:24 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | During the review of the construction record package for the C&C tunnel and the Covered Ramp base slabs, it became apparent many of the post pour inspections and cover surveys were not being produced contemporaneously. All cover surveys provided appear to have been conducted by MPB on 15th September (2 weeks after the last slab was cast). __s construction documents indicate that in most cases there were no contemporaneous records confirming that the cover to the slabs was acceptable. The first slab was cast in May 2015 and the records only presented for review in October. Furthermore, almost every post pour sheet and cover survey was not offered to Crossrail for inspection until the submission of these records. As a result, there are many documents in the record packages for the C&C tunnel and Covered Ramp base slabs, that cannot be counter-signed by Crossrail. The first slab was cast in May 2015 and the records only presented for review in October. Despite numerous verbal and written requests, __ are failing to invite Crossrail to witness various construction activities as specified in the ITPs. This is in contradiction to Parts 20.8 and 20.9 of the Works Information. This issue has previously been raised in Cxxx-NCR-001900.
| 03SR - Stations (RfL) | Cxxx-NCR-002124 | NCR | C&C3 Roof Slab Bay 8 oversized spacer blocks |  | Crossrail | XRL | PML - Pudding Mill Lane Portal (Central) |  | 2016-01-29 | 2016-03-11 17:27 | 42 | 2015-11-06 11:45 | Civil - Structural Engineering | 2000 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Supervision - Other | Completed |  | Taking into account the answer given in Cxxx-RFI-003346, several spacer blocks oversized were found during the pre-pour inspection of C&C3 Roof Slab Bay 8 (this location is shown in the attached Cxxx-SWN-S-DDL-CR094_PT002_Z-72003.pdf). CRL has pointed out the requirements for the spacer blocks length to MS several times, including in the Quality Weekly Meetings. These requirements have not been addressed for the bay mentioned above. Photos are attached.
| 03SR - Stations (RfL) | Cxxx-NCR-002125 | NCR | EIP – Vent Wall & Cross Wall 3 on 1st Floor Concrete Cube Strength |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2016-01-15 | 2015-12-01 09:33 | -45 | 2015-11-26 18:20 | Civil - Civil Engineering General | 1000 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | Drawings: Cxxx-SWN-S-DDD-CR094_PT002_Z-80417 EIP Cross Wall 3 U/S 1st Floor was poured 26/09/15. 28 day Concrete Cube test results show 42.6N/mm2 and 41.6N/mm2 which below the required strength.
| 03SR - Stations (RfL) | Cxxx-NCR-002126 | NCR | Foam boxout for pile 37 floated during plunging the cage |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2015-12-12 | 2015-12-03 10:15 | -9 | 2015-11-07 15:44 | Civil - Civil Engineering General | 1000 |  | Manufacturing Defect | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | It appears that the roof slab box out foam has come loose and floated up the pile during plunging. This has been found on Pile 37 @ an approximate level of 105.6mATD
| 03SR - Stations (RfL) | Cxxx-NCR-002127 | NCR | C&C3 Repairs on Secant Wall Piles 3 to 61 |  | Crossrail | XRL | PML - Pudding Mill Lane Portal (Central) |  | 2016-03-18 | 2016-03-18 13:54 | 0 | 2015-11-09 16:44 | Civil - Structural Engineering | 8500 |  | Supervision/Management | Use As-Is | 2 (6-60k) | Complete | Management Problem - Other management problem | Completed |  | A series of repairs carried out on secant piles 3 to 61 during the night shift 07/11/15 – 08/11/15 of the C&C3 Secant Wall. None of them had been identified and agreed between all the parties mentioned above and the advice and opinion of the FE was disregarded as there was not identification of repair method done. MS have used a repair method approved just for D-Walls under NCR 1985, 2055 and 2080, also knowing that there are issues with the strength of the material (Aqualite) used to do these repairs. Moreover, there is no accepted site concrete repair procedure as at the moment it is code 3.
| 03SR - Stations (RfL) | Cxxx-NCR-002128 | NCR | Missing couplers in bay 11 roof slab at SUW |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2015-12-11 | 2015-12-05 14:42 | -6 | 2015-11-09 17:18 | Civil - Civil Engineering General | 2500 |  | Incomplete Works | Repair | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | A further 6no couplers have been found to be missing in bay no 11 on the SUW, The location survey is attached
| 03SR - Stations (RfL) | Cxxx-NCR-002129 | NCR | EIP - South Sump Wall underside of Platform |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2016-01-31 | 2016-01-11 12:33 | -20 | 2015-11-10 18:31 | Civil - Civil Engineering General | 3000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Drawing: Cxxx-SWN-S-DDD-CR094_PT002_Z-80410 Upon striking the formwork for the wall section, it was noticed that an F2 was not achieved. See attached photo.
| 03SR - Stations (RfL) | Cxxx-NCR-002130 | NCR | Cut and Cover Phase 3 Base Slab 1 Missing Column Couplers |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2016-01-29 | 2015-12-07 19:07 | -53 | 2015-11-10 17:03 | Civil - Civil Engineering General | 1000 |  | Supervision/Management | Repair | 4 (0.5-3k) | Complete | Supervision - Insufficient supervision | Completed |  | It has been found that couplers for one column at Cut and Cover Phase 3 Base Slab one have been omitted. This is likely due to the fact that the close spacing required between the columns would not have been expected/required due to the adjusted position of the Expansion Joint. The column layout was not adjusted when the Expansion Joint was re-located. Please refer also to existing PTRs RFI 1015 and FCDs 1038, 2008 and 2239 (cancelled). The omission of this column has led to an increased centre spacing between columns to 4m (design = 3m).
| 03SR - Stations (RfL) | Cxxx-NCR-002131 | NCR | Four Span Underpass - Kicker installed along GL_2-3 for the Up ELectric Loop Wall is a 150mm to high |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2016-01-08 | 2015-12-17 08:29 | -22 | 2015-11-11 10:00 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Please refer to: DWG - Cxxx-SWN-S-DDD-CR094_PT0002_Z-68427 & Cxxx-SWN-S-DDc-CR094_PT0002_Z-69221 PTR: Cxxx-FCD-2087 & 2235 See attached photo The kickers located at GL_2 & GL_3 were previously installed 150mm to high. Subsequently, the kicker spanning between GL_2-3 has been installed 150mm to high. Due to the curtain wall soffit being raised 150mm at GL_2-3, the bottom U-bar B dimension BM47(a-ab) is now too big to fit underneath the recess on the front face of the wall.
| 03SR - Stations (RfL) | Cxxx-NCR-002132 | NCR | Missing Couplers in the SUW and NUW in bay 9 cut and cover phase 3 |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2015-12-11 | 2015-12-05 15:12 | -6 | 2015-11-11 15:12 | Civil - Civil Engineering General | 2500 |  | Supervision/Management | Repair | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | 1) 4no couplers do not seem to have been installed during SUW construction in roof bay 9/10 CJ (bay 9). Please see attached photograph 2) 4no couplers do not seem to have been installed during NUW construction in roof bay 9/10 CJ (bay 9). Please see attached photograph 3) There has also been identified an area where the coupler spacing is between 220-280mm. This is approximately 8.5m going west from the CJ at the joint between bays 9/10. Please see attached photograph
| 03SR - Stations (RfL) | Cxxx-NCR-002133 | NCR | EIP - EIP Ground Floor Levels |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2016-08-05 | 2016-07-18 15:38 | -18 | 2015-11-24 08:16 | Civil - Civil Engineering General | 3000 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | Drawings: Cxxx-SWN-S-DDA-CR094_PT002_1-80103 Level as-built on the ground slab are out of tolerance as per attached survey drawing.
| 03SR - Stations (RfL) | Cxxx-NCR-002134 | NCR | Secant pile 56 - box out has broken loose and floated |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2015-12-11 | 2015-12-09 18:24 | -2 | 2015-11-11 15:17 | Civil - Civil Engineering General | 1000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During plunging of the cage to Secant pile 56 it appears that the base slab foam box out has broken loose and floated up 700mm.
| 03SR - Stations (RfL) | Cxxx-NCR-002135 | NCR | Couplers out of tollerance |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2015-12-18 | 2015-12-11 09:29 | -7 | 2015-11-11 15:38 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | There is an area of couplers on the SUW that seem to be out of tollerance. This has been identified in bay 9 of the cut and cover phase 3 section. The survey is attached
| 03SR - Stations (RfL) | Cxxx-NCR-002137 | NCR | leaking interface between north D-wall & secant pile 1 |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2016-01-15 | 2016-01-13 12:37 | -2 | 2015-11-13 11:03 | Civil - Civil Engineering General | 2000 |  | Incomplete Works | Repair | 4 (0.5-3k) | Complete | External Phenomenon - Other | Completed |  | Now the liner wall has been installed over piles 1 - 3 essentially capping the interface between north D-wall & secant pile 1. This joint has been inspected and running water seems to be coming through the wall at low level at the interface location along with 2 patches of beading further up the joint.
| 03SR - Stations (RfL) | Cxxx-NCR-002138 | NCR | Structural repairs to secant piles, D-walls and south upstand wall (phase 3) |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2016-03-25 | 2016-03-22 15:43 | -3 | 2015-11-17 15:43 | Civil - Civil Engineering General | 9000 |  | Incomplete Works | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Other | Completed |  | Further to removal of the C&C phase 3 / covered ramp temporary propping, the D-walls, Secant piles and south up-stand wall have a large number repairs required to cut back the gallow bracket bolts.
| 03SR - Stations (RfL) | Cxxx-NCR-002139 | NCR | Four Span Underpass - Starter Bars from Pile Cap clashing with Recess in Curtain Wall |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2016-01-29 | 2015-12-17 08:43 | -43 | 2015-11-18 10:35 | Civil - Civil Engineering General | 1000 |  | Design | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Please refer to: DWG - Cxxx-SWN-S-DDD-CR094_PT002_Z-68421, DWG - Cxxx-SWN-S-DDD-CR094_PT002_Z-68422, DWG - Cxxx-SWN-S-DDD-CR094_PT002_Z-68423, DWG - Cxxx-SWN-S-DDD-CR094_PT002_Z-68424, DWG - Cxxx-SWN-S-DDD-CR094_PT002_Z-68427. Spec - Cxxx-SWN-S-RSP-CR094_PT002-0002. PTR - RFI-2580, PTR - FCD 2237 Please refer to attached photo. The starter bars protruding up from the pile caps at GL_4 to GL_2 are currently positioned so that they extend into the recess and therefore have no cover. Furthemore, all lacers in front of these starter bars also exetnd into the recess. The photograph attached highlights the starter bars but it must be noted that all reinforcement in front of the starter bars also have no cover within the vicinity of the recess. The reinforcement extending out from the pier walls are detailed to go around the starter bars, consequently these bars are also clashing with the recess. Please note addition of lacers as per reequest from FCD -2237.
| 03SR - Stations (RfL) | Cxxx-NCR-002140 | NCR | CMR - CRL/ DLR cover plate fabrication |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2016-01-08 | 2015-11-27 11:38 | -42 | 2015-11-17 14:53 | Civil - Civil Engineering General | 500 |  | Manufacturing Defect | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | An error in the fabrication process of the CRL/ DLR cover plates has lead to them being manufactured from an incorrect grade of steel.
| 03SR - Stations (RfL) | Cxxx-NCR-002141 | NCR | Non structural repairs to phase 3 D-walls & secant piles further to base slab construction |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2016-03-31 | 2016-03-30 16:57 | -1 | 2015-11-18 08:40 | Civil - Civil Engineering General | 8000 |  | Incomplete Works | Repair | 2 (6-60k) | Complete | Management Problem - Other management problem | Completed |  | Further to completion of C&C phase 3 / Covered Ramp base and roof slabs, there are numerous minor repairs required to cut back small bolts / rebar & divi dag bar.
| 03SR - Stations (RfL) | Cxxx-NCR-002142 | NCR | Four Span Underpass - Cut RCS bar in Four Span tunnel corridor |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2016-01-29 | 2016-01-06 09:58 | -23 | 2015-11-18 09:04 | Civil - Civil Engineering General | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Worker not correctly instructed | Completed |  | Please refer to: DWG - Cxxx-SWN-S DDD-CR094-PT002_Z-68425, PTR-FCD-2033. Attached photos The incorporated reinforcement continuity system into the Central CRL Wall for the West end of the stair landing was cut in order to fit under the door way. It was found when pulling out the RCS that the bars were also cut and four bars are now not to length.
| 03SR - Stations (RfL) | Cxxx-NCR-002143 | NCR | Secant pile 49 - base slab box out has broken loose & floated during cage plunging |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2016-01-11 | 2015-12-15 12:21 | -27 | 2015-11-18 10:44 | Civil - Civil Engineering General | 1500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The base slab foam box out to secant pile 49 appears to have broken loose during cage plunging and is now sitting just above the base slab upturn bean.
| 03SR - Stations (RfL) | Cxxx-NCR-002144 | NCR | Secant pile 30 - base slab box out has broken loose & floated during cage plunging |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2016-01-11 | 2015-12-14 18:47 | -28 | 2015-11-18 10:53 | Civil - Civil Engineering General | 1500 |  | Incomplete Works | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The base slab foam box out to secant pile 30 appears to have broken loose during cage plunging and is now sitting just above the base slab upturn beam.
| 03SR - Stations (RfL) | Cxxx-NCR-002145 | NCR | C&C phase 3 cracks in roof slab |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2016-01-15 | 2016-01-05 14:14 | -10 | 2015-11-23 15:43 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | There are cracks in the roof slab of the Cut and Cover phase 3 that are greater than 0.2mm. Bays 1-8 eastbound have been surveyed to date, please see attached crack width surveys. The allowable crack width intended for the Cut & Cover roof slab phase 3 is 0.2mm (and not 0.3mm as assumed by __ when raising RFI 3607), as confirmed by CRL (Cxxx __) at a site meeting on 16/11/15. We believe that the cracking is a result of the nature of concrete, the geometry of the slabs and how they are restrained. These factors have led to a build-up of tensile stresses caused by early age contraction in the slab which have been relieved through cracking. The primary cracks can be expected to extend to the full depth the section. This cracking in reinforced concrete slabs is to be expected and is controlled by the reinforcement, as such it is not a construction defect.
| 03SR - Stations (RfL) | Cxxx-NCR-002146 | NCR | Covered ramp base slab cover survey readings out of tollerance by 1mm in bays 13, 14 & 15 |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2015-12-18 | 2015-12-05 16:25 | -13 | 2015-11-18 14:00 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | This NCR is to reflect 1No cover reading that is 1mm outside tollerance to covered ramp base slab surface to bays 13, 14 & 15. See attached copy of survey.
| 03SR - Stations (RfL) | Cxxx-NCR-002147 | NCR | 4SU - Cracks in roof slab |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2016-01-29 | 2016-01-04 13:52 | -25 | 2015-11-19 10:06 | Civil - Civil Engineering General | 10000 |  | Design | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Cracks have appeared on the roof slab of the 4SU that fail the specification limit of 0.2mm. A crack width survey has been completed upon request by CRL/Cxxx and ttached to this NCR. Following a site meeting between CRL/Cxxx/MS on 16/11/15, Cxxx (__) mentioned the allowable limit for the 4SU roof is 0.2mm rather than 0.3mm, as previously understood. __ believe that the cracking is a result of the nature of concrete, the geometry of the slabs and how they are restrained. These factors have led to a build-up of tensile stresses caused by early age contraction in the slab which have been relieved through cracking. The primary cracks can be expected to extend to the full depth the section. This cracking in reinforced concrete slabs is to be expected and is controlled by the reinforcement, as such it is not a construction defect.
| 03SR - Stations (RfL) | Cxxx-NCR-002148 | NCR | Cut and Cover Phase 3 - First 3 Secants Pour Honey Combing and Making Good |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2016-02-26 | 2016-01-12 14:22 | -45 | 2015-12-08 08:54 | Civil - Civil Engineering General | 1000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Honey combing has been identified at the bottom of the lower wall panel cast in from of the first 3 secants on the Eastbound Cut and Cover Phase 3 around the injection hoses (please see attached photos). A formwork tie bar has also been identified cast into the pour. Under previous NCR 2137 it has been identified that the interface between the North Diaphragm Wall and the first secant pile is leaking.
| 03SR - Stations (RfL) | Cxxx-NCR-002149 | NCR | Secant Pile leaks |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2016-01-23 | 2016-01-06 14:05 | -17 | 2015-11-24 09:28 | Civil - Civil Engineering General | 10000 |  | Workmanship | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | More leaks have been found on the secant piles which are out of tolerance. See attached drawing referencing the location of these leaks.
| 03SR - Stations (RfL) | Cxxx-NCR-002150 | NCR | EIP - Concrete Honeycombing in Western Staircore |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2016-02-05 | 2016-01-14 09:07 | -22 | 2015-11-24 12:57 | Civil - Civil Engineering General | 1000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | Drawings: Cxxx-SWN-S-DDD-CR094_PT002_Z-80416 This section of wall was poured on 21st May 2015. Upon striking the Cross Wall 6 shutter at intermediate level, which is part of the Western Staircore, it was noticed there was an area of localised honeycombing.
| 03SR - Stations (RfL) | Cxxx-NCR-002151 | NCR | Greenway Ramp Wall Movement Joint Detail |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2016-01-08 | 2016-01-08 14:22 | 0 | 2015-11-24 17:07 | Civil - Civil Engineering General | 1000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Please refer to Drawing Cxxx-SWN-S-DDL-CR094_PT002_Z-37106 The Movement joint (MJ) detail in the wall between the main Greenway Ramp Structure and the Transition Structures were not constructed as per design.
| 03SR - Stations (RfL) | Cxxx-NCR-002152 | NCR | RRVR Attenuation Tank outlet connection leakage |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2015-12-25 | 2015-12-10 14:11 | -15 | 2015-11-25 08:07 | Civil - Drainage | 1000 |  | System Defect | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | As per Cxxx-NCR-2058 corrective actions a water test was conducted to determine the rate of leakage of the RRVR Attenuation tank following internal joint sealing. The recorded rate of leakage which corresponds to approx 40mm fall in water level in the Attenuation Tank over an hour was not judged as being acceptable as per Cxxx-RFI-3201 . During the test once the water level reached approx 1.3m above outlet invert level leakage was observed between the joint of the outlet pipe and the attenuation tank. This pipe was cast in place and surrounded with ST4 concrete as per HCD Drawing Number F1 Type Z (MCHW Vol 4 Section 2) and benched as per standard MH detail. This detail is not adequate to seal the tank and forms the basis of this NCR.
| 03SR - Stations (RfL) | Cxxx-NCR-002153 | NCR | Four Span Underpass - Up Electric Wall Footing extended beyond Pile Cap at GL_4 |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2015-12-11 | 2015-12-16 11:52 | 5 | 2015-11-27 14:36 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Please refer to; DWG - Cxxx-SWN-S-DDD-CR094_PT002_Z-68427 DWG - Cxxx-SWN-S-DDD-CR094_PT002_Z-68424 PTR - RFI-3625 Attached Photographs. The pile cap was set out as per the construction drawings to the dimensions specified. The reinforcement drawing for the Up Electric wall shows the footing of the wall bearing completely on the pile cap. However, as shown in the attached photographs a section of the footing is not bearing on the pile cap and is bearing on the ground. On DWG-684242 it shows 16No. starter bars but for the size of the kicker specified only 14No. starter bars could fit. On the DWG-68427, 15-B20-U bars were detailed and were supposed to be tied on to the starter bars. As there was a reduction in starter bars there were left over U-bars, these U-bars were not omitted but kept in. By keeping them in, the wall has been extended to accommodate them. This was originally captured in RFI-3625 but after further investigations it was instructed to raise this an NCR Please note that 16No. starter bars were installed but two number were installed in the corner of the kicker which are to be removed. All starter bars have U-bars attached to them.
| 03SR - Stations (RfL) | Cxxx-NCR-002154 | NCR | Foam boxout floated during plungin of the secant pile cages |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2015-12-24 | 2015-12-17 14:48 | -7 | 2015-11-27 10:32 | Civil - Civil Engineering General | 2000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Secant pile numbers 112, 113, 114 and 115 in the cut and cover phase 3 section have all had thier foam box-out float between 20-100mm above the top of roof slab position. Drawing references; Cxxx-SWN-S-DDD-CR094_PT002_Z-72440 and Cxxx-S-DDL-CR094_PT002_Z-72001 As per contract drawings, the remainder of the foam was removed during the shear key preparation of the roof slab.
| 03SR - Stations (RfL) | Cxxx-NCR-002155 | NCR | Footpringts and indentations on bay 14 covered ramp roof slab |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2016-01-15 | 2016-01-13 16:00 | -2 | 2015-11-27 10:58 | Civil - Civil Engineering General | 1000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | There have been footprints and indentations identified in the roof slab in the covered ramp bay 14. These were first found once the curing protection was removed.
| 03SR - Stations (RfL) | Cxxx-NCR-002156 | NCR | Four Span Underpass - Non Compliace of 28day Cube Tests to BE-EN-206 |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2015-12-11 | 2015-12-03 15:30 | -8 | 2015-11-27 14:19 | Civil - Civil Engineering General | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | Please refer to: ITP - Cxxx-MRG-C-ITP-CR094_WS111-50003, Sch - Cxxx-SWN-S-RSP-CR094_WS111-50001, DWG -Cxxx-SWN-SDDA-CR094_PT002_B-69102, Marked-Up Drawings, Concrete Test Reports. The following concrete pours did not achieve the required 28day concrete cube strength of 46N/mm^2 in accordacne with BS-EN-206; 1) North Wall - Pour 8, 2) North Wall - Upstand on Roof between GL_1-2, 3) East Bound Tunnel Mass Infill Stairs, 4) West Bound Tunnel Mass Infill Stairs.
| 03SR - Stations (RfL) | Cxxx-NCR-002157 | NCR | Covered ramp - Cracks in roof slab |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2016-01-15 | 2016-01-08 15:01 | -7 | 2015-12-07 13:13 | Civil - Civil Engineering General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | There are some cracks in the roof slab of the Covered Ramp. Although they all meet width specification they do appear to go full depth through the slab. please see attached crack width surveys.
| 03SR - Stations (RfL) | Cxxx-NCR-002159 | NCR | Secant Pile Leaks |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2016-01-26 | 2016-01-06 14:06 | -20 | 2015-11-27 15:30 | Civil - Civil Engineering General | 10000 |  | Workmanship | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | More leaks have been found on the secant piles which are out of tolerance. See attached drawing referencing the location of these leaks.
| 03SR - Stations (RfL) | Cxxx-NCR-002160 | NCR | C&C 11kv - Phase 3 completed roof Movement joints leaking |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2016-10-19 | 2016-10-19 15:58 | 0 | 2015-12-02 08:10 | Civil - Civil Engineering General | 50000 |  | Design | Repair | 2 (6-60k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | We have noted that on the following completed roof slab works, the below MJ's are leaking. 1) 11KV / ph2a roof MJ south 2) 11KV / ph2a roof MJ north 3) Ph2a / ph2b roof MJ north 4) Ph2a / ph2b roof MJ south 5) ph2b / ph3 roof MJ south All leaks seem to be coming in between roof slab and D-wall. RFI 832 was raised back in sept 2012 highlighting the concern over possible water ingress. It was noted by Cxxx that it would be likely that a gutter drain detail would be required and would be confirmed later. EWN 267 was raised to CRL.
| 03SR - Stations (RfL) | Cxxx-NCR-002161 | NCR | Stage 1 Concrete - Bay 28 to 29 EJ Ammendment |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2016-01-29 | 2015-12-09 12:59 | -51 | 2015-12-02 09:31 | Civil - Civil Engineering General | 1000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Cxxx have omitted the 4 dimple wide section of PRD membrane over the expansion joint as per the construction drawings (ref Cxxx-SWN-S-DDA-CR094_PT002_Z-81106) CH NE14710. Bay 29 Pour A has been poured without the 2 PRD dimples cast beneath it. The location of the EJ is situated at 106m A.O.D approx - 3m above the water table.
| 03SR - Stations (RfL) | Cxxx-NCR-002162 | NCR | Covered Ramp Roof Slab Hand Rail Fixings Clashes with Reinforcement |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2016-01-29 | 2016-01-20 12:30 | -9 | 2015-12-03 12:03 | Civil - Civil Engineering General | 1500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Other management problem | Completed |  | When drillings works were undertaken to install the required hand rail along the North and South Walls at the required 1250mm spacing, clashes with the existing reinforcement were encountered. The fixing locations were adjusted up and down the hand rail alignment to avoid clashes while maintaining required maximum centres, however after optimal adjustment a small number of clashes remain (8 along North Wall and 8 along South). Please see attached asbuilt information.
| 03SR - Stations (RfL) | Cxxx-NCR-002163 | NCR | C&C2 - Emergency Walkway Cube failure |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2016-03-31 | 2016-03-09 10:24 | -22 | 2016-01-18 12:11 | Civil - Civil Engineering General | 5000 |  | Material | Use As-Is | 3 (3-6k) | Complete | Material/Preservation Problems - Other | Completed |  | Westbound kickers for columns #28, #33-#39 inclusive, Eastbound Column #31, Eastbound Columns #20-#24 and Eastbound Walkway Platform was poured on 03/06/15. There is one of two 28day results not achieving the required 46N/mm2. It achieved 42.2N/mm2 while the second achieved 42.2N/mm2.
| 03SR - Stations (RfL) | Cxxx-NCR-002164 | NCR | Water seepage between 11KV plunge column and stage 1 concrete EB portal |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2016-03-31 | 2016-03-23 12:09 | -8 | 2015-12-04 16:46 | Structural Engineering - Concrete Member | 3000 |  | Design | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Water has been observed seeping from the joint between the stage 1 concrete and 11KV plunge column (2nd column from the west end) in the eastbound portal, refer attached photograph. The flow of water is very slight, there is no clear indication from exactly which location around the column the water is leaking.
| 03SR - Stations (RfL) | Cxxx-NCR-002166 | NCR | New Secant leaks 05/12/15 |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2016-02-03 | 2016-01-06 14:10 | -28 | 2015-12-05 15:25 | Civil - Civil Engineering General | 10000 |  | Workmanship | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | More leaks have been found on the secant piles which are out of tolerance. See attached drawing referencing the location of these leaks.
| 03SR - Stations (RfL) | Cxxx-NCR-002167 | NCR | Crack in joint between Secant P166 & P167 (at movement joint) |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2016-03-31 | 2016-03-23 17:11 | -8 | 2015-12-08 11:06 | Civil - Civil Engineering General | 7000 |  | Design | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Not Defined | Completed |  | The joint between pile 166 & 167 (at the expansion joint between C&C3 and Covered Ramp) has opened up (see attached photo). This was noted following removal of the falsework in this area and was highlighted to Crossrail during the monthly QFM site walk. The gap is approximately 8mm wide. Also note that the end of the Covered Ramp capping beam has also been cracked by this relative movement. Following conversations with the CRL field engineering department we are raising this NCR.
| 03SR - Stations (RfL) | Cxxx-NCR-002168 | NCR | Leak in Panel S30 D-Wall (CSJV C248) |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2016-02-07 | 2016-01-06 14:54 | -32 | 2015-12-09 15:36 | Civil - Civil Engineering General | 10000 |  | Workmanship | Repair | 2 (6-60k) | Complete | Previous Construction - Problems based on previous construction errors | Completed |  | A leak has appeared in panel S30, constructed by (C248) which requires sealing. The leak is coming through the middle of the panel and is running.
| 03SR - Stations (RfL) | Cxxx-NCR-002169 | NCR | CMR Tow Path Rail Post Pocket |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2016-03-08 | 2016-02-19 14:31 | -18 | 2015-12-09 11:14 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | This NCR relates to the incorrect positioning of 1 no Rail Post Pocket in Capping Beam 3. Please find attached drawing outlining coordinate of installed post pocket.
| 03SR - Stations (RfL) | Cxxx-NCR-002170 | NCR | More leaks on Secants |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2016-02-07 | 2016-01-06 14:10 | -32 | 2015-12-09 18:56 | Civil - Civil Engineering General | 20000 |  | Workmanship | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | More leaks have been found on the secant piles which are out of tolerance. See attached drawing referencing the location of these leaks. Some leaks have been found which are within tolerance but these have also been identified.
| 03SR - Stations (RfL) | Cxxx-NCR-002171 | NCR | C&C phase 3 cracks in roof slab |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2016-03-11 | 2016-03-11 15:15 | 0 | 2015-12-11 15:26 | Civil - Civil Engineering General | 600 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Further to NCR 2145 it was discussed that a seperate NCR will be raised for the soffit crack in bay 5 cut and cover phase 3 which was previously measured at 0.9mm
| 03SR - Stations (RfL) | Cxxx-NCR-002172 | NCR | Cut and Cover Phase 3: Above Roof Slab Temp Works Propping Making Good |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2016-02-26 | 2016-02-18 09:27 | -8 | 2015-12-15 12:39 | Civil - Civil Engineering General | 10000 |  | Design | Repair | 2 (6-60k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | A number of locations where the connections to the Temporary Works Propping Gallows Brackets need to be made good through Cut and Cover Phase 3 above the cast roof slab.
| 03SR - Stations (RfL) | Cxxx-NCR-002173 | NCR | EIP - Corbels Rebar out of Position |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2016-04-29 | 2016-02-05 08:47 | -84 | 2016-01-18 12:24 | Civil - Civil Engineering General | 10000 |  | Planning | Repair | 2 (6-60k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | Drawings: Cxxx-SWN-S-DDD-CR094_PT002_Z-80419 BM1252 in detail A and BM1278 in detail B have been cast 50mm out of position in the four Corbels that are attached to the EIP South Core Wall. BM Dimensions: A - 680 B - 205 C - 495 D - 495
| 03SR - Stations (RfL) | Cxxx-NCR-002174 | NCR | Covered Ramp - North Capping Soffit Protruding Bars |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2016-03-18 | 2016-03-07 16:28 | -11 | 2015-12-16 12:15 | Civil - Civil Engineering General | 1500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Subcontractor Problems - Insufficient work planning by the subcontractors | Completed |  | Steel pins have been found protruding along the soffit of the Covered Ramp North Capping Beam (please see attached photographic records). These pins must be removed to complete the remaining works in the area including Fire Lining of the Secant Piles below.
| 03SR - Stations (RfL) | Cxxx-NCR-002175 | NCR | Cut and Cover Phase 3: Damaged Tie Hole Central Wall Bay 5 WB |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2016-03-25 | 2016-02-24 11:58 | -30 | 2015-12-16 13:31 | Civil - Civil Engineering General | 1500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | After striking the Central Wall Panel at Cut and Cover Bay 5 it has been found that the area around one of the tie holes (please see attached photographic record) has been damaged.
| 03SR - Stations (RfL) | Cxxx-NCR-002177 | NCR | Covered Ramp - Insufficient Cover at Capping Beam Bay 15 |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2016-03-25 | 2016-02-23 14:23 | -31 | 2015-12-17 14:43 | Civil - Civil Engineering General | 3000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | On the South face of the Capping Beam at Covered Ramp Bay 15 a small area of insufficient cover has been identified below the Upstand Wall at the coner of the North return (please see attached photographic records and cover meter readings). In order to ensure the Upstand Wall pour had sufficient cover at the interface a small lip was introduced at the bottom of the pour. The lip is 20mm at the worst case (corner of return) and fades to nothing at 500mm from the corner. This adjustment of the Upstand pour 5/6 alignment was identified under separate NCR Cxxx-NCR-002078.
| 03SR - Stations (RfL) | Cxxx-NCR-002178 | NCR | Covered Ramp - Poor Quality Concrete and Damaged Chamfer at Top of South Upstand Wall |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2016-02-26 | 2016-02-26 10:37 | 0 | 2015-12-17 16:04 | Civil - Civil Engineering General | 3000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | Three areas along the top of the South Upstand Wall at the Covered Ramp have been identified as requiring remedial work. Location 001 - 88220.174, 38082.904 Damage to chamfer. Area affected 500mm x 100mm Location 002 - 88230.999, 38092.195 Poor quality concrete, top layer of latence / debonded concrete. Area affected 1000mm x 200mm Location 003 - 88243.873, 38102.791 Poor quality concrete, top layer of latence / debonded concrete. Area affected 1750mm x 500mm Please see attached photographic records.
| 03SR - Stations (RfL) | Cxxx-NCR-002179 | NCR | Emergency Walkway Column Positions from EIP to C&C |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2016-03-31 | 2016-03-11 12:21 | -20 | 2016-01-28 16:59 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Change to drawings not provided on time | Completed |  | Drawings: Cxxx-SWN-S-DDD-CR094_PT002_3-80401 Multiple Emergency Walkway columns out of positional tolerance in both tunnels from EB Chainage 14,160-14,345 and WB Chainage 14,330-14,520. See attached marked up drawing. The maximum disposition towards the rail line is 28mm (column EB8) and the maximum disposition longitudinally is 373mm (column WB28).
| 03SR - Stations (RfL) | Cxxx-NCR-002181 | NCR | Stage 1 Concrete - FSC within the 4SU structure time between concrete loads above 30 mins |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2016-03-11 | 2016-01-14 12:43 | -57 | 2016-01-08 16:32 | Civil - Civil Engineering General | 500 |  | Manufacturing Defect | Use As-Is | 4 (0.5-3k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | The Stage 1 Concrete is now complete within the 4SU structure. There were a total of 9no. pours to complete this section, one of which (Bays 30, 31 & 32 Pour B, ACO side only) occurred with a total of 60 minutes between loads 1 and 2. The maximum time between loads within the specification is 30 minutes.
| 03SR - Stations (RfL) | Cxxx-NCR-002182 | NCR | EIP - Roof Levels |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2016-05-27 | 2016-04-21 10:59 | -36 | 2016-03-31 16:55 | Civil - Civil Engineering General | 5000 |  | Supervision/Management | Use As-Is | 3 (3-6k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | Drawings: Cxxx-SWN-S-DDD-CR094_PT002_Z-80472, Cxxx-SWN-S-DDD-CR094_PT002_Z-80474 EIP structural roof as built is out of level tolerance in two localised areas. As per attached as built, north east corner is up to -2mm out of tolerance and the southern area is up to +3mm out of tolerance.
| 03SR - Stations (RfL) | Cxxx-NCR-002183 | NCR | North Capping Beam and Upstand Wall - Cover Meter Survey Points Out of Tolerance |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2016-03-25 | 2016-03-02 10:57 | -23 | 2016-01-06 09:58 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | During a review of the quality package for the North Capping Beam a number of individual points have been identified as out of tolerance at North Capping Pour 11 and Upstand Wall Pours 1 and 4. Please see attached cover meter survey record sheets.
| 03SR - Stations (RfL) | Cxxx-NCR-002184 | NCR | Stage 1 - 4SU As-Built Survey Levels Out of Tolerance |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2016-03-25 | 2016-03-22 10:53 | -3 | 2016-01-08 16:30 | Civil - Civil Engineering General | 3000 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | Cxxx have now completed the Stage 1 works within the 4SU structure. As-built surveys have been carried out and show there are a handful of points out of the required tolerance. Please refer to attached as-built surveys with out of tolerance points highlighted (the remainder of the bays within the 4SU which are not included in the attachment have no points out of tolerance).
| 03SR - Stations (RfL) | Cxxx-NCR-002185 | NCR | Stage 1 - Central Track Way Width Out of Tolerance (4SU Sturcture) |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2016-03-25 | 2016-01-12 08:54 | -73 | 2016-01-08 16:30 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | Cxxx has completed the Stage 1 Concrete works within the 4SU structure. The as-built survey of the WB Bays 29 to 32 sections shows the line of the central track way shoulders to be out of tolerance. From the as-built surveys the point most out of tolerance has a measurement of 2991mm between shoulders of the track way. The allowable tolerance for the track way is a minimum width of 3000mm. Please see attached as-built surveys.
| 03SR - Stations (RfL) | Cxxx-NCR-002187 | NCR | Secant leaks Re-appear |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2016-02-12 | 2016-01-20 09:42 | -23 | 2016-01-13 17:38 | Civil - Civil Engineering General | 1000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Leaks have re-appeared in two locations on the secant piles (P53/P54 & P78/P79). These leaks are out of tolerance and need to leak sealed.
| 03SR - Stations (RfL) | Cxxx-NCR-002188 | NCR | Cracks in Covered Ramp Base Slab |  | Crossrail | XRL | PML - Pudding Mill Lane Portal (Central) |  | 2016-03-04 | 2016-02-05 14:29 | -28 | 2016-01-15 11:48 | Civil - Civil Engineering General | 5000 |  | Workmanship | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | Several cracks have appeared in the base slab of the westbound covered ramp. The cracks run generally north to south (across the width of the slab) and are the full depth of the slab (they are wet due to the ground water from below.). They seem to range between 0.1 and 0.3mm wide (although without being cleaned, this is difficult to tell). It is not clear if other cracks have been covered by the first stage concrete, or if similar cracks are also present in the eastbound tunnel.
| 03SR - Stations (RfL) | Cxxx-NCR-002189 | NCR | Four Span Underpass_ Excess Cover for Beam Section of Up Electric Wall between GL_2-3 |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2016-04-29 | 2016-04-21 08:56 | -8 | 2016-01-20 12:30 | Civil - Civil Engineering General | 2000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Please refer to; Cxxx-SWN-S-DDD-CR094_PT002_Z-68427, Attached sketch, Areas pertaining to the beam section of the Up-Electric wall between GL_2-3 has excess cover over the reinforcement as detailed in the attached sketch
| 03SR - Stations (RfL) | Cxxx-NCR-002190 | NCR | Placement of MGL stairs in CRL 4SU box |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2016-04-01 | 2016-03-21 11:56 | -11 | 2016-01-18 15:53 | Civil - Civil Engineering General | 5000 |  | Planning | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | The 4 number steel staircases which land within the 4SU CRL box clash with the stage 1 concrete which has been placed in this location.
| 03SR - Stations (RfL) | Cxxx-NCR-002191 | NCR | Stage 1 Concrete - Damage to Slab from 13T Excavator Access |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2016-03-03 | 2016-02-16 11:43 | -16 | 2016-01-18 13:13 | Civil - Civil Engineering General | 3000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | In order for Cxxx to carry out the 11kV soffit remediation works access for an 13T excavator was required from the 4SU through the tunnel sections to the 11kV. En route the 13T excavator has damaged various sections of the Stage 1 concrete works (see attached photos).
| 03SR - Stations (RfL) | Cxxx-NCR-002192 | NCR | Movement cracks in fire lining at C&C phase 2a/2b (Both sides) |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2016-03-31 | 2016-03-31 08:21 | 0 | 2016-01-19 14:31 | Civil - Civil Engineering General | 5000 |  | Design | Repair | 3 (3-6k) | Complete | Material/Preservation Problems - Other | Completed |  | The hair line cracks 1st noted some time back during a project quality walk vertically through the fire lining, running between roof & base slab movement joints between C&C ph 2a / 2b appear to be growing in size as the structure moves and tempreture falls. The cracks are no longer hair line and measure at 1.5mm to the north and 2.5mm to the south.
| 03SR - Stations (RfL) | Cxxx-NCR-002193 | NCR | EIP - Ground Floor Slab out of positional tolerance |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2016-06-30 | 2016-04-15 10:33 | -76 | 2016-01-27 10:40 | Civil - Civil Engineering General | 5000 |  | Supervision/Management | Repair | 3 (3-6k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | Drawings: Cxxx-SWN-S-DDA-CR094_PT002_1-80103 After stripping of the eastern core box shutter for the ground floor, it was noticed that there was a positional disposition. The disposition has been measured as approximately 12-16mm
| 03SR - Stations (RfL) | Cxxx-NCR-002194 | NCR | C&C ph3 leaking movement joint between ph2b / 3 eastbound |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2016-09-25 | 2016-09-14 10:23 | -11 | 2016-01-20 10:25 | Civil - Civil Engineering General | 6000 |  | Design | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Further to NCR 2160 we have now noted that the roof slab movement joint between phase 2b / 3 in the eastbound tunnel is also leaking. Water appears to be tracking over the waterbar and causing dampness to the central wall to (this is eveident both side of the central wall)
| 03SR - Stations (RfL) | Cxxx-NCR-002195 | NCR | 4SU - Box Walls Gridline 1-3 As-Built positional non-conformance |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2016-03-14 | 2016-02-09 14:22 | -34 | 2016-01-27 17:18 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Drawing: Cxxx-SWN-S-DDD-CR094_PT002_Z-68428 & Cxxx-SWN-S-DDD-CR094_PT002_Z-68429 See attached asbuilt drawings of the Four Span, Central and South Walls in gridlines 1-3. Note that there are few points out of tolerance. They are the following: Central Wall on gridline 3 = north face max 7mm towards the south, south face max 6mm towards south. South wall on gridline 1 = north face max 14mm towards the south, south face max 18mm towards south.
| 03SR - Stations (RfL) | Cxxx-NCR-002196 | NCR | Further leakage to D-wall / Secant pile interface |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2016-02-26 | 2016-01-29 13:43 | -28 | 2016-01-20 11:01 | Civil - Civil Engineering General | 1500 |  | Incomplete Works | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Further to closed NCR 2137, the interface between the North D-wall / Secant pile 1 appears to be leaking again. Water is of a running nature. See attached picture
| 03SR - Stations (RfL) | Cxxx-NCR-002197 | NCR | Cut and Cover Phase 3 / Covered Ramp Base Slabs Delays in Delivery |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2016-04-21 | 2016-04-14 09:56 | -7 | 2016-03-11 11:11 | Civil - Civil Engineering General | 2000 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | Some deliveries have been found outside of the specified tolerance as agreed in the concrete works ITP Cxxx-MRG-C-ITP-CR094_WS111-50003 as follows: Bay 001 - 55 minutes between last 2 loads Bay 003 - 35 minutes between last 3rd/4th loads Bay 004 - 35 minutes between 1st/2nd loads and 3rd/2nd last loads Bay 005 - 45 minutes between 3rd/4th and 7th/8th loads Bay 007 - 40 minutes between 7th/8th loads. 45 minutes between 2nd last/last load Bay 008 - 46 minutes between 2nd last and last loads Bay 013 - 35 minutes between 19th/20th loads Bay 014 - 50 minutes between 1st/2nd loads and 11th/12th loads The slump consistence and strength results in each instance have been within tolerance (please see attached evidence for each relevant pour).
| 03SR - Stations (RfL) | Cxxx-NCR-002198 | NCR | Four Span Underpass - Missing Cube Tests for South Box Portal Wall Pour 4 |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2016-03-14 | 2016-02-19 15:19 | -24 | 2016-01-30 12:02 | Civil - Civil Engineering General | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Please refer to; Spec - Cxxx-SWN-S-RSP-CR094_PT002-00002 - Clause E10.508 The concrete pour for the South Box Portal Wall - Pour 4 - required a total of 31m^3 of concrete. The number of tests required that was stated on the concrete check-list was for 8 cubes but only 4 cubes were taken at the time of the concrete pour.
| 03SR - Stations (RfL) | Cxxx-NCR-002199 | NCR | EIP - Intermediate Slab __ Installation |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2016-05-31 | 2016-04-22 11:24 | -39 | 2016-01-25 16:23 | Civil - Civil Engineering General | 6000 |  | Design | Use As-Is | 3 (3-6k) | Complete | Management Problem - Misunderstand the definition of the requirement | Completed |  | 41MM x 21MM unistrut channels have been installed in the intermediate slab (sub surface level) soffit of the EIP in line with drawing Cxxx-MRG-E-DDA-CR094_PT002_2-80116 We have now been made aware that although shown on drawings Cxxx-MRG-E-DDA-CR094_PT002_2-80116 and Cxxx-SWN-E-DDA-CR094_PT002_2-80116, these channels were not required and should not have been installed.
| 03SR - Stations (RfL) | Cxxx-NCR-002200 | NCR | Floated Foam Box Out Pile 17 |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2016-03-31 | 2016-03-04 09:02 | -27 | 2016-01-21 13:21 | Civil - Civil Engineering General | 1500 |  | Material | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | A further foam box out has been located at Pile 17 below roof slab. Same scenario as those recorded under NCRs 2126 and 2154. Coordinated position and height: E 88115.333, N 38009.106, H 103.401
| 03SR - Stations (RfL) | Cxxx-NCR-002201 | NCR | Covered Ramp - Cover Meter Points out of Tolerance |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2016-03-31 | 2016-03-24 16:42 | -7 | 2016-03-11 16:56 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Bays 12, 13 and 14 each have a single point which is marginally outside of tolerance; 2mm, 1mm and 1mm respectively (please see attached cover meter readings).
| 03SR - Stations (RfL) | Cxxx-NCR-002202 | NCR | Cut and Cover Phase 3 - Covered Ramp Central Walls Minor Gap at Walkway Connection |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2016-03-31 | 2016-03-22 12:17 | -9 | 2016-01-21 16:14 | Civil - Civil Engineering General | 2000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Sporadic small gaps (please see attached surveys for locations) have been found along the Emergency Walkway at the connection to the Central Walls through Cut and Cover Phase 3 and Covered Ramp.
| 03SR - Stations (RfL) | Cxxx-NCR-002203 | NCR | South Upstand Wall Cut and Cover Phase 3 - Covered Ramp Expansion Joint Westbound Concrete Repair |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2016-03-31 | 2016-03-02 17:42 | -29 | 2016-01-30 11:15 | Civil - Civil Engineering General | 2500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Not Defined | Completed |  | At the expansion joint in the SUW between Cut and Cover Phase 3 - Covered Ramp an area of damaged concrete has been identified (please see attached photographic record). Cracking appears shallow, but a structural repair will likely be required. Coordinated position: E 88215.401, N 38079.12, H 104.316
| 03SR - Stations (RfL) | Cxxx-NCR-002204 | NCR | EIP - Slump/Flow Tests (Concrete Precast Cladding Units) |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2016-06-17 | 2016-06-14 07:34 | -3 | 2016-01-22 14:01 | Architectural - Roofing & Exterior Treatment | 3000 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Training Deficiency - Other | Completed |  | Following the factory visit completed on 24th November 2015 at __ works in Alfreton, Derbyshire a surveillance report was completed by __ reporting the findings for quality and assurance. The report was issued to the Project Managers i.e. Crossrail for review and it was recorded that the slump/flow tests being completed by EPC was not being carried out in accordance with BS EN 12350 Part 8: 2010 (as attached). The orientation of the testing cone was observed to be incorrect. Please see Figure 1 (attached). Further advice has since been sought for ‘The Concrete Society’ and the following guidance has been provided; BS EN 12350-2 clause 4.1 states that: The mould shall be in the form of a hollow frustum of a cone having the following internal dimensions: ⎯ diameter of base: (200 ±2) mm; ⎯ diameter of top: (100 ±2) mm; ⎯ height: (300 ±2) mm and Figure 2 (attached) shows the test cone in the correct orientation. Thus it is clear that the base of the mould is 200mm in diameter and the top is 100mm in diameter.
| 03SR - Stations (RfL) | Cxxx-NCR-002206 | NCR | Secant pile leak P12/P13 |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2016-03-08 | 2016-02-03 13:21 | -34 | 2016-01-26 12:58 | Civil - Civil Engineering General | 1500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | A leak has re-appeared on secant p12/p13. The dqamp patch detail was already installed but prior to fire-lining inspection water could be seen running beyond the damp patch detail.
| 03SR - Stations (RfL) | Cxxx-NCR-002207 | NCR | EIP - Cladding Fixings not cast in walls |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2016-04-22 | 2016-04-14 11:48 | -8 | 2016-01-27 09:04 | Civil - Civil Engineering General | 10000 |  | Incomplete Works | Repair | 2 (6-60k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | Drawings: Cxxx-MRG-A-DWG-CR094_WS111-50777, 50779-50781 7065/BW-003 (__ - Bespoke Precast Concrete) There is 8 Cladding Channels that have not been cast in the EIP external walls.
| 03SR - Stations (RfL) | Cxxx-NCR-002208 | NCR | Cxxx Dewatering - Hydro-Demolition of Stage 1 to Decommission Wells |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2016-03-26 | 2016-03-14 16:46 | -12 | 2016-01-26 18:01 | Civil - Civil Engineering General | 50000 |  | Supervision/Management | Repair | 2 (6-60k) | Complete | Management Problem - Misunderstand the definition of the requirement | Completed |  | 5no dewatering and monitoring wells combined have been concreted over with stage 1 concrete without the wells being grouted. The wells have been sealed with the bolted down sealing plate. The stage 1 concrete varies in thicknesses between 180 and 300mm in the pour A base of the stage 1.
| 03SR - Stations (RfL) | Cxxx-NCR-002210 | NCR | EIP - D Wall Damage |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2016-04-08 | 2016-03-09 10:30 | -30 | 2016-01-27 08:53 | Civil - Civil Engineering General | 5000 |  | Damaged | Repair | 3 (3-6k) | Complete | Previous Construction - Problems based on previous construction errors | Completed |  | PTR: RFI#3563 Following Cxxx tunnelling works being completed and the hand back of the EIP chamber extensive damage to the Diaphragm wall tops was recorded, the repair to these walls was subsequently instructed to Cxxx and included saw cutter down and drilling into the wall tops. The remaining damage to the D-wall face is below the instructed cut off line. RFI-3563 was raised to agree the required repair for these area, it has now been answered. We have been asked to raise this NCR to capture this Cxxx defect/damage.
| 03SR - Stations (RfL) | Cxxx-NCR-002211 | NCR | CMR Tow Path retaining wall type 2 sleeved pipe |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2016-02-10 | 2016-02-05 14:41 | -5 | 2016-01-27 17:11 | Civil - Civil Engineering General | 1000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The sleeved 375mm diameter pipe cast into retaining wall type bulged in the course of the concrete pour. Please find attached photograph.
| 03SR - Stations (RfL) | Cxxx-NCR-002212 | NCR | Emergency Walkway Levels |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2016-03-31 | 2016-03-03 13:44 | -28 | 2016-01-29 17:33 | Civil - Civil Engineering General | 1500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | Drawings: Cxxx-SWN-S-DDD-CR094_PT002_3-80401 Between Eastbound Chainage 14157 (Tunnel Headwall Collar) to 14281, and Westbound Chainage 14331 (Tunnel Headwall Collar) to 14402, the walkways levels have been picked up in areas as out of tolerance (+0/-15mm). The actual levels range from -25mm to +6mm in localised areas. Note: the high areas in the Eastbound walkway close to the tunnel eye is covered under RFI#3042.
| 03SR - Stations (RfL) | Cxxx-NCR-002213 | NCR | Cable Riser 6 Leak |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2016-03-11 | 2016-02-15 15:53 | -25 | 2016-01-29 10:22 | Civil - Civil Engineering General | 2000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | A leak has appeared in cable riser 6 between the kicker and riser wall.
| 03SR - Stations (RfL) | Cxxx-NCR-002214 | NCR | South Upstand Wall North Face Bay 15 Surface Repair |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2016-03-31 | 2016-02-18 15:13 | -42 | 2016-01-30 13:30 | Civil - Civil Engineering General | 1000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Not Defined | Completed |  | A small surface area (500mm x 200mm) on the South Upstand has been identified as having been scabbled back and there is a single form tie conduit tube in the area (see photographic records attached). The concrete has been inspected and is in a sound condition and there is no exposed reinforcement. The tie hole has been cleaned and there are no obstructions.
| 03SR - Stations (RfL) | Cxxx-NCR-002215 | NCR | Four Span Underpass - Up-Electric wall out of tolerance between at GL_3-4 |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2016-04-29 | 2016-04-21 08:53 | -8 | 2016-02-02 15:31 | Civil - Civil Engineering General | 60000 |  | Incorrect Installation | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Please refer to the following; DWG-Cxxx-SWN-S-DDD-CR094_PT002_Z-68427, DWG-Cxxx-SWN-S-DDA-CR094_PT002_C-60103- Cross Section-P, Spec-Cxxx-SWN-S-RSP-CR094_PT002-00002-Concrete, Attached photos, Attached Survey, After carrying out post pour inspections on the Up-Electric wall between GL_3-4 it was discovered that the section of the wall located at GL_4 had deflected by 119mm. From GL_4 towards GL_3 there is a further 4m of wall out of tolerance ranging from 119mm to 10mm.
| 03SR - Stations (RfL) | Cxxx-NCR-002216 | NCR | C&C 3 base slab surface blown when injecting base slab crack |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2016-03-04 | 2016-02-10 14:41 | -23 | 2016-02-04 13:34 | Civil - Civil Engineering General | 1500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Further to NCR 2188, when injecting crack E to C&C 3 base slab it has blown and lifted a small area of concrete out of the cover zone. Once the lifted area had been removed only 15mm cover remained.
| 03SR - Stations (RfL) | Cxxx-NCR-002217 | NCR | Trapped De-Watering Pump at Well Location G7 |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2016-05-27 | 2016-02-19 13:50 | -98 | 2016-02-02 12:51 | Civil - Civil Engineering General | 5000 |  | Damaged | Repair | 3 (3-6k) | Complete | Material/Preservation Problems - Improper handling of material | Completed |  | When attempting to de-commission de-watering well G7 (please see attached location drawing) is has been identified that the previously used pump has become trapped within the sleeve. Multiple unsuccessful attempts have been made to retrieve the pump unit by pulling and pushing to dislodge. As the top pump unit has been dipped at 0.45m from the top of the slab, it can be assumed that the pump is sitting with the lower 0.4m of the surrounding Cut and Cover Phase 3 base slab.
| 03SR - Stations (RfL) | Cxxx-NCR-002218 | NCR | Four Span Underpass -Up-Electric Wall at Pier_4 Unsatisfactory finish to the Reckli wall |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2016-03-04 | 2016-02-25 11:02 | -8 | 2016-02-02 16:44 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Reject | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Please refer to the following; DWG-Cxxx-SWN-S-DDD-CR094_PT002_Z-68427, DWG-Cxxx-SWN-S-DDA-CR094_PT002_C-60103- Cross Section-P, Spec-Cxxx-SWN-S-RSP-CR094_PT002-00002-Concrete, Attached photo, Due to the incident detailed in NCR#2215, grout managed to pour between the stiffened concrete and the formwork causing an unsatisfactory finish.
| 03SR - Stations (RfL) | Cxxx-NCR-002219 | NCR | Covered ramp roof drainage outlets not cast in north & south walls |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2016-07-01 | 2016-07-01 13:40 | 0 | 2016-02-03 08:34 | Civil - Civil Engineering General | 4500 |  | Design | Repair | 3 (3-6k) | Complete | Management Problem - Other management problem | Completed |  | No Covered Ramp roof drainage outlet pipes were cast into the south up-stand wall or the north capping beam as a part of the RC works. IFC drawing Cxxx-SWN-S-DDL-CR094_PT002_Z-61003 (GA roof slab) has a note referring to drawings Cxxx-SWN-R4-DDD-CR094_PT002_Z-95043 & 95044. These are not currently IFC drawings. The capping beam was constructed using IFC drawing Cxxx-SWN-S-DDD-CR094_PT002_Z-60405 and the south wall to IFC drawing Cxxx-SWN-S-DDD-CR04_PT002_Z-72485 neither makes an allowance for pipes to be cast into the wall. We also note that no detail of any cast in pipe is shown on any of the above drawings
| 03SR - Stations (RfL) | Cxxx-NCR-002220 | NCR | CMR Tow Path Capping Beam Survey of pocket locations |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2017-04-10 | 2017-03-28 07:22 | -13 | 2016-02-03 12:00 | Civil - Civil Engineering General | 3000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Please find attached as built survey drawing (160527 Post pocket survey attached) of the post pocket locations with the design centre posts as per IFC drawing Cxxx-MMD-D-DDL-CRG06_Z-00012 revised to incorporate the actual answer from FCD2270 and RFI3665. As per BS5606 table T1.5 as referenced in the actual answer of this NCR the centre point tolerance of the pockets are greater than +/- 6mm.
| 03SR - Stations (RfL) | Cxxx-NCR-002221 | NCR | Stage 1 Concrete - Expansion Joint Damage |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2016-04-08 | 2016-03-15 16:50 | -24 | 2016-02-08 16:24 | Civil - Civil Engineering General | 3000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | The stage one concrete is spalling at the east bound bay 8 & 9 expansion joint. The damaged area is approximately 1m in length and a maximum of 0.15m in width. It is thought moisture within the expansion foam membrane has caused the concrete to spall when vehicles pass over the stage 1 concrete.
| 03SR - Stations (RfL) | Cxxx-NCR-002222 | NCR | EIP - Stage '0' Concrete Cube Strength |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2016-03-31 | 2016-03-30 15:28 | -1 | 2016-03-01 15:01 | Civil - Civil Engineering General | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | Drawing: Cxxx-SWN-S-DDB-CR094_PT002_Z-80200 PTR: Cxxx-FCD-002162 The mentioned drawing indicates that a C20 Concrete mix is to be used for ‘Stage 0' as set out in the Concrete Specification Cxxx-SWN-S-RSP-CR094_PT002-00002 - TABLE E10/1 – Designed Concrete Schedule C20/25/ST. Due to supply and documentation issues, it was agreed to use a C40/50C mix in lieu of C20/25/ST mix as captured under FCD 2162. Despite the concrete strength exceeding the design strength requirement, the 56 Day cubes did not to achieve the minimum requirement of 46N for a C40/50C mix. These can be seen in the following pours: 1. Pour 1A: 05/09/2015 – Westbound 410 m3 - Cube No 1859, 1860, 1861 & 1864. 2. Pour 1B: 24/1/2015 – Westbound 48 m3 - Cube No 2033 3. Pour 2B: 03/11/2015 – Eastbound 72 m3 - Cube No 2064 & 2065
| 03SR - Stations (RfL) | Cxxx-NCR-002223 | NCR | Four Span Underpass - Discolouration of the Finish on the Up-Electric Wall between GL_3-4 |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2016-07-30 | 2016-07-12 13:25 | -18 | 2016-02-05 14:40 | Civil - Civil Engineering General | 5000 |  | Material | Repair | 3 (3-6k) | Complete | Material/Preservation Problems - Other | Completed |  | Please refer to; DWG-Cxxx-SWN-S-DDC-CR094_PT002_Z-69221, Spec-Cxxx-SWN-S-RSP-CR094_PT002-00002. The lower section of the Up-Electric wall between GL_3-4 has begun to develop black markings on the surface.
| 03SR - Stations (RfL) | Cxxx-NCR-002225 | NCR | New leak to CSJV D wall panel S15/S16 joint |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2016-03-31 | 2016-03-31 17:01 | 0 | 2016-02-05 09:52 | Civil - Civil Engineering General | 4000 |  | Workmanship | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | D-wall panel S15/S16 appears to have sprung a new leak which is now evident through the completed Cxxx fire lining. See attached picture.
| 03SR - Stations (RfL) | Cxxx-NCR-002226 | NCR | C&C3 base slab cracks to east bound bays 1, 2, 3 & 4 |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2016-03-31 | 2016-03-14 18:52 | -17 | 2016-02-08 11:00 | Civil - Civil Engineering General | 7500 |  | Workmanship | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Several cracks have appeared in the base slab of the eastbound C&C3 bays 1-4. The cracks run generally north to south (across the width of the slab) and appear to be allowing water up with minor dampness recorded either side. Most cracks are barely visable to the eye and so are unable to have the width measured. See attached survey detailing locations.
| 03SR - Stations (RfL) | Cxxx-NCR-002227 | NCR | Leak QA signatures not chased up. |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2016-03-21 | 2016-02-19 16:12 | -31 | 2016-02-08 14:13 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Verification Problems - Other | Completed |  | A number of leak sealing checksheets had been filled out but had missing signatures over a prolonged period of time.
| 03SR - Stations (RfL) | Cxxx-NCR-002228 | NCR | No dewatering ITP |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2016-03-09 | 2016-03-24 15:34 | 15 | 2016-02-10 07:51 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Misunderstand the definition of the requirement | Completed |  | There is no dewatering ITP as it was understood that there is no requirement for ITP's for Temporary Works at the beginning of the Cxxx PML project.
| 03SR - Stations (RfL) | Cxxx-NCR-002229 | NCR | Floated Foam Box out in Secant Piles |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2016-03-23 | 2016-03-10 15:00 | -13 | 2016-02-10 15:55 | Civil - Civil Engineering General | 2500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | An area of foam box-out has been found on secant piles P25 and P37 whilst breaking out the Aqualite repairs. The full extent of foam box out has been removed.
| 03SR - Stations (RfL) | Cxxx-NCR-002230 | NCR | New leak appeared through completed fire lining at D-wall N29 |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2016-04-21 | 2016-04-07 10:44 | -14 | 2016-02-10 10:38 | Civil - Civil Engineering General | 500 |  | Incomplete Works | Repair | 4 (0.5-3k) | Complete | Previous Construction - Other | Completed |  | A new leak has appeared through the completed fire lining located at D-wall panel N29. This is new leak that has appeared. It is uncertain if this falls on a joint at this stage. It is noted that this is only a damp patch and within specification as its under 1m2, however; Cxxx / CRL have requested that this be investigated and sealed if need be.
| 03SR - Stations (RfL) | Cxxx-NCR-002232 | NCR | Cut and Cover Phase 3 - Central Wall Bay 7 Eastbound Proud Joint |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2016-03-31 | 2016-03-04 09:59 | -27 | 2016-02-10 16:01 | Civil - Civil Engineering General | 1000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | An area of central wall was recast on the Eastbound at Bay 7 under previous NCR Cxxx-NCR-002077. It has been found after striking the a joint on the West side of the repair is 10mm proud from the adjacent wall panel and requires attention.
| 03SR - Stations (RfL) | Cxxx-NCR-002233 | NCR | Covered Ramp - North Capping Repairs Damaged During Fire Lining Works |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2016-03-31 | 2016-03-08 14:00 | -23 | 2016-02-10 15:32 | Civil - Civil Engineering General | 1000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | During the course of applying required mesh to the North Capping Beam for fire lining works as per agreed detail in previous Cxxx-NCR-002174 two locations were damaged by fixing of __ anchors and require repair (please see attached photos and location sketch.
| 03SR - Stations (RfL) | Cxxx-NCR-002234 | NCR | Leak at roof slab in EIP EB side D-wall panel N5 |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2016-04-21 | 2016-04-08 11:12 | -13 | 2016-02-10 16:02 | Civil - Civil Engineering General | 2500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | A new leak has appeared between the EIP D-wall panel N5 & the roof slab. This is evident both above and below the roof slab and appears to be coming through the D-wall itself as its not located near a joint.
| 03SR - Stations (RfL) | Cxxx-NCR-002236 | NCR | CMR Tow Path Time between concrete loads |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2016-03-13 | 2016-02-22 16:09 | -20 | 2016-02-12 13:50 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | During capping beam 1 pour the time between the first and second load was recorded at 38min. Please find attached PML 2207 for records.
| 03SR - Stations (RfL) | Cxxx-NCR-002237 | NCR | EIP First Floor Cladding Channel Disposition |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2016-03-31 | 2016-03-23 08:55 | -8 | 2016-02-19 13:16 | Civil - Civil Engineering General | 2000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Previous Construction - Problems based on previous construction errors | Completed |  | Drawings: Cxxx-MRG-A-DWG-CR094_WS111-50780 rev p01, Cxxx-MRG-A-DWG-CR094-WS111-50725-rev P03 PTR: Cxxx-NCR-00207 MCR: Cxxx-MRG-A-QAP-CR094_WS111-50013 F1 type cladding fixing on underside of first floor cast 800mm from the adjacent F1 type cladding fixing. Drawing state 900mm, hence 100mm out of position. This will hold Unit 39 in place.
| 03SR - Stations (RfL) | Cxxx-NCR-002238 | NCR | NOS Bridge - Deck spray waterproofing thickness in west plate recess |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2016-03-31 | 2016-02-25 11:27 | -35 | 2016-02-16 07:45 | Civil - Civil Engineering General | 5000 |  | Incorrect Installation | Repair | 3 (3-6k) | Complete | Supervision - Insufficient supervision | Completed |  | Deck spray waterproofing thickness in the west plate recess has been applied at an excessive thickness over a 1.5m length, this will stop the cover plate being installed correctly.
| 03SR - Stations (RfL) | Cxxx-NCR-002239 | NCR | Works continuing without an approved MCR |  | Crossrail | XRL | PML - Pudding Mill Lane Portal (Central) |  | 2016-03-24 | 2016-03-21 10:38 | -3 | 2016-02-15 16:15 | Materials - Approval | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | After being asked to attend an inspection of grouting works to the RRV ramp, it became apparent that the grout being proposed had not been accepted by Crossrail. The MCR for Instarmac HF grout was not available on eB, nor was provided to Crossrail until being requested. Despite this, __ continued with the works.
| 03SR - Stations (RfL) | Cxxx-NCR-002240 | NCR | MGL Bridges - Eastbound bridge end walkway planels |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2016-03-02 | 2016-03-02 13:54 | 0 | 2016-02-17 08:31 | Civil - Civil Engineering General | 5000 |  | Manufacturing Defect | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The end walkway panels to the MGL Eastbound bridge do not fit and therefore require modification. The pre-drilled holes in the PFC channels do not line up with the walkway brackets.
| 03SR - Stations (RfL) | Cxxx-NCR-002241 | NCR | Stage 1 Concrete - West Bound EIP Man-hole |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2017-05-05 | 2017-05-04 13:48 | -1 | 2016-02-19 15:51 | Civil - Civil Engineering General | 20000 |  | Design | Repair | 2 (6-60k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | Cxxx have constructed the west bound EIP manhole as detailed in Cxxx-RFI-003597 and Cxxx-RFI-003666. As seen on the attached photograph, water is penetrating between the stage 0 and stage 1 concrete. The water is collecting within the manhole. Cxxx are not aware of any permanent drainage or pumping from the manholes.
| 03SR - Stations (RfL) | Cxxx-NCR-002242 | NCR | Dewatering Well L15 Removed During Excavation |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2016-03-16 | 2016-02-23 11:40 | -22 | 2016-02-17 11:25 | Civil - Base Course | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Dewatering Well L15 was removed during excavation, backfilled with bentonite pellets and no records are available. This was removed during the excavation/formation dates (between 30-06-15 and 02-07-15). The well was damaged beyond repair and was therefore backfilled using bentonite pellets and blinded over. There is no defect within the Permanent Works. Please find attached the best photographic evidence available showing the well in existence and then not at blinding level. The original marked up photographs will be included into the dewatering package. Also attached are statements from the operational/site team involved with the excavation works. A ground radar scan was also undertaken to ensure the validity of the statements. This will be made available and screen shots uploaded to EB
| 03SR - Stations (RfL) | Cxxx-NCR-002243 | NCR | Access Ramp Retaining Wall N2 Parapet Bedding Grout |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2016-05-17 | 2016-04-15 09:26 | -32 | 2016-02-17 17:10 | Civil - Street Furniture | 500 |  | Testing and Commissioning | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | The bedding grout for the N2 Parapet base plate was undertaken without a part of item 4.2 of the ITP for Handrail and Parapets to all Structures Cxxx-MRG-C-ITP-CR094_WS111-50050 Rev 08 being complete (the flow test).
| 03SR - Stations (RfL) | Cxxx-NCR-002244 | NCR | Pre cast concrete cladding documents sitting at a Code 2 for over 3 months |  | Crossrail | XRL | PML - Pudding Mill Lane Portal (Central) |  | 2016-05-09 | 2016-05-05 15:42 | -4 | 2016-02-17 15:55 | Architectural - General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Improper resource allocation | Completed |  | During a planned Crossrail surveillance undertaken on 17th Feb 2016 which looked at documentation relating to the pre cast cladding works, it was identified that ITP (design, manufacture and supply) Cxxx-MRG-A-ITP-CR094_WS111-50024 which involves the control of fabrication works at __ Pre cast yard, has been at a Code 2 Decal since October 2015. Additionally it was noted that ‘pre cast cladding design calculations’ document Cxxx-MRG-A-XCL-CR094_WS111-50001 which involves the design of the pre cast panels has also been at a Code 2 Decal since October 2015. Works Information Vol 2B Part 14 states “In the case of the first submission of a deliverable, in this section, for the Project Manager’s acceptance, the Project Manager replies within 4 weeks of the date of submission. Any further revisions, submissions and responses by the Contractor or Project Manager shall be made within the period for reply.”
| 03SR - Stations (RfL) | Cxxx-NCR-002245 | NCR | Cladding panels delivered to site are not being green cable tied and accompanied by __ advice note as required by the ITP |  | Crossrail | XRL | PML - Pudding Mill Lane Portal (Central) |  | 2016-05-06 | 2016-05-05 16:35 | -1 | 2016-02-17 15:58 | Architectural - General | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Supervision - Insufficient supervision | Completed |  | During a planned Crossrail surveillance undertaken on 17th Feb 2016 which looked at the delivery and receipt of the pre cast cladding panels, it was witnessed during a site visit that the delivered pre cast cladding panels were not being green cable tied and accompanied by an __ advice note as required by ITP (design, manufacture and supply) Cxxx-MRG-A-ITP-CR094_WS111-50024 Inspection Numbers below: “9.02 Ensure all units for intended delivery have Green cable tie tags.” Which should be a check undertaken by __ prior to dispatch and recorded on QA check sheet D1.12. “9.06 Record units to be transported onto __ Advice Note which will be presented on site for signature.” Which should be completed by __ on all successfully loaded pre cast units.
| 03SR - Stations (RfL) | Cxxx-NCR-002246 | NCR | No evidence available to provide assurance that cladding panels delivered to site are being checked prior to installation |  | Crossrail | XRL | PML - Pudding Mill Lane Portal (Central) |  | 2016-05-09 | 2016-05-06 09:09 | -3 | 2016-02-17 16:00 | Architectural - General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Other management problem | Completed |  | During a planned Crossrail surveillance undertaken on 17th Feb 2016 which looked at the pre installation checks of the pre cast cladding panels, no evidence could be available to demonstrate that the following has been undertaken prior to installation of the panels; checks against the design drawings; checks against the agreed finish sample and checks for damage or defects following transportation. Additionally it was noted that ITP (installation) Cxxx-MRG-A-ITP-CR094_WS111-50092 omitted any requirement for such checks referring to only setting out and post installation checks prior to handover. It was also found that the finish reference sample was located in the site offices and not at site; as such it was not being used to check against the delivered panels. As no checks are documented as being undertaken prior to installation, pre cast panels could be installed that are outside of the design tolerances and/or contain damage/ defects. “ISO 9001 (Quality Management System), requires that organisations establish and implement the inspection, or other activities, necessary for ensuring that purchased products meet specified purchase requirements (cl.7.4.3), whilst ensuring records are established providing evidence of conformance to requirements (cl. 4.2.4) and that the personnel performing the inspections are competent (cl. 6.2.1).“
| 03SR - Stations (RfL) | Cxxx-NCR-002248 | NCR | Cut and Cover Phase 3 - Central Walls Low Strength Results at 28 Days |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2016-03-31 | 2016-03-04 13:15 | -27 | 2016-02-24 08:17 | Civil - Civil Engineering General | 500 |  | Material | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | On review it has been identified that at wall panels 8A and 9B a strength lower than target 50 N/mm2 and acceptable minimum 46 N/mm2. Panel 8A recorded a result of (average) 44.1 Nmm2 and 9B showed average of 44.4 N/mm2.
| 03SR - Stations (RfL) | Cxxx-NCR-002249 | NCR | Cut and Cover Phase 3 - Covered Ramp Central Walls Points Out of Positional Tolerance |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2016-03-31 | 2016-03-04 14:53 | -27 | 2016-02-24 08:29 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | This NCR is related to previous NCR 2077 which highlighted 4 points recorded out of positional tolerance on the Westbound side of the Central Wall at Bay 7. On review, it has been found that there are a further 14 points out of tolerance through the Cut and Cover Phase 3 and 22 points out of tolerance through the Covered Ramp (please see highlighted as-built survey attached). The locations were found to be out of tolerance by between 1 - 8mm.
| 03SR - Stations (RfL) | Cxxx-NCR-002250 | NCR | Cut and Cover Phase 3 - Covered Ramp Central Walls Cover Meter Survey Points Out of Tolerance |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2016-03-31 | 2016-03-10 15:10 | -21 | 2016-02-24 08:27 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | On review it has been identified that there are a number of cover meter readings out of tolerance along the Central Walls through Cut and cover Phase 3 and Covered Ramp. The points have been found to be out of tolerance between 1 – 4mm as per the attached highlighted cover meter surveys.
| 03SR - Stations (RfL) | Cxxx-NCR-002251 | NCR | Cut and Cover Phase 3 - Covered Ramp Central Walls Delayed Concrete Deliveries |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2016-03-31 | 2016-03-07 16:58 | -24 | 2016-02-24 08:25 | Civil - Civil Engineering General | 500 |  | Equipment Breakdown | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | During Central Wall pours at Bay 7 and 15 there was an interruption from the usual prompt delivery service from the __ Batching Plant at Canning Town for unknown reasons. The time lapse between the delivery of the second and third loads was 65 minutes and 50 minutes at wall panels 7A and 15B respectively.
| 03SR - Stations (RfL) | Cxxx-NCR-002252 | NCR | Cut and Cover Phase 3 - Covered Ramp Central Walls Missing Signatures |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2016-04-21 | 2016-04-12 16:49 | -9 | 2016-02-24 08:21 | Civil - Civil Engineering General | 0 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | A number of MPB Subcontractor sign-off signatures have been found to have been missed within the Central Walls Quality documentation.
| 03SR - Stations (RfL) | Cxxx-NCR-002253 | NCR | Four Span Underpass - Missing Cube Tests - North Wall Pour_3 & South Wall Pour_1 |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2016-04-29 | 2016-04-14 11:58 | -15 | 2016-02-26 12:47 | Civil - Civil Engineering General | 2000 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Worker not correctly instructed | Completed |  | Please refer to; Spec - Cxxx-SWN-S-RSP-CR094_PT002-00002 - Clause E10.508 The concrete pours for the South Wall Pour 1 & North Wall Pour 3 initially were estimated to require 24m^3 of concrete, however as the pour progressed the order for both pours were increased. Consequently the number of test samples required also increased from 4No. cubes per pour to 8No. cubes per pour. Unfortunately for each pour only 4No. cubes were taken instead of the required 8No. cubes
| 03SR - Stations (RfL) | Cxxx-NCR-002254 | NCR | MGL EB/WB paintwork |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2016-04-14 | 2016-04-01 10:57 | -13 | 2016-02-26 11:48 | Civil - Civil Engineering General | 5000 |  | Damaged | Repair | 3 (3-6k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | The web plates the EB and WB CRL MGL bridges require a repaint due to damage caused by construction activities.
| 03SR - Stations (RfL) | Cxxx-NCR-002255 | NCR | ITP - STRUCTURAL CONCRETE |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2016-04-08 | 2016-03-31 13:08 | -8 | 2016-02-29 10:25 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Supervision - Insufficient supervision | Completed |  | Documentation procedure. ITP affects the following packages (dated between 09/09/2015 - 07/03/2016) EIP - Headwall - Cxxx-MRG-O-CER-CR094_WS111-50044 (waiting to be coded) CRL Retaining Wall 1 Base Phase 2 - Cxxx-MRG-O-CER-CR094_WS111-50067 (already received code 1) Wall Phase 2 - Cxxx-MRG-O-CER-CR094_WS111-50131 (already received code 1) Cut & Cover Phase 2A & 11kV Roof Slab (Excluding Cxxx Opening) - Cxxx-MRG-O-CER-CR094_WS111-50210 (already received code 1) Waterproofing and Backfill to Roof - Cxxx-MRG-O-CER-CR094_WS111-50220 (waiting to be coded) Covered Ramp South Upstand Wall (1 to 7) RC - Cxxx-MRG-O-CER-CR094_WS111-50187 (already received code 1) 4 Span Underpass Pier Wall 5 - Cxxx-MRG-O-CER-CR094_WS111-50205 (already received code 1) CRL Deck GL 1-5 - Cxxx-MRG-O-CER-CR094_WS111-50206 (already received code 1) Track Support Slab Slab Cxxx-MRG-O-CER-CR094_WS111-50072 (already received code 1) Road Rail Vehicle Ramp - Base Slab and Walls - Phase 2 (Pile Cap Pour 3 / Ramp & Main Wall ‘A’/CRL 2 Wall) Cxxx-MRG-O-CER-CR094_WS111-50209 (already received code 1) Greenway Ramp RC Structure Cxxx-MRG-O-CER-CR094_WS111-50093 (already received code 1) East Track Slab RC Slab Cxxx-MRG-O-CER-CR094_WS111-50216 (already received code 1)
| 03SR - Stations (RfL) | Cxxx-NCR-002256 | NCR | CMR CRL-DLR cover plates - Position and holes size |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2016-10-23 | 2016-10-19 10:49 | -4 | 2016-03-02 16:49 | Civil - Civil Engineering General | 2000 |  | Design | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The cover plates positioned between CMR CRL-DLR bridge have being installed with the following deficiencies. Photos 1 & 2 highlight the locations of the items below. - Gap no. 1 between plates 1-2mm (Photo 3) - Gap no. 2 between plates 5-6mm (Photo 4) - Gap no. 3 between plates 5-6mm (Photo 5 - Gap between all plates and DLR handrail is 0-2mm (Photo 6) - Fixing hole size does not allow for top hat to be inserted (Various photos)
| 03SR - Stations (RfL) | Cxxx-NCR-002257 | NCR | EIP - Waterbar in Ground Slab Opening Damaged |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2016-04-08 | 2016-03-14 12:28 | -25 | 2016-03-09 12:46 | Civil - Civil Engineering General | 5000 |  | Damaged | Repair | 3 (3-6k) | Complete | Material/Preservation Problems - Improper preservation of material after installation | Completed |  | Drawings: PTR: Cxxx-NCR-001982, Cxxx-FCD-002130 The waterstop detailed in FCD#2130 has been damaged in one isolated location as per attached drawing. See attached photo of damage.
| 03SR - Stations (RfL) | Cxxx-NCR-002258 | NCR | Stage 1 Concrete – C&C2, C&C3 and Covered Ramp Waiting time between concrete loads above 30 mins |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2016-05-02 | 2016-04-01 15:19 | -31 | 2016-03-23 16:13 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Supervision - Insufficient supervision | Completed |  | Stage 1 Concrete – C&C2, C&C3 and Covered Ramp Waiting time between concrete loads above 30 mins Stage One Concrete has now been completed throughout the Cut and Cover 2, Cut and Cover 3 and Covered Ramp structures. During these works, 18 of the 52 concrete pours carried out occurred with waiting times between concrete loads of over 30 minutes, hence not meeting specification requirements. However, Cxxx propose that the concrete poured is still acceptable for the reasons below: a) Please refer to the Slump testing of the Stage One trial, with the use of the same S3 concrete mixture. The workability results show that the mix loses an average slump of 30mm over an hourly period, and the material was workable for the two hour duration of the test. Due to the fact that all of the pours stated above had waiting times between concrete loads of less than 120 minutes, and slumped at the top end of the allowable workability range (see attached slump records) it can be assumed that the slump for these pours will have still been within S3 tolerance, and hence acceptable. b) The concrete within each pour was tested to check whether it was in a workable state continually during the waiting time, with no resulting signs of concrete cracking or cold joints with the base slab. c) Finally, the first load of concrete would also have been partially still within the concrete pump awaiting arrival of the second load. Upon arrival of the second load this older material was pushed through the pump without blockage, meaning the 1st load of concrete would still have been within a workable state
| 03SR - Stations (RfL) | Cxxx-NCR-002259 | NCR | Leaks on roof slab soffit C&C ph3 |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2016-04-21 | 2016-04-18 12:56 | -3 | 2016-03-09 12:51 | Civil - Civil Engineering General | 4500 |  | Workmanship | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | It has been noticed that there are a number of leaks that have appeared between secant piles and roof slab interface in Cut and Cover Ph3. The leaks are weeping and require sealing as agreed with Cxxx and Crossrail. The locations of these leaks are at the following chainages in the Eb tunnel: 1. 14356 2. 14365 3. 14379
| 03SR - Stations (RfL) | Cxxx-NCR-002261 | NCR | C&C phase 3 roof slab pours - time between concrete loads |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2016-03-21 | 2016-03-17 12:46 | -4 | 2016-03-04 15:49 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | During final review of the QA package for C&C phase 3 roof slab, we have noted 4No occasions where the max time between loads was exceeded. 1) bay 9 = 1 min over, 2) bay 8 = 16 mins over, 3) Bay 4 = 7 mins over & 4) bay 1+2 = 4 mins over.
| 03SR - Stations (RfL) | Cxxx-NCR-002262 | NCR | Covered Ramp roof slab - cover readings out of tolerance |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2016-03-21 | 2016-03-17 12:49 | -4 | 2016-03-07 13:49 | Civil - Civil Engineering General | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | during final review of the quality pack for Covered Ramp roof slab, it has been noted that some cover readings are outside of the specified tolerance to the top surface of the slabs. Details are below. bay 10/11 - 2No @ 1mm bay 12 - 2N0 @ 1mm bay 13 - 1No @ 4mm bay 14 - 3No @ 1mm & 1No @ 2mm bay 15 - 2No @ 1mm bay 16 - 1No @ 1mm, 2No @ 2mm & 1No @ 3mm
| 03SR - Stations (RfL) | Cxxx-NCR-002263 | NCR | Covered Ramp roof slab concrete pours - max time between loads exceeded |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2016-03-31 | 2016-03-18 13:24 | -13 | 2016-03-07 14:01 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | During a final review of the Covered Ramp roof slab quality package, it has been noted that the max specified time between loads had been exceeded a few times. Details are below. bay 10/11 - 3 mins over & 2 mins over bay 13 - 19 mins over bay 16 - 2 mins over.
| 03SR - Stations (RfL) | Cxxx-NCR-002264 | NCR | Secant wall Capping Beam concrete - max time between loads exceeded |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2016-03-31 | 2016-03-10 15:21 | -21 | 2016-03-07 16:05 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | during final review of the Capping Beam quality package, it has been noted that the max specified time between concrete loads had been exceeded on various pours. Details are below. Pour 1 - 1No 10 mins over Pour 3 - 1No 18 mins over Pour 8 - 1No 3 mins over Pour 12 - 1No 16 mins over Pour 6 - 1No 5 mins over Pour 10 - 1No 3 mins over
| 03SR - Stations (RfL) | Cxxx-NCR-002265 | NCR | Secant wall Capping beam & north wall concrete cover readings exceeding the limits |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2016-04-01 | 2016-03-22 12:32 | -10 | 2016-03-08 21:08 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | During a final review of the quality package for the Covered Ramp capping beam & north wall, it has been noted that several cover readings exceed the specified limits ranging from 1mm - 6mm.
| 03SR - Stations (RfL) | Cxxx-NCR-002266 | NCR | Cut and Cover Phase 3 - Covered Ramp Base Slabs Points Outside Positional Tolerance |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2016-05-20 | 2016-04-19 12:10 | -31 | 2016-03-11 09:36 | Civil - Civil Engineering General | 1000 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During the review of quality records it has been found that a number of as-built survey points in the Cut and Cover Phase 3 and Covered Ramp are slightly outside of the specified tolerance. Bay 2 - 1 point out of tolerance 3mm. Bay 4 - 1 point out of tolerance 8mm. Bay 5 - 2 points out of tolerance 4mm and 10mm. Bay 6 - 4 points out of tolerance 3 x 1mm, and 1 x 7mm. Bay 8 - 1 point out of tolerance 6mm. Bay 10/11 - 2 points out of tolerance 2mm and 5mm Bay 12 - 2 points out of tolerance 4mm and 5mm. Bay 16 - 1 point out of tolerance 1mm. Please see attached as-built surveys as reference.
| 03SR - Stations (RfL) | Cxxx-NCR-002267 | NCR | Leaks coming through firelining |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2016-04-26 | 2016-04-12 16:37 | -14 | 2016-03-15 10:56 | Civil - Civil Engineering General | 8000 |  | Workmanship | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | A number of leaks have come through the firelining system and Cxxx and Crossrail would like these to be sealed. Details below: 1. Ch14245 EB Panel N10/N11 () joint leaking with heavy running water. This leak appeared once 11kV/2A soffit joint was sealed. 2. Very minor small damp patches coming through firelining <1.0m2 between D-wall joint S11/S12 (). 3. Very minor small damp patches coming through firelining <1.0m2 between D-wall joint S14/S15 ().
| 03SR - Stations (RfL) | Cxxx-NCR-002268 | NCR | Leaks Coming through D-wall and Roof interface |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2016-04-21 | 2016-04-15 09:28 | -6 | 2016-03-15 14:19 | Civil - Civil Engineering General | 3000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | A couple of damp patches have appeared on the roof slab soffit which seem to be coming through the roof and D-wall interface. Crossrail/Cxxx would like these to be sealed. Details below: 1. CH14293 EB small damp patch < 1.0m2 appearing on roof slab soffit adjacent to D-wall Panel N29 (__) (leak No.5 on attached drawing) 2. CH14464 WB small damp patch < 1.0m2 appearing on roof slab soffit adjacent to D-wall Panel S21/S22 () (leak No.21 on attached drawing)
| 03SR - Stations (RfL) | Cxxx-NCR-002269 | NCR | Leaks coming through secant and roof interface |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2016-04-01 | 2016-03-29 12:30 | -3 | 2016-03-15 16:03 | Civil - Civil Engineering General | 3000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | A number of leaks are appearing to be coming through secant and roof interface. Crossrail/Cxxx would like these to be sealed. Details below: 1. Small damp <1.0m2 weeping coming through secant pile and roof joint between P16/P17. (leak No. 8 on attached drawing) 2. 2 small damp patches <1.0m2 weeping coming through secant pile. (leak No. 11 on attached drawing)
| 03SR - Stations (RfL) | Cxxx-NCR-002270 | NCR | CMR CRL Bridge - Bull head rails to be installed in NCR 1793 remedial location |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2016-12-16 | 2016-11-25 10:29 | -21 | 2016-03-16 16:06 | Civil - Civil Engineering General | 1000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | NCR 1793 remedial action implemented in 2014 did not fully clarify how the Bull head rails should be positioned on the stepped section of wall. The exact positions of the rails identified on drawing Cxxx-MMD-C-EDR-CRG06-00086 will need to be modified to fit the 50mm step in the concrete installed as part of the NCR remedial.
| 03SR - Stations (RfL) | Cxxx-NCR-002272 | NCR | Stage 1 Concrete - UTX Duct Height Above Concrete |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2016-04-21 | 2016-04-05 11:07 | -16 | 2016-03-21 11:09 | Civil - Civil Engineering General | 5000 |  | Damaged | Use As-Is | 3 (3-6k) | Complete | Material/Preservation Problems - Improper preservation of material after installation | Completed |  | In accordance with drawing Cxxx-SWN-S-DDD-CR094_PT002_Z-81131 the stage 1 UTX ducts situated in the centre of the four foot track bed are shown to extend to the level of the second stage concrete. Although the height of the second stage concrete hasn't been provided, Cxxx have are not going to comply with this requirement in the east bound tunnel. All 10no. HDPE UTXs within the east bound tunnel have been cut to the level of the four foot stage 1 concrete (refer to photograph 1). This has been to allow plant to access through the tunnels during the construction in addition to minimising the trip hazard of the ducts. The stainless steel UTXs within the west bound tunnel will be left proud of the stage 1 concrete, although as no levels of second stage concrete have been provided, Cxxx are not able to determine if these are being left at the height of the second stage. Due to the requirement to move plant around the tunnels during the Cxxx construction works, a number of the stainless steel UTXs have been dented above concrete level.
| 03SR - Stations (RfL) | Cxxx-NCR-002273 | NCR | C&C2 - Central Wall Finish |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2016-03-31 | 2016-04-02 13:30 | 2 | 2016-03-22 10:49 | Civil - Civil Engineering General | 1000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Drawings: Cxxx-SWN-S-DDD-CR094_PT002_Z-71475 The Central Wall at Eastbound Chainage 14300 was poured with C40/50B-fibres (S4 slump) from __ on 28/03/13. It has recently been noticed that there is a non-uniform pattern on the face of the wall, not complying to the required F2 trial panel. This appears to be from ‘Sand Runs’ during the concrete pour. The max depth of the sand is approx. 10mm. It has been requested from Crossrail that this must be raised as an NCR as opposed to a Snag.
| 03SR - Stations (RfL) | Cxxx-NCR-002274 | NCR | Attenuation Tank NRTW 1.9 Incorrect Blinding Level |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2016-04-04 | 2016-03-23 08:57 | -12 | 2016-03-21 10:24 | Civil - Drainage | 3000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Personnel Error - Inattention to detail | Completed |  | The founding layer of attenuation tank NRTW 1.9 was designed to comprise of a minimum 75mm concrete blinding layer overlaid with 50mm of natural sand or 6L material. The concrete blinding level for the underside of the attenuation tank NRTW 1.9 has been set out incorrectly level of the blinding was up to 100mm low at the up-stream end of the culvert.
| 03SR - Stations (RfL) | Cxxx-NCR-002275 | NCR | Four Span Underpass - Concrete Poured with Open FCD |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2016-05-20 | 2016-04-21 11:20 | -29 | 2016-03-22 17:03 | Civil - Civil Engineering General | 1500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | Please refer to: PTR-FCD-2356, TW-DWG-1838-83-C0 (attached), The concrete pour for the Up-Electric wall was poured without FCD 2356 being closed out.
| 03SR - Stations (RfL) | Cxxx-NCR-002276 | NCR | CSJV DWall leak |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2016-04-21 | 2016-04-08 11:31 | -13 | 2016-03-23 09:46 | Civil - Civil Engineering General | 3500 |  | Workmanship | Repair | 3 (3-6k) | Complete | Previous Construction - Other | Completed |  | A leak has appeared between D-Wall panel N7/N8 ( D-Wall) which is running and requires sealing. Leak sealing has commenced on this joint and will be sealed in the same way as previous leaks. Location of the leak is CH14198 EB. This was classified as Leak #2 on the attached drawing and was previously a small damp patch where a monitoring station was fixed.
| 03SR - Stations (RfL) | Cxxx-NCR-002277 | NCR | Leak on D-wall panel N29 |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2016-04-21 | 2016-04-08 12:14 | -13 | 2016-03-23 10:20 | Civil - Civil Engineering General | 2000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Previous Construction - Problems based on previous construction errors | Completed |  | A leak has appeared on D-Wall panel N29 which is weeping and requires sealing. Leak sealing has already commenced on this panel however, the weeping damp patch has only moved up. It has been agreed wit Cxxx and Crossrail to install a damp patch detail over the damp patch and reinstate firelining.
| 03SR - Stations (RfL) | Cxxx-NCR-002278 | NCR | Stage One - C&C2 and C&C3 As-Built Survey Levels Out of Tolerance |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2016-04-06 | 2016-03-30 08:57 | -7 | 2016-03-23 18:11 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Cxxx have now completed the Stage 1 works within the C&C2 and C&C3 structures. As-built surveys have been carried out and show there are a number of points out of the required concrete level tolerance, within Bays 5 to 19 Eastbound and Westbound. Please refer to the attached as-built surveys with out of tolerance points highlighted in orange. There are also locations with track edges marginally out of alignment (generally by 1mm or 2mm.) These are seen as being within the survey tolerances of the equipment being used during the works.
| 03SR - Stations (RfL) | Cxxx-NCR-002280 | NCR | NR Up Electric Attenuation Tank NRTW 1.9 joint widths and damaged concrete |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2016-07-29 | 2016-07-11 10:33 | -18 | 2016-03-24 15:44 | Civil - Drainage | 10000 |  | Workmanship | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The precast concrete Attenuation Tank NRTW 1.9 consists of 22 culvert units and 2 end units, precast concrete units were supplied by __. The __ standard installation detail, refer attached, shows a bitumen Tokstrip sealant placed central within the joint, with the joint closed during the culvert install to provide a nominal 10mm gap. To provide a watertight seal, this gap is sealed around the internal faces with __ __ 600 in accordance with NCR 2058 and the manufacturer’s instructions. The gap spacing between adjacent units of attenuation tank NRTW 1.9 varies between 2-3mm and 35mm at certain locations, please refer the attached survey of each unit.
| 03SR - Stations (RfL) | Cxxx-NCR-002281 | NCR | NR Up Electric Attenuation Tank NRTW 1.9 damaged concrete |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2016-04-28 | 2016-04-26 10:30 | -2 | 2016-03-24 17:23 | Civil - Drainage | 1000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The precast concrete Attenuation Tank NRTW 1.9 consists of 22 culvert units and 2 end units, precast concrete units were supplied by __. There are two issues covered in this NCR. During the pulling together of the units with the culvert puller in 3 number locations the concrete has been damaged on the edge of the culverts, refer attached photographs.
| 03SR - Stations (RfL) | Cxxx-NCR-002282 | NCR | Damaged Waterbar |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2016-04-24 | 2016-04-12 15:41 | -12 | 2016-04-04 07:51 | Civil - Civil Engineering General | 1000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | The Rearguard waterstop installed has been damaged in the location of the joint between the South Upstand Wall and Discreet Wall. It is not known how this damage has happened, but one can surmise that it has been damaged by mechanical plant during excavating/backfilling activities. Please see attached photograph of damage.
| 03SR - Stations (RfL) | Cxxx-NCR-002283 | NCR | Cut and Cover Phase 3: Minor Seepage at Central Wall |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2016-05-27 | 2016-04-14 08:25 | -43 | 2016-04-02 07:24 | Civil - Civil Engineering General | 3000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Not Defined | Completed |  | A damp patch has been found at both sides of the central wall at the East end of the Central Diaphragm wall at the interface with the Bay 3 Central Wall. Please see attached photograph records.
| 03SR - Stations (RfL) | Cxxx-NCR-002284 | NCR | TSS Drainage- Pipe Run NRTE1.4 Backdrop incorrect level |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2016-06-11 | 2016-05-13 15:44 | -29 | 2016-04-12 15:49 | Civil - Drainage | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | When constructing NRTE1.4 run on the Track Support Slab we had to construct a backdrop that was over 2 metres high for the inlet pipe of NRE01 manhole. This required MS to order a bespoke 450mm T intersection pipe to be able to make the levels work. We ordered the bespoke rocker pipe to the best of our abilities with help from our manufacturer __'s (Attached Sketch) and was installed by our contractor (Caulfield's Contractors) meaning the pipe was installed 69mm too high (107.66. After informal consultation with Cxxx the proposal was to lay the pipe at 1/389 and raise the outlet invert level to 107.707m of NRTE1.4 chamber which is 54mm higher than design.
| 03SR - Stations (RfL) | Cxxx-NCR-002285 | NCR | Cxxx EIP - CDFM Thrust Brackets |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2016-08-01 | 2016-07-22 08:30 | -10 | 2016-04-04 15:20 | Mechanical - Piping | 1000 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Thrust Brackets on CDFM pipework within EIP not installed to correct design as detailed on the attached drawings.
| 03SR - Stations (RfL) | Cxxx-NCR-002286 | NCR | Cut and Cover Phase 3 Central Walls - Low Cube Strengths at 28 Days |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2016-05-31 | 2016-04-14 10:03 | -47 | 2016-04-05 12:17 | Civil - Civil Engineering General | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | It has been identified that 2 central wall panels in the Cut and Cover Phase 3 structure, (8A and 9B) have recorded below target strengths at 28 days. Please see attached cube sample reports.
| 03SR - Stations (RfL) | Cxxx-NCR-002287 | NCR | Four Span Underpass - Making Good to Construction Joint at Pier 3 on Up Electric Wall |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2016-11-21 | 2016-10-19 16:50 | -33 | 2016-04-07 16:06 | Civil - Civil Engineering General | 5000 |  | Workmanship | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Other | Completed |  | Please refer to: Attached Image. After striking the formwork for the Up-Electric wall between GL_2-3 it was noticed that the concrete created a 10-15mm lip that lapped on to the GL_-3-4 wall.
| 03SR - Stations (RfL) | Cxxx-NCR-002288 | NCR | EIP - Western Core Disposition |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2016-05-13 | 2016-05-09 13:58 | -4 | 2016-04-07 11:44 | Civil - Civil Engineering General | 5000 |  | Supervision/Management | Use As-Is | 3 (3-6k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | Drawings: Cxxx-SWN-S-DDA-CR094_PT002_4-80100, Cxxx-SWN-S-DDB-CR094_PT002_Z-80200 An as-built (attached) on the EIP western staircore at ground level shows that the internal core wall is out of positional tolerance. This is also visible as per attached photo.
| 03SR - Stations (RfL) | Cxxx-NCR-002289 | NCR | EIP - Chipped Cladding Corbels during Installation |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2016-06-24 | 2016-05-25 07:52 | -30 | 2016-04-07 16:56 | Architectural - Roofing & Exterior Treatment | 3000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Improper handling of material | Completed |  | During the installation process for the EIP Cladding panels positioned on the North Elevation it has been identified that several corbels have suffered small chips on the surface. One corbel for cladding panel Unit Ref. 48 sustained a larger affected area which exposed the reinforcement. (See attached photographic evidence and mark-up drawing)
| 03SR - Stations (RfL) | Cxxx-NCR-002290 | NCR | Four Span Underpass - Ommission of Dummy Expansion Joints |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2016-09-16 | 2016-08-06 14:31 | -41 | 2016-04-07 16:08 | Civil - Civil Engineering General | 5000 |  | Incorrect Installation | Repair | 3 (3-6k) | Complete | Management Problem - Other | Completed |  | Please refer to: Attached Sketches, PTR-RFI-2973, PTR-FCD-2242. In order to keep the break-up in the curtain wall into the panels replicating those of the wall behind the DLR station, dummy movement joints were proposed in PTR-RFI-2973 positioned at the construction joints. After pouring the wall between GL_2-3 and GL_3-4 it was noted by Cxxx that no dummy joints were placed in at CJ_2, CJ_3 and once poured the dummy joint at CJ_4 will be left out as well. The location of the CJ's at Pier_2 and Pier_4 are not where they are when the dummy joints were proposed in RFI-2973 due to changes made in PTR-FCD-2242.
| 03SR - Stations (RfL) | Cxxx-NCR-002291 | NCR | Covered Ramp Central Wall Panel 12B - Check Sheets Signed After Hold Point Date |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2016-05-31 | 2016-04-08 15:37 | -53 | 2016-04-07 12:14 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | It has been identified that the formwork/false-work and pre-pour check sheets for Pour 12B were signed after the Hold Point date (pour date). Relevant check sheets are attached.
| 03SR - Stations (RfL) | Cxxx-NCR-002292 | NCR | Stage 1 Concrete - Running Water within Pressure Relief Drainage |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2017-05-26 | 2017-05-11 15:03 | -15 | 2016-04-07 16:03 | Civil - Civil Engineering General | 20000 |  | Incorrect Installation | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | While carrying out the leak injection of the WB manhole detailed in the response to Cxxx-NCR-002241 it was noted that water was flowing out of the Pressure Relief Drainage (PRD) vent to the east of the manhole. The resin injection ceased immediately and the issue was reported to CRL and Cxxx. After discussions with Crossrail and Cxxx, Cxxx were asked to break out a section of the stage 1 shoulder in the location of the pressure relief vent to identify the source of the water. This break out concluded that the water was flowing through the PRD and the injection must have caused a blockage of the channel in the location of the manhole (see attached marked up drawing - Note: this can not be attached to the NCR so emailed to BS). Cxxx were asked by CRL and Cxxx during a pre-Cxxx handover meeting to carry out further investigation in to the initial source of the water. Dip and dye tests were carried out in the PRD concluding that the water was entering the PRD was contained within the 11kVA or EIP. To try and remediate the issue prior to the Cxxx handover, voids were broken in the stage 1 concrete at the joint between the C&C2 and 11kVA and within the 11kva. To date the source of the leak has not been identified.
| 03SR - Stations (RfL) | Cxxx-NCR-002293 | NCR | EIP - Headwall Collar Grout Tubes |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2016-05-10 | 2016-05-05 07:52 | -5 | 2016-04-12 06:44 | Civil - Civil Engineering General | 10000 |  | Supervision/Management | Use As-Is | 2 (6-60k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | Drawings: Cxxx-SWN-S-DDD-CR094_PT002_Z-80200 PTR: RFI#3671 Tubes for multiple injectable hydrophilic water stops in the EIP Headwall Collar have had the resin as per MCR Cxxx-MRG-C-QAP-CR094_WS111-50484 and RFI#3671 run through them, however, the tubes were unable to flush the product through.
| 03SR - Stations (RfL) | Cxxx-NCR-002294 | NCR | Stage 1 Concrete - Water Within Expansion Joints |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2017-05-05 | 2017-05-05 12:49 | 0 | 2016-04-08 10:03 | Civil - Civil Engineering General | 15000 |  | Design | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | In reference to drawing Cxxx-SWN-S-DDD-CR094_PT002_Z-81132 detail 05, Cxxx have installed __ 1 compressible filler within the stage 1 expansion joints. Upon the completion of the stage 1 works, Crossrail have raised a concern that there is water within the expansion joints. The expansion joint has been constructed in accordance with the design detail. As there has been a large amount of water created during the green-cutting of the concrete surfaces and cleaning the tunnels in advance of the Cxxx handover. It is thought that this water has entered the expansion joints.
| 03SR - Stations (RfL) | Cxxx-NCR-002295 | NCR | Evacuation Walkways - Points out of positional tolerance EB 14308 to 14541 and WB 14454 to 14711 |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2016-06-30 | 2016-05-09 12:46 | -52 | 2016-04-16 12:53 | Civil - Civil Engineering General | 1000 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | Further from previous NCR-2212 It has been it has been identified that a number of additional walkway platform points are outside tolerance between EB 14308 to 14541 and WB 14454 to 14711. The vertical out of tolerance points identified range from 1 - 15mm low and 1 - 3mm high. There are no points identified that are out of tolerance towards track alignment. There are 2 points out of tolerance with additional clearance away from track alignment; 1 point with 18mm additional at WB Ch 14617 and another with 2mm additional at EB 14320.
| 03SR - Stations (RfL) | Cxxx-NCR-002296 | NCR | C&C Capping Beam and North Wall Low Concrete Strength Results |  | Crossrail | XRL | PML - Pudding Mill Lane Portal (Central) |  | 2016-05-27 | 2016-05-24 09:29 | -3 | 2016-04-11 12:51 | Civil - Civil Engineering General | 500 |  | Material | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | After reviewing the construction records for the C&C tunnel capping beam and north wall, it appears that there are several instances where some of the concrete samples have not reached the required compressive strengths. This is true for Capping Beam pour 3 and North Wall pours 7 and 12. In all cases, the average 28 day strengths are low, and there are no 56 day results to confirm the strength of the concrete after this time.
| 03SR - Stations (RfL) | Cxxx-NCR-002297 | NCR | C&C Capping Beam and North Wall - Missing As-built Surveys |  | Crossrail | XRL | PML - Pudding Mill Lane Portal (Central) |  | 2016-05-16 | 2016-05-12 09:35 | -4 | 2016-04-11 13:16 | Civil - Civil Engineering General | 0 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Other management problem | Completed |  | While reviewing the construction records for the C&C tunnel north wall, it became apparent that there are several missing pre-pour and as-built survey. This is true for the North Wall pours 10, 11 12 and 13. In addition to this, the as-built surveys for pours 4, 5, 6, 7, 8 and 9 do not have the required level information (the surveys do not give a comparison to the design level information).
| 03SR - Stations (RfL) | Cxxx-NCR-002298 | NCR | CMR Tow Path Capping Beam level tolerance |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2016-07-31 | 2016-07-26 08:03 | -5 | 2016-04-14 13:47 | Civil - Structural Engineering | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Capping beams on the CMR tow path were set out to design position and level and jet washed post pour to leave an exposed aggregate finish as detailed on dwg Cxxx-MMD-D-DDD-CRG06_Z-00002. The as built survey for capping beams 1 - 5 shows difference to design level, please advice if the attached is acceptable.
| 03SR - Stations (RfL) | Cxxx-NCR-002299 | NCR | CMR Type 2 retaining wall and capping beam below strength cube result |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2016-07-15 | 2016-06-24 10:56 | -21 | 2016-04-22 09:01 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The specified mix for Type 2 retaining wall is C40/50C as per Cxxx-FCD-002207. The concrete cube result PML2150 (see attached) achieved a strength of 44.4N/mm2.
| 03SR - Stations (RfL) | Cxxx-NCR-002300 | NCR | Stage 1 - Stage One UTX and EIP Blockwork Interface Clash |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2017-02-28 | 2016-12-20 15:35 | -70 | 2016-04-19 16:25 | Civil - Civil Engineering General | 6000 |  | Design | Repair | 3 (3-6k) | Complete | Design Problem - Conflicting information on drawings | Completed |  | In order for Cxxx to produce the block work walls within the EIP cable riser, it was necessary to partially deconstruct a section of the Stage One UTX Up-stand housing the ducts (coded WUTX07-12). This problem was due to a conflict in design between the Stage One and EIP drawings. The resulting damage involves an area of 1100mmx100mm of the Permanent works being deconstructed. The UTX up-stand was removed prior to gaining acceptance from CRL due to the contractor standing awaiting a resolution. Sequentially, the Stage One duct Up-stand was produced on the 14.12.2015, with the EIP block work wall being installed during January 2016. The block work contractor was on site at the time of deconstruction, so Cxxx proceeded with the programme despite the design clash.
| 03SR - Stations (RfL) | Cxxx-NCR-002301 | NCR | Four Span Underpass - Problems Concerning Installation of Dowel Bars for U-bars in Up -Electric Wall |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2016-04-28 | 2016-04-28 15:00 | 0 | 2016-04-14 16:32 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Please refer to; PTR-FCD-2370, PTR-FCD-2303 The deck falsework has been installed between piers 2 and 3 and therefore there is insufficient working room to drill at the correct level.
| 03SR - Stations (RfL) | Cxxx-NCR-002302 | NCR | Four Span Underpass - Moving Construction joint at Pier 4 |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2016-05-16 | 2016-04-19 14:37 | -27 | 2016-04-14 16:31 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Please refer to; DWG-Cxxx-SWN-S-DDD-CR094_PT002_Z-68427, PTR-NCR-2290. As discussed in NCR-2290 the construction joint was going to be moved to the east side fof pier_4. As the wall has since be poured before a FCD was submitted Crossrail have requested that a NCR be raised. This NCR will in effect replace the FCD that was to be raised.
| 03SR - Stations (RfL) | Cxxx-NCR-002303 | NCR | EIP - Discrepancies for the Cladding Fixings |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2016-07-15 | 2016-07-06 14:01 | -9 | 2016-05-04 14:04 | Architectural - Roofing & Exterior Treatment | 6000 |  | Design | Repair | 3 (3-6k) | Complete | Design Problem - Conflicting information on drawings | Completed |  | Following progressive design reviews for the precast cladding units and builderswork fixing details we have identified discrepancies between the initial design Cxxx-MRG-A-DWG-CR094_WS111-50780 Rev P01 and the current design Cxxx-MRG-A-DWG-CR094-WS111-50780 Rev P04 (See attached mark-up drawings)
| 03SR - Stations (RfL) | Cxxx-NCR-002304 | NCR | MGL Bridge Country side abutment clashes with Bridge staircase upper brackets |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2016-07-15 | 2016-07-06 12:26 | -9 | 2016-04-25 11:22 | Civil - Civil Engineering General | 2500 |  | Design | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Please refer to: Cxxx-SWN-S-DDD-CR094_PT002_Z-51373 C02, Cxxx-SWN-S-DDD-CR094_PT002_2-51102 C01 Cxxx currently installing MGL Bridge staircases on Country side abutment and experiencing several design clashes. There are 3no staircases where upper outer side of the handrail bracket clashes with concrete abutment upstands (for locations of clashes see drawing attached with photographs). Cxxx carried out investigation and identified that bridge is not clashing with abutment upstands and there is no problem with steps aligning to bridge, just upper handrail brackets which extends 150mm sideways clashes with abutment. Thus original design has not considered position of bridge staircases against some Country side abutment up stands. To support this see attached 3D design model (not asbuilt) view of bridge staircases in relation to east abutment upstands showing that upper staircase bracket clashes with it (abutment upstand boundaries in yellow). In addition design distance between Country side bridge abutment upstands (CRL westbound) has insufficient room to accommodate bridge with walkways and staircases with handrail brackets.
| 03SR - Stations (RfL) | Cxxx-NCR-002305 | NCR | Covered ramp capping beam & north wall as-built tollerances (2No up to 3mm out) |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2016-06-17 | 2016-06-08 15:54 | -9 | 2016-04-21 13:32 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | During formal review of the Covered ramp capping beam & north wall, it has been requested by CRL to raise an NCR against as-built positional tolerances. 1No point on the capping beam in (pour 12) is 3mm out of tolerance and 1No point on the North wall (pour 6) is 2mm out of tolerance. see attached surveys.
| 03SR - Stations (RfL) | Cxxx-NCR-002306 | NCR | MGL bridge staircase handrail bracket cut on wrong side |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2016-06-30 | 2016-06-30 07:51 | 0 | 2016-05-03 17:42 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Cxxx-SWN-S-DDD-CR094_PT002_Z-51373 drawing asks for upper handrail bracket and handrail to be removed on track side, as it potentially clashes with train envelope. After removing all brackets it has been noticed that 1 of 12 the brackets have been cut on a wrong side, instead of track side the outer side was cut (CRL Westbound South side steps on Country side of the bridge).
| 03SR - Stations (RfL) | Cxxx-NCR-002307 | NCR | Missing Concrete Cube Results for Secant Piles |  | Crossrail | XRL | PML - Pudding Mill Lane Portal (Central) |  | 2016-05-13 | 2016-05-09 14:07 | -4 | 2016-04-22 11:29 | Civil - Civil Engineering General | 500 |  | Testing and Commissioning | Rework | 4 (0.5-3k) | Complete | Procedure Problem - Other | Completed |  | When reviewing the construction records for the secant piles, it was noted that several piles were missing the compressive cube results. This is the case for Piles 72, 104, 105, 109, 113 and 135 (and possibly others).
| 03SR - Stations (RfL) | Cxxx-NCR-002308 | NCR | EIP - Cladding Fixing F1 for Panel 35 not cast |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2016-06-30 | 2016-06-20 10:44 | -10 | 2016-05-04 14:53 | Civil - Civil Engineering General | 6000 |  | Incomplete Works | Repair | 3 (3-6k) | Complete | Supervision - Insufficient supervision | Completed |  | The cladding fixing F1 (2 No __ Channels) for Panel Unit Ref.35 on East Elevation shown on drawing No.Cxxx-MRG-A-DWG-CR094_WS111-50721 (__ - Bespoke Precast Concrete) have not been cast. (See attached marked-up drawings)
| 03SR - Stations (RfL) | Cxxx-NCR-002309 | NCR | 11kVa Soffit Works - Proximity of AEW & OLE Brackets to Spray Repair Areas |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2016-07-22 | 2016-07-21 08:48 | -1 | 2016-04-26 09:18 | Civil - Civil Engineering General | 5000 |  | Incorrect Installation | Repair | 3 (3-6k) | Complete | Management Problem - Inadequate supervision | Completed |  | It has become apparent that Cxxx have scabbled and sprayed the repair mix to the 11kVa soffit in areas which over lap with the locations of the AEW & OLE brackets to be fixed to the soffit. All repair areas have been scabbled, with mesh and retaining anchors fixed before then spraying the soffit with the repair mortar. These areas have been set out in accordance to areas of low cover to the B1 layer of rebar in the soffit. However, in the location of the AEW & OLE brackets the specification states that the areas of low cover on the soffit should be left as is in order to provide a flat level surface to install the bracket bolts. Please see attached as-built coordinates spread sheet, and mark up drawing showing the as-built dimensions from the centre of the bracket locations to the edge of the repair areas where the required 500mm distance has not been met.
| 03SR - Stations (RfL) | Cxxx-NCR-002310 | NCR | 11kVa - W10 Repair Area OLE Bracket Clash |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2016-06-10 | 2016-05-05 14:32 | -36 | 2016-04-26 16:18 | Civil - Civil Engineering General | 3000 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Misunderstand the definition of the requirement | Completed |  | Cxxx have prepared and broken out behind exposed rebar in the repair area W10 in order to expose rebar, which clashes OLE Bracket - XRA/14/321. specification states in Section 5.1 - "The repair in this location (XRA/14/321) is to provide a level area 1m by 1m centred on the OLE bracket coordinate. The total repair thickness at this location is not to exceed 105mm". The specification states a requirement to break out 25mm behind the B1 layer of rebar. In the location of bracket XRA/14/321 Cxxx have broken out 35mm behind the B1 layer of rebar, which means the total depth of repair in this location will be 115mm approx.
| 03SR - Stations (RfL) | Cxxx-NCR-002312 | NCR | Evacuation Walkways - Low Strength at 28 Days |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2016-08-31 | 2016-05-25 10:42 | -98 | 2016-05-24 09:28 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | During the course of the final review of the Evacuation Walkway quality documentation it has been identified that a low strength was recorded on cube test certificate PML 2034 at 28 days. There is also an error on the certificate as it shows the average of the 28 result with one of the 56 day results.
| 03SR - Stations (RfL) | Cxxx-NCR-002313 | NCR | EIP - Western Staircore Walls |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2016-06-30 | 2016-06-23 08:35 | -7 | 2016-05-12 11:33 | Civil - Civil Engineering General | 1000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | PTR: NCR#2288 Where stair unit 1/3 meets the western wall (approx level 97.997), there is kick back in the wall creating an approx 300mm long gap between the bracket for the stairs and the western wall in the north corner.
| 03SR - Stations (RfL) | Cxxx-NCR-002314 | NCR | EIP - Lintel Support Bracket Fabrication |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2016-07-29 | 2016-07-08 07:39 | -21 | 2016-05-13 09:48 | Civil - Civil Engineering General | 5000 |  | Supervision/Management | Use As-Is | 3 (3-6k) | Complete | Supervision - Other | Completed |  | Following the receipt of design information for required lintel angle support brackets within the EIP blockwork walls (over cladding panel corbels) it was agreed with the CRL Project Manager to progress with the fabrication of these brackets at the same time as progressing with the production of paperwork (i.e. weld procedure and ITP) due to the programme critical natural of these angles. It was agreed that installation into the permanent works would not commence until all the required paper works was in place. Therefore Off-site fabrication for blockwork support steels started without approved ITP and Welding Procedure.
| 03SR - Stations (RfL) | Cxxx-NCR-002315 | NCR | Attenuation Tank NRTW 1.9 Failure of Water Test |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2016-07-29 | 2016-07-25 15:29 | -4 | 2016-05-10 08:48 | Civil - Drainage | 10000 |  | Workmanship | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | NR Up Electric Drainage specification Cxxx-SWN-D-RSP-CR094_PT002-50001 Clause 185.024 part 5 states the attenuation tank shall be tested by filling with water and measuring the loss of water over a set period of time. The allowable water loss for the attenuation tank is provided in RFI 3623 (0.4litres per m2 on wetted internal area, per half an hour of test period), this equates to approximately 280L over 1 hour. It became apparent during the filling of the tank that water was leaking through several locations (through the southern bottom bolt hole in the downstream end unit and also through the joints in the base between culvert units 11 and 12 and 1 and 2 from the upstream end). Water may also have been leaking very slightly through the concrete surround of the inlet and outlet pipes, further assessment will be undertaken to try and establish if this was the case. A judgement was made that tank would not meet the parameters of the specification and the water test was abandoned.
| 03SR - Stations (RfL) | Cxxx-NCR-002316 | NCR | Stage 1 Concrete - EB CC2A to 2B EJ Sealant |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2017-02-28 | 2017-01-13 16:14 | -46 | 2016-05-18 15:49 | Civil - Civil Engineering General | 5000 |  | Design | Repair | 3 (3-6k) | Complete | Material/Preservation Problems - Improper preservation of material after installation | Completed |  | Cxxx have installed __ Instumesent Acrylic sealant between the stage 1 expansion joints and around the emergency walkway columns. This product was detailed on drawing Cxxx-SWN-S-DDD-CR094_Z-81131. There are a number of locations within the tunnels in which the acrylic sealant hasn't cured and is still soft to touch. These include the C&C2A to C&C2B EB expansion joint and the Covered Ramp to C&C3 EB joint.
| 03SR - Stations (RfL) | Cxxx-NCR-002317 | NCR | New soffit leak C&C WB CJ between bay 4/5 |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2016-06-18 | 2016-05-25 10:29 | -24 | 2016-05-17 07:46 | Civil - Civil Engineering General | 3000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Further to closed out NCR 2259 where it was requested we continue to monitor a minor damp patch in the WB roof slab to a CJ located at CH14552 (bay 4/5 CJ). The continued monitoring has suggested that the damp patch has remained and possibly grown. The leak appears to be coming in from the side and tracking along the CJ. see attached picture.
| 03SR - Stations (RfL) | Cxxx-NCR-002319 | NCR | DLR Viaduct GL12 south column-Repair to concrete defect |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2016-10-07 | 2016-09-22 08:33 | -15 | 2016-05-25 06:45 | Civil - Civil Engineering General | 3000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | When excavating to install impermeable membrane underneath the DLR viaduct on Site 2B a concrete defect was found on north face of the GL12 south column (as shown on attached file). As shown in Concrete defect at GL 12 (South) drawings the defect is 230mm wide and a deepest depth of 120mm. We propose to make a 20-30mm deep saw cut for tidy edges to the repair then handbreak 30mm back behind reinforcement. A letterbox shutter with be installed and C40/50B concrete will be used to fill cutout to match the concrete that was used when pier was originally poured.
| 03SR - Stations (RfL) | Cxxx-NCR-002320 | NCR | CMR Bridge handrail |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2016-12-23 | 2016-12-15 15:39 | -8 | 2016-05-23 16:08 | Civil - Civil Engineering General | 1500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The handrails for the north and south cess walkway steps have been installed with the follow defects: - End rails at incorrect angle (Should be vertical) due to incorrect connector components. - Top and bottom rails are not continuous over the posts due to incorrect connector components. - Kick boards are missing.
| 03SR - Stations (RfL) | Cxxx-NCR-002321 | NCR | Cxxx PML - __ Lift MCR |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2017-08-26 | 2017-09-25 13:14 | 30 | 2016-05-25 08:17 | Mechanical - Lifts | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Subcontractor Problems - Insufficient work planning by the subcontractors | Completed |  | Systemwide __ MCR tier 1 contractor raise MCR for Internal Lift Shaft Lift and Lift Car materials being used/installed at Cxxx PML. __ have raised a systemwide MCR 001490 this MCR has been approved.
| 03SR - Stations (RfL) | Cxxx-NCR-002322 | NCR | 11kVa Soffit Remedials - Poor Adhesion Test Results |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2016-11-18 | 2016-10-31 10:53 | -18 | 2016-05-26 10:28 | Civil - Civil Engineering General | 5000 |  | Material | Use As-Is | 3 (3-6k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | Cxxx have carried out adhesion tests to the 11kVa Soffit repair material - 3no. tests WB, and 3no. tests EB. Please find attached a summary of the test results (an official report from the testing contractor shall be issued in due course). None of the cores tested reached the 2MPa adhesion strength stated within the 11kVa soffit repairs specification (Doc. No: Cxxx-MMD-C-RSP-CRG06-50001). It is worth noting that 2MPa is the expected adhesion strength after 28 days of curing. The attached draft test results show that the ahesion testing was carried out up to 19 days after spraying only.
| 03SR - Stations (RfL) | Cxxx-NCR-002323 | NCR | __ installing materials without accepted MCR's |  | Crossrail | XRL | PML - Pudding Mill Lane Portal (Central) |  | 2018-09-14 | 2017-09-25 13:18 | -354 | 2016-05-27 11:34 | Mechanical - Escalators | 1000 |  | Material | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | __ have commenced installation of materials without accepted MCR's in place
| 03SR - Stations (RfL) | Cxxx-NCR-002324 | NCR | Evacuation Walkways Delay in Concrete Delivery |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2016-08-31 | 2016-06-21 10:01 | -71 | 2016-06-09 11:42 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | In the Evacuation Walkway pour WB Chainages 14632 - 14684 it has been identified that a gap of 53 minutes was recorded between the last two loads.
| 03SR - Stations (RfL) | Cxxx-NCR-002325 | NCR | Attenuation Tank NRTW 16.2 - Failure of Water Test |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2016-08-12 | 2016-08-04 14:37 | -8 | 2016-06-01 16:53 | Civil - Drainage | 5000 |  | Incorrect Installation | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Other | Completed |  | NR Up Electric Drainage specification Cxxx-SWN-D-RSP-CR094_PT002-50001 Clause 185.024 part 5 states the attenuation tank shall be tested by filling with water and measuring the loss of water over a set period of time. The allowable water loss for the attenuation tank is provided in RFI 3623 (0.4litres per m2 on wetted internal area, per half an hour of test period). It became apparent during the filling of the tank that water was leaking through two locations on the north face of the tank (refer appended marked up drawing).
| 03SR - Stations (RfL) | Cxxx-NCR-002326 | NCR | Missing Dewatering Records for L18/L19 |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2016-06-20 | 2016-06-08 12:38 | -12 | 2016-06-06 09:05 | Civil - Civil Engineering General | 1000 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | All the dewatering wells (L1-L21 and G4, G7-G11 and PZ1-3) have all been backfilled in accordance with the specification. The records for L18 and L19 are unfortunately missing and no electronic copies held
| 03SR - Stations (RfL) | Cxxx-NCR-002328 | NCR | DLR Cover plates over expansion joints - Extension of elongated holes |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2016-12-23 | 2016-11-28 10:17 | -25 | 2016-06-09 10:20 | Civil - Civil Engineering General | 60000 |  | Workmanship | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Other | Completed |  | Please refer to: Specification: Cxxx-SWN-O-AAG-CR094_PT002-50015 rev02 PMI545 After installation of cover plates over expansion gaps on DLR viaduct, it has been noted that some of the fixings on slotted side of plates have been placed not in the middle of slotted holes as required.
| 03SR - Stations (RfL) | Cxxx-NCR-002329 | NCR | EIP - Damage to Precast Concrete Stair Unit 2/4 (Intervention Stair) |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2017-03-03 | 2017-03-02 13:47 | -1 | 2016-06-18 22:49 | Architectural - Finishes | 1000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | Following the recent delivery of the Intervention and Maintenance Stair for installation at within Emergency Intervention Point (EIP) it has noted that 1No. precast concrete stair unit i.e. Unit 2/4 has been damaged during the off-loading of the units upon delivery. Please refer to the attached photograph showing the damage recorded.
| 03SR - Stations (RfL) | Cxxx-NCR-002330 | NCR | EIP - Concrete Cube Strengths in Small Slab Openings |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2016-07-29 | 2016-06-28 10:01 | -31 | 2016-06-27 08:10 | Civil - Civil Engineering General | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | Drawings: The Cxxx Openings left in the Intermediate Slab on the South side and in the Ground Slab on the North side of the EIP have obtained 28-day Compressive Strengths of 45.8N/mm2 and 40.0N/mm2.
| 03SR - Stations (RfL) | Cxxx-NCR-002331 | NCR | Laboratory Concrete Testing |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2016-07-29 | 2016-06-28 10:13 | -31 | 2016-06-24 14:23 | Civil - Civil Engineering General | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | Due to administrative errors made at both the __ Heathrow Laboratory and also separate incidents at __ and __ laboratories the following sets of cubes do not have 2 cubes crushed on their specific compliance dates. The target compressive strength for their respective mixes has been achieved at either 28 days or 56 days demonstrating that the concrete within the works is fit for purpose. __ - C40/50C PML 1128 cast on the 24/3/14 did not have any cubes crushed at 56 days the compliance age for this mix. The 2 cubes crushed at 28 days achieved 62.1 and 58.3 N/mm2 and are therefore compliant with the requirements of a C40/50 mix. __ 10mm – C40/50B PML 2034 cast on 24th Oct 2015 did not have 2 cubes crushed at 28 days the compliance age for this mix. The 2 cubes crushed at 56 days achieved 58.7 and 61.5 N/mm2 and demonstrates that concrete has achieved its design strength. __ 10mm – C40/50B PML 2124 cast on 16th Oct 2015 did not have 2 cubes crushed at 28 days the compliance age for this mix. The 1 cube crushed at 56 days achieved 61.5 N/mm2 and demonstrates that concrete has achieved its design strength. __ – C40/50C PML2296 cast on 24th March 2016 did not have 2 cubes crushed at 56 days the compliance age for this mix. The 1 cubes crushed at 56 days achieved 51.6 N/mm2 and are therefore compliant with the requirements of a C40/50 mix.
| 03SR - Stations (RfL) | Cxxx-NCR-002332 | NCR | Dip in Concrete Strength Tests |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2016-07-29 | 2016-07-05 14:59 | -24 | 2016-06-27 08:12 | Civil - Civil Engineering General | 1500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | External Phenomenon - Other | Completed |  | On the following mixes there has been a slight dip in strengths which has resulted in a very marginal statistical failure in the running mean of 6. This dip in strengths has been caused by natural variability in the mix constituents and more than likely within one of the cementious materials. During this period the ready mix suppliers have had a number of issues with the availability of cement replacements and increased demand can have an impact on the production process of the sources they are using. We have not encountered any individual failures on these mixes during this period and the strengths have now returned to a comfortable level with running mean of 6 compliance being achieved. __ 20mm C35/45A – the dip has been caused by marginal compliant 28 day results cast between the 8th January 2014 and the 22nd January 2014. A similar dip was experienced on the C35/45C at the same time of year and has been covered in NCR 1899. The dip on the C35/45 A mix was not visible at the time of raising NCR 1899 due to the number of samples tested at that time. __ 20mm C40/50C – The running mean of 6 dip has only occurred on 2 No 56 day samples from the 26th June. This is the same period of time when NCR 2100 was raised but these results were not available at the time and were not included in NCR 2100. The reason for the dip was due to natural variability in the constituent materials and strengths have since recovered.
| 03SR - Stations (RfL) | Cxxx-NCR-002333 | NCR | DLR Station Eliptical Bench Condition |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2017-02-17 | 2017-02-01 09:17 | -16 | 2016-06-29 11:11 | Architectural - General | 2000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Improper storage of material | Completed |  | As seen in the attached photographs, two elliptical benches detailed in drawing Cxxx-SWN-L-DDD-CR094_PT002-Z-96144 are water stained. The four. benches were brought to site in March/April 2014 during for the opening of the DLR station. Only two of the benches could be installed at this time due to the partial opening of the station and the area between Pudding Mill Lane and Marshgate Lane remaining within the Cxxx site. The other two benches were stored within the polythene wrapping but water has entered the polythene and stained the timber bench.
| 03SR - Stations (RfL) | Cxxx-NCR-002334 | NCR | EIP - Design Discrepancies Civil / Architectural |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2016-08-12 | 2016-07-06 14:03 | -37 | 2016-07-04 13:51 | Architectural - General | 2000 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Conflicting information on drawings | Completed |  | During the installation stage for the cladding panels situated at 1st Floor South – West Elevation on Grid Line 3/B-C and Roof Level South – East Elevation on Grid Line B/3-7, it has been identified there is a design discrepancy between the Cxxx Civil drawings 1) Cxxx-SWN-S-DDA-CR094_PT002_A-80104, 2) Cxxx-SWN-S-DDA-CR094_PT002_B-80105 and __ Bespoke Precast Concrete Architectural drawing Cxxx-MRG-A-DWG-CR094-WS111-50725. (See attached drawing mark-up) The RC plinth on which the panels sit on with the D6 fixing detail (i.e. dowel pocket) has been cast 200mm wide as shown on Cxxx-SWN-S-DDA-CR094_PT002_A-80104 (Level 01) and Cxxx-SWN-S-DDA-CR094_PT002_B-80105 (Roof Level). However __ drawing Cxxx-MRG-A-DWG-CR094-WS111-50725 shows the plinth as being 250mm wide with an offset dimension of 125mm from the front face of the plinth for the dowel pocket. As an effect the pockets cast don’t mirror the position of the dowel fixed into the panel. (See attached drawing mark-up)
| 03SR - Stations (RfL) | Cxxx-NCR-002335 | NCR | EIP - Cladding Panels installed out of tolerance |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2016-07-29 | 2016-07-25 11:13 | -4 | 2016-07-04 13:52 | Architectural - General | 1500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | Further to #FCD1973 which refers to the installation and workmanship tolerances to be relaxed to the tolerances specified in the BS 8297:2000 Clause 11.5. The cladding panels and copping stones fixed onto the EIP building have been marginally installed out of positional tolerance (i.e. required installation and workmanship tolerances +/- 4mm). Drawings: 1. Cxxx-MRG-A-DWG-CR094-WS111-50718 2. Cxxx-MRG-A-DWG-CR094-WS111-50719 3. Cxxx-MRG-A-DWG-CR094-WS111-50720 4. Cxxx-MRG-A-DWG-CR094-WS111-50721 5. Cxxx-MRG-A-DWG-CR094-WS111-50724 See attached as-built surveys. 4. Cxxx-MRG-A-DWG-CR094-WS111-50721 5. Cxxx-MRG-A-DWG-CR094-WS111-50724
| 03SR - Stations (RfL) | Cxxx-NCR-002336 | NCR | Vehicular Safety Barrier Base Incorrect Level |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2016-09-29 | 2016-09-14 13:09 | -15 | 2016-07-01 16:09 | Civil - Street Furniture | 1000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The vehicle restraint barrier foundation was constructed in phases as per FCD2173 to maintain access for Cxxx handover. The RC bases were set out using the setting out coordinates as per the plan of the vehicular safety barrier on drawing Cxxx-SWN-L-DDD-CR094_PT002_Z-96151. The level of these coordinates were taken as top of the RC bases, however the roadside coordinate levels are road level and not top of base. This has meant the base has been constructed with a fall towards the road (see attached as built and sketch).
| 03SR - Stations (RfL) | Cxxx-NCR-002337 | NCR | Greenway Ramp anchor as-built bolt survey |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2016-11-26 | 2016-10-21 14:49 | -36 | 2016-07-04 16:42 | Civil - Street Furniture | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Please refer to Cxxx-FCD-002315. The following as built surveys were taken on the Greenway holding bolts 1- Design centre line to as built centre line 2- Difference between centre of bolts to wall and centre of bolts to design centre (2no. plates) 3- Parallel distances between bolt plates (North and South) 1 - The survey centre line has 8no deviations of greater than 10mm from design centre line with 2no greater than 12mm. To correct the centre line of the parapet posts to within 10mm Cxxx propose constructing the base plates of the parapet posts with slots to account for 12mm movement (see attached sample) this proposal will be incorporated into the fabrication drawings: - Cxxx-MRG-A-DWG-CR094_WS111-50775 - Cxxx-MRG-A-DWG-CR094_WS111-50776 2- There are 2no locations where the deviation is 13mm and 15mm, for Bolt locations A & B the plates can be adjusted to within 10mm and not overhang the chamfer. 3- There are 7no parallel distances between the parapet panel and barbican panel posts, the greatest being 14mm
| 03SR - Stations (RfL) | Cxxx-NCR-002338 | NCR | EIP - Door DA12 Level 01 |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2017-02-28 | 2017-03-02 13:48 | 2 | 2016-07-13 10:00 | Architectural - Doors | 1500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | Drawing no Cxxx-MRG-A-DWG-CR094_WS111-51116 P02(DA12) is a Code 1 drawing.i.e. Approved. However the following have been fitted to the corridor side of the door instead of the HVAC room side. • 2no G3 16mm heavy duty barrel bolts have been fitted to the corridor side instead of HVAC room side. • The morticed sashlock panic escape E which provides as means of escape is on the corridor side instead of HVAC room side. • The 1No F13/4/D Furniture set should be on the corridor side.
| 03SR - Stations (RfL) | Cxxx-NCR-002339 | NCR | Sludge main DN300 & DN80 Flange Set - ordered before approved MCR |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2016-07-19 | 2016-07-18 15:36 | -1 | 2016-07-05 07:36 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | Sludge main DN300 & DN80 Flange Set has been ordered by Cxxx before MCR (Cxxx-MRG-C-QAP-CR094_WS111-50536) approved. Due to notification from supplier that particular product have long 8 week lead time and in order to meet planned site activities, product have been ordered before Material Compliance Record has been approved by Crossrail. Cxxx are not in possession to install this product until this MCR approved.
| 03SR - Stations (RfL) | Cxxx-NCR-002340 | NCR | 4SU - Incorrect WPP used for 4SU Walkway Construction |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2016-07-19 | 2016-07-14 14:51 | -5 | 2016-07-05 09:46 | Civil - Civil Engineering General | 1000 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Drawings: Cxxx-SWN-S-DDD-CR094_PT002_Z-71478 Construction of the Emergency Walkways and associated works including columns, stairs, ramps etc. was built to the issued for construction drawings. The Fourspan structure had it's own Works Package Plan which did not identify the plan for these works. Instead, the WPP for the EIP was used as a plan for the construction given it uses most of the same drawings. The RC details in the Four Span are Titled 'CRL - Cut & Cover' which is covered under the EIP WPP.
| 03SR - Stations (RfL) | Cxxx-NCR-002341 | NCR | Sludge main DN300 & DN80 Flange Set installed before approved MCR |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2016-07-20 | 2016-07-18 15:38 | -2 | 2016-07-06 07:50 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Other management problem | Completed |  | Sludge main DN300 & DN80 Flange Set installed before approved MCR. Testing flanges were installed on site by construction team to ensure/check the correct length of spigot pipes to be cut. This were necessary for welder to complete all main run welds ready for 1st beforehand booked welding inspection and avoid necessary delays and standing time. Cxxx are not to carry out pressure testing without approved MCR.
| 03SR - Stations (RfL) | Cxxx-NCR-002342 | NCR | EIP - Intermediate Roof Screed Setting Out Error |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2016-08-26 | 2016-07-14 15:03 | -43 | 2016-07-06 17:03 | Architectural - Roofing & Exterior Treatment | 2000 |  | Supervision/Management | Repair | 4 (0.5-3k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | A setting out error has been found in the screed installation at the EIP Intermediate Roof. As the upstand at the top of the Emergency Intervention and Maintenance Staircase was not yet cast when the screed gully alignment was formed, it was not identified that the second setting out point generated from the design model was not in the centre of the gully alignment. The point generated at the West end of the gully was correctly positioned, the second point being out of place created a creep resulting in a 60mm difference where the gully meets the upstand (please see attached 'Location Reference').
| 03SR - Stations (RfL) | Cxxx-NCR-002343 | NCR | The WPP for Sludge Main works omitted detailing for the lifting and positioning of the welded pipe. |  | Crossrail | XRL | PML - Pudding Mill Lane Portal (Central) |  | 2017-01-13 | 2017-01-03 11:04 | -10 | 2016-07-11 13:39 | Civil - Drainage | 3000 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | During a planned Crossrail Quality surveillance undertaken on 5th July 2016 which looked at Sludge Main installation, the WPP was checked in line with the current and planned activities. At the time of the site visit, the welded pipe was seated on temporary sandbags to allow for welding. Following weld inspection, it was stated by the construction team that the continuous welded pipe would be lifted from the sandbags into the final line and level position. On checking, the WPP only provided the following detailing for the setting out and positioning of the pipe runs; “two 300mm Fuchs steel pipe will be laid to the co-ordinates and levels provided on the latest IFC drawings”. It was stated that more detailed information was contained within a Task Statement which is briefed to the site team; however following discussion it was noted that this is an internal document which Crossrail (and Stakeholders) gets no visibility of. As such, the WPP failed to detail the methodology and risks concerning the temporary seating of the pipes and the lifting activities to final position to Crossrail and Stakeholders, resulting in this NCR. Works Information Vol2B Part 19 states; “the Contractor shall produce task-specific method statements and health and safety risk assessments. The Contractor may use the work package plan system as an alternative to method statements but must ensure these are acceptable to the Project Manager for the works.” This relationship between the WPP and internal Task Statement should be reviewed as part of the close out to avoid any re-occurrences for other planned activities.
| 03SR - Stations (RfL) | Cxxx-NCR-002344 | NCR | The Weld Checklist for Sludge Main works does not form part of the ITP, and the record had only been completed following the surveillance visit |  | Crossrail | XRL | PML - Pudding Mill Lane Portal (Central) |  | 2016-10-07 | 2016-09-22 16:40 | -15 | 2016-07-11 13:55 | Civil - Drainage | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Supervision - Other | Completed |  | During a planned Crossrail Quality surveillance undertaken on 5th July 2016 which looked at Sludge Main installation, weld records generated in support of the works were checked to ensure compliance with the requirements. At the time of the site visit 14 welds had been completed. The Weld Supervisor was requested to provide the Welding Log for those welds as defined in ITP Inspection Number 3.3 (Cxxx-MRG-C-ITP-CR094_WS111-50077). The Trent Energy Supervisor, who is responsible for the inspection within the ITP, stated that the Weld Logs had yet to be completed and would be produced following weld inspection on 6th July 2016. During a follow up meeting on 7th July 2016, a Weld Checklist record was provided for weld SP14. On checking, the record included sections for pre-welding and post-welding checks; these had been completed and dated 5th July 2016, the day of the site visit. There was no mention of this checklist when the Welding Log was requested, as such it had only been completed post visit, and not maintained progressively as and when the activities had been completed, i.e. pre installation checks. Works Information Part 13 requires the continual confirmation of compliance by the generation of contemporaneous records. Additionally, the ITP did not include pre installation and installation checks as an activity, made no reference to the Weld Checklist as a deliverable and did not include the record as an attachment to the ITP. Works Information Part 20 states the following; “Records and other deliverables generated as part for the inspection and test process shall be identified within the ITPs.”
| 03SR - Stations (RfL) | Cxxx-NCR-002345 | NCR | EIP - Roof Screed Weather Damage |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2016-09-30 | 2016-07-29 16:03 | -63 | 2016-07-12 16:30 | Architectural - Roofing & Exterior Treatment | 2000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | External Phenomenon - Weather or ambient condition | Completed |  | At the end of shift on 25-6-2016 during roof screeding works, an expected rain shower fell causing damage to the top of the finished screed. The screed was covered with polythene however when exposed it was found that there was an area of surface delamination. This delaminated material and partially delaminated material was removed to expose sound substrate. Drop hammer testing was carried out in the damaged area by independent test house __, which passed. A technical representative of Flowcrete (responsible for warranty to screed) confirmed that the screed below the delamination was sound and proposed remedial action to achieve a smooth inform finish.
| 03SR - Stations (RfL) | Cxxx-NCR-002346 | NCR | EIP - Installation of Non-accepted Door Seals / Fire Stopping |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2017-12-29 | 2017-10-11 12:17 | -79 | 2016-07-13 12:14 | Architectural - Doors | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | The installation of the internal doors to the Sub-surface level i.e. Intermediate, Surface Level and Level 1 at the Emergency Intervention Point (EIP) has commenced using non-accepted materials. A Material Compliance Record i.e. MCR (Doc. No. Cxxx-MRG-A-QAP-CR094_WS111-50325 rev 2.0) prepared and submitted for the use of 'Door Seal / Fire Stopping' and was subsequently returned by Crossrail on 26/04/16 at CODE 3 i.e. Not Accepted. Revise and resubmit. Work may not proceed . The comment on the 'Document Review Sheet' states that confirmation that the proposed seals are compliant with the fire test standards detailed in LUL -1085. Initial testing data submitted with the MCR concluded that the product was 'S2' standard whereas 'S1' is the requirement. As such further testing was commissioned on the seals/fire-stopping by the sub-contractor responsible for the installation of the doors i.e. __ Industries.
| 03SR - Stations (RfL) | Cxxx-NCR-002347 | NCR | EIP - Installation of Non-accepted Intumescent 'Mastic' Sealant |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2016-09-30 | 2016-09-30 09:12 | 0 | 2016-07-13 12:16 | Architectural - Doors | 1500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Use of unapproved materials | Completed |  | The installation of the internal doors to the Sub-surface level i.e. Intermediate, Surface Level and Level 1 at the Emergency Intervention Point (EIP) has commenced using non-accepted materials. A Material Compliance Record i.e. MCR (Doc. No. Cxxx-MRG-A-QAP-CR094_WS111-50340 rev 1.0) prepared and submitted for the use of 'Intumescent Mastic' i.e. Sealant was returned by Crossrail on 22/03/16 at CODE 3 i.e. Not Accepted. Revise and resubmit. Work may not proceed . The comment on the 'Document Review Sheet' states that the LUL -1085 certificate needs to be submitted for the proposed 'ARBO XL1075' intumescent mastic. Mistakenly the works have commenced using the non-accepted product. Furthermore, it has recently been confirmed by the sub-contractor responsible for the installation of the doors i.e __ Industries that 'ARBO XL1075' Intumescent mastic used is NOT LUL-1085 compliant and will now be removed and replaced by an alternative acceptable mastic. Details of this material are to be resubmitted via MCR.
| 03SR - Stations (RfL) | Cxxx-NCR-002348 | NCR | NR Pier 1 Pile Cap - damaged rear-guard waterstop |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2016-07-28 | 2016-07-28 11:28 | 0 | 2016-07-14 15:42 | Civil - Civil Engineering General | 1000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | During the excavation and pile cropping of NR Pier 1 Pile Cap it has been identified the water bar requested in FCD 1863 has been damaged in three locations, refer attached photographs
| 03SR - Stations (RfL) | Cxxx-NCR-002350 | NCR | Cover to cut and cover tunnel |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2016-09-05 | 2016-08-16 16:09 | -20 | 2016-07-26 09:52 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Verification Problems - Other | Completed |  | Further to RFI 3516, the as constructed cover to the steel reinforcement to the roof slab is 50+- 10mm due to the steel design and bending tolerances.
| 03SR - Stations (RfL) | Cxxx-NCR-002351 | NCR | EIP - M16 Sockets cast in the wrong location to the underside of coping |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2016-09-30 | 2016-08-18 15:32 | -43 | 2016-07-28 12:26 | Architectural - Roofing & Exterior Treatment | 2000 |  | Design | Repair | 4 (0.5-3k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | During the copings installation it has been identified that 2No M16 sockets located into the underside have been cast in the incorrect location. As an effect the location of M16 dowel do not match with the pockets formed at the top of the panel. There are 2No Coping stones affected with the unit ref. 116 and 130 (See attached). Drawings: Cxxx-MRG-A-DWG-CR094-WS111-50721 Cxxx-MRG-A-DWG-CR094-WS111-50720
| 03SR - Stations (RfL) | Cxxx-NCR-002352 | NCR | Urban Realm - Type A filter drain material |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2016-11-26 | 2016-11-18 14:46 | -8 | 2016-08-02 13:06 | Civil - Civil Engineering General | 5000 |  | Manufacturing Defect | Repair | 3 (3-6k) | Complete | Subcontractor Problems - Other | Completed |  | The type A material in the EIP and site 2B has been tested and a grading analysis carried out, these results showed that the 0.5mm passing was in excess of the requirement on the majority of the tests. See attached results and relevant pages from the Specification for Highway Works and drawing & MCR referenced.
| 03SR - Stations (RfL) | Cxxx-NCR-002353 | NCR | Barbers Road Kerbs - BN Kerbs Installed to incorrect height at Crossings |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2016-12-23 | 2016-11-10 16:29 | -43 | 2016-08-05 16:21 | Civil - Streets & Highways | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Procedure Problem - Other | Completed |  | The kerbs on Barbers Road are detailed in drawing Cxxx-SWN-D-DDD-CR094_PT002_Z-95464 and specification Cxxx-SWN-C-RSP-CR094_PT002-50001. The kerbs at vehicle crossing location on the north side of Barbers Road have been installed at Ch 225, Ch 190, Ch 110 and Ch 070. In these locations the bull nose drop kerbs have been installed flush with the top of tarmac level. Specification Cxxx-SWN-C-RSP-CR094_PT002-50001 Appendix 1/12 clause 3 states that 'All Barbers Road kerb faces are (100mm) except where otherwise shown on the drawings at pedestrian crossings (6mm) or vehicular crossovers (25mm)'. This clause states that the kerbs at crossings should be installed 25mm higher than the asphalt level.
| 03SR - Stations (RfL) | Cxxx-NCR-002354 | NCR | Blacktop works had commenced without an approved WPP in place. |  | Crossrail | XRL | PML - Pudding Mill Lane Portal (Central) |  | 2017-01-13 | 2016-12-22 14:31 | -22 | 2016-08-05 12:12 | Civil - Civil Engineering General | 1500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Other management problem | Completed |  | During a planned Crossrail Quality surveillance undertaken on 3rd August 2016 which looked at Blacktop Works at Barbers Road, the controlling documentation was checked for its approval and content. On checking the acceptance status on eB for WPP ‘New Barbers Road’ Cxxx-MRG-C-GMS-CR094_WS111-50210, it was noticed that the document was still ‘Draft’ and ‘Not Approved’ at the time. As a consequence of this, the New Barbers Road works had commenced on 2nd August 2016 without an approved WPP in place. An approved WPP is a Hold Point within the ‘__ and CBGM Placing’ ITP (Cxxx-MRG-C-ITP-CR094-WS111-50049) under inspection number 1.2 for the Sub-Contractor, Contractor and __. It was stated that there was verbal agreement to proceed with the works by Crossrail; however no verifiable evidence could be produced to demonstrate this. On the basis of the above, this NCR was raised resulting from the surveillance.
| 03SR - Stations (RfL) | Cxxx-NCR-002355 | NCR | Failed NDM to Barbers Road Base course |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2016-08-23 | 2016-08-22 10:27 | -1 | 2016-08-09 10:13 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | 1no Failed NDM at location ch 100 on Barbers Road. Density 89.3% Air voids 10.7%
| 03SR - Stations (RfL) | Cxxx-NCR-002356 | NCR | Base and Binder course dips out of tolerance (Barbers Road) |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2016-10-30 | 2016-10-27 07:51 | -3 | 2016-08-09 10:28 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Dips out of tolerance on both Base and Binder courses.
| 03SR - Stations (RfL) | Cxxx-NCR-002357 | NCR | Cable Management (CMS) |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2016-09-02 | 2016-08-23 14:57 | -10 | 2016-08-10 08:34 | Electrical - Cable Management | 5000 |  | Material | Repair | 3 (3-6k) | Complete | Subcontractor Problems - Insufficient surveillance of subcontractors | Completed |  | CMS (trunking) within EIP is not compliant to required standard of IP4X 1mm gauge was used to verify this and the trunking does not meet the required standard and therefore deviating from the M&W specification.
| 03SR - Stations (RfL) | Cxxx-NCR-002358 | NCR | __ Up Electric Pier 1 CFA Pile P01V out of tolerance |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2016-10-28 | 2016-09-29 07:21 | -29 | 2016-09-02 10:47 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | Please refer drawing Cxxx-SWN-S-DDD-CR094_PT002_Z-69470. The as built location of CFA pile P01V exceeds the allowable set out tolerance of 75mm, refer attached as built drawing Cxxx-MRG-SRV-SK-CR094-10654
| 03SR - Stations (RfL) | Cxxx-NCR-002359 | NCR | CRL1 Wall incorrect recess construction |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2016-11-30 | 2016-11-29 17:03 | -1 | 2016-08-15 14:52 | Structural Engineering - Concrete Member | 6000 |  | Incorrect Installation | Repair | 3 (3-6k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | The recess at the top of CRL1 retaining wall has been constructed in accordance with RFI 296 with the top of recess 500mm above FGL and the bottom of the recess (where installed, refer later section) constructed at the FGL (104.600m). The recess levels on the NR Up Electric Curtain Wall between GL 2 to 4 have been constructed to RFI 3579 (Generally the bottom of the recess is designed at 100mm above the finished pavement level in front of the wall). Additionally the lower concrete protrusion on the CRL1 wall that forms the base of the recess has been missed on an approximate 35m section from the eastern end of CRL1 wall, refer attached photograph.
| 03SR - Stations (RfL) | Cxxx-NCR-002360 | NCR | NR Up Electric Drainage - MH Chamber NRTW 16.6 Backdrops installed at incorrect level |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2016-08-29 | 2016-08-24 16:36 | -5 | 2016-08-15 12:17 | Civil - Drainage | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Management Problem - Misunderstand the definition of the requirement | Completed |  | Refer drawings Cxxx-SWN-R4-DDB-CR094_PT002_Z-95070 and Cxxx-SWN-R4-DDB-CR094_PT002_Z-95071. The Perforated Collector Pipe (PCD) NRTW 24 and NRTW 23 have been constructed too low, the I.L of the PCD the entering MH NRTW 16.6 is 107.580m, due to the proximity of the drainage runs to the NR Up Electric Track the collector drain now lies within the zone of influence at 45 degree from edge of sleeper.
| 03SR - Stations (RfL) | Cxxx-NCR-002361 | NCR | Marshgate Lane Pavix Check Sheets |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2017-01-13 | 2016-12-21 15:41 | -23 | 2016-08-15 14:50 | Civil - Civil Engineering General | 3000 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | It has been found that check sheets were not completed for the control of the application of Pavix protection.
| 03SR - Stations (RfL) | Cxxx-NCR-002362 | NCR | Fire Lining Quality Package Non-Procedural Sign Offs |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2016-12-23 | 2016-12-16 10:00 | -7 | 2016-08-15 15:06 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Personnel Error - Violation of requirement or procedure | Completed |  | On review of the Fire Lining Quality Package it has been identified that a number of sheets have been signed as 'pp', or 'per procurationem', by __ for Ardent the Sub-Contractor who undertook the works after the works had been completed.
| 03SR - Stations (RfL) | Cxxx-NCR-002363 | NCR | CRL1 Wall and NR Up Electric wall thickness |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2016-11-18 | 2016-11-01 14:40 | -17 | 2016-08-15 17:15 | Structural Engineering - Concrete Member | 6000 |  | Incorrect Installation | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Other | Completed |  | Please refer Contract Drawings Cxxx-SWN-S-DDD-CR094_PT002_Z-31400 and Cxxx-SWN-S-DDA-CR094_PT002_1-31150 and the attached As Built Drawings. The east end of CRL1 wall has been constructed slightly south of the design location (19mm). The parapet section at the top of the CRL1 Wall (east end) has been constructed 33mm south of the design location, approximately 14mm wider than the design thickness. At pier 2 the parapet is 5mm wider than design (as built line of the south/front face of the parapet wall is 7mm south, the northern face is 2mm south). This is within tolerance. The thickness of the 500mm deep recess in the Recki wall is detailed at 50mm at the narrowest point, this thickness varies along the length of the wall, refer attached as built drawing ' Recki Depth of Recess'
| 03SR - Stations (RfL) | Cxxx-NCR-002364 | NCR | EIP Drainage - Line SB1.002 |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2016-10-07 | 2016-08-30 13:35 | -38 | 2016-08-22 07:16 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | Drawing: Cxxx-SWN-D-DDA-CR094_PT002_Z-95222 During installation of drainage chamber SB04, the rocker pipes for drainage line SB1.002 were set in the concrete surround of the chamber on the correct grade but slightly off the alignment.
| 03SR - Stations (RfL) | Cxxx-NCR-002365 | NCR | NR Up Electric Drainage phase 1 - As Built Levels out of Tolerance |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2016-10-29 | 2016-09-23 12:08 | -36 | 2016-08-18 16:42 | Civil - Drainage | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Please refer attached drawing Cxxx-SWN-R4-DDB-CR094_PT002_Z-95071 and the attached As Built drawings. MCHW Volume 1 Specification 503 Bedding, Laying and Surrounding of pipes states that the maximum deviation on level shall not exceed +/-20mm and in addition the algebraic difference of the deviation in level at any two points on the pipe shall not exceed 30mm overall. Two locations are slightly outside these parameters; refer below Manhole Chamber NRTW 15.3 – – Perforated Collector Drain (PCD) Inlet Design level – 109.119m Design Gradient PCD NRTW 15.2A – 1:70 Perforated Collector Drain (PCD) Inlet As Built level – 109.087m Variance = -32mm As Built Gradient PCD NRTW 15.2A – 1:67 (As Built of MH NRTW 15.2 Outlet – 109.485m) This exceeds the +/-20mm and the maximum 30mm. Manhole Chamber NRTW 15.4 – Perforated Collector Drain (PCD) Inlet Design Level - 108.980m Perforated Collector Drain (PCD) Outlet Design Level - 109.000m Perforated Collector Drain (PCD) Inlet As-built Level - 108.955m Perforated Collector Drain (PCD) Outlet As-built Level - 108.979m Variance Inlet - 25mm Variance Outlet - 21mm Design Gradient PCD NRTW 15.3A – 1:100 As Built Gradient PCD NRTW 15.3A – 1:93 (As Built of MH NRTW 15.2 Outlet – 109.485m) This exceeds the +/-20mm but is within the maximum cumulative 30mm deviation. Manhole Chamber NRTW 15.5 Perforated Collector Drain (PCD) Inlet Design Level - 109.000m Perforated Collector Drain (PCD) Outlet Design Level - 108.778m Perforated Collector Drain (PCD) Inlet As-built Level - 109.003m Perforated Collector Drain (PCD) Outlet As-built Level - 108.763m Variance Inlet + 3mm Variance Outlet - 15mm This manhole is compliant.
| 03SR - Stations (RfL) | Cxxx-NCR-002366 | NCR | Barbers Road - DLR Concourse Tree Pits |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2016-11-22 | 2016-10-14 07:10 | -39 | 2016-08-24 08:59 | Civil - Civil Engineering General | 500 |  | Material | Repair | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | Three tree pits in the Barbers Road DLR concourse were installed by Cxxx in 2014 prior to the opening of the DLR station (refer to marked up sketch). The tree pits had cold roll asphalt placed over them after construction as the trees were not installed. During the 2016 Barbers Road works, Cxxx have removed the cold roll asphalt from the top of the tree pits to uncover the materials used. Although the tree sand, anchor system and gravel have been installed in accordance with drawing Cxxx-SWN-D-DDD-CR094_PT002_Z-95463, Cxxx have no record that the materials have an accepted Materials Conformance Report.
| 03SR - Stations (RfL) | Cxxx-NCR-002367 | NCR | MGL up-stand poured without approved MCR for concrete mix |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2016-10-28 | 2016-10-21 08:21 | -7 | 2016-09-01 15:55 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Use of unapproved materials | Completed |  | Drawing: Cxxx-SWN-D-DDD-CR094_PT002_2-51102. On 24th July 2015, __ poured 4m3 of the southern up-stand of the MGL East abutment using a C40/50 S4 10mm mix. This mix design did not have an approved material compliance record (MCR) - this has now been produced Cxxx-MRG-C-QAP-CR094_WS111-50455.
| 03SR - Stations (RfL) | Cxxx-NCR-002368 | NCR | CMR West Abutments corner plate fabrication |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2016-10-29 | 2016-09-21 12:23 | -38 | 2016-09-09 10:09 | Civil - Civil Engineering General | 500 |  | Manufacturing Defect | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Not Defined | Completed |  | The corner plates for the CMR east abutment have been manufactured with a small gap between the plates where the galvanising dip is unlikely to have penetrated. This will leave an area where corrosion may be possible.
| 03SR - Stations (RfL) | Cxxx-NCR-002370 | NCR | FSU - Cracks to Up-Electric deck soffit |  | Crossrail | XRL | PML - Pudding Mill Lane Portal (Central) |  | 2016-12-23 | 2016-12-16 13:55 | -7 | 2016-10-03 16:51 | Civil - Concrete Pavement | 3000 |  | Manufacturing Defect | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | FSU - Cracks to Up-Electric deck soffit, GL1-2 8No cracks were found with a width between 0.25-0.3mm GL2-3 10No cracks were found with a width between 0.25-0.3mm GL3-4 1No crack was found with a width between 0.25-0.3mm
| 03SR - Stations (RfL) | Cxxx-NCR-002371 | NCR | MGL - Damage to MGL Upstand by Cxxx |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2016-12-23 | 2016-11-28 13:34 | -25 | 2016-10-07 10:41 | Civil - Civil Engineering General | 3000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Improper preservation of material after installation | Completed |  | Please refer to: RIVO-6168318, Attached Photos Findings are that the Cxxx RRV operator did not follow the instructions by moving towards a restricted area to pick up a tool from another machine and moreover without a banksman. Whilst moving he damaged the concrete upstand.
| 03SR - Stations (RfL) | Cxxx-NCR-002372 | NCR | EIP - Bonded Screed at Emergency Staircase Landings Remedial Works |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2016-11-25 | 2016-11-18 14:48 | -7 | 2016-10-10 17:05 | Architectural - Flooring | 5000 |  | Workmanship | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | A hammer tap survey carried out on the Emergency Staircase Landings' bonded screed to assess adhesion has identified to areas of apparent delamination (see attached NCR Bonded Screed - Locations). Area 1: 700mm x 500mm Area 2: 300mm x 300mm Four temporary hand rail edge protection standards were also left in place and screeded to. These had to be cut out to remove, leaving 250mm x 200mm full depth (55mm) pockets.
| 03SR - Stations (RfL) | Cxxx-NCR-002373 | NCR | Up Electric Drainage Water Testing Requirement |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2017-05-20 | 2017-05-18 12:11 | -2 | 2016-10-12 15:54 | Civil - Drainage | 25000 |  | Design | Use As-Is | 2 (6-60k) | Complete | Design Problem - Inadequate or defective design | Completed |  | The Up Electric Drainage Specification - Cxxx-SWN-D-RSP-CR094_PT002-50001, section 185.024 Part 4 requires that the Contractor shall test the water tightness of new chamber construction. It then goes on to give test criteria. Section 185.109, Part 4 states that Catchpits shall be constructed with all joints closed. __ have constructed the drainage chambers in accordance with the construction drawings, for example Cxxx-SWN-R4-DDD-CR094_PT002_Z-95040. The chambers have been constucted using integral insitu ST4 concrete base walls benching with an insitu formed invert. All chamber rings have been fitted with a bitumen rubber seal (Tok Strip). It is noted that there is no additional sealing requirements around the pipe / base interface and the watertight construction is wholly reliant on the concrete to concrete bond from a the realtively smooth wall of the concrete pipe and the ST4 concrete, which was installed with an S2 consistency. This is not sufficient to ensure water tightness. __ have carried out some preliminary water tightness tests on 2 different chambers and both have failed. Visual inspections have been carried out on the chambers and there are no construction defects in the chambers. For the chambers to be constructed allowing the minimal leaking in accordance with the specification (2l/hr) a hydrophillic strip system could have been detailed. For example the hydrophillic strip system detailed on the outfall pipes from the concrete attenuation tanks could have been employed. With the current chamber construction, the chambers will not achieve the water tightness requirements required. It should be noted that BS 8301 states that visual inspection may be sufficient for acceptance without testing, this was detailed in FCD 2461.
| 03SR - Stations (RfL) | Cxxx-NCR-002374 | NCR | Urban Realm Installation of Palisade Gateway Posts |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2016-12-16 | 2016-12-15 16:31 | -1 | 2016-10-14 06:55 | Civil - Street Furniture | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Please refer to fabrication drawing Cxxx-MRG-C-DWG-CR094_WS111-50227 & IFC drawing Cxxx-SWN-L-DDD-CR094_PT002_Z-96154. The RHS post delivered to site was the incorrect dimension (120*120) as opposed to that stated on fabrication drawing DWG-50227 (200*200). It is proposed to install the correct post dimension, this will close the hinge gap to within design intend. Please refer to RFI4136 regarding gap between CRL2 wall and Palisade fence post.
| 03SR - Stations (RfL) | Cxxx-NCR-002375 | NCR | Excess fines in Up Electric Track Ballast |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2016-11-30 | 2016-11-07 10:54 | -23 | 2016-10-14 11:04 | Civil - Track | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Contamination | Completed |  | During a __ T-4 inspection on the Up Electrics it was observed that there were areas of newly installed ballast that appeared to have an excessive amount of fine material. The area observed was coincident with the location of a ballast stock pile, so it is thought that there may have been some settling out of some fines as the stock pile was used. The ballast stock pile location are marked up on the attached drawing.
| 03SR - Stations (RfL) | Cxxx-NCR-002376 | NCR | Palisade Fence Gates Fabrication ITP |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2017-01-31 | 2017-01-17 13:26 | -14 | 2016-10-17 16:42 | Architectural - Security | 500 |  | Documentation and Records | Reject | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | It has been identified that an ITP is not in place for the fabrication of the Barkers palisade fencing gates.
| 03SR - Stations (RfL) | Cxxx-NCR-002377 | NCR | Attenuation tank NBC 1.1 - Protection slab damage |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2016-11-18 | 2016-11-10 17:40 | -8 | 2016-10-19 15:02 | Civil - Civil Engineering General | 3000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The north west section of tank protection slab identified on the attached marked up drawing is damaged and has changed level on the north west section The top of the slab was uncovered as part of the urban realm works, this revealed the slab had cracked and changed in level. The section of broken slab has now been removed to allow further investigation works to be carried, the tank membrane and no fines concrete has been removed as shown on the attached photos revealing that the tank creates have not been damage.
| 03SR - Stations (RfL) | Cxxx-NCR-002378 | NCR | Dips out of tolerance |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2016-12-15 | 2016-12-08 11:32 | -7 | 2016-10-27 16:14 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | After the installation of the Base and Binder courses to the Barbers Road Cooks Road tie-in, it was found that there are dips out of tolerance on the subbase (type 1)
| 03SR - Stations (RfL) | Cxxx-NCR-002379 | NCR | EIP - Coping interface with Cladding panels |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2018-01-10 | 2017-10-06 15:02 | -96 | 2016-11-01 15:21 | Architectural - General | 2000 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | Drawing No’s: Cxxx-MRG-A-DWG-CR094_WS111-50814 Unit Details Panel Ref 054 Cxxx-MRG-A-DWG-CR094_WS111-51025 Unit Details Panel Ref 061 Cxxx-MRG-A-DWG-CR094_WS111-50900 Unit Details Panel REF 062 Cxxx-MRG-A-DWG-CR094_WS111-51027 Unit Details Panel Ref 076 & Cxxx-MRG-A-DWG-CR094_WS111-50820 Unit Details Panel Ref 072 The above Code 1 unit drawings show a recess area for each of these panels interfacing with the coping units. The coping units at these junctions were supposed to fit within the recess cast in the panels. (See attached drawing mark-ups) However, due to precast units being approved and issued for production out of casting sequence, __ we’re unable to address the comments on time and cast the coping units long enough to sit within the recess. As such, we are now faced with an increased joint width varying from 40 to 60mm. (See attached photographic report)
| 03SR - Stations (RfL) | Cxxx-NCR-002380 | NCR | Dips out of tolerance |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2016-11-30 | 2016-10-28 14:27 | -33 | 2016-10-26 11:32 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Dips out of tolerance in New Barbers Road construction There are 2 dips 5mm out of tolerance in the Northern footpath at ch 95 There is 1 dip 10mm, and 5 dips 5mm out of tolerance in Barbers Road bellmouth 2
| 03SR - Stations (RfL) | Cxxx-NCR-002381 | NCR | __ Fill Materials - Points Outside ITP Positional Tolerance |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2016-12-02 | 2016-11-17 13:21 | -15 | 2016-11-02 11:30 | Civil - Fill | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During the review of the __ Phase 1 Formation and Ballast Records package a number of points have been identified outside the tolerances set under Cxxx-MRG-C-ITP-CR094_WS111-50082 (please see attached surveys for reference): 1) Rail Ballast – Tolerance +0mm/-50mm The rail ballast was generally installed high as a second layer is outstanding in the follow-on works. In terms of the working ITP, the worst case differences in level are as follows: Section A – Worst case + 176mm Section B – Worst case + 44mm Section C – Worst case + 54mm Section D – Worst case + 176mm Section E – Worst case + 149mm Section F – Worst case + 49mm Section G – Worst case + 212mm Section H – Worst case + 216mm Section I – Worst case + 180mm Section J – Worst case + 173mm Section K – Worst case + 318mm Phase 2 – Worst case + 320mm 2) 6N Fill – Tolerance +0mm/-30mm. Area above __ Attenuation Tank. Verbally agreed at the time of works that levels must be raised, however formal confirmation via PTR cannot be found. Out of tolerance points: Section I (above tank) – 11 points, worst case + 102mm 3) 6N Fill – Tolerance +0mm/-30mm. Out of tolerance points: Section A – 2 x 1mm Section C – 2 x 1mm, 2 x 2mm Section D – 3 x 1mm, 2 x 2mm Section E – 3 x 1mm, 5 x 2mm Phase 2 – 6 x 1mm, 1 x 2mm, 2 x 4mm, 1 x 6mm
| 03SR - Stations (RfL) | Cxxx-NCR-002382 | NCR | EIP - Flashings damaged @Ground Floor |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2017-02-27 | 2017-02-22 13:11 | -5 | 2016-11-18 16:37 | Architectural - General | 5000 |  | Damaged | Repair | 3 (3-6k) | Complete | Material/Preservation Problems - Improper preservation of material after installation | Completed |  | Drawing No: Cxxx-MRG-A-DWG-CR094_WS111-51124 Ground Level – West and South Elevations The following 3no flashing units have been damaged during the cladding installation – M116, M115 and M119-01 (See attached drawing mark-up and photographic evidence)
| 03SR - Stations (RfL) | Cxxx-NCR-002385 | NCR | Urban Realm - Kerb Lengths cut less than 75% |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2016-12-16 | 2016-12-06 17:10 | -10 | 2016-11-07 15:53 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Worker not correctly instructed | Completed |  | Please refer to: Cxxx-SWN-D-RSP-CR094_PT002-0001 - cl11/1.1 Kerbs were cut and installed beyond the minimum length of 0.75 of the original length along the drop kerb in site 2a
| 03SR - Stations (RfL) | Cxxx-NCR-002386 | NCR | Marshgate lane Watermain Installation |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2017-01-20 | 2017-01-05 15:31 | -15 | 2016-11-16 14:01 | Civil - Civil Engineering General | 3000 |  | Material | Reject | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | Marshgate lane water main was installed without 2No. MCRS being approved: Cxxx-MRG-C-QAP-CR094_WS111-50581 Cxxx-MRG-C-QAP-CR094_WS111-50582
| 03SR - Stations (RfL) | Cxxx-NCR-002387 | NCR | Gabion Basket Upper Section Top Soil Mixing |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2017-02-14 | 2017-01-18 08:39 | -27 | 2016-11-16 17:35 | Civil - Landscaping | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Please refer to drawing Cxxx-SWN-L-DDD-CR094_PT002_Z-96177. The Upper sections of the Gabion Baskets were hand filled with 40-100mm gabion stone without mixing of the stone with topsoil to fill voids. As per note 2.
| 03SR - Stations (RfL) | Cxxx-NCR-002388 | NCR | Greenway Ramp Parapet Chamfer |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2017-02-15 | 2017-01-28 10:40 | -18 | 2016-11-17 08:03 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Please refer to drawing Cxxx-SWN-S-DDL-CR094_PT002_Z-95010 & Cxxx-SWN-S-DDD-CR094_PT002_Z-37422. The eastern section of walls 5 & 6 parapets were constructed without the lower bottom chamfer as per note C7 on general notes drawing DDD-95010. (see attached photo).
| 03SR - Stations (RfL) | Cxxx-NCR-002389 | NCR | FDW - Waterstop Installation at W6/7 Expansion Joint |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2017-01-14 | 2017-01-09 09:55 | -5 | 2016-11-17 09:21 | Civil - Civil Engineering General | 3000 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | The below PTR was raised as an FCD (FCD - 2550), however was rejected and cancelled by CRL stating "This is an NCR not an FCD": The Base slab for wall section W7 steps in to allow for the construction of the drainage Man Hole in that area. Due to this the Waterstop cannot be installed up the back of the slab at the line of the W6/W7 Expansion Joint as per the detail on drawing Cxxx-SWN-S-DDA-CR094_PT002_1-80021
| 03SR - Stations (RfL) | Cxxx-NCR-002390 | NCR | FDW - Time Between Concrete Loads - Pour Date 10.11.2016 |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2016-12-23 | 2016-12-19 16:31 | -4 | 2016-11-25 07:48 | Civil - Civil Engineering General | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | Due to the concrete supply on the FDW pour for walls W2,4,6, & 8 (date: 10.11.2016) the time between loads exceeded the allowable 30mins (as stated within clause E10.680 of the concrete the specification). This was due to the 2nd load being rejected for exceeding allowable slump measurements (220mm). The 3rd load also came in out of slump specification (210mm), however the 3rd load was re slumped after waiting 30 minutes on site and reached a slump value of 190mm. Please note that the third load was not poured until the slump value of 190mm was reached. As the time between loads of concrete increased the risk of a cold joint to the concrete already poured within the walls was also increasing. The third load of concrete was slumped every 10 minutes, and after 30 minutes it had reached a slump of 190mm (10mm out of tolerance). At this point it was agreed with Cxxx that the third load could be poured to reduce the risk of a cold joint. Following discussion with Cxxx,
| 03SR - Stations (RfL) | Cxxx-NCR-002391 | NCR | Blacktop material laid without MCR approval in place |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2017-01-31 | 2017-01-27 08:20 | -4 | 2016-11-24 16:33 | Civil - Civil Engineering General | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Subcontractor Problems - Interfacing problems | Completed |  | Unapproved blacktop material has been placed in areas of the project. Due to reasons of weight restrictions, falls to be accommodated and access issues in areas of the project, __’s blacktop supplier have used a more workable material in areas where only hand lay application is possible. This increase in the penetration grade is preferred for hand laying operations as it doesn’t harden as quick therefore a better finish can be achieved. Both of the AC20 and AC32 mixes have been used with a 100/150 pen, however our current MCR only has 40/60 pen approved.
| 03SR - Stations (RfL) | Cxxx-NCR-002392 | NCR | Barbican Gates South of Greenway incorrect plinth level |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2017-02-23 | 2017-01-17 09:01 | -37 | 2016-11-25 15:19 | Civil - Civil Engineering General | 1000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The Northern plinth was cast at an incorrect level due to an error reading from drawing Cxxx-SWN-L-DDD-CR094.
| 03SR - Stations (RfL) | Cxxx-NCR-002394 | NCR | EIP - Installation of Door Closers to Internal Doors |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2017-02-10 | 2017-02-10 10:29 | 0 | 2016-11-30 19:31 | Architectural - Doors | 5000 |  | Incorrect Installation | Repair | 3 (3-6k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | __ (MS) & Crossrail (CRL) have now commenced inspections of the installation of the internal doors within the Emergency Intervention Point (EIP) as part of the Architectural Verification Activity Plan (VAP). A planned site inspection was completed on Thursday 24th November 2016 and attended by representatives of CRL – Anthony Buckley (CEG – Architect) , __ Foster (Cxxx-Field Engineer) and MS - James Donga (EIP - Agent). During this inspection it was observed that ‘door closers’ fitted to a number of internal doors throughout the EIP, as witnessed at Track Level and Sub-surface Level i.e. Intermediate Level appear to have been installed outside specified tolerances as given by the manufacturer i.e. DORMA UK. On a number of doors the ‘sliding arm’ of the closer was observed to be positioned at a ‘slope’ when the door was in its closed position – please refer to attached photograph showing installation. Whereas the referenced guidance documentation shows that the ‘sliding arm’ and ‘body’ of the closers should be parallel at the specified distances, when the door is in a closed position. Further reference to the manufacturer’s trade literature and subsequent communication with DORMA UK, Technical Support has confirmed that the ‘observed’ closers have been installed incorrectly. DORMA UK also advised that consequently such installation will degrade the seals for more quickly. __ have now referred this matter to the specialist ‘door’ subcontractor, __ Industries Ltd responsible for the manufactured and installation of the internal doors at the EIP.
| 03SR - Stations (RfL) | Cxxx-NCR-002395 | NCR | Gabion Basket Green Organic Polymer Powder Coating |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2017-02-27 | 2016-12-12 13:38 | -77 | 2016-11-29 07:43 | Civil - Landscaping | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Please refer to drawing Cxxx-SWN-L-DDD-CR094_PT002_Z-96177 and MCR Cxxx-MRG-C-QAP-CR094_WS111-50549. The installed gabion baskets on the South Greenway Wall do not have the green coloured organic powder coating for the mesh fabric and lacing wire as per Gabion Basket Details note 4 on drawing DDD-96177.
| 03SR - Stations (RfL) | Cxxx-NCR-002396 | NCR | EIP - Strengthening the sides of the Louvres to avoid deflection |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2017-04-30 | 2017-04-10 14:26 | -20 | 2017-01-17 13:55 | Architectural - General | 5000 |  | Incorrect Installation | Repair | 3 (3-6k) | Complete | Design Problem - Inadequate or defective design | Completed |  | During the sealing application for the vertical joints for the EIP façade (I.e. Louvre to Louvre and Louvre to Cladding) it has been observed that the sides of the Louvres are warping which resulted in increased joint width and uneven joint lines.
| 03SR - Stations (RfL) | Cxxx-NCR-002397 | NCR | TSS to ETS Ballast Levels Outside Positional Tolerance |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2016-12-13 | 2016-12-06 10:32 | -7 | 2016-11-29 13:51 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Further from previous NCR-2381; during the review of the Ballast Records from Track Support Slab to East Track Slab a number of additional points have been identified outside the tolerances set under Cxxx-MRG-C-ITP-CR094_WS111-50082 (please see attached as-built drawing for reference).
| 03SR - Stations (RfL) | Cxxx-NCR-002398 | NCR | FSU - Black Stainings on wall |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2017-03-31 | 2017-03-23 15:44 | -8 | 2016-12-07 08:49 | Civil - Civil Engineering General | 20000 |  | Workmanship | Repair | 2 (6-60k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | The walls between GL_4-5 have dark stainings on the them that can't be removed by any conventional means.
| 03SR - Stations (RfL) | Cxxx-NCR-002399 | NCR | Greenway Ramp Parapet Installation |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2017-03-31 | 2017-03-03 11:39 | -28 | 2016-12-07 16:03 | Civil - Street Furniture | 3000 |  | Manufacturing Defect | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Please refer to fabrication drawing Cxxx-MRG-A-DWG-CR094_WS111-50775 P04. Fabrication error regarding the welding of the internal spigot connection to the S.H.S post.
| 03SR - Stations (RfL) | Cxxx-NCR-002400 | NCR | CMR Reinstatement - Dewatering well leak |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2017-01-13 | 2016-12-21 09:17 | -23 | 2016-12-14 10:15 | Civil - Civil Engineering General | 3000 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Dewatering well in green area of the drawing Cxxx-MMD-D-DDL-CRG06_Z-00014 has been successfully decommissioned by Cxxx subcontractor on 28/11/2016. Dewatering well installed as per details (Cxxx-MRG-C-QAP-CR094_WS111-50608) and backfilled and compacted as per Highway and CRL specification. Next day after completion of decommission works Cxxx noticed that one of two dewatering wells is leaking through the small gap in clay above the decommissioned well. Cxxx believe that 300mm of clay backfill is not sufficient for the water pressure under this dewatering well.
| 03SR - Stations (RfL) | Cxxx-NCR-002402 | NCR | Barbers Road North Footpath - Alignment of Granite Strip |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2017-02-17 | 2017-01-27 08:55 | -21 | 2016-12-20 14:30 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Please refer drawings Cxxx-SWN-L-DDA-CR094_PT002_Z-96013 and Cxxx-SWN-L-DDA-CR094_PT002_Z-96014. The granite strip within the north footpath west of the DLR station has been part constructed earlier in the project, the strip has been installed parallel to the station building as opposed to parallel to Barbers Rd kerb alignment. Consequently, at the western end the constructed alignment the granite strip is 1.43m north of the original location, refer attached marked up survey plan (constructed alignment shown in red).
| 03SR - Stations (RfL) | Cxxx-NCR-002403 | NCR | FDW - W15 - Inconsistencies in Drawings for Coping Width |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2017-02-24 | 2017-01-25 08:34 | -30 | 2017-01-03 13:12 | Civil - Civil Engineering General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Conflicting information on drawings | Completed |  | Upon construction of the top section of wall section W15 it was found that the drawings conflicted with regards to the thickness of the coping: Drawing Cxxx-SWN-S-DDJ-CR094_PT002_1-80035 - Shows the coping to be at 670mm wide on the coping bar bending schedule Planning Drawing Cxxx-SWN-L-DDL-CR094_PT002_Z-96116 - Also shows the W15 section of the wall to have a brick cladding - which would require the thicker coping Drawing Cxxx-SWN-S-DDB-CR094_PT002_Z-80023 - Shows the coping to be 500mm wide on the General Arrangement drawings RFI 4215 was raised to clarify which thickness was actually required, with 500mm thickness being the response. However, prior to pouring W15 the issue was discussed with CRL's Project Manager and Construction Manager and the decision made to install the coping to a thickness of 670mm - in line with the planning drawing.
| 03SR - Stations (RfL) | Cxxx-NCR-002404 | NCR | Joint bays for __ connection |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2017-02-03 | 2017-01-27 08:57 | -7 | 2017-01-06 12:16 | Civil - Civil Engineering General | 6000 |  | Incorrect Installation | Rework | 3 (3-6k) | Complete | Design Problem - Change to drawings not provided on time | Completed |  | The design intent for the New Barbers Road lighting supply has changed from a LBN feeder pillar supply to __ direct supply. During discussions with __ the jointing pit detail and dimension were never finalised with __ and __ have installed 600 x 600 stakka boxes at joint locations site wide. Following a site inspection by __ on 5th January 2017, __ have been advised these boxes do not provide sufficient room for __ to carry out their jointing works. __ are required to remove these (15 number boxes) site wide and open up a sufficient area within the footpath (approximately 1.5m long x 0.6m wide) to allow__ access. Paving of areas to be inspected on an individual basis as most location currently have a recessed paved lid installed. Reinstated paving to blend in with existing and be aesthetically pleasing with minimal amount of cuts.
| 03SR - Stations (RfL) | Cxxx-NCR-002405 | NCR | Decommissioning of Monitoring Wells/Boreholes without an approved Grout MCR |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2017-01-31 | 2017-01-27 09:21 | -4 | 2017-01-13 09:53 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The __ subcontractor, Ecologia, proceeded to de-commission the monitoring wells without an approved grout MCR in place. __ did not believe an MCR was required given the approved ITP, Cxxx-MRG-C-ITP-CR094_WS111-50085, section 2.1 states MCR will not be required for the materials.
| 03SR - Stations (RfL) | Cxxx-NCR-002406 | NCR | Installation of non-approved control cables |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2017-03-03 | 2017-03-02 09:19 | -1 | 2017-01-17 12:42 | Electrical - General | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | The following MCR’s have not been approved by CRL after several reworks of the MCR’s CRL-MCR-003556 CRL-MCR-003557 CRL-MCR-003558 One of the review’s CRL-MCR-003556-001 Stated The CY LSZH Control Cable is acceptable for use in the specified areas with the following conditions: The cable will not be used for safety related systems, i.e. Fire Alarm or PA/VA. The cable will be contained within metal containment. All these criteria have been met however further review now requires test evidence for the following: 1. Smoke emission according to EN 50268-2, IEC 61034 – 2 2. Acid gas emission according to EN 50267-2-1, EN 50267-2-3, IEC60754-1+2 In response the supplier questions the reason behind 1-085 compliance as the cable is not intended to be used in any tunnel environment. The manufacturer has also stated that the cable's meet the requirement of JY61.2201 a-b. Refer also JY61.1302 a-e inclusive,JY61.1309,JY61.1404. Please note that it is expected that the required Test Results will be issued on Wednesday 18th January Propose use as is.
| 03SR - Stations (RfL) | Cxxx-NCR-002407 | NCR | EIP Builderswork Penetrations - Firestopping clash with M&E services |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2017-08-18 | 2017-08-31 15:49 | 13 | 2017-01-25 12:53 | Electrical - Cable Management | 20000 |  | Incorrect Installation | Repair | 2 (6-60k) | Complete | Management Problem - Inadequate supervision | Completed |  | Firestopping Contractor __ have been assessing the status of the penetrations that they are due to complete at the PML EIP and have provided feedback of Non Compliance of services passing through Builderswork penetrations at the building. A meeting with CEG Fire Engineers has highlighted agreement of __'s concerns although some actions can be closed on acceptance of FCD's
| 03SR - Stations (RfL) | Cxxx-NCR-002408 | NCR | EIP - Floor Paint failed |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2017-07-31 | 2017-07-25 15:47 | -6 | 2017-02-16 09:12 | Architectural - Finishes | 5000 |  | Incomplete Works | Rework | 3 (3-6k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | Refer to the following documents: Finishes Schedule: Emergency Intervention Point – Document No. Cxxx-SWN-A-TSC-CR094_PT002-00005 Rev. 6.0 Product: Betolux Akva Floor Paint – Document No. Cxxx-MRG-C-QAP-CR094_WS111-50306 Rev 2.0 During the site inspection and following slip resistance test carried out on the finished floor paint it has been observed that the floor paint is detaching in places back to the original concrete surface and where the Pendulum test has been carried out only the top coat has been removed. (See attached photographic report) (Test results will be provided in due course)
| 03SR - Stations (RfL) | Cxxx-NCR-002411 | NCR | Installation of Non Approved Heater - CRL-MCR- 002897 |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2017-05-31 | 2017-06-01 17:33 | 1 | 2017-01-27 09:30 | Electrical - LV Equipment | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Procedure Problem - Other | Completed |  | CRL-MCR-002897 has been rejected several times. The heater has been installed. It has been rejected on the basis of: The comment remains that the proposed domestic models are not suitable for sub-surface use in terms of durability and will be prone to misuse by the maintainer, even at back of house area. Approval of this item is holding the completion of the IRN required for energisation.
| 03SR - Stations (RfL) | Cxxx-NCR-002412 | NCR | Drainage line FDC01 to FDC03 |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2017-03-31 | 2017-03-24 14:17 | -7 | 2017-01-28 12:59 | Civil - Drainage | 10000 |  | Design | Repair | 2 (6-60k) | Complete | Design Problem - Inadequate or defective design | Completed |  | Refer drawing Cxxx-SWN-D-DDA-CR094_PT002_Z-95223, Cxxx-SWN-D-DDA-CR094_PT002_Z-95226, Cxxx-SWN-D-DDA-CR094_PT002_Z-95228. The drainage line between chambers FDC01, FDC02 and FDC03 has been constructed in a straight line between chambers in accordance with standard practice drainage works, not on a curve as per the design intent.
| 03SR - Stations (RfL) | Cxxx-NCR-002413 | NCR | EIP Access Road - Incorrect type of Aco drain installed |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2017-03-31 | 2017-01-31 14:16 | -59 | 2017-01-30 18:10 | Civil - Drainage | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Misunderstand the definition of the requirement | Completed |  | Refer Drawing C12-SWN-D-DDA-CR094_PT002_Z-95222 and Drawing C12-SWN-D-DDD-CR094_PT002_Z-95468. Drawing C12-SWN-D-DDA-CR094_PT002_Z-95222 shows a 150mm wide 250mm deep Park Drain along the EIP (ATFS) Access Road, a 150mm wide 250mm Aco Multidrain has been installed
| 03SR - Stations (RfL) | Cxxx-NCR-002414 | NCR | Barbers Road HRA Surfacing |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2017-03-17 | 2017-03-07 14:12 | -10 | 2017-02-03 16:39 | Civil - Wearing Course | 30 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | Barbers Road surfacing has not met the required texture depth from Part 2 of Appendix 7/1 of Cxxx-SWN-C-RSP-CR094_PT002-50001
| 03SR - Stations (RfL) | Cxxx-NCR-002415 | NCR | 146°C delivery temperature reported for laid HRA55/10 surf 40/60 site 2A Barbers Road on 06/12/2016. |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2017-03-17 | 2017-03-07 13:37 | -10 | 2017-02-07 08:12 | Civil - Civil Engineering General | 500 |  | Material | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Cxxx-SWN-C-RSP-CR094_PT002-50001_Rev3 Barbers Road Redesign Spec-URS specifies minimum delivery temperature 155°C. __ report No: RS162864 reports delivery temperature 146°C. Laying records UXB0355780 shows rolling temperature 125°C.
| 03SR - Stations (RfL) | Cxxx-NCR-002417 | NCR | Urban Realm - Greenway ramp tactile types |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2017-03-03 | 2017-03-03 11:34 | 0 | 2017-02-13 08:31 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The incorrect type of tactile pavers have been installed on the Greenway ramp, cycle path tactile pavers are required.
| 03SR - Stations (RfL) | Cxxx-NCR-002418 | NCR | NOS Platform - Pilaster Capping Stone Clash with Fence |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2017-03-24 | 2017-03-23 15:46 | -1 | 2017-02-22 17:03 | Civil - Civil Engineering General | 1000 |  | Design | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Please refer to: Attached photographs The 75mm recess of the pilaster capping stone is clashing with the fence panel preventing it from being installed. If the pilaster was not constructed then there would have been no issue with the fence.
| 03SR - Stations (RfL) | Cxxx-NCR-002419 | NCR | No Approved Shedule for samples, mock-ups, prototypes, test panels and benchmarks |  | Crossrail | XRL | PML - Pudding Mill Lane Portal (Central) |  | 2018-09-05 | 2017-09-27 12:59 | -343 | 2017-02-23 11:52 | Architectural - General | 1000 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | A planned Crossrail surveillance was undertaken on 22nd February 2017 to look at the Management of Architectural Samples, Benchmarks and Mock ups. On reviewing the EIP (Architecture) Schedule of Samples, Mock ups, Prototypes and Quality Benchmarking that had been supplied by the Contractor, it was found that the document Cxxx-MRG-A-STP-CR094_WS111-50001 (Rev 1) was incomplete and had not submitted to Crossrail (CRL) for approval.
| 03SR - Stations (RfL) | Cxxx-NCR-002420 | NCR | Inspection and Request Forms (IRF) |  | Crossrail | XRL | PML - Pudding Mill Lane Portal (Central) |  | 2017-05-12 | 2017-05-04 13:53 | -8 | 2017-02-23 13:10 | Materials - Approval | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Misunderstand the definition of the requirement | Completed |  | 2) A planned Crossrail surveillance was undertaken on 22nd February 2017 to look at the Management of Architectural Samples, Benchmarks and Mock ups. On review of the documentation supplied by the Contractor, it was found that the Contractor had failed to issue Inspection and Request Forms (IRF) for the inspection of Quality Benchmarking for works carried out at the EIP building.
| 03SR - Stations (RfL) | Cxxx-NCR-002421 | NCR | Quality Benchmarking |  | Crossrail | XRL | PML - Pudding Mill Lane Portal (Central) |  | 2018-09-05 | 2017-09-27 13:02 | -343 | 2017-02-23 13:17 | Architectural - General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | 3) A planned Crossrail surveillance was undertaken on 22nd February 2017 to look at the Management of Architectural Samples, Benchmarks and Mock ups. During a review of the documentation supplied by the Contractor and a site visit to the EIP building it was found that the Contractor had no approved Quality Benchmarks for the following; Painting (floors and walls),Roof materials, External Louvre’s, Fire stopping, Stair Balustrade, Doors and Blockwork. The Contractor presented a Benchmark form for the external pre-cast concrete cladding panels to External Building Façade (EIP 009) on review had not been approved.
| 03SR - Stations (RfL) | Cxxx-NCR-002422 | NCR | EIP - Comms clash with blockwork walls |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2017-04-28 | 2017-03-23 15:39 | -36 | 2017-02-27 10:06 | Civil - Civil Engineering General | 10000 |  | Design | Repair | 2 (6-60k) | Complete | Management Problem - Inadequate supervision | Completed |  | Communication trunking and cabling has been installed within the EIP and passes through the block work walls into various rooms within the building. In 7no. locations where the trunking passes through the walls the required 50mm clearance to the block work for fire stopping can not be achieved, it is proposed to increase the depth of the openings in the block as shown on the attached schedule. Relocation of the trunking is not practical/possible in these locations due to volume of other CMS positioned within the openings and the cables already installed within.
| 03SR - Stations (RfL) | Cxxx-NCR-002423 | NCR | Lack of segregation between safety critical cables. |  | Crossrail | XRL | PML - Pudding Mill Lane Portal (Central) |  | 2017-09-15 | 2017-09-19 15:18 | 4 | 2017-02-28 14:24 | Electrical - General | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | A planned Crossrail surveillance was undertaken at Pudding Mill Lane on the 23.02.17. As part of the surveillance we visited UPS room 1/763 where it was noticed that above the UPS there is a length of cable tray with a mixture of cables tie rapped to it. It is believed that there is a mixture of LVAC and LVDC supply cables associated with the supply to the Emergency Lighting Distribution Board located further along the wall. Emergency Lighting is regarded as a safety system and therefore should be separated by the means of a barrier from other supplies. Additionally as part of a UPS system there are DC supplies linking the UPS to the Bypass switch which means there will be both LVAC and LVDC supply cables installed in parallel on the same tray. This installation does not conform to BS7671.
| 03SR - Stations (RfL) | Cxxx-NCR-002424 | NCR | FP200 Enhanced Cable in Cxxx UPS Room |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2017-06-23 | 2017-06-13 13:06 | -10 | 2017-02-28 21:17 | Electrical - Lighting | 0 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Supervision - Not Defined | Completed |  | FP200 Enhanced Cable has been used on the UPS System in the UPS room. There is an MCR in place for Cxxx where this cable is installed in the LV SWitchrooms. unfortunately this is the only location the cable is approved for.
| 03SR - Stations (RfL) | Cxxx-NCR-002425 | NCR | Resin bonded surface decorative aggregate installed while MCR was code 3 |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2017-04-14 | 2017-04-06 14:54 | -8 | 2017-03-17 13:07 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Resin bonded surface decorative aggregate (Amber Gold - same aggregate all across the Olympic Park) installed before approved MCR. __ carried out the 1m2 sample trial panel which was accepted by CRL matching existing resin bonded surface on Marshagate Lane footpath. Due to only minor comments on rev01 MCR (Cxxx-MRG-C-QAP-CR094_WS111-50632), Cxxx progressed with installation process to avoid necessary delays and standing time.
| 03SR - Stations (RfL) | Cxxx-NCR-002426 | NCR | MGL uncontrolled crossing kerb height |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2017-06-20 | 2017-04-05 08:47 | -76 | 2017-03-22 14:51 | Civil - Kerbs | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Following the stage 3 road safety audit conducted by Newham Council it was observed that the kerbs at the uncontrolled crossing at Marshgate Lane are greater than 6mm (see attached photos and extract from Road Safety Audit).
| 03SR - Stations (RfL) | Cxxx-NCR-002427 | NCR | FDW - Instllation of Fencing with Fabrication Drawing Code 3 |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2017-05-31 | 2017-05-23 10:58 | -8 | 2017-03-03 14:41 | Civil - Civil Engineering General | 10000 |  | Planning | Repair | 2 (6-60k) | Complete | Design Problem - Use of unapproved drawings | Completed |  | 1. Cxxx have installed the FDW fencing with the fabrication drawing (Cxxx-MRG-C-DWG-CR094_WS111-50240) at Code 3. 2. The fabrication drawing was submitted initially on 13.01.2017 3. Rev 1.0 was then given code 3 and returned with comments on 19.01.2017 4. These were passed on to the specialist fencing fabricator whom addressed the comments and updated the fabrication drawing 5. Due to the need to erect the fencing on the FDW as of 01.02.2017 to meet the agreed completion dates Cxxx decided best to proceed with the fabrication process on the basis that the Rev 2.0 fabrication drawing had been submitted on 26.01.2017 (but not approved to any code at the time) and the comments had been addressed. Further to this as the fencing fabricators are specialist and the detailed design down to them rather than Cxxx, Cxxx believed this should not cause any further issue as the initial code 3 comments had been addressed. 6. On 27.02.2017, three weeks after the fencing erection had been completed Cxxx received the Rev 2.0 fabrication drawing back, at code 3. NOTE: Cxxx do not take on design responsibility
| 03SR - Stations (RfL) | Cxxx-NCR-002428 | NCR | NOS Low Platform Cradle anchor out of tolerance |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2017-06-04 | 2017-03-28 15:26 | -68 | 2017-03-06 09:28 | Civil - Street Furniture | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | A complete resurvey has been undertaken by our survey dept of the fence line position showing fence in tolerance. This NCR is similar to NCR2337 which outlined cause and corrective action (see attached).
| 03SR - Stations (RfL) | Cxxx-NCR-002429 | NCR | Material Sample acceptance |  | Crossrail | XRL | PML - Pudding Mill Lane Portal (Central) |  | 2017-12-29 | 2017-09-27 13:17 | -93 | 2017-03-06 14:59 | Materials - Approval | 1000 |  | Material | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | A planned Crossrail surveillance was undertaken on 22nd February 2017 to look at the Management of Architectural Samples, Benchmarks and Mock ups. During a review of the architectural MCRs for the EIP building found; Door Carcasses Cxxx-MRG-A-QAP-CR094_WS111-50321 (Rev 1) Decal code 1, Precast Concrete Cladding Cxxx-MRG-A-QAP-CR094_WS111-50292 (Rev 1) Decal code 1 and External Louvers Cxxx-MRG-A-QAP-CR094_WS111-50309 (Rev 1) Decal code 1. The Contractors Materials Approvals Schedule Cxxx-MRG-O-TSC-CR094_WS111-50001 (Rev 12) indicates the requirement of a sample for the sampled materials. There is no evidence in the above MCRs that the samples have been reviewed and accepted by Crossrail.
| 03SR - Stations (RfL) | Cxxx-NCR-002430 | NCR | Architectural Prototypes and Mock-ups |  | Crossrail | XRL | PML - Pudding Mill Lane Portal (Central) |  | 2017-12-29 | 2017-09-27 13:46 | -93 | 2017-03-06 15:17 | Materials - Approval | 1000 |  | Material | Rework | 4 (0.5-3k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | A planned Crossrail surveillance was undertaken on 22nd February 2017 to look at the Management of Architectural Samples, Benchmarks and Mock ups for the EIP Building. During a review of the documentation supplied by the Contractor found that their is no evidence of acceptance of the Prototype for the Pre-cast cladding and Door set Mock-up.
| 03SR - Stations (RfL) | Cxxx-NCR-002431 | NCR | Urban Realm __V 5m gate hinge security detail |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2017-06-13 | 2017-06-12 07:49 | -1 | 2017-03-15 18:40 | Civil - Street Furniture | 2000 |  | Documentation and Records | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The hinge detail as required on Cxxx-SWN-L-DDD-CR094_PT002_Z-96175 details a M20 shear nut as a security detail. This was not detailed in fabrication drawing Cxxx-MRG-C-DWG-CR094_WS111-50218 Rev 1-3.
| 03SR - Stations (RfL) | Cxxx-NCR-002432 | NCR | Site 2B Hard Landscaping RRVR AC32 & AC20 laid below |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2017-07-05 | 2017-05-02 11:16 | -64 | 2017-04-06 12:42 | Civil - Street Furniture | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Please refer to the attached temperature laying record for AC32 & AC20 for the RRVR on the 1/12/16. The temperature of the Asphalt laid immediately prior to rolling is marginally below the recommended delivery and rolling temperature as per BS 594987 Annex A Table A.1.
| 03SR - Stations (RfL) | Cxxx-NCR-002433 | NCR | EIP - Firestoping around services that are too close to RC walls/slab |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2017-05-05 | 2017-04-21 13:13 | -14 | 2017-03-21 16:33 | Architectural - General | 2000 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | Please refer to Cxxx-NCR-2407 Many services have been installed within the EIP building that passes through the RC walls/slabs into various rooms within the building. In 8no. locations where the services passes through the walls/slabs are less that 50mm clearance to the RC walls/slabs for fire stopping. Services and RC openings installed as per IFC drawings. Due to services or openings cannot be resized/relocated alternative fire stopping solution are required at 8no locations. List of locations where services are to close to RC wall/slabs are below (and also in attached drawing): • Level 01 – 39/40 (39/40) • Level 01 – 57/58(428/57) • Level 01 – 83/84 (82/83) • Surface level – 235/236 (256/257) • Surface level – 237/238 (258/259) • Surface level – 215/216 (236/237) • Sub-surface level – 331/332 (350/351) • Sub-surface level – 289/290 ( 320/321) Numbers in brackets are __ internal references.
| 03SR - Stations (RfL) | Cxxx-NCR-002434 | NCR | EIP - Security Bar-sets require notching around Steel Members |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2017-04-14 | 2017-04-10 10:36 | -4 | 2017-03-17 10:46 | Architectural - Security | 3000 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | Refer to Drawing No.: Cxxx-MRG-A-DWG-CR094_WS111-51199 (BS002) Cxxx-MRG-A-DWG-CR094-WS111-51200 (BS003) Cxxx-MRG-A-DWG-CR094-WS111-51201 (BS004) Cxxx-MRG-A-DWG-CR094-WS111-51202 (BS005) Cxxx-MRG-A-DWG-CR094-WS111-51203 (BS006) Cxxx-MRG-A-DWG-CR094-WS111-51204 (BS007) During the installation of security bar-sets it has been observed the top modules have not been notched around the "L" bracket for the Louvre/Blockwork steel members installed in the RC openings @Ground Floor Rooms. Please find attached photographic report.
| 03SR - Stations (RfL) | Cxxx-NCR-002435 | NCR | Greenway Ramp Handrail inadequate fixings |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2017-06-25 | 2017-06-07 09:58 | -18 | 2017-03-27 12:49 | Civil - Street Furniture | 2500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The self drilling screws to fix the handrail bracket to the RHS posts as stated on the fabrication drawing Cxxx-MRG-A-DWG-CR094_WS111-50775 and installed are not fit for purpose (see attached design brief).
| 03SR - Stations (RfL) | Cxxx-NCR-002436 | NCR | Greenway Ramp Parapet Panel Countersunk fixing to internal spigot not centred in slotted socket |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2017-06-25 | 2017-05-24 16:08 | -32 | 2017-03-27 12:41 | Civil - Street Furniture | 500 |  | Manufacturing Defect | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | A small number of the countersunk fixings on the Greenway ramp that fix the spigot end of the RHS posts to socket of the rail panels are not centred in the slot of the socket. This is resulting some screws being too tight to one edge of the slot and not allowing for the effects of thermal expansion of the panel.
| 03SR - Stations (RfL) | Cxxx-NCR-002437 | NCR | Greenway Parapet Handrail coincident movement joint with structure movement joint |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2017-07-31 | 2017-07-07 14:27 | -24 | 2017-03-27 12:28 | Civil - Street Furniture | 2000 |  | Manufacturing Defect | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | Please refer to drawing Cxxx-SWN-S-DDD-CR094_PT002_Z-37120 the handrail expansion joints on the Greenway Ramp do not coincide with the Movement Joint on the Greenway ramp.
| 03SR - Stations (RfL) | Cxxx-NCR-002439 | NCR | Un-controlled Installation of fire stopping |  | Crossrail | XRL | PML - Pudding Mill Lane Portal (Central) |  | 2017-07-31 | 2017-07-17 10:07 | -14 | 2017-03-28 08:35 | Fire - Compartmentation | 1000 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | A planned Crossrail surveillance was undertaken on 27th March2017 to look at Fire stopping installation in the EIP Building. During the site visit and the subsequent review of documentation it was found that the installation of fire stopping to blockwork joints, had been omitted from the ‘EIP Blockwork Installation’ ITP Cxxx-MRG-A-ITP-CR094_WS111-50029 (Rev 3) and the ‘EIP Blockwork Installation’ Method Statement Cxxx-MRG-GMS-CR094_WS111-50016 (Rev 1). No inspections have been carried out on the installation of the fire stopping to blockwork joints. It could not be verified that the accepted materials had been used in the installation as no inspections had been carried out. On a visual inspection of the installed fire stopping to blockwork joints, it was witnessed that sections of the joint filler had not adhered to the blockwork and areas joint filler had been missed. See attached Photos.
| 03SR - Stations (RfL) | Cxxx-NCR-002440 | NCR | Site 2B Portals, Walls, Fencing, Barriers and Foundations - Foundation Bases Out of Tolerance |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2017-06-26 | 2017-05-10 15:39 | -47 | 2017-03-28 15:00 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Please refer to Cxxx-SWN-L-DDD-CR094_PT002_Z-96151 & Cxxx-SWN-L-DDD-CR094_PT002_Z-96195. As-built surveys have been carried out and show there are a number of points out of the required concrete level tolerance, in accordance with BS 5606 Table 1 In situ concrete Beams and floor slabs ± 23mm. Please refer to the attached as-built surveys with out of tolerance points highlighted in orange.
| 03SR - Stations (RfL) | Cxxx-NCR-002441 | NCR | Site 2B Hard Landscaping - Grasscrete As Built Out of Tolerance |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2017-07-05 | 2017-05-18 10:42 | -48 | 2017-04-06 08:46 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | Please refer to the as built drawing Cxxx-MRG-SRV-SK-CR094-11689 (attached). Isolated locations of the Grasscrete bays are out of tolerance as per BS5606 Beams & floor slabs Table 1 highlighted in the attached drawing.
| 03SR - Stations (RfL) | Cxxx-NCR-002443 | NCR | EIP roof slab damaged waterproofing membrane |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2017-05-26 | 2017-04-10 08:27 | -46 | 2017-03-31 14:03 | Civil - Civil Engineering General | 6000 |  | Damaged | Repair | 3 (3-6k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | During the Cxxx excavation to install electrical ducts between MH1 and the National Grid Bulk Supply Point the excavator has contacted the corner of the EIP roof slab causing damage to the PmB Polyurethane Elastomer waterproofing membrane and minor damage to the concrete slab, refer attached photograph
| 03SR - Stations (RfL) | Cxxx-NCR-002444 | NCR | Air conditioning final IRF |  | Crossrail | XRL | PML - Pudding Mill Lane Portal (Central) |  | 2017-06-01 | 2017-05-10 16:05 | -22 | 2017-04-03 15:48 | Mechanical - Heating Ventilation & Air Conditioning | 500 |  | Incomplete Works | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | A final IRF for air conditioning was raised, the field engineer attended the inspection only to find it had not been inspected correctly by both the tier 1 and tier 2 contractors, incomplete works such as dust and debris on the cooling units and inside the filters. This is not the first time a final IRF has been announced and the installation is incomplete
| 03SR - Stations (RfL) | Cxxx-NCR-002445 | NCR | Urban Realm - DLR Gate |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2017-06-23 | 2017-06-14 15:37 | -9 | 2017-04-05 14:57 | Civil - Civil Engineering General | 5000 |  | Manufacturing Defect | Repair | 3 (3-6k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | Please refer to: Attached design drawing It was picked up by the Cxxx design engineer that the DLR gate was not fabricated as per the design drawing. The shroud plate around the lock was not installed.
| 03SR - Stations (RfL) | Cxxx-NCR-002446 | NCR | Manhole Chamber EIP 04 exceeds 675mm between top of ladder and ground level |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2017-05-19 | 2017-04-25 07:59 | -24 | 2017-04-10 08:43 | Civil - Drainage | 5000 |  | Incorrect Installation | Rework | 3 (3-6k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | Manhole Chamber EIP 04 has been constructed with 6 number raising pieces and a distance between the top rung of the ladder to the ground level of approximately 800mm. MCHW Drawing F4 Type 2 Precast Concrete Chamber states a maximum allowable distance of 675mm between the top step iron and ground level.
| 03SR - Stations (RfL) | Cxxx-NCR-002447 | NCR | EIP - Manhole chambers SB02, SB03 and SB04 constructed without inverts and junctions |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2017-06-09 | 2017-06-08 11:34 | -1 | 2017-04-10 08:51 | Civil - Drainage | 5000 |  | Incorrect Installation | Rework | 3 (3-6k) | Complete | Management Problem - Inadequate supervision | Completed |  | Manhole chambers SB02, SB03 and SB04 have been constructed without granolithic concrete inverts and junctions
| 03SR - Stations (RfL) | Cxxx-NCR-002448 | NCR | Urban Realm Palisade Fixing Method of Fixing Pales (FCD2594) |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2017-08-01 | 2017-06-28 12:56 | -34 | 2017-05-03 09:41 | Civil - Street Architecture | 1000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Refer to FCD 2594 the SP24 and SP36 Palisade fences (refer to Cxxx-SWN-L-DDD-CR094_PT002_Z-96168 & Cxxx-SWN-L-DDD-CR094_PT002_Z-96155) were installed with M8 X25 Grade 8.8 T Bolt HDG and 43 M8X17mm Shear Nut Slim Type 0.3mm HDG under the assumption that the fixings were in compliance with __ standard NR/SP/ELP/21081 however the fixings are not considered the same fixity as riveting.
| 03SR - Stations (RfL) | Cxxx-NCR-002449 | NCR | MEP Asset Labeling Installation started without Approved ITP |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2017-06-16 | 2017-06-08 12:36 | -8 | 2017-04-12 06:44 | Electrical - General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Supervision - Insufficient supervision | Completed |  | The Asset Labelling was started on the whole MEP installation of the EIP without an approved ITP
| 03SR - Stations (RfL) | Cxxx-NCR-002450 | NCR | RRVR Kerbs surface and alignment out of tolerance |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2017-07-11 | 2017-05-19 10:03 | -53 | 2017-04-12 14:15 | Civil - Kerbs | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Not Defined | Completed |  | Please refer to survey drawing Cxxx-MRG-SRV-SK-CR094-11508. The highlighted areas are marginally out of tolerance for horizontal alignment ±13 mm and level ±6 mm in accordance with BS 594987.
| 03SR - Stations (RfL) | Cxxx-NCR-002452 | NCR | Site 2B Hard Landscaping Greenway Ramp AC20 Testing Requirement |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2017-07-01 | 2017-06-12 10:22 | -19 | 2017-04-28 10:05 | Civil - Base Course | 500 |  | Testing and Commissioning | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Not Defined | Completed |  | Please refer to drawing Cxxx-SWN-L-DDD-CR094_PT002_Z-96170 Note 2 AC20 dense bin 40/60 in accordance with clause 929. To maintain full accordance with Clause 929 as stated in External Works Specification Cxxx-SWN-D-RSP-CR094_PT002-00001 would require cores to be taken on the Greenway Ramp cycle track however with verbal agreement with Cxxx no cores were taken. Note cores for AC20 were taken on the RRVR ramp showing compliance with clause 929 (see attached) also see attached laying temperatures and grading results.
| 03SR - Stations (RfL) | Cxxx-NCR-002453 | NCR | Failure to install pipe sleeving through penetration |  | Crossrail | XRL | PML - Pudding Mill Lane Portal (Central) |  | 2017-05-25 | 2017-05-19 07:50 | -6 | 2017-04-24 10:45 | Mechanical - Public Health Engineering | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | during a final IRF inspection for public health the CRL MEP engineer noticed pipework going through a penetration without a sleeve installed. The location is ground floor slab, escape stairs lobby.
| 03SR - Stations (RfL) | Cxxx-NCR-002454 | NCR | EIP - Firestopping expantion seal around the ventilation duct |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2017-06-30 | 2017-05-16 11:13 | -45 | 2017-05-03 14:45 | Architectural - General | 1500 |  | Planning | Repair | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | Relating to the compound fire stopping works at EIP building void 288/289 shown on the attached drawing and photo, Cxxx subcontractor cannot achieve the additional recommended 20mm expansion seal in addition to minimum requirement of 50mm surround of firestopping compound around the service. This void is through an RC wall (as per attached document), there is a 55-60mm clearance between the RC and ventilation duct on one side, all other sides are free from issues, therefore recommended 20mm expansion seal cannot be achieved at this location. The ventilation duct is fully restricted/fixed at several locations where is passes through the floor above, relocation or moving of duct is not possible due to this restriction. Cxxx and __ (specialised firestoping contractor) propose that the minimum 50mm of firestoping compound around the service is maintain and that the expansion seal is reduced to 5-10 mm.
| 03SR - Stations (RfL) | Cxxx-NCR-002455 | NCR | Non Compliant Retrospective Submission of CE Certification Evidence to MEP MCR's |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2018-09-05 | 2017-09-27 12:31 | -343 | 2017-05-18 09:29 | Materials - Approval | 1000 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Personnel Error - Verbal communication problem | Completed |  | A substantial amount of MEP MCR's were submitted and approved with agreement that CE Marking or declaration of conformance was present without the evidence being provided. Retrospective evidence was applied to the Code 1 MCR's. As the Materials were already approved it was not possible to reapprove the MCR's.
| 03SR - Stations (RfL) | Cxxx-NCR-002456 | NCR | Riveco Pipework - CDFM - Installed without approved MCR |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2017-09-01 | 2017-09-20 07:35 | 19 | 2017-07-11 12:25 | Fire - Fire Systems & General | 2000 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Subcontractor Problems - Insufficient surveillance of subcontractors | Completed |  | __Pipework has been installed without an Approved MCR.
| 03SR - Stations (RfL) | Cxxx-NCR-002457 | NCR | Damage to drainage line SB1.007 |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2022-12-15 | 2018-07-10 13:16 | -1619 | 2017-05-24 13:24 | Civil - Drainage | 2000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | Please refer drawing Cxxx-SWN-D-DDA-CR094_PT002_Z-95222, drainage line SB1.007. During the CCTV inspection of drainage line SB1.007 following Cxxx installation of the HV electrical ducts between the bulk supply unit and MH1 it was identified the drainage line has been damaged. The HV electrical ducts are surrounded in concrete and pass over drainage line SB1.007. A CCTV Inspection conducted prior to the installation of the electrical ducts shows no damage sustained to the drainage line, Cxxx therefore conclude the damage has been caused by others
| 03SR - Stations (RfL) | Cxxx-NCR-002458 | NCR | EIP - Vertical crack in pressurisation room block work wall |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2018-12-19 | 2018-03-07 16:04 | -287 | 2017-05-30 15:51 | Civil - Civil Engineering General | 1000 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Not Defined | Completed |  | 3no. cracks have formed in the block work at level 01, these are shown on attachment 'Revise vertical crack mark up showing 3 locations.pdf'. Crack 1 starts a 3rd of the way up the wall and goes to the ceiling. Crack 2 extends from the 2nd block up from the floor to the ceiling, the crack runs through the centre of the blocks and mortar joints vertically (see attached photos). Crack 3 extends from the lintel of door DA04 up to the ceiling. We believe this occurred due to a contraction or expansion issue during curing not allowed for in the design of the wall.
| 03SR - Stations (RfL) | Cxxx-NCR-002459 | NCR | Installation of Enclosure for Surge Protection without MCR Approval |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2018-09-05 | 2017-09-27 12:46 | -343 | 2017-05-31 07:42 | Electrical - Electrical Engineering General | 1000 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Personnel Error - Other human error | Completed |  | Approval for Surge Protection device took place in time for installation, without approvals for the required enclosure. Approvals for the enclosure are on-going, but the installation was relating to a critical supply for Cxxx cubicles and was required to be installed.
| 03SR - Stations (RfL) | Cxxx-NCR-002460 | NCR | CMR Tow Path AC20 Laying records |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2017-07-20 | 2017-06-16 11:25 | -34 | 2017-06-06 07:11 | Civil - Roadworks Formation | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The __ technician assigned for testing of the asphalt laid for the CMR tow path footpath construction experienced delays getting to site and was thus not able to take laying records for the AC20 material see UXB037290.
| 03SR - Stations (RfL) | Cxxx-NCR-002461 | NCR | EIP - Door DAO6 threshold and fixing issues |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2018-09-28 | 2017-09-05 08:21 | -388 | 2017-06-05 08:24 | Civil - Civil Engineering General | 5000 |  | Incorrect Installation | Repair | 3 (3-6k) | Complete | Management Problem - Inadequate supervision | Completed |  | The PFCs installed either side of DA06 were positioned against the roof slab leaving a gap between the 150mm RC upstand and the bottom of the column, this resulted in the bottom door frame fixing missing the PFCs aligning with the void between the RC upstand and PFC base plate. See attached 'Door DA06 Fixing clash with void'.
| 03SR - Stations (RfL) | Cxxx-NCR-002462 | NCR | EIP - Intervention stair - 50mm gap on handrail returns |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2017-07-28 | 2017-06-16 15:38 | -42 | 2017-06-08 11:41 | Civil - Civil Engineering General | 5000 |  | Design | Repair | 3 (3-6k) | Complete | Design Problem - Conflicting information on drawings | Completed |  | The infill panels on the intervention staircase returns have not been made in a way that allows for the 50mm clearance around handrail.
| 03SR - Stations (RfL) | Cxxx-NCR-002463 | NCR | EIP Architectural - Failure to submit mock-up of external door |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2017-08-18 | 2017-09-22 08:52 | 35 | 2017-06-13 11:19 | Architectural - Doors | 1000 |  | Planning | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Not Defined | Completed |  | As part of the Architectural Specification Cxxx-SWN-A-RSP-CR094_PT002-00011 Rev 2.0 Clause JL20.2104, there is a requirement to produce a mock-up for the external door. This was not submitted as per the requirements.
| 03SR - Stations (RfL) | Cxxx-NCR-002464 | NCR | MGL Asset Revised Tagging |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2017-07-31 | 2017-07-26 08:06 | -5 | 2017-06-19 15:22 | Civil - Civil Engineering General | 2000 |  | Design | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | __ was instructed under Cxxx-PMI-00873 to replace 8 Asset Labels due to a CRL Asset Data Dictionary change (asset class “L43121 Footbridges/Walkways” text adjustment). The asset labels require fixing at the corner positions to meet the CRL Asset label guidance. There was no issue on the West side of the bridge as the labels were installed onto concrete walls where adequate space was available to fix normally. However, on the East side of MGL Bridge the label locations were on narrow RC columns in line with the end of the MGL Bridge steel walkways which have usable faces roughly the width of the labels themselves (please see attached photographic records) meaning that such adjustment was not possible. To fix the labels at the corners would put them within well within the minimum 50mm clearance to the edge of the adjacent concrete face meaning ‘spalling’ of the concrete and damage to the permanent works extremely likely.
| 03SR - Stations (RfL) | Cxxx-NCR-002465 | NCR | GWY Ramp Basecourse Blacktop material laid without MCR approval in place |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2017-07-23 | 2017-07-13 09:37 | -10 | 2017-06-23 11:01 | Civil - Base Course | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | As per NCR2391 details unapproved blacktop material was placed on the Greenway Ramp cycletrack. Due to reasons of weight restrictions, falls to be accommodated and access issues, __’s blacktop supplier have used a more workable material in areas where only hand lay application is possible. This increase in the penetration grade is preferred for hand laying operations as it doesn’t harden as quick therefore a better finish can be achieved.
| 03SR - Stations (RfL) | Cxxx-NCR-002466 | NCR | Luminaire Height In Intervention Stair Lobby - PML - EIP |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2018-09-05 | 2017-09-22 10:31 | -348 | 2017-06-24 14:15 | Electrical - Lighting | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Error by manufacturer in shipping or marking | Completed |  | To avoid headroom clashes with C1 luminaires Cxxx-FCD-002558 was raised. "2 no. C1 luminaires at Surface Level Intervention Staircase changed from ceiling mounted to wall mounted on angle brackets. Due to the height of the soffit in this area the current design means the underside of the luminaires is < 2000mm which could impede access. " This FCD was submitted and accepted without any supporting standards or Lux level checks provided. The Staircase lobby is only 2.1meters and very tight for services, CRL-OBS-13667 was raised questioning heights of smoke detectors CMS and light fittings. Referring to the Observation CRL-OBS-13667 The text states: The services installation - lights, conduit, CMS - in part of the intervention stair impinges the required 2m headroom over the stairs, which is not in accordance with the applicable standards (BS9999 and BS5395). It has since been accepted that the smoke detector and main runs of CMS are above 2 meters, however the luminaires were at 1.85 meters at their lowest point although moved to the sides of the staircase. Moving the luminaires to the sides has since raised questions on the lux levels of the luminaires from these positions.
| 03SR - Stations (RfL) | Cxxx-NCR-002467 | NCR | EIP - Emergency escape stairs 3no gaps |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2017-07-28 | 2017-07-27 14:29 | -1 | 2017-07-04 09:51 | Architectural - Flooring | 2000 |  | Design | Repair | 4 (0.5-3k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | Cxxx have removed temporary plywood protection over the EIP Emergency Escape stairs and have identified that there are 3no gaps over the Surface to Track levels (picture attached).
| 03SR - Stations (RfL) | Cxxx-NCR-002468 | NCR | EIP - Step height from companion ladder to roof hatch landing |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2019-09-27 | 2018-07-09 10:36 | -445 | 2017-07-05 11:58 | Civil - Civil Engineering General | 3000 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | The step between the top of the companion ladder and the roof hatch landing is approximately 100mm greater than the ladder step rise height, this is not in line with BS 5395-:1985 section 7. The top section of handrail fixed to the companion ladder has also been terminated short of what is required on the Cxxx drawing and BS 5395-:1985 section 7.
| 03SR - Stations (RfL) | Cxxx-NCR-002469 | NCR | Collapsed drainage line FDR 10.0 |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2019-12-27 | 2018-09-28 14:02 | -455 | 2017-07-06 13:54 | Civil - Drainage | 5000 |  | Damaged | Rework | 3 (3-6k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | During the CCTV Inspection it was identified the drainage line FDR 10.0 has collapsed
| 03SR - Stations (RfL) | Cxxx-NCR-002470 | NCR | The durasteel panels above the riser doors at ground and first floor levels |  | Crossrail | XRL | PML - Pudding Mill Lane Portal (Central) |  | 2018-08-03 | 2017-10-02 13:59 | -305 | 2017-07-13 12:48 | Civil - Civil Engineering General | 1000 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Misunderstand the definition of the requirement | Completed |  | The durasteel panels above the riser doors at ground and first floor levels has been constructed with double skin panels: It should be 6mm single skin as per detail on drawing Cxxx-SWN-A-DDD-CR094_PT002_Z-80624. Singe skin panels allows simple and efficient removal for future maintenance work to the CMS within the risers.
| 03SR - Stations (RfL) | Cxxx-NCR-002471 | NCR | Gap between the aluminium flashing and the cladding |  | Crossrail | XRL | PML - Pudding Mill Lane Portal (Central) |  | 2017-08-31 | 2017-08-03 14:42 | -28 | 2017-07-13 13:04 | Civil - Civil Engineering General | 3000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | There is a gap between the aluminium flashing and the cladding: It should be 2mm thick PPC aluminium flashing with no gap. As per detail: Cxxx-SWN-A-DDD-CR094_PT002_Z-80549. The flashing should be tight to the PC cladding units and fixed in a manner that no gap results. It was noted that the vertical line of the flashing was “snaking” and divergent.
| 03SR - Stations (RfL) | Cxxx-NCR-002472 | NCR | Louvres on the EIP are not align |  | Crossrail | XRL | PML - Pudding Mill Lane Portal (Central) |  | 2018-09-21 | 2017-09-01 15:06 | -385 | 2017-07-13 13:14 | Civil - Civil Engineering General | 2000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | It was noted that panels on the “Country” and DLR elevations had steps (both horizontal and vertical) at the joint between panes at first floor level. They should be as per detail on drawing: Cxxx-SWN-A-DDD-CR094_PT002_Z-80541
| 03SR - Stations (RfL) | Cxxx-NCR-002473 | NCR | No signage on the beam in sump room |  | Crossrail | XRL | PML - Pudding Mill Lane Portal (Central) |  | 2017-07-28 | 2017-07-27 14:36 | -1 | 2017-07-13 13:51 | Civil - Civil Engineering General | 2000 |  | Incomplete Works | Repair | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | During a site inspection carried out between Cxxx, CRL and Cxxx it was noted that there was not signage on the beam in sump room. The Beam SWL to be clearly and permanently marked / stamped in a visible location on the beam as per RFI 3595.
| 03SR - Stations (RfL) | Cxxx-NCR-002475 | NCR | Covered Ramp / Cut and Cover 3 Roof Slab Joint Mastic |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2017-07-31 | 2017-07-26 08:55 | -5 | 2017-07-14 12:42 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | The leak that was previously encountered between the Covered Ramp and Cut and Cover Phase 3 structures at the roof soffit mastic was successfully sealed by remedial work to the joint sealing at surface level. Due to difficulties in access through the Cxxx possession of the portal, it was agreed verbally to remove the damaged mastic but not to replace it. The decision not to replace the mastic was not covered before hand in an FCD.
| 03SR - Stations (RfL) | Cxxx-NCR-002476 | NCR | Using unapproved P status drawings |  | Crossrail | XRL | PML - Pudding Mill Lane Portal (Central) |  | 2017-09-15 | 2017-09-04 08:57 | -11 | 2017-07-18 09:35 | Fire - Compartmentation | 5000 |  | Design | Repair | 3 (3-6k) | Complete | Design Problem - Use of unapproved drawings | Completed |  | A planned Crossrail surveillance was undertaken on 27th March2017 to look at Fire stopping installation in the EIP Building, during the site visit it was found that the Contractor installing the Fire Stopping was using unapproved P status design drawings.
| 03SR - Stations (RfL) | Cxxx-NCR-002478 | NCR | EIP - 'Fire door keep shut' door sign |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2019-12-20 | 2018-05-09 15:33 | -590 | 2017-07-21 14:39 | Architectural - Signage | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Not Defined | Completed |  | The 'Fire door keep shut' signs are installed on 62no. doors (both faces) in accordance with the approved MCR referenced below (submitted 20/04/2016 and approved code 1 19/05/16). The signage was then installed as per the code 1 MCR, positioned on the doors as advised be Tom Kimbel in accordance with the Approved ironmongery for the railway environment version 5 see attached emails. Following this RFI 3944 response was received 13/07/16: 'Please refer to updated signage schedule. Crossrail should confirm which standards apply, not the design team. As discussed at technical meeting 07.07.16, the team proposed to progress with LU standards where they conflict from BS requirements. Follow LU-S1004 version A7 - Signage for Operational Purposes'
| 03SR - Stations (RfL) | Cxxx-NCR-002480 | NCR | EIP Blockwork Cracks - Reference to NCR 2458 |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2019-03-09 | 2018-03-09 16:38 | -365 | 2018-03-09 11:47 | Architectural - Brickworks/Blockworks | 1000 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | This NCR has been raised to amalgamate the information from NCR 2458. “It was found that the annotated sketch that MS forwarded to Cxxx did not have the correct as-built information and in fact ties were installed at wind post and pier locations as per the works information. Photos have been uploaded showing ties being installed during construction at wind post locations. (See Photographic Records of Bonded Ties.) Further to this new information it has been agreed with CRL during Engineering Meetings to implement Option 1 from Cxxx's recommendation, "1. The cracks could be left as is at the discretion of the Project Manager providing an appropriate flexible fire sealant is applied to seal the crack." The works to seal the cracks has been carried out. See photos appended to attached checksheet.”
| 03SR - Stations (RfL) | Cxxx-NCR-002481 | NCR | Covered Ramp South Upstand Wall Waterbar |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2018-12-21 | 2018-08-31 09:07 | -112 | 2018-04-21 11:29 | Civil - Civil Engineering General | 1000 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Design Problem - Not Defined | Completed |  | A length of rear faced PVC water stop has been installed full height above ground at a vertical construction joint needs to be removed. During the Engineering meeting (05/04/18), it was agreed that this would be resolved by cutting the waterbar just above ground level to divorce it from the active waterbar below ground level (i.e. the active waterbar should have a clear gap from the redundant waterbar). This was agreed as the most practical solution. A Punchworks item has also been raised for this NCR - Cxxx*PWK*00161
| 03SR - Stations (RfL) | Cxxx-NCR-002482 | NCR | EIP - Soakaway - Damaged Yard Gully (Gully A) Connection |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2019-12-20 | 2018-07-10 14:38 | -528 | 2018-05-16 14:43 | Civil - Drainage | 3000 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Insufficient information made available to the worker. | Completed |  | On review of CCTV report Cxxx-MRG-C-MDA-CR094_WS111-50001 2.0 Site Wide Drainage CCTV Records, section of Yard Gully A connection at CH9.5 (adjacent to Yard Gully A) was found to be damaged.
| 03SR - Stations (RfL) | Cxxx-NCR-002483 | NCR | Crack at CRL Retaining Wall 1 |  | Contr | MRG | PML - Pudding Mill Lane Portal (Central) |  | 2018-12-28 | 2018-09-28 14:04 | -91 | 2018-05-23 14:53 | Civil - Civil Engineering General | 6000 |  | Damaged | Repair | 3 (3-6k) | Complete | Design Problem - Other | Completed |  | A full height crack has been identified adjacent a movement joint at CRL1 Retaining Wall. See attached photos and location sketch.
| 03SR - Stations (RfL) | Cxxx-NCR-000011 | NCR | Ply wood face and skirting have dislodged at various locations along the phase 1 Eleanor Street hoarding |  | Contr |  | ELS - Eleanor Street Shaft (Central) |  | 2012-10-10 | 2012-10-15 12:59 | 5 | 2012-10-10 08:48 | Construction Health & Safety - Construction Health & Safety General | 500 |  | Damaged | Repair |  | Complete |  | Completed |  | Ply wood face and skirting have dislodged at various locations along the phase 1 Eleanor Street hoarding. Ply can have a moisture content that is hard to detect including the Elliotis Grade supplied. This when it dries out can cause some minor warping. With the skirting there is a couple of areas where additional screws may be required.
| 03SR - Stations (RfL) | Cxxx-NCR-000034 | NCR | Quality Non Conformance on DBM Base |  | Contr |  | ELS - Eleanor Street Shaft (Central) |  | 2012-12-18 | 2012-12-12 11:03 | -6 | 2012-12-04 | Civil - Base Course | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | 160 square meters of DBM Base has been laid by hand on Friday 30-11-12. After a straight edge examination, it was clear that the surface flatness of the DBM base was not within tolerance. If left in place, this would lead to the thickness of sand exceeding the allowable limit of 50mm set out in the ITP. In addition, the joints between pours are not neat and have a ridge on the surface level. Please refer to the attached photos for examples of the surface irregularities. This non conformance is due to poor workmanship by inexperienced operatives.
| 03SR - Stations (RfL) | Cxxx-NCR-000036 | NCR | Gully Pot 1 damage to pre cast ring |  | Contr |  | ELS - Eleanor Street Shaft (Central) |  | 2012-12-19 | 2012-12-17 15:43 | -2 | 2012-12-05 | Civil - Drainage | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | To get the gully in tight with the kerb line, the operatives saw cut the edge of the gully down to size. In doing so, they have fractured one side of the pre cast ring resulting in a gap in the ring. The gap can be seen in the attached picture.
| 03SR - Stations (RfL) | Cxxx-NCR-000039 | NCR | Mile End Survey Control error |  | Contr |  | ELS - Eleanor Street Shaft (Central) |  | 2013-01-01 | 2013-01-02 11:00 | 1 | 2012-12-18 08:58 | Surveying - Defects and Condition | 500 |  | Planning | Use As-Is |  | Complete |  | Completed |  | There was an error on the survey control points used. The previous issue of control point data included a 30mm error in the horizontal element. However, the levels remain unchanged. As a result the overall position of the coach park is out of survey tolerances.
| 03SR - Stations (RfL) | Cxxx-NCR-000041 | NCR | Incomplete brickwork to gully pots |  | Contr |  | ELS - Eleanor Street Shaft (Central) |  | 2013-01-22 | 2013-01-23 12:49 | 1 | 2013-01-08 | Civil - Drainage | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | Instead of completing the build up of the gully using engineering brick (as per the design on drawing Cxxx-JUL-D-DDD-CR0994_SH006-00404) only 3 sides of the brick chamber have been completed. The concrete for the kerb benching has been used to enclose the chamber.
| 03SR - Stations (RfL) | Cxxx-NCR-000049 | NCR | Mile End Shaft Segments |  | Contr |  | ELS - Eleanor Street Shaft (Central) |  | 2013-03-04 | 2013-03-19 09:00 | 15 | 2013-02-08 | Civil - Civil Engineering General | 500 |  | System Defect | Reject |  | Complete |  | Completed |  | During an audit of __, it was noted that production of the Pre Cast Concrete Segments for the Mile End Park shaft had commenced without an approved ITP or Material Compliance Record. Documentation had been submitted by Cxxx but was rejected at Code 3. Whilst these segments are a proprietary (off the shelf) product, and were being manufactured in accordance with BCS’s own ITP and ISO 9001 processes, this NCR has been raised to cover any potential documentation deficiencies pending clarifications of the requirements. No product has been brought on to site or into the work area and the segments have been quarantined at BCS.
| 03SR - Stations (RfL) | Cxxx-NCR-000057 | NCR | UKAS Lab documentation & sampling |  | Contr |  | ELS - Eleanor Street Shaft (Central) |  | 2013-04-12 | 2013-04-16 10:50 | 4 | 2013-03-08 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | Procedure detailed in EN 14488-1:2005 which specifies the procedure under clause (E) 5.5 for Obtaining a fresh sample from a test panel was not available. This resulted in an attempt to sample concrete from the test panel defective zone.
| 03SR - Stations (RfL) | Cxxx-NCR-000059 | NCR | UKAS sampling & testing |  | Contr |  | ELS - Eleanor Street Shaft (Central) |  | 2013-03-27 | 2013-04-16 10:52 | 20 | 2013-03-13 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | Testing sprayed concrete BS EN 14488-7:2006 - Part 7: Fibre content of fibre undertaken by __ Laboratory who do not have the above referenced BS EN test on their accreditation schedule.
| 03SR - Stations (RfL) | Cxxx-NCR-000060 | NCR | MEP Sports Pitch - 5m high fence post foundations |  | Contr | SKC |  |  | 2013-05-02 | 2013-05-02 14:22 | 0 | 2013-04-18 09:52 | Structural Engineering - Structural Engineering - General | 500 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | MEP Sports Pitch 5m high fence post foundations have been constructed by __ as 350mm x 350mm x 1100mm deep. However, section 7.7 of the Crossrail Specification for the artificial grass pitch (Cxxx-JUL-T1-RSP-CR094_SH006-50001) states that concrete footings of 450mm x 450mm x 850mm deep are required.
| 03SR - Stations (RfL) | Cxxx-NCR-000061 | NCR | Hydrophillic Strip |  | Contr | SKC |  |  | 2013-05-09 | 2013-05-08 12:10 | -1 | 2013-04-25 13:28 | Shafts - Shafts General | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | The hydrophillic strip on one side of one segment was short by approximately 10mm
| 03SR - Stations (RfL) | Cxxx-NCR-000062 | NCR | Small Crack at Rear of Choker Ring Segment |  | Contr | SKC |  |  | 2013-05-24 | 2013-05-21 12:59 | -3 | 2013-05-10 14:26 | Shafts - Shafts General | 500 |  | Damaged | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | The rear of a Choker Ring PCC Segment has suffered minor damage (cracking) during installation.
| 03SR - Stations (RfL) | Cxxx-NCR-000063 | NCR | Boundary wall footing alignment |  | Contr | SKC | ELS - Eleanor Street Shaft (Central) |  | 2013-07-01 | 2013-07-08 13:46 | 7 | 2013-05-08 11:28 | Architectural - Walls | 500 |  | Supervision/Management | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The boundary wall footing, for part of the Eleanor Street Travellers Site south facing wall, has been constructed out of alignment with the centre line of the brick wall. The footing runs for approximately 30m. The distance from the centre line to edge of footing varies linearly from east (600mm as per design) to west (400mm). The footing is adequately wide and deep throughout. The eastern end of the footing could not be installed in line with the wall centre line due to a clash with already installed drainage for utility block M.
| 03SR - Stations (RfL) | Cxxx-NCR-000064 | NCR | Access road gully and manhole covers |  | Contr | 200180 | ELS - Eleanor Street Shaft (Central) |  | 2013-05-28 | 2013-06-20 12:34 | 23 | 2013-05-14 11:47 | Civil - Civil Engineering General | 200 |  | Workmanship | Rework |  | Complete |  | Completed |  | Some gully covers in the access road have not been installed flush with the adjacent kerb, gaps as follows: G6 5-10mm G7 20-25mm G2 10mm G5 Potential clash between cover and kerb Additionally, manhole cover S40 is also approximately 20mm high compared to the projected road surface. Manhole covers have been installed to design levels.
| 03SR - Stations (RfL) | Cxxx-NCR-000066 | NCR | Surface crack at rear of key stone Ring 5 |  | Contr | SKC |  |  | 2013-05-28 | 2013-05-15 15:19 | -13 | 2013-05-14 14:50 | Shafts - Shafts General | 500 |  | Damaged | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | A small surface crack is located at the rear of keystone ring 5.
| 03SR - Stations (RfL) | Cxxx-NCR-000072 | NCR | Surface concrete chipped exposing the aggregate, to the bottom left corner of the top right segment in ring 6 |  | Contr | SKC |  |  | 2013-05-29 | 2013-05-17 09:21 | -12 | 2013-05-15 17:41 | Shafts - Shafts General | 0 |  | Damaged | Use As-Is | 4 (0.5-3k) | Complete | Constructability | Completed |  | The surface concrete was chipped exposing the aggregate, to the bottom left corner of the top right segment in ring 6. The depth of the spalling is less than 10mm. The area of damage extends a small distance from the edge of the segment.
| 03SR - Stations (RfL) | Cxxx-NCR-000073 | NCR | Surface concrete chipped exposing the aggregate, to the top rear edge of segments in ring 12 |  | Contr | SKC | ELS - Eleanor Street Shaft (Central) |  | 2013-09-01 | 2013-07-08 13:52 | -55 | 2013-05-16 13:41 | Shafts - Shafts General | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | The surface concrete was chipped exposing the aggregate, to the top rear edge of the segments in ring 12. The depth of the spalling was 15mm to the back of ordinary segment 11. Spalling was 10mm or less at other identified locations. These being ordinary segment 13, ordinary segment 14 and top right segment.
| 03SR - Stations (RfL) | Cxxx-NCR-000074 | NCR | Damage to surface of concrete segments around grout holes |  | Contr | SKC |  |  | 2013-05-31 | 2013-05-21 09:14 | -10 | 2013-05-17 08:29 | Shafts - Shafts General | 500 |  | Damaged | Use As-Is | 4 (0.5-3k) | Complete | Constructability | Completed |  | The rear surface of two ordinary segments was chipped, around the grout holes.
| 03SR - Stations (RfL) | Cxxx-NCR-000075 | NCR | Insufficent surround to water main |  | Contr | 200180 | ELS - Eleanor Street Shaft (Central) |  | 2013-05-30 | 2013-06-20 12:32 | 21 | 2013-05-16 17:57 | Civil - Sewage/Water services | 1840 |  | Supervision/Management | Rework |  | Complete |  | Completed |  | Whilst undertaking the gas and water diversion works in front of the business units along the Bow Triangle Business Centre it was brought to __ Utilities attention that the incorrect surround was being achieved to the water main. The distance between the trench wall and water main was less than the 150mm required under the __ guidelines. The 270mm distance between the water and gas mains was the maximum which could have been achieved and the minimum to comply with the National Joint Utilities Group (NJUG) guidelines.
| 03SR - Stations (RfL) | Cxxx-NCR-000076 | NCR | Drainage removed for boundary wall footing |  | Contr | 200180 | ELS - Eleanor Street Shaft (Central) |  | 2013-07-10 | 2013-07-15 16:53 | 5 | 2013-05-17 14:07 | Civil - Drainage | 0 |  | Planning | Rework | 4 (0.5-3k) | Complete |  | Completed |  | The van connection point (VCP) for foul drainage in travellers plot M (FM3) was installed prior to the adjacent boundary wall. It was later discovered that the footprint of the boundary wall footing overlapped with the VCP in plan. Consequently, the VCP + 1 length of connecting pipe, had to be removed in order to procede with the footing construction.
| 03SR - Stations (RfL) | Cxxx-NCR-000077 | NCR | Sports pitch catchpit cover |  | Contr | SKC |  |  | 2013-06-04 | 2013-06-05 09:19 | 1 | 2013-05-21 11:34 | Civil - Drainage | 1000 |  | Damaged | Rework |  | Complete |  | Completed |  | The catchpit cover for the Sports Pitch works (location shown in drawing Cxxx-SKC-C-DWG-CR094_WS109-50005) was initially installed correctly. However, the cover sustained significant damage post installation. We propose replacing this with a new catchpit cover.
| 03SR - Stations (RfL) | Cxxx-NCR-000079 | NCR | Process failure in the approval of mortar |  | Contr | SKC | ELS - Eleanor Street Shaft (Central) |  | 2013-06-06 | 2013-05-30 11:05 | -7 | 2013-05-23 14:31 | Materials - Approval | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Lack of procedure | Completed |  | MCR Documentation was submitted to the Cxxx Quality Manager 2 days prior to use of the material on site. This did not allow time for the documentation to be reviewed and approved before use. This morning, mortar to be used on the Travellers Site (Boundary Wall) was delivered despite there not being an approved MCR in place. Work was stopped to prevent use of the unapproved material Upon review of the certification, it was noted that the supplier (__) did not have ISO 9001 certification for the plant supplying the mortar. __ do however hold the following certificates: BES 6001: Framework Standard for the Responsible Procurement of Construction Products Kitemark for BS EN 998-1 and BS EN 998-2: Mortar for Rendering and Plastering & Masonry for Mortar ISO 14001: 2004 Environmental Management System __ have stated that the requirements for the BS EN 998-1 and BS EN 998-2 Kitemark supersede the requirements for ISO 9001. We do not believe that this is the case as the Kitemark is for product quality whereas ISO 9001 is for Management Systems. Due to the lack of ISO 9001 certification, a concession needed to have been approved before delivery of the material.
| 03SR - Stations (RfL) | Cxxx-NCR-000081 | NCR | MEP Coach Park Phase 2 Gully Installation |  | Contr | SKC |  |  | 2013-06-11 | 2013-06-04 17:02 | -7 | 2013-05-28 18:17 | Civil - Drainage | 500 |  | Workmanship | Rework |  | Complete |  | Completed |  | New gully installed for Coach Park Phase 2 does not have a gully cover slab and the brickwork above supporting the gully frame was corbelled on one side, whereas drawings show this to be a vertical face of brickwork. It is proposed that the gully is reworked such that a gully cover slab is installed along with vertical brickwork.
| 03SR - Stations (RfL) | Cxxx-NCR-000082 | NCR | Crack to front face of segment on Ring 5 |  | Contr | SKC |  |  | 2013-11-15 | 2013-11-14 11:00 | -1 | 2013-05-30 17:15 | Shafts - Linings | 500 |  | Damaged | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | A crack has been identifed on the front of an ordinary segment 3 on ring 5 of the shaft at Mile End. The surafce crack does not affect the structural performance of the segment, but does require monitoring.
| 03SR - Stations (RfL) | Cxxx-NCR-000083 | NCR | Drawings discrepancy |  | Contr | SKC | ELS - Eleanor Street Shaft (Central) |  | 2013-10-15 | 2013-09-30 10:31 | -15 | 2013-06-07 09:59 | Civil - Civil Engineering General | 0 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Change to drawings not provided on time | Completed |  | The drawing revisions detailed on the RIR Submissions differed from those on eB A review by CRL found that, out of 116 documents listed on the RIR: 21 were not on eB 24 drawings on eB were earlier revisions than those stated on the RIR 63 drawings were later revisions than those stated on the RIR
| 03SR - Stations (RfL) | Cxxx-NCR-000084 | NCR | West boundary wall footing alignment |  | Contr | SKC | ELS - Eleanor Street Shaft (Central) |  | 2013-11-15 | 2013-11-14 11:43 | -1 | 2013-06-11 09:26 | Architectural - Walls | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | The boundary wall footing, for part of the Travellers Site west facing wall, has been constructed out of alignment with the centre line of the brickwork. The footing runs for approximately 30m. The distance from the centre line to edge of footing, which should be 600mm as per design, varies from 480mm to 725mm. The overall footing width varies from 1165mm to 1225mm and is a minimum of 300mm deep throughout.
| 03SR - Stations (RfL) | Cxxx-NCR-000088 | NCR | Mile End Park Shaft SCL Advance overdig |  | Contr | SKC |  |  | 2013-07-16 | 2013-07-10 12:51 | -6 | 2013-07-02 19:13 | Shafts -Sprayed Concrete | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Supervision - Insufficient supervision | Completed |  | During the excavation for the 4th advance of the SCL section of the Mile End Shaft, sections of the shaft were overdug by approximately 300mm. Approximately one half of the shaft was exposed in preparation for the spraying of the initial primary lining to a 1m depth and the required toe to form the construction joint to the next advance. The ground conditions encountered were stiff/dry London Clay. Although this event does not effect the performance of the design, there was an error in workmanship and survey control.
| 03SR - Stations (RfL) | Cxxx-NCR-000089 | NCR | Finish level of Mile End PCC segments |  | Contr | SKC |  |  | 2014-12-08 | 2014-11-24 08:47 | -14 | 2013-07-03 10:48 | Shafts - Linings | 3000 |  | Supervision/Management | Repair | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | The precast segments installed at Mile End are at a level of 109.300mAOD approximately 200mm lower than shown on Cxxx-JUL-S-DDD-CR094_SH006-00511 detail 4. Essentially, the segments have been driven to the same level as the Jacking beam. The level should have been 109.500mAOD as confirmed on Cxxx-RFI-066 and Drg Cxxx. Cxxx-OVE-C4-DDD-CR001_Z-23751.
| 03SR - Stations (RfL) | Cxxx-NCR-000090 | NCR | Boundary wall pier dimension defect |  | Contr | SKC | ELS - Eleanor Street Shaft (Central) |  | 2013-07-18 | 2013-07-30 14:09 | 12 | 2013-07-04 14:00 | Architectural - Walls | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete |  | Completed |  | One of the boundary wall piers is only one brick wide (approx. 215mm) as shown in the attached image. This is different to all the other piers, which show the brick piers to be 1.5 bricks wide (328mm) as per the boundary wall detail drawing attached. The pier in question is near the southwest corner with location at E=87652.0246, N=37022.261 (see attached setting out drawing).
| 03SR - Stations (RfL) | Cxxx-NCR-000092 | NCR | Amentiy block partition wall clash with drainage pipe |  | Contr | SKC | ELS - Eleanor Street Shaft (Central) |  | 2013-09-16 | 2013-09-27 08:52 | 11 | 2013-07-18 12:43 | Architectural - Partitions | 500 |  | Supervision/Management | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | A partition wall in the Travellers Site amenity blocks K,L & M clashes with a drainage upstand pipe which penetrates the slab. In order to fit the partition walls, the timber panel had to be cut around the pipe (see attached photo).
| 03SR - Stations (RfL) | Cxxx-NCR-000094 | NCR | Earthing mat Earth resistance |  | Contr | SKC |  |  | 2013-08-12 | 2013-08-22 11:25 | 10 | 2013-07-29 17:23 | Systems - Earthing and Bonding | 500 |  | Material | Repair | 4 (0.5-3k) | Complete | External Phenomenon - Not Defined | Completed |  | On Friday the 26th July a residual earth test was carried out to the earthing mat in the pit bottom of the Mile End Shaft. The result of this test was 0.58 Ω (photo attached), this tape was carried out under partially saturated ground conditions. On this basis the earthing tapes and rods were concreted in to provide protection from future works and allow a final test to be carried out so that the structural base could be constructed followed by the mass fill. On Monday the 29th of July, post concrete, a final test was carried out following the concrete protection application to the earthing tapes. The result under dewatered sands came back at 1.85 Ω. This result is outside of the specification JW51.1206.b.
| 03SR - Stations (RfL) | Cxxx-NCR-000095 | NCR | Acceptance of testing that is not carried out by laboratories accredited by UKAS. |  | Crossrail | PDP |  |  | 2013-08-13 | 2013-08-01 14:51 | -12 | 2013-07-30 15:27 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete |  | Completed |  | During surveillance QS360-03 it was witnessed that sampling and testing for determining the flow of fresh concrete and young concrete compressive strength was undertaken by site personnel and not by UKAS accredited laboratory.No objective evidence was made available to demonstrate that the Project Manager’s acceptance was in place for the testing to be undertaken by site personnel
| 03SR - Stations (RfL) | Cxxx-NCR-000096 | NCR | Records of training for BSEN 14488-2:2006 testing |  | Crossrail | PDP |  |  | 2013-08-01 | 2013-08-01 14:44 | 0 | 2013-07-30 15:39 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete |  | Completed |  | Records of training for BSEN 14488-2:2006 testing as witnessed during surveillance QS360-03 were not made avaialble.
| 03SR - Stations (RfL) | Cxxx-NCR-000097 | NCR | Sample cores for compression testing |  | Crossrail | PDP |  |  | 2013-08-13 | 2013-08-01 14:45 | -12 | 2013-07-30 15:52 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete |  | Completed |  | Surveillance QS360-03 witnessed unmarked cores taken as samples for compression testing left to dry out in the sun before transport to testing laboratory
| 03SR - Stations (RfL) | Cxxx-NCR-000098 | NCR | SRG Reports not Uploaded on to eB on a Daily Basis |  | Contr | SKC |  |  | 2013-08-28 | 2013-08-27 13:19 | -1 | 2013-07-31 13:17 | Shafts - Linings | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete |  | Completed |  | Specification KT20 requires SRG Reports to be produced and uploaded on to eB on a daily basis. Whilst the reports were being produced and circulated, they were not being uploaded on to eB
| 03SR - Stations (RfL) | Cxxx-NCR-000100 | NCR | Overspray of adit rebar rebate in P2 layer |  | Contr | SKC |  |  | 2013-08-16 | 2013-08-27 13:26 | 11 | 2013-08-02 18:29 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During the spraying operation of the Primary SCL Layer (P2) in the Mile End shaft, areas that should be left 85 mm deeper for rebar installation as shown on drawing Cxxx-SKC-C4-DWG-CR094-WS109-50001 Rev. 4 (Section B-B and C-C) were over spayed. Because of that __ are not able to maintain the cover to the reinforcement as per drawing Cxxx-MMD-C4-DDD-CR094_SH006-06000 Rev C04. See attached survey for reference.
| 03SR - Stations (RfL) | Cxxx-NCR-000101 | NCR | Overdig at Rounton Road Shaft |  | Contr | SKC | ELS - Eleanor Street Shaft (Central) |  | 2013-08-21 | 2013-08-21 08:56 | 0 | 2013-08-07 18:07 | Shafts -Sprayed Concrete | 500 |  | Planning | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Worker not correctly instructed | Completed |  | A 1.2m advance was excavated at Rounton Road Temporary Shaft. In view of the very competent ground conditions within the Rounton Road shaft, the advance increments of 1m were increased to 1.25m to provide greater efficiency in shaft lining operations. This would negate the requirement for a shorter advance length when forming the base of the shaft before Adit eye construction commenced. Crossrail engineering rejected Cxxx-FCD-000107 detailing the slightly extending the stage extent s. It had been agreed in RESS by CRL, and OTB participants and with OTB senior partner for design so we thought the FCD would be used to formalise the agreement.
| 03SR - Stations (RfL) | Cxxx-NCR-000102 | NCR | SCL Modulus of Elasticity Results |  | Contr | SKC |  |  | 2013-11-15 | 2013-11-14 13:36 | -1 | 2013-08-14 19:18 | Shafts -Sprayed Concrete | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | To date have obtained results for the Modulus of Elasticity of below 31.9Gpa. These results were produced from tests which have been carried out by __ have been completed in accordance with BS 1881-121 1983 Testing concrete Part 121. Please reference to Cxxx-RFI-00087 – Mile End SCL Testing – Modulus of Elasticity Results for more information.
| 03SR - Stations (RfL) | Cxxx-NCR-000103 | NCR | Breakdown of Oruga Equipment |  | Contr | SKC |  |  | 2013-11-15 | 2013-09-23 13:29 | -53 | 2013-08-15 18:57 | Shafts -Sprayed Concrete | 500 |  | Equipment Breakdown | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | On 14.8.13, were excavating for Rounton Road Shaft Adit Eye opening and Mile End Adit IA1. The project operates 2 Orugas, 3 Suprema Pumps and 1 set of hand spraying equipment. During this excavation a malfunction occurred in the remote of the Oruga at Rounton Road. As per the contingency plan the remote from the second Oruga was used to complete the spray ensuring the works were kept in a safe state. The sealing layer was completed and the remote was returned to Mile End to complete the spraying works which continued into the Night Shift. As of 8am Friday Morning the repaired remote for the 2nd Oruga will be returned to site and 2 fully operational robotic spraying sets will be available with the option of hand spraying in the exceptional situation where both Orugas were to fail (there would still be a third Suprema available to facilitate these works.) Due to Rounton Road site constraints. are using backup equipment between the 2 sites (10mins travel time).
| 03SR - Stations (RfL) | Cxxx-NCR-000105 | NCR | __ delayed audit on Callysteel |  | Contr | SKC | ELS - Eleanor Street Shaft (Central) |  | 2013-09-16 | 2013-09-12 11:54 | -4 | 2013-08-16 13:49 | Civil - Civil Engineering General | 500 |  | Material | Rework | 4 (0.5-3k) | Complete |  | Completed |  | Fabrication of the solar panels frames by __ Ltd have proceed prior to __ audit approval due to date of audit being rescheduled to earliest auditor availability. __ (__ Ltd) has confirmed that the weld testing required has been completed by __ on 07/08/13 and that all test pieces where acceptable (please see attached email).
| 03SR - Stations (RfL) | Cxxx-NCR-000106 | NCR | Re-levelling of Inspection chamber covers throughout Eleanor Street new travellers Site |  | Contr | SKC | ELS - Eleanor Street Shaft (Central) |  | 2013-12-01 | 2013-11-28 11:04 | -3 | 2013-08-16 15:01 | Civil - Drainage | 1000 |  | Design | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | After the finished floor levels inside the travellers plots were set out for the surface finishing works, it was discovered that these levels did not take account the amenity block doorways. These finished floor levels then needed to be changed, to ensure that the drainage of the surface water in the plots was effective. The covers were installed at an early stage before the finishing groundworks were started for H&S reasons, to reduce the number of open chambers through the site. All manhole and inspection chamber covers set to the orginal levels will now need to be reset to the new levels, to maintain this drainage.
| 03SR - Stations (RfL) | Cxxx-NCR-000107 | NCR | Defective fence posts to be replaced |  | Contr | SKC | ELS - Eleanor Street Shaft (Central) |  | 2013-09-27 | 2013-09-27 09:17 | 0 | 2013-08-16 16:37 | Architectural - Landscape Architectural | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Improper storage of material | Completed |  | 10no. fence posts and 16no. gravelboards have been installed along the L/K and K/M plot boundaries. The majority are cracked and/or chipped.
| 03SR - Stations (RfL) | Cxxx-NCR-000108 | NCR | Boundary wall footing extension adjacent to Security Hut |  | Contr | SKC | ELS - Eleanor Street Shaft (Central) |  | 2013-09-02 | 2013-10-09 15:35 | 37 | 2013-08-19 11:47 | Architectural - Walls | 500 |  | Design | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Worker not correctly instructed | Completed |  | A short section of the boundary wall footing adjacent to the new Security Hut was constructed to the original design position, not the new position shown on Cxxx--RFI-044. The wall/gate across the new Access Road has been repositioned to avoid clashing with the road gullies.
| 03SR - Stations (RfL) | Cxxx-NCR-000109 | NCR | Non Compliant Product |  | Contr | SKC | ELS - Eleanor Street Shaft (Central) |  | 2013-09-04 | 2013-09-09 11:11 | 5 | 2013-08-21 12:57 | Structural Engineering - Welding | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete |  | Completed |  | In addition to NCR Ref: Cxxx-NCR-000105, this NCR has been raised due to the Solar Panel Support Frames being a non compliant product. This is due to the fabrication commencing prior to all required procedures and approvals being in place.
| 03SR - Stations (RfL) | Cxxx-NCR-000110 | NCR | Testing not carried out at a UKAS accredited laboratory |  | Contr | SKC |  |  | 2013-09-18 | 2013-09-12 11:26 | -6 | 2013-08-21 13:45 | Shafts - Linings | 500 |  | Material | Rework | 4 (0.5-3k) | Complete |  | Completed |  | Whilst the Compressive Strength Tests for the PCC Segments were carried out at a UKAS accredited laboratory, the scope did not include Tensile or Flexural Testing. The results for these tests were not therefore provided by a UKAS accredited laboratory
| 03SR - Stations (RfL) | Cxxx-NCR-000111 | NCR | Underspray of sealing layer to face of Adit IA1 |  | Contr | SKC |  |  | 2013-09-04 | 2013-09-09 11:14 | 5 | 2013-08-21 16:53 | Shafts -Sprayed Concrete | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete |  | Completed |  | A sealing layer of 75mm is required to be sprayed to the face of each advance during construction of Adit IA1 at the Mile End site. During spraying a small section to the top right of the face was not sealed to the full thickness of 75mm. It was observed during the inspection of the works that a section of the sealing layer was undersprayed by approximately 30mm.
| 03SR - Stations (RfL) | Cxxx-NCR-000112 | NCR | Door and window issues to Plots K, L & M |  | Contr | SKC | ELS - Eleanor Street Shaft (Central) |  | 2013-09-26 | 2013-10-02 13:59 | 6 | 2013-08-22 16:43 | Architectural - Doors | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The following issues have been identified following the installation of the windows and doors to plots K, L and M - Doors currently have a 28mm reval from the brickface, this should be 65mm - Windows currently have a 28mm reval from the brickface, this should be 60mm - Door frame straps have been fixed to the brickwork, should be to the SIPs - Doors have incorrect threshold fitted creating a 45mm step, this should be <15mm - No lintel, with brickwork, has been installed above the doors Drawing numbers as follows, all construction issue. To be submitted to CRL in latest Travellers Site pack: - Cxxx-SKC-A-DWG-CR094_WS110-50066 to 50071 Proposed Door Details Sheets 1 to 6 - Cxxx-SKC-A-DWG-CR094_WS110-50072 Amenity Block Window & Rooflight Details
| 03SR - Stations (RfL) | Cxxx-NCR-000113 | NCR | Density Testing for Foam Concrete - Eleanor Street Temporary Shaft Base Pour |  | Contr | SKC | ELS - Eleanor Street Shaft (Central) |  | 2013-09-05 | 2013-09-09 11:17 | 4 | 2013-08-22 17:44 | Shafts - Shafts General | 500 |  | Material | Rework | 4 (0.5-3k) | Complete |  | Completed |  | A non conformance was raised during density testing for the foam concrete pour for the base of the Eleanor Street Temporary Shaft. The pour was for the first meter of the base on the 22.08.13. Plastic Density tests were carried out for each load of concrete delivered to site by our registered test house __. The tests were to be carried out in accordance with BS EN 12350-6:2009. While witnessing the tests it was observed by that the testing method was being incorrectly conducted by __. The concrete was being placed in the weighing container in 3 layers with 3 compression tamps with a steel rod at each layer. BS EN 12350-6:2009 states that for self compacting concrete the weighing container should be filled in one layer with no compression tamping. The observation was made after a density out of tolerance was recorded for load 2 in the pour. The recorded plastic density for this load was recorded as 1214 kg/m3. This exceeds the tolerance stated in the ITP Cxxx-SKC-C-ITP-CR094-50012 of; 1100kg/m3 +/- 100kg/m3. The load had already been pumped into the shaft by the time the result was stated by __.
| 03SR - Stations (RfL) | Cxxx-NCR-000114 | NCR | Rebound Test |  | Contr | SKC |  |  | 2013-09-06 | 2013-09-23 09:20 | 17 | 2013-08-23 18:07 | Shafts -Sprayed Concrete | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | planned to calculate amounts of SCL rebound using the Amberg system. Due to deviation of the results, this is detrimental to their validity.
| 03SR - Stations (RfL) | Cxxx-NCR-000115 | NCR | Damaged fence post |  | Contr | SKC | ELS - Eleanor Street Shaft (Central) |  | 2013-11-10 | 2013-11-08 10:00 | -2 | 2013-08-28 11:39 | Architectural - Landscape Architectural | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | 1no. concrete post and 1no. timber panel have been broken by an excavator slewing around and striking the newly installed fence between plots L and M.
| 03SR - Stations (RfL) | Cxxx-NCR-000116 | NCR | Damaged door glazing |  | Contr | SKC | ELS - Eleanor Street Shaft (Central) |  | 2013-09-27 | 2013-10-09 15:41 | 12 | 2013-08-28 11:39 | Architectural - Glazing | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Reinforcement mesh for plot L yard slab was being cut in-situ - the sparks generated have damaged the glazing to the amenity block door
| 03SR - Stations (RfL) | Cxxx-NCR-000117 | NCR | Adit IA1 profile |  | Contr | SKC |  |  | 2013-09-13 | 2013-09-09 16:09 | -4 | 2013-08-30 09:36 | Shafts -Sprayed Concrete | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The enlargement of Adit IA1 was to be constructed in accordance with the revised Adit enlargement profile (Drawing Cxxx-SKC-C-DWG-CR094_WS109-50023 and Cxxx-FCD-000105). Although the enlargement was completed to the revised alignment, the cross sectional profile dimension of the primary lining is as per the original Cxxx design( Drawing Cxxx-MMD-C4-DDB-CR094_SH006-02001.
| 03SR - Stations (RfL) | Cxxx-NCR-000118 | NCR | Fencing drawing not available on eB |  | Contr | SKC | ELS - Eleanor Street Shaft (Central) |  | 2013-09-30 | 2013-10-02 10:16 | 2 | 2013-09-02 15:26 | Architectural - General | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Design Problem - Change to drawings not provided on time | Completed |  | During a Surveillance Visit at Eleanor Street, it was found that drawing ref: Cxxx-SKC-C-DWG-CR094_WS110-50085 was not available on eB
| 03SR - Stations (RfL) | Cxxx-NCR-000119 | NCR | Material Supplied by unapproved supplier |  | Contr | SKC | ELS - Eleanor Street Shaft (Central) |  | 2013-09-17 | 2013-09-09 11:19 | -8 | 2013-09-03 06:18 | Civil - Fill | 500 |  | Material | Rework | 4 (0.5-3k) | Complete |  | Completed |  | A delivery of Type 1 was made at Eleanor Street by a non Crossrail approved Supplier. The material had been ordered by Blu3, a subcontractor of __ Utilities, and was made without the knowledge or approval with Cxxx.
| 03SR - Stations (RfL) | Cxxx-NCR-000120 | NCR | Measuring of Flexural Strengths for Fibre Reinforced Beam Specimens |  | Contr | SKC |  |  | 2013-09-26 | 2013-09-12 11:20 | -14 | 2013-09-05 21:48 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete |  | Completed |  | carried out flexural beam specimen tests on the Shotcrete mix at Mile End. The required standard to which this test should be performed as per KT20 is BS EN 14651:2005. The test were in fact undertaken utilising BS 14488-3:2006 which although gave similar results to previous tests compliant with KT20, it is not the required specification.
| 03SR - Stations (RfL) | Cxxx-NCR-000121 | NCR | Eleanor St Temporary Works - Drawing Error |  | Contr | SKC | ELS - Eleanor Street Shaft (Central) |  | 2013-09-25 | 2013-10-08 16:57 | 13 | 2013-09-11 09:12 | Civil - Civil Engineering General | 500 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Conflicting information on drawings | Completed |  | It was identified on temporary works drawing reference Cxxx-SKC-C-DWG-CR094_WS110-50054 Rev03 that there was a typing error made on width dimension of section SECTION VA1 - VA6/IA1-IA2. The dimension shown as 6140mm should read 5410mm. Note this drawing is for temporary works excavation support and that all permanent works are constructed to dimensions/requirements of Cxxx IFC drawings.
| 03SR - Stations (RfL) | Cxxx-NCR-000122 | NCR | Incorrect slump used in Plot M concrete pavement |  | Contr | SKC | ELS - Eleanor Street Shaft (Central) |  | 2013-09-27 | 2013-10-02 10:09 | 5 | 2013-09-13 12:51 | Civil - Concrete Pavement | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The correct mix for the travellers site concrete pavements is PAV2 Slump S3, as per ITP. For Plot M, 's subcontractor ordered and poured PAV2 Slump S2 without 's knowledge. The concrete hardened more quickly than expected by the concrete finishers who were also experiencing difficulties with the logisitcs of finishing the relatively large area. Consequently, the concrete went hard over about half of the slab area before it could be finished satisfactorily. Once it was determined that the unfinished concrete within the shutter was beyond its workability level, the pour was cancelled to minimise concrete wastage.
| 03SR - Stations (RfL) | Cxxx-NCR-000123 | NCR | Eleanor Street Adits Early Age Strength Results |  | Contr | SKC | ELS - Eleanor Street Shaft (Central) |  | 2014-01-15 | 2013-12-05 09:09 | -41 | 2013-09-13 15:54 | Shafts -Sprayed Concrete | 0 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | External Phenomenon - Other | Completed |  | During spraying of the 3rd advance of Adit VA6 at Eleanor Street, conducted Early age strength testing in accordance with BS EN 14488-2 and KT20-06. At 1 and 3 hours the compressive strength of the Shotcrete was below the modified J2 curve. continued to monitor the strength at 1 hour increments until the strength rose above the modified J2 curve.(Please see attached graph).
| 03SR - Stations (RfL) | Cxxx-NCR-000124 | NCR | Kerb backing concrete |  | Contr | SKC | ELS - Eleanor Street Shaft (Central) |  | 2013-10-03 | 2013-10-14 11:18 | 11 | 2013-09-19 15:35 | Civil - Civil Engineering General | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Some of the concrete backing to edging kerbs installed in Traveller plots K,L,M & O is defective, the concrete was delivered with insufficant mosture content to act as a catilist to make the concrete work correctly. The concrete is now crubling off the kerbs and is nolong providing support to the edging kerb.
| 03SR - Stations (RfL) | Cxxx-NCR-000125 | NCR | Cracked paving slab in traveller plot M area |  | Contr | SKC | ELS - Eleanor Street Shaft (Central) |  | 2013-11-15 | 2013-11-21 11:27 | 6 | 2013-09-19 15:42 | Civil - Roadworks Formation | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | A paving slab in Traveller plot M has been damaged and cracked
| 03SR - Stations (RfL) | Cxxx-NCR-000126 | NCR | Damage to ceiling of plot K |  | Contr | SKC | ELS - Eleanor Street Shaft (Central) |  | 2013-10-03 | 2013-10-02 13:43 | -1 | 2013-09-19 17:27 | Structural Engineering - Finishes | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Damage has been coursed to the ceiling of plot K. It appears that an access tower has been carelessly moved and has contacted the ceiling powerfully.
| 03SR - Stations (RfL) | Cxxx-NCR-000127 | NCR | Overdosing of accelerator with SCL pump |  | Contr | SKC | ELS - Eleanor Street Shaft (Central) |  | 2013-09-30 | 2013-09-23 13:01 | -7 | 2013-09-16 16:00 | Shafts -Sprayed Concrete | 500 |  | Equipment Breakdown | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Error by manufacturer in shipping or marking | Completed |  | There was a calibration problem with the suprema pump used for SCL works at Rounton Road during advance 5 of Adit VA6. During Nightshift works, performed a test and found that the suprema was pumping accelorator over the indicated value.(Approximately 9% immediately stopped them spraying after the face was fully sealed and did a calibration test.
| 03SR - Stations (RfL) | Cxxx-NCR-000128 | NCR | Latest drawings not available on eB |  | Contr | SKC | ELS - Eleanor Street Shaft (Central) |  | 2013-10-07 | 2013-09-30 13:28 | -7 | 2013-09-23 11:14 | Architectural - Flooring | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Change to drawings not provided on time | Completed |  | The latest revisions of the following drawings were not available on eB: Cxxx-SKC-A-DWG-CR094_WS110-50023 Rev 4 (Rev 3 on eB) Cxxx-SKC-A-DWG-CR094_WS110-50024 Rev 3 (Rev 2 on eB) Cxxx-SKC-A-DWG-CR094_WS110-50025 Rev 5 (Rev 3 on eB)
| 03SR - Stations (RfL) | Cxxx-NCR-000129 | NCR | Overspray in crown of Eleanor Street Adit VA6 |  | Contr | SKC | ELS - Eleanor Street Shaft (Central) |  | 2015-05-04 | 2015-04-24 11:12 | -10 | 2013-09-18 15:52 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | The crown of Adit VA6 has been oversprayed at Advance 1,2 and 3 by 30mm to 80mm. Please see attached Amburg profiles. The error displayed on the Amburg plots is relative to drawing "Cxxx-SKC-C-DWG-CR094_WS110-50054 - the Eleanor Street Shaft Temporary works design shaft and adit primary lining setting out sheet 1 of 2" which has a tolerance 100mm bigger than the design profile.
| 03SR - Stations (RfL) | Cxxx-NCR-000130 | NCR | Site Rebound test for Eleanor Street |  | Contr | SKC | ELS - Eleanor Street Shaft (Central) |  | 2013-10-31 | 2013-10-22 07:59 | -9 | 2013-09-18 16:02 | Shafts -Sprayed Concrete | 500 |  | Planning | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | A SCL rebound estimation test is required to be completed once every 2 months as per KT20-06. This test was required at Eleanor Street last week but it was missed.
| 03SR - Stations (RfL) | Cxxx-NCR-000131 | NCR | Underspray of SCL to face of Eleanor Street Adit VA6 |  | Contr | SKC | ELS - Eleanor Street Shaft (Central) |  | 2013-10-02 | 2013-09-23 12:03 | -9 | 2013-09-18 17:01 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | The face of Adit VA6 was under sprayed in certain sections on Friday 13th September. drilled the face upon request of the SCL inspector on Tuesday 17th and a section of the face was found to be 75mm - 200mm thick. KT20 defines a required safe stoppage SCL thickness of minimum 200mm for faces left over 72hours.
| 03SR - Stations (RfL) | Cxxx-NCR-000132 | NCR | Concrete Drying Shrinkage results |  | Contr | SKC | ELS - Eleanor Street Shaft (Central) |  | 2013-10-02 | 2013-10-09 14:55 | 7 | 2013-09-18 17:35 | Shafts -Sprayed Concrete | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The recent set of Mile End SCL production results for test panels sprayed 8th July 2013, tested by __ Centre through __. The initial reading was recorded as completed at 10 days. ASTM C157 and ASTM C341 and both state initial readings are required at approx. 24hrs with further readings taken at intervals. In addition, KT20-06 states that production testing requires concrete drying shrinkage tests to be completed in accordance with ASTM C341. However, the test completed, was in accordance with the test requirements for the trials which utilises ASTM C157.
| 03SR - Stations (RfL) | Cxxx-NCR-000133 | NCR | Poor quality bathroom tiling in traveller plots K & N |  | Contr | SKC | ELS - Eleanor Street Shaft (Central) |  | 2013-10-08 | 2013-10-02 13:49 | -6 | 2013-09-24 09:39 | Architectural - Finishes | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | In traveller plots K & N the bathroom tiling has been installed unevenly and the tiled corner joints do not line up with the return wall
| 03SR - Stations (RfL) | Cxxx-NCR-000134 | NCR | Plot A kitchen worktop damage |  | Contr | SKC | ELS - Eleanor Street Shaft (Central) |  | 2013-10-08 | 2013-10-14 10:53 | 6 | 2013-09-24 11:53 | Architectural - Finishes | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Plot A kitchen worktop has been damaged by adjacent traders
| 03SR - Stations (RfL) | Cxxx-NCR-000135 | NCR | Plot K cracked brickwork above the toilet window |  | Contr | SKC | ELS - Eleanor Street Shaft (Central) |  | 2013-11-11 | 2013-11-12 10:44 | 1 | 2013-09-24 12:05 | Architectural - Masonary | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The brickwork above the toilet window at plot K has cracked due to damage coursed during weather proofing
| 03SR - Stations (RfL) | Cxxx-NCR-000136 | NCR | Broken edging kerb around Plot M parking bay |  | Contr | SKC | ELS - Eleanor Street Shaft (Central) |  | 2013-10-14 | 2013-10-14 14:26 | 0 | 2013-09-30 10:52 | Civil - Kerbs | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | An edging kerb around Plot M parking bay has been damaged post installation.
| 03SR - Stations (RfL) | Cxxx-NCR-000137 | NCR | Unsatisfactory tile finishes |  | Contr | SKC | ELS - Eleanor Street Shaft (Central) |  | 2013-10-15 | 2013-10-14 15:59 | -1 | 2013-10-01 09:19 | Architectural - Finishes | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Poor installation of tiles in general across the following locations: Bathroom tiles in Amenity blocks K, L and O Entrance lobby floor tiles in Amenity blocks K and L Utility room floor tiles in Amenity blocks - K and L Edgings around the kitchen splashback tiles do not meet in Amenity blocks K, L, M, O, A
| 03SR - Stations (RfL) | Cxxx-NCR-000138 | NCR | Incorrect Thresholds Installed |  | Contr | SKC | ELS - Eleanor Street Shaft (Central) |  | 2013-10-15 | 2013-10-16 10:26 | 1 | 2013-10-01 08:09 | Architectural - Finishes | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Incorrect thresholds installed on the kitchen double doors in Amenity Plots J, K, L, M and N.
| 03SR - Stations (RfL) | Cxxx-NCR-000139 | NCR | Wrong location of hob extractor fan cable |  | Contr | SKC | ELS - Eleanor Street Shaft (Central) |  | 2013-10-15 | 2013-10-16 10:27 | 1 | 2013-10-01 09:20 | Architectural - Walls | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The cable for the hob extractor fan has been installed through the drylining in the wrong location resulting in it not lining up with the unit.
| 03SR - Stations (RfL) | Cxxx-NCR-000140 | NCR | Premature Drylining Installation |  | Contr | SKC | ELS - Eleanor Street Shaft (Central) |  | 2013-10-15 | 2013-10-14 16:01 | -1 | 2013-10-01 09:24 | Architectural - Walls | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Drylining has been installed prematurely below the kitchen bay window before the bay window timbers and metal brackets were installed.
| 03SR - Stations (RfL) | Cxxx-NCR-000141 | NCR | Electric socket / gas pipe design location clash |  | Contr | SKC | ELS - Eleanor Street Shaft (Central) |  | 2013-11-11 | 2013-11-12 10:20 | 1 | 2013-10-01 09:25 | Architectural - Finishes | 500 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | The designed location of an electrical socket and gas pipe in the kitchen clash.
| 03SR - Stations (RfL) | Cxxx-NCR-000142 | NCR | Bricks installed under external toilet door threshold |  | Contr | SKC | ELS - Eleanor Street Shaft (Central) |  | 2013-10-15 | 2013-10-14 16:02 | -1 | 2013-10-01 09:27 | Architectural - Brickworks/Blockworks | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Bricks have been installed under the threshold of the external toilet door where the paving slabs are to be installed.
| 03SR - Stations (RfL) | Cxxx-NCR-000143 | NCR | Removal of dry lining to install toilet water feed |  | Contr | SKC | ELS - Eleanor Street Shaft (Central) |  | 2013-11-11 | 2013-10-24 12:11 | -18 | 2013-10-10 15:24 | Architectural - Sanitary Fittings | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Dry lining in Plot M utility room had been installed before the toilet water feed. Drylining had to be removed and water feed installed.
| 03SR - Stations (RfL) | Cxxx-NCR-000144 | NCR | Repositioning external toilet water feed |  | Contr | SKC | ELS - Eleanor Street Shaft (Central) |  | 2013-11-11 | 2013-11-08 14:18 | -3 | 2013-10-10 15:35 | Architectural - Sanitary Fittings | 3000 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | External toilet water feed installed in the wrong position. This has to be taken out and re-positioned.
| 03SR - Stations (RfL) | Cxxx-NCR-000145 | NCR | Premature drylining - Water feed requires installation |  | Contr | SKC | ELS - Eleanor Street Shaft (Central) |  | 2013-11-11 | 2013-11-08 14:39 | -3 | 2013-10-10 15:38 | Architectural - Sanitary Fittings | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Drylining has been installed before the external toilet water feed
| 03SR - Stations (RfL) | Cxxx-NCR-000146 | NCR | Exposed reinforcement around adit IA2 eye |  | Contr | SKC |  |  | 2013-10-18 | 2013-10-16 13:45 | -2 | 2013-10-04 12:33 | Shafts - Linings | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During construction of IA2, the wash out from spraying built up under the eye opening, forming areas where the shaft lining is tight. While preparing for the spraying of the regulating layer, remedial works were carried out to remove the hardened wash out from the shaft permanent primary lining. During these attempts, some rebar below the invert of the adit eye became exposed.
| 03SR - Stations (RfL) | Cxxx-NCR-000147 | NCR | Underspray of ESS Adit VA6 advance 6 |  | Contr | SKC | ELS - Eleanor Street Shaft (Central) |  | 2013-10-18 | 2013-10-10 12:11 | -8 | 2013-10-04 16:10 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | During excavation of advance 7 of ESS adit VA6 it was discovered during further exploratory drilling to that undertaken on dayshift that areas of advance 6 had less than the design thickness of SCL applied. The works were immediately suspended and a safe stop instructed to seal the face and profile. The deficient areas of Advance 6 were then sprayed to attain the full design thickness. Please find attached as built survey of proof drilling have completed since the occurrence.
| 03SR - Stations (RfL) | Cxxx-NCR-000148 | NCR | Damaged manhole gully near planter wall |  | Contr | SKC | ELS - Eleanor Street Shaft (Central) |  | 2013-11-21 | 2013-11-18 11:55 | -3 | 2013-10-10 15:41 | Civil - Drainage | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Improper preservation of material after installation | Completed |  | Manhole gully lid damaged by 5T excavator whilst excavating the planter wall footing
| 03SR - Stations (RfL) | Cxxx-NCR-000149 | NCR | External brickwork - cracked brick |  | Contr | SKC | ELS - Eleanor Street Shaft (Central) |  | 2013-11-14 | 2013-11-13 17:05 | -1 | 2013-10-31 08:20 | Architectural - Brickworks/Blockworks | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | Cracked brick on the external brickwork of Plot K (see attached picture).
| 03SR - Stations (RfL) | Cxxx-NCR-000150 | NCR | Plot L - Additional hole drilled in wall |  | Contr | SKC | ELS - Eleanor Street Shaft (Central) |  | 2013-11-14 | 2013-11-13 17:01 | -1 | 2013-10-31 08:23 | Architectural - Walls | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Supervision - Other | Completed |  | Additional hole has been drilled next to the smoke alarm in Plot L
| 03SR - Stations (RfL) | Cxxx-NCR-000151 | NCR | Damage to plot O gully cover |  | Contr | SKC | ELS - Eleanor Street Shaft (Central) |  | 2013-11-14 | 2013-11-13 16:58 | -1 | 2013-10-31 08:27 | Civil - Drainage | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Plot O gully cover has been cracked and damaged (see attached picture).
| 03SR - Stations (RfL) | Cxxx-NCR-000152 | NCR | Plot M - Paint on glulam beam |  | Contr | SKC | ELS - Eleanor Street Shaft (Central) |  | 2013-11-14 | 2013-11-12 10:12 | -2 | 2013-10-31 08:30 | Architectural - Finishes | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Supervision - Other | Completed |  | White paint from the walls has gone onto the glulam beam (see attached picture).
| 03SR - Stations (RfL) | Cxxx-NCR-000153 | NCR | Insufficent blow out of drilled holes in security hut foundation |  | Contr | SKC | ELS - Eleanor Street Shaft (Central) |  | 2013-10-29 | 2013-10-31 09:16 | 2 | 2013-10-15 14:19 | Civil - Structural Engineering | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The new security hut for the Bow Business Triangle is partially supported by a steel frame. This frame is connected to the concrete foundation via a base plate fixed with a threaded bar and nut connection. The threaded bar is anchored to the foundation with __ Hit anchor resin. The process of drilling and subsequently blowing out the holes for this connection was not observed by a engineer. It was later brought to the attention of the engineers that the holes were not blown out using either a mechanical pump or compressed air as per __ instructions but rather by the operative blowing down the hole. Consequently, the full strength of the anchor resin can not be guaranteed.
| 03SR - Stations (RfL) | Cxxx-NCR-000154 | NCR | Incorrect kerb line and level in ESS2 |  | Contr | SKC | ELS - Eleanor Street Shaft (Central) |  | 2013-10-28 | 2013-10-24 08:30 | -4 | 2013-10-14 20:39 | Civil - Kerbs | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Back of footpath edging kerbs and flat road edge kerbs were installed to incorrect line and level outside plot O in Travelers Site ESS2.
| 03SR - Stations (RfL) | Cxxx-NCR-000155 | NCR | ESS Adit Advance 10 |  | Contr | SKC | ELS - Eleanor Street Shaft (Central) |  | 2013-11-04 | 2013-11-05 15:28 | 1 | 2013-10-21 09:10 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Design | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Advance 10 of ESS Adit VE1 was sealed with a minimum 150mm of SCL on Friday Nightshift. The profile was then sprayed to full thickness on the following Monday morning. Although this complied with the safe stop requirements detailed in the RESS, it has been challenged by the SRG.
| 03SR - Stations (RfL) | Cxxx-NCR-000156 | NCR | OTB Drawings for ESS VE1 Adit Transition |  | Contr | SKC | ELS - Eleanor Street Shaft (Central) |  | 2013-11-04 | 2013-11-04 12:50 | 0 | 2013-10-21 14:46 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Subcontractor Problems - Other | Completed |  | The OTB revised sequence drawing for Eleanor Street Adit VE1 Transition has not been uploaded onto eB. Although the drawing has been agreed and drafted, the construction issue drawing is not on eB.
| 03SR - Stations (RfL) | Cxxx-NCR-000157 | NCR | Use of 7.5% accelerator |  | Contr | SKC | ELS - Eleanor Street Shaft (Central) |  | 2014-02-23 | 2013-12-10 13:38 | -75 | 2013-10-21 15:57 | Tunnelling - Linings - Sprayed Concrete | 0 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Please refer to Cxxx-NCR-000123 and Cxxx-RFI-000087 Throughout SCL works at Eleanor Street early age compressive strength testing has been undertaken on each advance in accordance with BS EN 14488-2:2006. Although compressive strength core results far exceed the specification requirements, the Modified J2 curve defined in KT20:01 has not been met on several occasions using 6% accelerator. Therefore, to ensure the safety of the working environment and early ground support the accelerator dosage has been increased to 7.5% to comply with the J2 curve profile. The increased dosage is only to be reduced to 6% when early age strength results confirm that the required modified J2 curve is achieved The locations in the work where 7.5% accelerator dosing has been used are recorded on the ITP approved check sheets.
| 03SR - Stations (RfL) | Cxxx-NCR-000158 | NCR | Cxxx Monitoring trigger alerts |  | Contr | SKC |  |  | 2013-11-18 | 2013-11-15 14:53 | -3 | 2013-10-21 18:25 | Surveying - Surveying General | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Supervision - Other | Completed |  | Datum Monitoring (the company hosting the Cxxx monitoring data presentation website) have been requested to include a means of identification of prisms which are in breach of triggers (amber/red/black).
| 03SR - Stations (RfL) | Cxxx-NCR-000159 | NCR | MCR not approved for asphalt construction |  | Contr | SKC | ELS - Eleanor Street Shaft (Central) |  | 2013-11-08 | 2013-11-11 13:09 | 3 | 2013-10-22 13:18 | Civil - Base Course | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | s subcontractor did not order asphalt material from their pre-approved supplier and consequently unapproved material was delivered to site . Rather than wasting the material, allowed the material to be laid after the ISO:9001 and UKAS accreditation for the material was verified. The reason that the approved MCR was not in place was that the manufacturer would not provide the CE Mark Certificate until the material had been delivered to site.
| 03SR - Stations (RfL) | Cxxx-NCR-000160 | NCR | Plot N edging kerbs |  | Contr | SKC | ELS - Eleanor Street Shaft (Central) |  | 2013-11-06 | 2013-11-08 09:34 | 2 | 2013-10-23 17:13 | Civil - Kerbs | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Approximately 12no. edging kerbs have been laid to the back of the footpath adjacent to the Plot N yard slab. Road pins with levels were provided at either end of the run but the edgings were not installed to the string line correctly resulting in a rise of 15mm in the centre of the run - see attached photo.
| 03SR - Stations (RfL) | Cxxx-NCR-000161 | NCR | Hot Tool Welding Calibration |  | Contr | SKC |  |  | 2013-11-08 | 2013-11-05 08:48 | -3 | 2013-10-25 09:19 | Shafts - Shafts General | 500 |  | Planning | Rework | 4 (0.5-3k) | Complete | Subcontractor Problems - Interfacing problems | Completed |  | Item 2.1 of ITP Cxxx-SKC-C-ITP-CR094-50013 states that a calibration certificate will be provided for the welding machine used to fix the waterproofing membrane. This is incorrect. The manufacturers / installers recommendation for this procedure is as follows: Prior to the welding operation to the permanent works commences, a test sample will be welded and Air Pressure Testing as per item 3.4.5 on the ITP will be completed. Following a prolonged gap in welding works of over 3 hours then the procedure will be repeated to ensure the welding plant is functioning properly.
| 03SR - Stations (RfL) | Cxxx-NCR-000162 | NCR | Aquaproof Waterproofing system not installed in Plot S shower unit floor |  | Contr | SKC | ELS - Eleanor Street Shaft (Central) |  | 2013-11-13 | 2013-11-13 16:42 | 0 | 2013-10-30 16:49 | Architectural - Flooring | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Supervision - Other | Completed |  | In Plot S shower unit floor, floor tiles have been installed without the Aquaproof Waterproofing system.
| 03SR - Stations (RfL) | Cxxx-NCR-000163 | NCR | Incorrect worktop installed in Plot S kitchen |  | Contr | SKC | ELS - Eleanor Street Shaft (Central) |  | 2013-11-13 | 2013-11-13 15:37 | 0 | 2013-10-30 16:57 | Architectural - General | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Supervision - Other | Completed |  | Incorrect worktop installed in Plot S kitchen. Worktop installed to plot S is currently Blackstone, in the brochure it shows Dark Grey.
| 03SR - Stations (RfL) | Cxxx-NCR-000164 | NCR | Incorrect vinyl flooring installation to plot N |  | Contr | SKC | ELS - Eleanor Street Shaft (Central) |  | 2013-11-13 | 2013-11-11 13:57 | -2 | 2013-10-30 17:00 | Architectural - Flooring | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Supervision - Other | Completed |  | Incorrect vinyl flooring installation to plot N. Vinyl floor installed to plot N is currently soft oak, in the brochure it shows smoked oak.
| 03SR - Stations (RfL) | Cxxx-NCR-000165 | NCR | Incorrect installation of pipe works in the water-heater cupboard of plot A |  | Contr | SKC | ELS - Eleanor Street Shaft (Central) |  | 2013-11-13 | 2013-11-13 15:33 | 0 | 2013-10-30 17:12 | Utilities Engineering - Utilities General | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Supervision - Other | Completed |  | Pipeworks in plot A inside the water-heater cupboard were installed and fixed incorrectly by the agency plumber. The screws on the pipe clips were too short and pulled out of the dry lining – they should have been longer to fix into the sip panel, also the pipework was incorrectly installed. Pipe works are now re-installed and fixed correctly (see attached pictures).
| 03SR - Stations (RfL) | Cxxx-NCR-000166 | NCR | Regulating Layer |  | Contr | SKC |  |  | 2013-11-27 | 2013-11-22 10:50 | -5 | 2013-10-30 10:09 | Shafts - Linings | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | It was not possible to spray a small section of regulating layer to the shaft walls, due to obstruction from the fixed position SCL pipe lines. To create the smooth regulating layer to prevent any puncture of the waterproofing system, Tetracaulk has been manually applied to an area behind the concrete pipe line and hose area.
| 03SR - Stations (RfL) | Cxxx-NCR-000167 | NCR | __ Not UKAS accredited for Modulus of Elasticity Test |  | Contr | SKC |  |  | 2013-11-26 | 2013-11-15 11:30 | -11 | 2013-11-12 15:18 | Shafts -Sprayed Concrete | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Subcontractor Problems - Other | Completed |  | __ Not UKAS accredited for Modulus of Elasticity Test. Works Information Vol 2B section 20.8 states: All on-site and off-site testing shall be carried out by laboratories accredited by UKAS or similar, acceptable national body or by persons accredited to a similar standard. The samples shall be taken by staff appointed by the laboratory. The requirement for UKAS accreditation may be waived for the testing of systems and their components, subject to an alternative testing proposal by the Contractor and the acceptance of the proposal by the Project Manager.
| 03SR - Stations (RfL) | Cxxx-NCR-000170 | NCR | Plot L damaged glass door |  | Contr | SKC | ELS - Eleanor Street Shaft (Central) |  | 2013-12-04 | 2013-11-28 11:07 | -6 | 2013-11-20 08:52 | Architectural - Doors | 1000 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | In plot L a glass door found to be damaged. The glass is damaged on both the inside and outside (see attached pictures). The glass requires replacing.
| 03SR - Stations (RfL) | Cxxx-NCR-000171 | NCR | Early Age Strength Testing - Stud Pull Out Testing |  | Contr | SKC | ELS - Eleanor Street Shaft (Central) |  | 2013-12-04 | 2013-11-26 16:10 | -8 | 2013-11-20 16:32 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Information not detailed | Completed |  | It was noted following one set of pull out tests for early strength testing, that the subcontractors engineer had not spaced the __ Nails the minimum required distance of 80mm apart.
| 03SR - Stations (RfL) | Cxxx-NCR-000172 | NCR | Mile End base slab construction |  | Contr | SKC |  |  | 2013-12-04 | 2013-11-26 15:30 | -8 | 2013-11-20 17:12 | Shafts - Shafts General | 500 |  | Planning | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | Due to the urgency of the Cxxx programme following delays incurred by changes to the base slab design, the base slab was poured with material compliance records at code 2. The required certification will be added to MCR asap.
| 03SR - Stations (RfL) | Cxxx-NCR-000173 | NCR | Premature laying for wearing course before manhole S20 was reset |  | Contr | SKC | ELS - Eleanor Street Shaft (Central) |  | 2013-12-05 | 2013-11-28 11:05 | -7 | 2013-11-21 11:08 | Civil - Wearing Course | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | S20 manhole lid had previously knocked off during construction works and reseting was required. Wearing course in ESS2 was laid before this lid could be reset and thus the lid was tarmac'd in too low. __ was required to be broken out for the lid to be reset.
| 03SR - Stations (RfL) | Cxxx-NCR-000174 | NCR | Below specification flexural and tesile test results for PCC shaft segments |  | Contr | SKC |  |  | 2013-12-20 | 2013-12-09 15:29 | -11 | 2013-11-22 10:26 | Structural Engineering - Pre-cast | 0 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Further to NCR Cxxx-NCR-000110, a concession was granted to accept tensile and flexural testing reports from a non UKAS accredited laboratory. On reviewing the test results, it was found that the strengths recorded were below those required by the Specification KH11.2202 - 3 and the ITP (Cxxx-SKC-O4-ITP-CR094-50006).
| 03SR - Stations (RfL) | Cxxx-NCR-000175 | NCR | Early age strength result below Modified J2 Curve |  | Contr | SKC | ELS - Eleanor Street Shaft (Central) |  | 2013-12-12 | 2013-12-05 10:31 | -7 | 2013-11-28 15:58 | Tunnelling - Linings - Sprayed Concrete | 0 |  | Material | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Not Defined | Completed |  | During advance 55 of adit VE1, early age strength results up to 3 hours were below the J2 curve. However our safe system of work requires that adit construction does not advance until the shotcrete mix has reached sufficient strength. The mix accelerator was dosed at 7.5%, with the shotcrete temperature measured at 25 oC and all fresh concrete tests are compliant with KT20. have increased the temperature of the water supply producing higher shotcrete temperatures. The early age strength results are currently shown to be above the modified J2 curve requirement. We will continue to adjust the temperature within the KT20 specified range (15-35oC) to conform with the J2 curve requirement. The additive temperature has been checked and is shown to be above the specified 5 oC minimum temperature, generally being stored at approx 15 oC. are also completing early age strength tests a higher frequency than KT20 requires to monitor mix performance. Batch records from our shotcrete provider, CPI __, are also continually monitored to ensure compliance.
| 03SR - Stations (RfL) | Cxxx-NCR-000176 | NCR | Compliance with KT 20 specification clause 2202c |  | Crossrail | PDP | ELS - Eleanor Street Shaft (Central) |  | 2014-01-17 | 2013-12-10 15:33 | -38 | 2013-11-28 15:55 | Civil - Tunnelling | 0 |  | Supervision/Management | Repair | 4 (0.5-3k) | Complete | Procedure Problem - Other | Completed |  | The requirement of KT 20 specification clause 2202c) is “All cores shall be visually inspected to verify that the sprayed concrete is dense and homogeneous without segregation of aggregate or other visible imperfections” The only records available at the time of surveillance to demonstrate that the cores were visually inspected were that of the independent testing laboratory. The record was for concrete core compressive strength test to BS EN 12504-1:2009 without any reference to the above KT 20 specification for visual examination. The reports record the visual inspection as “Satisfactory” without any other description or accompanying photograph.
| 03SR - Stations (RfL) | Cxxx-NCR-000179 | NCR | Damage to drainage pipe in plot N |  | Contr | SKC | ELS - Eleanor Street Shaft (Central) |  | 2014-02-21 | 2014-01-22 09:19 | -30 | 2013-11-29 08:58 | Civil - Drainage | 0 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | recently carried out a CCTV survey of the installed drainage throughout the recently constructed Travellers Site. Damage was discovered on the clay drainage pipe running from Inspection Chamber FN1 to the main run between manholes F62 and F63. Due to the pipe's close proximity to the amenity block foundations in Plot N, we are proposing to carry out non-destructive repair work by re-lining the pipe, using the Fernco Pipe Doctor, which has been specifically recommended to by the specialist sub-contractor that was brought in to carry out the CCTV survey. This technique is described in the following passage. "The Fernco Pipe Doctor, the only WRC approved patch repair system in the marketplace (certificate number PT/318/0311), is a high performance, no dig pipe repair solution that provides a quick and easy to use method of repairing damaged drainage and sewerage pipe systems. The Fernco Pipe Doctor is installed internally and eradicates the need for costly, disruptive and time consuming excavation work therefore enabling both vehicle and pedestrian traffic to move freely without realizing drainage and sewer work is being carried out underground. The Pipe Doctor system is ideal for specialist contractors who carry out CCTV surveys and repairs as it complements the standard installation equipment required for the pipe repair process. Following extensive water leak tests carried out by the WRc and approved by various Water Companies and Local Authorities (including __, South West Water and Dublin City Council), the performance of the silicate resin successfully achieved the WRc Standard. Applications Used by specialized __ Engineers that carry out CCTV surveys and repairs Repair damaged pipes that have a bore diameter of between 70-560mm Excellent bonding to most pipe materials including UPVC, clay, cast iron, ductile iron, stainless steel, pitch fiber and asbestos cement Applied to pipes that are damaged due to corrosion, displaced joints, tree roots and ground movement.
| 03SR - Stations (RfL) | Cxxx-NCR-000180 | NCR | Plot S paving slab falls |  | Contr | SKC | ELS - Eleanor Street Shaft (Central) |  | 2014-01-17 | 2014-01-07 10:16 | -10 | 2013-12-02 10:42 | Civil - Landscaping | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Supervision - Insufficient supervision | Completed |  | There are two isolated areas in plot S with incorrect direction of fall. Firstly, infront of the patio doors and secondly, behind the WC door next to the boundary wall.
| 03SR - Stations (RfL) | Cxxx-NCR-000181 | NCR | Plot N loose caravan yard mastic |  | Contr | SKC | ELS - Eleanor Street Shaft (Central) |  | 2013-12-18 | 2013-12-09 15:52 | -9 | 2013-12-04 08:46 | Civil - Concrete Pavement | 0 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Plot N caravan concrete yard mastic found loose (see attached pictures) and needs replacing.
| 03SR - Stations (RfL) | Cxxx-NCR-000182 | NCR | IA2 Re-alignment |  | Contr | SKC |  |  | 2014-04-03 | 2014-03-13 15:33 | -21 | 2013-12-10 13:45 | Tunnelling - Tunnelling General | 1500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Please see attached as-built information for IA2 regulating layer and 's proposed best fit re-alignment of the secondary lining. This is the most practical alignment for construction based on the as-built primary lining. The as-built information indicates the local tight spots. (tight spots also reviewed on site with Cxxx site representatives) Please confirm this proposal/local tight spots are acceptable.
| 03SR - Stations (RfL) | Cxxx-NCR-000183 | NCR | Damaged Brick to Plot S Boundary Wall |  | Contr | SKC | ELS - Eleanor Street Shaft (Central) |  | 2014-01-02 | 2013-12-16 11:50 | -17 | 2013-12-12 10:42 | Architectural - Brickworks/Blockworks | 0 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | Plot S Boundary Wall brick cracked in external brickwork.
| 03SR - Stations (RfL) | Cxxx-NCR-000188 | NCR | Early Age Strengths under J2 curve at one hour |  | Contr | SKC | ELS - Eleanor Street Shaft (Central) |  | 2014-04-03 | 2014-03-11 14:28 | -23 | 2014-01-28 18:09 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | At the commencement of spraying of advance 28a top heading, an early age strength panel was sprayed at 7.5%. Testing was completed on this panel as the profile was sprayed. At 1hour the strength of the panel was recorded as 0.495MPa. This rounded to two decimal figures as standard for the required accuracy of testing is 0.5MPa, which is compliant with the J2 curve at 1hour. During spraying of the profile a further panel was sprayed during and at the end of spraying to profile. These were tested with results above the J2 curve. A Shotcrete fallout of approximately 0.5m3 was witnessed during the advance. This was recorded on the Cxxx Shotcrete fallout register and reviewed at the Shift Review Group. This NCR has been raised at the request of Crossrail in view of the proximity of the 0.5MPa to the J2 curve plot at 1 hour . Attached is the early age strength results for panels sprayed: - At the start of spraying to profile - Mid spray - At the end of spraying to profile
| 03SR - Stations (RfL) | Cxxx-NCR-000189 | NCR | Settlement of carriageway surface over access road trench - Bow Business Triangle |  | Contr | SKC | ELS - Eleanor Street Shaft (Central) |  | 2014-03-04 | 2014-03-04 14:55 | 0 | 2014-02-18 16:25 | Civil - Utilities Engineering | 3000 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | A portion of the trench which was constructed to lay the new water main down the access road of the Bow Triangle Business centre has settled by an average 20mm. This indicates that the 20m length of trench in question had an insufficiently compacted sub-grade below the tarmac surface.
| 03SR - Stations (RfL) | Cxxx-NCR-000190 | NCR | Flexural Strength testing in accordance with BS EN 14651 |  | Contr | SKC | ELS - Eleanor Street Shaft (Central) |  | 2014-03-24 | 2014-03-05 14:33 | -19 | 2014-03-03 14:16 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Testing and Commissioning | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Improper handling of material | Completed |  | have used __ to undertake Structural Fibre Performance tests on our SCL mix in accordance with BS EN 14651. The performance requirement specified for SCL requires the residual flexural tensile strength of a concrete test specimen to be tested to a deflection of 4mm.The actual termination in these cases was completed at a deflection of approximately 3.6mm. A number of tests completed in accordance with 14651 were terminated before the specified deflection range as __ had not updated their software. The machine software has since been modified and this is reflected in the Secondary Lining test results. Email confirmation of this update from __ has been attached.
| 03SR - Stations (RfL) | Cxxx-NCR-000191 | NCR | Exposed Dywidag bars in shaft secondary lining |  | Contr | SKC |  |  | 2014-04-01 | 2014-03-27 09:15 | -5 | 2014-03-18 17:04 | Shafts - Linings | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During casting the shaft secondary lining, Dywidag bars were drill and fixed using a resin into the shaft secondary lining (max 150mm embedment), these were then used to tigthen up the bottom of the shutter for the next pour to ensure good alingment of the lining. However these bars were then cut flush with the lining, leaving the bar in the lining and exposed steel (see attached photo). These occur in 6 locations, 2 at the top of pour 3, and 4 at the top of pour 4. See attached sketch
| 03SR - Stations (RfL) | Cxxx-NCR-000192 | NCR | Early Age Strengths under J2 Curve at one hour |  | Contr | SKC | ELS - Eleanor Street Shaft (Central) |  | 2014-06-30 | 2014-06-11 15:32 | -19 | 2014-03-19 13:13 | Shafts -Sprayed Concrete | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Improper handling of material | Completed |  | During the application of the P2 thickening layer in Eleanor Street adit VE1, Early Age Strength testing was completed in accordance with BS EN 14488-2. Test results revealed that the modified J2 Curve as per KT20 was not met until 2 hours (Please see that attached document). safe system of work was in place and no access to the exclusion authorised, until the SCL had achieved a strength of 1 MPa.
| 03SR - Stations (RfL) | Cxxx-NCR-000193 | NCR | Shaft Waterproofing re-injectable tube grout system - injection patch tube detatched during pour |  | Contr | SKC |  |  | 2014-04-03 | 2014-03-25 17:13 | -9 | 2014-03-20 19:08 | Shafts - Shafts General | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During pouring the final section of the shaft secondary lining (107.429m to 109.500m), 1no. grout injection tube connecting a grout patch (contact grouting) in the previous pour 9 (104.779m to 17.429m) became disconnected from the junction box due to the concrete flow (see photos). It would have been unsafe to attempt to find and re-attach the injection tube as it is located at the bottom of the shutter in this pour. The concrete skip was repositioned when pouring adjacent to the other junction boxes, so the concrete flow forced the tubes towards the junction boxes so all other grout tubes remained connected. All grout tubes around the construction joint (green/red pipes) remained in positioned.
| 03SR - Stations (RfL) | Cxxx-NCR-000194 | NCR | Breakout of a section of P2 layer in invert of IE1 |  | Contr | SKC | ELS - Eleanor Street Shaft (Central) |  | 2014-05-23 | 2014-05-21 11:05 | -2 | 2014-03-25 14:51 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Improper handling of material | Completed |  | Further to the request of Cxxx, a localised area of approximately 3mx2m within the SCL P2 layer of IE1 invert was investigated for adherence between the P2 and P1 layers. 4no cores were taken through the P2 lining, being approximately 150mm in length. Also 1no core was taken through the P2 and P1 lining, being approximately 600mm in length. These cores confirmed good compaction of the SCL. All cores separated at the cold joint between P2 and P1 layers. 1no 150mm core of P2 separated at the leading edge joint approximately halfway through the core. Prior to spraying of the invert all rebound is blown out and the invert surface washed over. All cores are shown in the attached cores log.
| 03SR - Stations (RfL) | Cxxx-NCR-000195 | NCR | Mile End Shaft - Lift Shaft Starter Bars |  | Contr | SKC |  |  | 2014-05-01 | 2014-04-29 09:21 | -2 | 2014-03-27 14:00 | Structural Engineering - Reinforcement | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | The base slab at Mile End shaft was cast on 13/11/13, with lift shaft starter bars formed using couplers as per acceptance of Cxxx-RFI-000128. To protect the couplers during secondary lining works protection concrete as installed over the colupers. Either during concreting or breaking out the protective concrete some of the starter bars have been lost, please refer to as-built sketch showing approx. location of couplers and photos.
| 03SR - Stations (RfL) | Cxxx-NCR-000196 | NCR | __ did not advise CSJV that testing was taking place |  | Contr | SKC | ELS - Eleanor Street Shaft (Central) |  | 2014-04-14 | 2014-04-04 10:02 | -10 | 2014-03-31 15:19 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Insufficient information made available to the worker. | Completed |  | __ carried out sampling of concrete without informing or CRL. The sampling was therefore not witnessed in accordance with the requirements of the ITP. Note: As the Engineers were unaware of the presence of __ on site, a breifing was not given. This has been raised via RIVO.
| 03SR - Stations (RfL) | Cxxx-NCR-000197 | NCR | Headhouse Pile (P055) Cage not installed to design level. |  | Contr | SKC |  |  | 2014-04-23 | 2014-04-24 09:24 | 1 | 2014-04-09 10:43 | Geotechnical Engineering - Concrete - Bored Pile | 1500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | P055 (see attached drawing showing numbering system) , a 600mm diameter CFA pile was bored to depth of 16.5m and concreted. The reinforcement cage ( 8H25 -16.3m) long was then plunged into the pile. During the plunging process the cage stopped with the top of steel cage 1.8m above the piling platform. The hydraulic vibrator was then utilised to advance the cage to the design toe. It was not possible to plunge the cage to the design level. Design toe level of cage = 93.65mATD. Actual toe level of cage = 95.45mATD. The 1.8m of cage sitting above the mat has been cut off at 109.95mATD and removed for safety reasons. Please see attached sketch of pile installation
| 03SR - Stations (RfL) | Cxxx-NCR-000198 | NCR | Concrete fence posts |  | Contr | SKC | ELS - Eleanor Street Shaft (Central) |  | 2014-05-23 | 2014-05-22 12:11 | -1 | 2014-04-11 10:09 | Architectural - Landscape Architectural | 500 |  | Manufacturing Defect | Reject | 4 (0.5-3k) | Complete | Material/Preservation Problems - Not Defined | Completed |  | Poor quality concrete fence posts were delievered to travellers site. Some have been installed. The posts have excessvie blowholes and appear to be structurally weak.
| 03SR - Stations (RfL) | Cxxx-NCR-000200 | NCR | Amenity Block Foundation Surface Levels |  | Contr | SKC | ELS - Eleanor Street Shaft (Central) |  | 2014-05-21 | 2014-05-22 11:33 | 1 | 2014-05-07 17:34 | Civil - Structural Engineering | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | A section of amenity block P floor is out of level tolerance.
| 03SR - Stations (RfL) | Cxxx-NCR-000201 | NCR | Kerbs knocked by tarmac roller |  | Contr | SKC | ELS - Eleanor Street Shaft (Central) |  | 2014-05-21 | 2014-05-22 10:26 | 1 | 2014-05-07 17:45 | Civil - Kerbs | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | 3 kerbs outside of Plot H were knocked out of line when the vibrating roller passed during tarmacing operation.
| 03SR - Stations (RfL) | Cxxx-NCR-000202 | NCR | Lift Drain Pipe |  | Contr | SKC |  |  | 2015-09-14 | 2015-06-10 15:03 | -96 | 2014-05-09 16:34 | Civil - Drainage | 500 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Conflicting information on drawings | Completed |  | installed a void between the lift pit sump and main sump wall for a 100mm diameter pipe, as indicated on drawings Cxxx-MMD-C4-DDD-CR094_SH006-06020-C07 and Cxxx-JUL-P-DDA-CR094_SH006-00533-C02. However as per Cxxx-RFI-000241, a 150mm diameter pipe is required in order to achieve the required flow rate of 25l/s.
| 03SR - Stations (RfL) | Cxxx-NCR-000203 | NCR | Earthing Riser |  | Contr | SKC |  |  | 2015-03-02 | 2015-02-20 10:20 | -10 | 2014-05-15 10:51 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | After grouting the two earthing risers to level 83.379m as per agreed proposal in Cxxx-FCD-000158, it has been found that one of the earthing risers located closest to Adit IA2 is leaking water. This implies that the grouting was not installed sufficiently leaving a route for the water to escape. are also investigating the possibility of the water leaking through the cable sheathing but due to the volume of water this appears unlikely.
| 03SR - Stations (RfL) | Cxxx-NCR-000205 | NCR | Welding documentation for the Security Gates not reviewed |  | Contr | SKC | ELS - Eleanor Street Shaft (Central) |  | 2014-08-08 | 2014-08-06 13:47 | -2 | 2014-05-30 12:37 | Architectural - General | 2000 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | Item 1.7 of ITP ref: Cxxx-SKC-C-ITP-CR094_WS110-50014 requires that all documentation is reviewed to ensure that they are acceptable for the fabrication. Whilst all documentation was available, the review was not carried out.
| 03SR - Stations (RfL) | Cxxx-NCR-000206 | NCR | Use of C50/60 Concrete mix for shaft internal concrete works |  | Contr | SKC |  |  | 2014-06-13 | 2014-06-04 15:53 | -9 | 2014-05-30 13:43 | Structural Engineering - Concrete Member | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | used a higher strength C50/60 concrete mix to cast parts of the B9 structure, instead of the minimum C32/40 on the Cxxx drawings. This was so as to achieve earlier striking times. However this was carried out prior to a formal PTR closed-out acceptance of Cxxx-FCD-000213 being in place.
| 03SR - Stations (RfL) | Cxxx-NCR-000207 | NCR | Mile End Pile Integrity Testing |  | Contr | SKC |  |  | 2015-08-10 | 2015-06-24 09:12 | -47 | 2014-05-30 14:14 | Geotechnical Engineering - Concrete - Bored Pile | 500 |  | Incomplete Works | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | As stated in Cxxx-RFI-000235; Cxxx Mile End - Civil / Structural Specification Cxxx-JUL-S-RSP-CR094_SH006_Z-50001 Clause KP10.220 states Integrity testing shall be carried out between 7 days and 21 days after piles have been cast. Integrity testing has not been carried out on the headhouse piles within this time frame. Testing can only be carried out once the piles have been cropped. It was not possible to crop the piles within this time frame due to site sequencing. Exposing the piles at this time would create health and safety hazards.
| 03SR - Stations (RfL) | Cxxx-NCR-000208 | NCR | Secondary lining - low fresh fibre content result |  | Contr | SKC |  |  | 2014-07-16 | 2014-06-26 14:52 | -20 | 2014-06-04 17:20 | Tunnelling - Linings - In-situ Concrete | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | 3no. 10litre Fresh Fibre content samples were taken for Crown Pour 2 of the secondary lining to Adit IA2 on the 18/03/14 (see attached). This pour consisted of one 8m3 load of concrete. The design amount of steel fibre for the mix is 30kg/m3, with a minimum acceptance value of 24kg/m3 (80%) as per KF10. Subsequently the result of each sample for this pour have been found to below this acceptance value: 20.4kg/m3, 19.0kg/m3 & 19.9kg/m3. All other results for previous secondary lining pours with this mix have been between 28-44kg/m3 average.
| 03SR - Stations (RfL) | Cxxx-NCR-000209 | NCR | Backfill of Eleanor St Temporary Shaft - Use of SCL breakout |  | Contr | SKC | ELS - Eleanor Street Shaft (Central) |  | 2014-07-14 | 2014-06-24 09:25 | -20 | 2014-06-09 18:48 | Civil - Fill | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | SCL broken out around the base of the sheet piles was utilised for the continued backfill of the temporary shaft. SCL utilised for the backfill was as per the grading requirements of class 6F2 material, as stated in the specification for highway works, series 600, table 6/2. Large pieces of broken out SCL larger than the grading requirements of class 6F2 material were not used in backfilling and were removed from the shaft for removal from site. Utilised broken out SCL inline with the grading requirements of class 6F2 material was mixed with 6F2 material and backfilling continued as per Cxxx-SKC-C-GMS-CR094_WS110-50047 Method Statement for Backfill of temporary shaft to ground level. Plate bearing testing was carried out of the broken out SCL utilised for backfill as per Cxxx-SKC-C-ITP-CR094_WS110-50023 ITP for Temporary Shaft Backfill. Approx 15m^3 of broken out SCL was utilised. This was mixed with 6F2 and distributed throughout backfilling operations between 99-100mAOD. Therefore 15m^3 would have been distributed through a 1m layer which totals 78m^3. As a result, for compacted layers of 250mm, approx 4m^3 SCL was utilised and mixed with 16m^3 6F2 per 250mm compacted layers. As per the grading of 6F2 defined by Specification for Highways works Table 6/2. Max size 90mm. However, the quantity utilised mainly consisted of fines. Utilised SCL was as per MCR for __ Wet Sprayed Concrete Cxxx-SKC-C-LRC-CR094-50009.
| 03SR - Stations (RfL) | Cxxx-NCR-000210 | NCR | Ecocure Curing Agent Use on Core Walls |  | Contr | SKC |  |  | 2014-06-24 | 2014-06-16 14:31 | -8 | 2014-06-10 15:26 | Structural Engineering - Surface Treatment | 500 |  | Planning | Rework | 4 (0.5-3k) | Complete | Personnel Error - Violation of requirement or procedure | Completed |  | In line with the Civil Works Specification (Cxxx-JUL-S-RSP-CR094_SH006_Z-50001) KF10.3206 a curing compound was applied to the internal face of the core walls following striking. This curing compound 'Ecocure' did not have an approved MCR at the time of use. A MCR has been raised for this, Cxxx-SKC-C-LRC-CR094_WS109-50073. This is currently at code 3.
| 03SR - Stations (RfL) | Cxxx-NCR-000211 | NCR | Plot Q Parking Bay Blockwork |  | Contr | SKC | ELS - Eleanor Street Shaft (Central) |  | 2014-07-08 | 2014-06-26 11:16 | -12 | 2014-06-17 16:44 | Civil - Landscaping | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Plot Q parking bay - paving blocks have not been laid square with the edging kerbs (see attached photo)
| 03SR - Stations (RfL) | Cxxx-NCR-000212 | NCR | Plot Q - Van Connection Point Location |  | Contr | SKC | ELS - Eleanor Street Shaft (Central) |  | 2014-07-30 | 2014-07-17 11:55 | -13 | 2014-06-25 10:26 | Civil - Drainage | 0 |  | Design | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The position of the static caravan on plot Q was changed at the request of the resident. The pitch layout drawing was changed accordingly by the Cxxx designer, however the drainage design was not updated to match the new location. Consequently, the foul outlet for the caravan - AKA Van Connection Point (VCP) - was installed as per drawings but is not in a practical location for connection to the caravan. The pavement works have also been completed in the plot so the drainage can not be moved easily.
| 03SR - Stations (RfL) | Cxxx-NCR-000213 | NCR | Procedure for amending drawings not followed |  | Contr | SKC |  |  | 2014-07-16 | 2014-07-15 10:52 | -1 | 2014-07-02 13:48 | Consents - Planning and Heritage | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Amended drawings were sent informally to CRL for comment. These were in the incorrect format and contained changes that had not been discussed with or approved by CRL. The drawings were: CRL1-XRL-T3-DDA-CR094-0001 P03 Cxxx-SKC-A-DDC-CR094_SH006_1-00401 Cxxx-SKC-A-DDC-CR094_SH006_1-00412 CRL1-XRL-T3-DDA-CR094-0001 P03 was a CRL drawing that had not been issued to Cxxx
| 03SR - Stations (RfL) | Cxxx-NCR-000214 | NCR | Brickwork piers to boundary wall - Plots H,I,J,P |  | Contr | SKC | ELS - Eleanor Street Shaft (Central) |  | 2015-03-02 | 2015-02-24 09:45 | -6 | 2014-06-19 10:48 | Architectural - Walls | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Brickwork piers not built correctly to architect detail drawings
| 03SR - Stations (RfL) | Cxxx-NCR-000215 | NCR | Defect/damage to corners of core walls - Level B8 to B7 |  | Contr | SKC |  |  | 2014-11-03 | 2014-10-22 16:24 | -12 | 2014-06-19 15:48 | Structural Engineering - Concrete Member | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | After striking the internal shutters to the core walls between levels B8 to B7, two defects have been found to the finished concrete. Please see attached sketch including photos of the defects. Defect 1 - the former used to form the 25 x 25mm chamfer became detached from the shutter during the concrete pour due to concrete pressures (defect extents approx. 700mm from the base of the pour). This has meant that the chamfer has been formed incorrectly which can be seen in the photos. Since the cover is 30mm, this will not have effected the reinforcement as can be seen in the attached sketch. Defect 2 - during striking the shutters a small section of the corner of the wall, not requiring a chamfer, has been locally damaged. Again this is no more than 30mm deep so has not effected the reinforcement.
| 03SR - Stations (RfL) | Cxxx-NCR-000216 | NCR | Core Wall Surface Finish Defect |  | Contr | SKC |  |  | 2014-11-03 | 2014-10-22 16:26 | -12 | 2014-06-23 15:18 | Structural Engineering - Concrete Member | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | At the joint between pours of the core wall (88.4m) a small section of wall was found to exposed aggregate due to grout loss at the base of the shutter.
| 03SR - Stations (RfL) | Cxxx-NCR-000217 | NCR | Back fill not in accordance with series 600 of SHW |  | Crossrail | PDP | ELS - Eleanor Street Shaft (Central) |  | 2014-07-10 | 2014-07-04 10:06 | -6 | 2014-06-26 11:53 | Civil - Fill | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | PTR RFI number Cxxx-RFI-000101 details that back fill material was SHW 6F2 compacted in layers to SHW. Surveillance QS360-08 found that there was no OMC for the fill or MC taken prior to compaction and the compaction layers were 250mm deep undertaken with a vibratory roller less than 1800kg per metre roll in 8 passes . The requirement is to fill with a MC of -2% to + 0% of optimum with roll weight of over 3600Kg/meter width
| 03SR - Stations (RfL) | Cxxx-NCR-000218 | NCR | Materials forming part of the works not from source that holds appropriate certification from UKAS |  | Crossrail | PDP | ELS - Eleanor Street Shaft (Central) |  | 2014-07-07 | 2014-07-04 10:03 | -3 | 2014-06-23 15:22 | Civil - Fill | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | MCR Cxxx-SKC-C-LRC- CR094_WS110-50057 rev 1.0 cerification shedule was for plant hire not supply of 6F5/6F2
| 03SR - Stations (RfL) | Cxxx-NCR-000220 | NCR | Contemporaneous records for 6F5 back fill not avaialble |  | Crossrail | PDP | ELS - Eleanor Street Shaft (Central) |  | 2014-07-07 | 2014-07-04 10:04 | -3 | 2014-06-23 15:49 | Civil - Fill | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Supplier weekly grading and monthly constituent materials quantifying tests not avaialbe at time of surveillance QS360-08 , records available were those of included in MCR The Cxxx-SKC-C-LRC- CR094_WS110-50057 rev 1.0 from November 2013
| 03SR - Stations (RfL) | Cxxx-NCR-000221 | NCR | The lino flooring in Plot R become water damaged and needs to be replaced |  | Contr | SKC | ELS - Eleanor Street Shaft (Central) |  | 2014-07-28 | 2014-07-22 10:48 | -6 | 2014-06-30 13:36 | Architectural - Flooring | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Water was spilt on the lino flooring in Plot R
| 03SR - Stations (RfL) | Cxxx-NCR-000222 | NCR | Concrete defects in core walls at B6 level in MEP Shaft |  | Contr | SKC |  |  | 2015-02-02 | 2015-01-13 13:30 | -20 | 2014-07-02 08:20 | Civil - Civil Engineering General | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | When striking the shutters of the B6 level core wall pour, it was found that 2 sections had not been concreted sufficiently, due to poor compaction/placement of the concrete mix. Both sets of voids are between 10mm and 30mm thick, therefore not effecting the reinforcement.
| 03SR - Stations (RfL) | Cxxx-NCR-000224 | NCR | Hardwood Planter Fence Warping |  | Contr | SKC | ELS - Eleanor Street Shaft (Central) |  | 2014-10-06 | 2014-10-06 09:08 | 0 | 2014-07-08 10:05 | Architectural - Landscape Architectural | 3000 |  | Design | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The narrow infill hardwood strips on the planter fencing, next to plots O & Q, have warped (see attached photo). The strips were added following a request from the future residents and subsequent PMI from Crossrail. The parts of the fencing consistent with the original design have not warped.
| 03SR - Stations (RfL) | Cxxx-NCR-000225 | NCR | Concrete defect in core walls pour at B5-B4 level |  | Contr | SKC |  |  | 2014-11-03 | 2014-09-25 09:01 | -39 | 2014-07-08 12:30 | Civil - Civil Engineering General | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Having struck the shutters of the B5 level core wall pour, it has been found that a section of wall had not been concreted sufficiently. The section is between two box outs and therefore poor compaction has affected the placement of the concrete mix. The void extends through the wall exposing the reinforcement.
| 03SR - Stations (RfL) | Cxxx-NCR-000227 | NCR | Defect in Concrete Core Walls between Levels B4-B3 |  | Contr | SKC |  |  | 2014-07-25 | 2014-07-11 16:16 | -14 | 2014-07-11 13:16 | Structural Engineering - Finishes | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | After striking the internal shutters to the core walls between levels B4 to B3, a defect was found to the finished concrete. Please see attached sketch including photo of the defect. The depth of the defect is approx. 45mm deep and exposes the reinforcement locally. This is likely caused due to a lack of compaction with the pokers/shutter vibrators in this very local area.
| 03SR - Stations (RfL) | Cxxx-NCR-000231 | NCR | Stop End defects in Core walls Level 109.650 to 112.400 |  | Contr | SKC |  |  | 2015-06-15 | 2015-06-10 15:30 | -5 | 2014-08-05 11:43 | Structural Engineering - Concrete Member | 3000 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During a post pour inspection of the core walls pour between levels 109.650 & 112.400m, two defects around stop-ends were found: 1) The stop end used to form the corner of the wall adjacent to the lift shaft opening (see attached sketches), moved slightly out of position during the pour on one side and has formed at 10-20mm rebate (see attached photos). 2) The stop end used to form the end of central Lift/stair core (see attached sketch) wall became twisted in the middle section during installing the final steel internal shutter, this was readjusted from outside the shutter when carrying out the pre-pour inspection. However during the pour the concrete pressure must have dislodge the stop end back into the twisted position, hence the cast face of the wall is out of position on one side by approx. 30-40mm max at the centre of the pour (but correct at the top & bottom).
| 03SR - Stations (RfL) | Cxxx-NCR-000232 | NCR | Steelwork glavanisation defects on delivery to site |  | Contr | SKC |  |  | 2014-10-03 | 2014-09-17 14:08 | -16 | 2014-08-13 17:10 | Structural Engineering - Steel Member | 3000 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During an inspection of the first batch of structural steel columns to be installed in the shaft, observations were raised in various localised areas: 1. Localised rust to some plate welds 2. Surface scratches 3. Build-up of materials at welds 4. Surface shading & colour variance See attached report on remedial works
| 03SR - Stations (RfL) | Cxxx-NCR-000234 | NCR | Plot E foundation slab abandoned pour |  | Contr | SKC | ELS - Eleanor Street Shaft (Central) |  | 2014-10-03 | 2014-09-30 09:14 | -3 | 2014-09-05 11:31 | Civil - Base Course | 3000 |  | Material | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | While pouring the foundation Slab to Plot E, the concrete delivered went off before we had a chance to complete Slab E, this resulted in us having to break out the concrete.
| 03SR - Stations (RfL) | Cxxx-NCR-000236 | NCR | The rain water outlets on the security hut roof had not been installed correctly. |  | Contr | SKC | ELS - Eleanor Street Shaft (Central) |  | 2015-05-04 | 2015-04-23 15:09 | -11 | 2014-09-04 14:54 | Architectural - Roofing & Exterior Treatment | 2000 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The specification (Cxxx-SKC-A-RSP-CR094_WS110-50003) and R10 365 states that a parapet roof outlet to inverted roof (ref Axter SF 110) should be installed. The attached drawings, from the Axter catalogue, show how the outlet (Axter SF110) should be installed. This is not the case on site.
| 03SR - Stations (RfL) | Cxxx-NCR-000237 | NCR | Fractured Concrete Below Cut off Level |  | Contr | SKC |  |  | 2014-11-17 | 2014-10-13 12:12 | -35 | 2014-09-08 11:18 | Geotechnical Engineering - Concrete - Bored Pile | 2000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Contamination | Completed |  | During the first phase of ground slab excavation, which involved exposing the piles to then reduce down to cut off level. The top section of concrete of 4no. Piles (P006, P019, P020 & P021) fell away below cut off level, approx. 100mm (and locally 150mm) lower than cut off level. ------------------------------------------------------------------------------------------------------------ Update (23/09/2014) - Further to the initial piles found in Area 1 requiring further breaking down, smaller local fractures have been found on the following Piles: P001, P004, P011, P012, P014, P015, P017, P019, P022, P024, P025, P026, P028, P029, P030, P031, P032, P033, P034, P035. Details can be found in the log attached. These defects are much more localise than previous and likely caused due to a combination of a small amount of loose ground material entering into the top section of the concrete and cropping method used. An alternative cropping method will be utilised for the following phases.
| 03SR - Stations (RfL) | Cxxx-NCR-000238 | NCR | Pile Rebar above cut off level damage |  | Contr | SKC |  |  | 2014-09-22 | 2014-09-18 09:42 | -4 | 2014-09-08 13:00 | Geotechnical Engineering - Concrete - Bored Pile | 3000 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During cropping the piles the first section of piles to cut off level, two number piles the reinforcement above cut off level has been broken. Pile No.011 - 1no. vertical bar has been broken at cut off level (109.525m) Pile No.028 - 2no. vertical bars have been broken at cut off level (109.525m)
| 03SR - Stations (RfL) | Cxxx-NCR-000239 | NCR | Suprema pump pipe adapter |  | Contr | SKC | ELS - Eleanor Street Shaft (Central) |  | 2014-09-30 | 2014-09-16 12:09 | -14 | 2014-09-11 15:49 | Shafts -Sprayed Concrete | 2000 |  | System Defect | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | During Eleanor Street Shaft SCL construction the pipe adapter that connects the suprema pump to the shaft concrete lines failed. A suitable spare part was not available.
| 03SR - Stations (RfL) | Cxxx-NCR-000240 | NCR | Missing Slab Starter Bars from Core wall |  | Contr | SKC |  |  | 2014-11-17 | 2014-10-13 12:30 | -35 | 2014-09-12 17:18 | Structural Engineering - Concrete Member | 2000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | When folding out the starter bars from the 'startabox' used in the core wall construction for slab level B5, it was found a small section of starter box was missing (890mm long) as shown on the attached sketch.
| 03SR - Stations (RfL) | Cxxx-NCR-000241 | NCR | Scratch to Steel Colum B6 to B5 |  | Contr | SKC |  |  | 2015-06-29 | 2015-06-10 15:06 | -19 | 2014-09-12 19:05 | Structural Engineering - Steel Member | 1000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During a pre installation inspection of the steel columns being installed from B6 to B5, a scratch to the galvanisation was observed on the shelf angle plate of one column. See attached sketches and photo. When checked with the __ the galvanisation thickness was less than 115 microns as per Cxxx-JUL-S-RSP-CR094_SH006_Z-50001. All other areas to other columns were found to be satisfactory.
| 03SR - Stations (RfL) | Cxxx-NCR-000242 | NCR | Damage to Pile P030 Reinforcement |  | Contr | SKC |  |  | 2014-11-17 | 2014-10-08 12:02 | -40 | 2014-09-15 19:29 | Geotechnical Engineering - Concrete - Bored Pile | 3000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Since breaking down Pile P030 to cut off level it has been found that 2no. reinforcement bars have been broken at cut off level, and 2no. reinforcement bars have been damaged just above cut off level. See attached sketch for locations.
| 03SR - Stations (RfL) | Cxxx-NCR-000243 | NCR | Plot A yard slab - concrete pour issues |  | Contr | SKC | ELS - Eleanor Street Shaft (Central) |  | 2014-11-10 | 2014-11-06 12:15 | -4 | 2014-09-16 11:06 | Civil - Concrete Pavement | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | A few issues were noted during a concrete pour of one section of Plot A yard slab. 1) An unkown quantity of additional water was added by the driver (driver stated 20L) to the remainding 6m3 of concrete left in the wagon. 2) Possible insufficient or excessive cover. Note: side cover should be 60mm (+/- 20mm), top cover 50mm (+10mm / - 0mm).
| 03SR - Stations (RfL) | Cxxx-NCR-000244 | NCR | Shaft exclusion zone camera |  | Contr | SKC | ELS - Eleanor Street Shaft (Central) |  | 2014-10-03 | 2014-09-22 09:25 | -11 | 2014-09-19 12:44 | Shafts -Sprayed Concrete | 500 |  | Software | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The camera used to monitor the exclusion zone during shaft SCL construction stopped working on 15.9.14.
| 03SR - Stations (RfL) | Cxxx-NCR-000246 | NCR | Early age strength results below J2 at one hour |  | Contr | SKC | ELS - Eleanor Street Shaft (Central) |  | 2014-10-03 | 2014-09-22 13:52 | -11 | 2014-09-19 16:06 | Shafts -Sprayed Concrete | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During the SCL application of Eleanor Street shaft 3 of the 4 panels sprayed on 18.9.14 strengths were below J2 until 2 hours. All other quality checks were compliant with the ITP and KT20. The safe system of work was in place and no man access was allowed into the exclusion zone until the shotcrete had achieved a strength of 0.5MPa.
| 03SR - Stations (RfL) | Cxxx-NCR-000247 | NCR | Missing Hydrophilic Strip at Construction Joint |  | Contr | SKC |  |  | 2015-09-07 | 2015-09-04 15:11 | -3 | 2014-09-25 19:45 | Civil - Civil Engineering General | 3000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The requirements for waterproofing of external construction joints was not clear on the design drawings and a RFI (Cxxx-RFI-000302) was submitted for clarification. (27/07/14 submitted, returned 12/08/14) While this RFI was being reviewed the top section of shaft core walls was constructed 112.4m to u/s of roof level (cast 04/08/14). The majority of the walls are internal, however one horizontal joint at 112.4m becomes external above the plenum roof slab (see attached sketch). Therefore a hydrophilic strip was not installed in this location.
| 03SR - Stations (RfL) | Cxxx-NCR-000248 | NCR | Use of unapproved sketch |  | Contr | SKC | ELS - Eleanor Street Shaft (Central) |  | 2014-12-22 | 2014-11-17 15:40 | -35 | 2014-10-08 10:48 | Architectural - Brickworks/Blockworks | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Design Problem - Use of unapproved drawings | Completed |  | The construction details of traveller plot walls/fences are shown on various approved CRL drawings (produced by designer), at the north boundary of plot A 2 different types of wall/fence are shown on various drawings. The CRL drawings show a 1.8m high boundary fence, Cxxx-JUL-A-DDA-CR094_SH007_1-01200 and Cxxx-JUL-A-DDA-CR094_SH007_1-01201. 4 drawings (produced by ) also show a 1.8m high boundary fence and one shows a full height boundary wall. This contradiction in drawings was raise with the designer via an RFI, the designer confirmed the fence/wall to be a 1.8m high wall and provided a detail in RFI response. This upgrade from 1.8m fence to 1.8m wall was not confirmed with CRL via a PTR or drawing submission
| 03SR - Stations (RfL) | Cxxx-NCR-000249 | NCR | Fractured Concrete below Pile Cut off Level - Area 2 |  | Contr | SKC |  |  | 2014-10-22 | 2014-10-21 15:47 | -1 | 2014-10-08 17:14 | Geotechnical Engineering - Concrete - Bored Pile | 2000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | When exposing and breaking down piles P039 and P040, the concrete broke away very easily with the breakers and in local areas the concrete broke away below cut off level. See attached photos
| 03SR - Stations (RfL) | Cxxx-NCR-000250 | NCR | Pile Fractured Concrete Below Cut off - Area 3 |  | Contr | SKC |  |  | 2014-11-04 | 2014-10-23 07:52 | -12 | 2014-10-21 15:56 | Civil - Civil Engineering General | 2000 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | When breaking down Pile No. P023 to cut off level, one side of the concrete broke away very easily resulting exposing the rebar below cut off level. Maximum extend is 150mm below cut off level maximum locally, See attached photos.
| 03SR - Stations (RfL) | Cxxx-NCR-000252 | NCR | Plot C edging kerbs incorrect installation |  | Contr | SKC | ELS - Eleanor Street Shaft (Central) |  | 2014-12-01 | 2014-11-21 13:35 | -10 | 2014-10-27 15:14 | Civil - Kerbs | 3000 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Plot C eging kerbs were installed to the incorrect level.
| 03SR - Stations (RfL) | Cxxx-NCR-000253 | NCR | In-correct installation of access road kerbs. |  | Contr | SKC | ELS - Eleanor Street Shaft (Central) |  | 2014-12-01 | 2014-11-24 12:38 | -7 | 2014-10-27 15:37 | Civil - Kerbs | 3000 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Plot Q side kerbs were installed to the incorrect level and to the wrong string line twice. Plot C kerbs were installed to the wrong level.
| 03SR - Stations (RfL) | Cxxx-NCR-000254 | NCR | Holorib to soffit of Shaft Internal Slabs |  | Contr | SKC |  |  | 2014-12-08 | 2014-11-21 13:41 | -17 | 2014-10-30 18:59 | Structural Engineering - Structural Engineering - General | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Holorib has been included on the design of the soffit of the shaft internal slabs, which designed to act as permanent formwork, with the ribs to be utilised for M&E fixings to eliminate drill and fixing M&E fixings. Upon removing the falsework to the shaft internal slabs, it has been found that in some isolated locations that some of the ribs within the holorib units have pinched together. This may make it difficult to install M&E fixings in these locations. See attached photo.
| 03SR - Stations (RfL) | Cxxx-NCR-000255 | NCR | Plot C planter wall damaged |  | Contr | SKC | ELS - Eleanor Street Shaft (Central) |  | 2014-11-28 | 2014-11-11 13:39 | -17 | 2014-10-31 13:42 | Architectural - Walls | 2000 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The planter wall in plot C was discovered to be damaged and not fit for purpose.
| 03SR - Stations (RfL) | Cxxx-NCR-000256 | NCR | Early Age Strengths during adv 72 |  | Contr | SKC | ELS - Eleanor Street Shaft (Central) |  | 2014-12-08 | 2014-11-24 12:11 | -14 | 2014-10-31 17:43 | Shafts -Sprayed Concrete | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Not Defined | Completed |  | During the SCL application of Eleanor Street shaft the SCL panel sprayed during adv 72 strength was below J2 until 1.5 hours. All other quality checks were compliant with the ITP and KT20. The safe system of work was in place and no man access was allowed into the exclusion zone until the shotcrete had achieved a strength of 0.5MPa.
| 03SR - Stations (RfL) | Cxxx-NCR-000257 | NCR | Kerbs were knocked out of position during tarmac subbase road installation. |  | Contr | SKC | ELS - Eleanor Street Shaft (Central) |  | 2014-12-01 | 2014-11-12 09:03 | -19 | 2014-11-03 17:36 | Civil - Kerbs | 3000 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Whilst the tarmacers were rolling the tarmac subbase to correct thickness opposite plot E, three road kerbs were knocked out of place and pushed over.
| 03SR - Stations (RfL) | Cxxx-NCR-000258 | NCR | Eleanor Street Travellers Site Plot E concrete yard slab gully ponding issues |  | Contr | SKC | ELS - Eleanor Street Shaft (Central) |  | 2014-11-28 | 2014-11-14 14:49 | -14 | 2014-11-05 13:37 | Civil - Concrete Pavement | 3000 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Plot E concrete yard slab gully drainage concrete infill has been installed too high on one side resulting in slow flowing surface water to pond in this location and not drain effectively into the gully.
| 03SR - Stations (RfL) | Cxxx-NCR-000259 | NCR | Eleanor Street Travellers Site Plot E Parking Bay Incorrect Sizing (not square) |  | Contr | SKC | ELS - Eleanor Street Shaft (Central) |  | 2014-11-29 | 2014-11-25 10:41 | -4 | 2014-11-05 13:47 | Civil - Street Architecture | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Travellers site plot E parking bay is not to the correct size of 5.2m in depth resulting in not being square, parking bay is out by 20-30mm from corner to corner resulting in a line of split blocks along the front edge.
| 03SR - Stations (RfL) | Cxxx-NCR-000260 | NCR | Eleanor Street Travellers Site Homezone Damaged Road Kerbs & Block Paving Footpath Spacing |  | Contr | SKC | ELS - Eleanor Street Shaft (Central) |  | 2014-12-05 | 2014-11-14 16:06 | -21 | 2014-11-05 14:11 | Civil - Kerbs | 3000 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Travellers site tarmac access road kerb damaged in a number of locations which will either need to be repaired or replaced. Homezone block paving footpath spacing between edge row of block paving and edging kerb too great in some locations. Two no. flat channel kerbs within homezone block paving road misaligned and not straight at road gully point.
| 03SR - Stations (RfL) | Cxxx-NCR-000261 | NCR | Eleanor Street Travellers Site Plot D Parking Bay and Plot C Concrete Yard Slab Rebar Rust Staining |  | Contr | SKC | ELS - Eleanor Street Shaft (Central) |  | 2014-11-28 | 2014-11-21 13:36 | -7 | 2014-11-05 14:18 | Civil - Civil Engineering General | 2000 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Travellers site plot D parking bay and plot C concrete yard slab rebar rust staining where rebar mesh and been stored on both parking bay and concrete yard slab with no protection underneath during wet weather conditions.
| 03SR - Stations (RfL) | Cxxx-NCR-000263 | NCR | Two damp SIP panels installed to Plot B, one on the roof and one on the Utility room. |  | Contr | SKC | ELS - Eleanor Street Shaft (Central) |  | 2015-03-02 | 2015-02-26 09:36 | -4 | 2014-11-12 16:44 | Civil - Structural Engineering | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Two damp SIP panels were nstalled on to Plot B, one on the roof and one on the Utility room.
| 03SR - Stations (RfL) | Cxxx-NCR-000264 | NCR | Waterproofing detail omitted/changed from Mile End Shaft construction drawing |  | Contr | SKC |  |  | 2015-02-23 | 2015-02-11 14:55 | -12 | 2014-11-17 19:25 | Shafts - Shafts General | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Drawing Cxxx-MMD-C4-DDD-CR094_SH006-00012 termination Detail 1 was not installed as per this detail with a stainless steel strip. The waterproofing detail in this area was coordinated with Cxxx/Cxxx/Cxxx via PTR (Cxxx-RFI-000329), submitted, approved and then constructed as per this RFI detail. The stainless steel plate in termination detail 2, was not installed as per this detail. The stainless steel plate was moved down towards the collar end of the adit as agreed in Cxxx-FCD-000270.
| 03SR - Stations (RfL) | Cxxx-NCR-000265 | NCR | Headhouse Walls Finish - Minor Defects |  | Contr | SKC |  |  | 2015-07-13 | 2015-06-30 11:29 | -13 | 2014-12-04 16:16 | Structural Engineering - Concrete Member | 2000 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Generally the struck finish to the headhouse walls is of a good and acceptable standard in accordance with Cxxx-JUL-S-RSP-CR094_SH006_Z-50001. However in localised areas there are minor defects which require repair. Internal faces - some areas of minor localised honeycombing/blow holes, grout loss at construction joints and some localised staining to concrete face from initial use of shutters. External Faces - minor honeycombing/blowhoels, grout loss at joints and minor damage to concrete at some ties holes. Example photos attached
| 03SR - Stations (RfL) | Cxxx-NCR-000266 | NCR | Concrete Defects - Headhouse Wall Radius Wall section 1 |  | Contr | SKC |  |  | 2015-03-02 | 2015-02-27 16:26 | -3 | 2014-12-04 17:02 | Structural Engineering - Concrete Member | 2000 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During a post pour inspection of the first section of the front headhouse radius wall, the following defects have been found: 1) The soffit of the large opening on gridline 3 has deflected by approx. 30mm at the centre 2) The edge of the louvre opening next to gridline 2, has a local defect (see photo attached) 3) Below the louvre on gridline 2 there are some local areas of exposed aggregate
| 03SR - Stations (RfL) | Cxxx-NCR-000267 | NCR | Flow tests for concrete shaft base pour outside of specified range |  | Contr | SKC | ELS - Eleanor Street Shaft (Central) |  | 2015-03-09 | 2015-03-05 09:51 | -4 | 2014-12-03 19:28 | Materials - General | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | During the pouring of the first lift of the Eleanor Street shaft base, flow tests were completed prior to the discharge of the concrete delivery wagons. These flow tests were outside of the specified range.
| 03SR - Stations (RfL) | Cxxx-NCR-000269 | NCR | Early Age Strength Results - Eleanor Street Adits IE1 |  | Contr | SKC | ELS - Eleanor Street Shaft (Central) |  | 2015-01-26 | 2014-12-19 09:23 | -38 | 2014-12-02 17:43 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During spraying of the P2 IE1 crown, there was a small peel of SCL from the crown, measuring 0.5x0.5x0.15m. When this peel occured spraying of the permanenet works was stopped and a test panel sprayed. Early age strength testing was conducted in accordance with KT20. The reuslts of early age strength testing did not reach the requirements of the specification within an hour.
| 03SR - Stations (RfL) | Cxxx-NCR-000270 | NCR | __ commenced lift manufacture without a valid ITP |  | Contr | SKC |  |  | 2015-07-20 | 2015-06-11 14:36 | -39 | 2014-12-05 09:45 | Mechanical - Lifts | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | __ started to manufacture the lift for Mile End Shaft following recieving an instruction to commence production from the CRL Project Manager. This NCR has been raised as there wasn't a valid ITP in place at the start of production
| 03SR - Stations (RfL) | Cxxx-NCR-000271 | NCR | Insufficient thickness of SCL IA2 |  | Contr | SKC | ELS - Eleanor Street Shaft (Central) |  | 2015-03-02 | 2015-02-12 12:36 | -18 | 2014-12-10 16:50 | Tunnelling - Linings - Sprayed Concrete | 2000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | IA2 advance 9b invert was sprayed on day shift 8/12/14. During DS 9/12/14 the leading edge was proof drilled. It was found that the leading edge would not have a sufficient spray thickness for stoppages over 72hours.
| 03SR - Stations (RfL) | Cxxx-NCR-000272 | NCR | Use of C50/60 Concrete for Roof Slab |  | Contr | SKC |  |  | 2015-02-23 | 2015-02-20 10:09 | -3 | 2014-12-18 16:36 | Structural Engineering - Concrete Member | 3000 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Cxxx-JUL-S-DDJ-CR094_SH006-00010 - C02 States that all reinforced concrete elements are to be C32/40. However the C50/60 approved in material compliance record number Cxxx-SKC-C-LRC-CR094_WS109-50098 was used to form the roof slab, to achieve an earlier striking time.
| 03SR - Stations (RfL) | Cxxx-NCR-000273 | NCR | Use of concrete with out of specification workability |  | Contr | SKC |  |  | 2015-03-02 | 2015-02-27 14:14 | -3 | 2014-12-18 16:37 | Structural Engineering - Concrete Member | 2000 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | External Phenomenon - Other | Completed |  | The concrete used for the roof slab is of a S3 workability, which should have a slump of between 90-170mm in accordance with the ITP. When pouring the lower roof slab the first 3 loads of concrete that arrived to site were rejected as they had a slump of 220 to 240mm. The batcher was contacted and the cause was due to the additive used to achieve DC-4 sulphate resistance, the concrete when batched had a slump of approx. 35mm. The batcher then reduced the load size from 8m3 to 7m3 to try and bring the slump back into spec. However the next load received remained at a 220mm slump and was rejected. A 5th load of concrete was then received with a 220mm slump, the batcher was contacted again and stated it was not possible to batch the concrete any drier at the batching plant. As a result the concrete was used. All following loads of concrete were within the specification requirements. Updated 24/01/2015: Further Details as requested by Cxxx 1no. 7m3 batch of concrete was affected, location indicated within package attached See attached 28day cube results from this batch which show the concrete achieved the design requirements. There have been no signs of segregation of the concrete, if the concrete had segregated and the aggregate was not uniformly distributed there would be surface cracks due to the higher amount of cement paste in the upper layers which have not been observed (post pour inspection photos attached). Although the concrete slump was out of spec the concrete did not continue to flow after the slump test was completed which also gives an indication that the concrete did not segregate (slump test photo attached).
| 03SR - Stations (RfL) | Cxxx-NCR-000274 | NCR | Area of SCL broken out for tunnel drainage sleeve |  | Contr | SKC | ELS - Eleanor Street Shaft (Central) |  | 2015-01-17 | 2015-01-06 12:18 | -11 | 2014-12-18 07:46 | Shafts - Shafts General | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | A small area of 0.09m2 SCL was broken out within the SCL shaft at Eleanor street. This was due to the fact the sleeve for the installation of the eastbound track drainage was set 300mm to high.
| 03SR - Stations (RfL) | Cxxx-NCR-000275 | NCR | Pile Static Load Test |  | Contr | SKC |  |  | 2015-03-16 | 2015-03-09 09:42 | -7 | 2014-12-18 18:53 | Geotechnical Engineering - Concrete - Bored Pile | 3000 |  | Testing and Commissioning | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | Further to Cxxx-FCD-000243, static load testing was not carried out on the Mile End Headhouse piles as stated in clause Cxxx-JUL-S-RSP-CR094_SH006_Z-50001 - KP10.2204. This was due to health and safety concerns relating to the method of testing and available space on site.
| 03SR - Stations (RfL) | Cxxx-NCR-000276 | NCR | Use of hammer in anchors for internal drainage |  | Contr | SKC |  |  | 2015-06-29 | 2015-06-25 16:38 | -4 | 2015-01-14 17:33 | Materials - General | 3000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | To install the shaft internal drainage, hammer in anchors have been used to secure the unistrut supporting the drainage pipes into the secondary lining. These anchors do not comply with Material and Workmanship Specification JY90 (CRL1-XRL-M-RSP-CR001-50089) clause JY90.3208 d).
| 03SR - Stations (RfL) | Cxxx-NCR-000277 | NCR | Top of Ground Floor Slab Concrete Level |  | Contr | SKC |  |  | 2015-06-12 | 2015-06-10 14:57 | -2 | 2015-01-14 17:54 | Structural Engineering - Concrete Member | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The design level of the headhouse ground slab is 109.950m, however localised areas have been identifed to be up to a maximum of +10mm to - 20mm. This exceeds the specified tolerance of within 5mm of design level. This was identified during the post pour inspection.
| 03SR - Stations (RfL) | Cxxx-NCR-000278 | NCR | Eleanor Street __ security access gates fabrication started prior the assessment of documentation by __ |  | Contr | SKC | ELS - Eleanor Street Shaft (Central) |  | 2015-02-18 | 2015-02-04 10:56 | -14 | 2015-02-04 09:58 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Misunderstand the definition of the requirement | Completed |  | __ Ltd started the fabrication of Eleanor Street __ security access gates prior the assessment of the Weld Procedure Qualification records (WPQR), Weld Procedure Specifications and the Welder qualifications by __ Consulting Engineers.
| 03SR - Stations (RfL) | Cxxx-NCR-000279 | NCR | MCR- Closed Cell Foam Joint Filler |  | Contr | SKC | ELS - Eleanor Street Shaft (Central) |  | 2015-03-25 | 2015-03-06 16:08 | -19 | 2015-02-25 17:17 | Tunnelling - Tunnelling General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Information not detailed | Completed |  | MCR- Closed Cell Foam Joint Filler Cxxx-SKC-C-LRC-CR094-50112 used in the permanent works at code 3.
| 03SR - Stations (RfL) | Cxxx-NCR-000280 | NCR | Eleanor Street Travellers Site incorrect falls to paving slabs on pitch R |  | Contr | SKC | ELS - Eleanor Street Shaft (Central) |  | 2015-09-14 | 2015-09-14 12:55 | 0 | 2015-03-04 09:52 | Civil - Concrete Pavement | 3000 |  | Design | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Paving slabs situated infront of the double access doors to pitch R building do not fall the correct direction away from the door allowing surface/rain water to collect and pond instead of falling away from the building to the central yard gully drainage point.
| 03SR - Stations (RfL) | Cxxx-NCR-000281 | NCR | Eleanor Street Travellers Site Incorrect Motor Used Installing Boundary Wall Brickwork |  | Contr | SKC | ELS - Eleanor Street Shaft (Central) |  | 2015-04-13 | 2015-03-31 09:17 | -13 | 2015-03-04 10:04 | Architectural - Walls | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | During the installation to sections of the boundary wall brickwork between pitchs M & N, the incorrect motor colour was used to install the blue engineering brick course. Colour of motor that was used was yellow instead of blue/black to match the same colour engineering bricks.
| 03SR - Stations (RfL) | Cxxx-NCR-000282 | NCR | Eleanor Street Travellers Site Pitches Metal Removable Fencing Rusting & Incorrect Fixing Installed |  | Contr | SKC | ELS - Eleanor Street Shaft (Central) |  | 2015-07-03 | 2015-06-16 11:15 | -17 | 2015-03-04 10:22 | Architectural - Landscape Architectural | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | Sitewide travellers pitches metal removable fencing panels and posts are rusting and discolouring, also the incorrect fixings have been used to fix fence panel to post - anti-vandal nuts have been installed instead of standard nut & bolt arrangement.
| 03SR - Stations (RfL) | Cxxx-NCR-000283 | NCR | Eleanor Street Travellers Site Pitch G Damaged Roof Tiles Installation |  | Contr | SKC | ELS - Eleanor Street Shaft (Central) |  | 2015-05-25 | 2015-03-19 16:28 | -67 | 2015-03-04 10:32 | Architectural - Roofing & Exterior Treatment | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During the installation of pitch G roof tiles the proposed on site tiles to be used were discoloured and surface damange to the tile face through incorrect storage and protection from the weather and dust.
| 03SR - Stations (RfL) | Cxxx-NCR-000284 | NCR | Eleanor Street Travellers Site Pitch G Floor Tiles Manufacture Product Discontinue |  | Contr | SKC | ELS - Eleanor Street Shaft (Central) |  | 2015-03-31 | 2015-03-19 16:35 | -12 | 2015-03-04 11:11 | Architectural - Flooring | 3000 |  | Material | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Original floor tiles to be installed to pitch G flooring area are no longer available due to manufacture product discontinuation, closest match floor tiles to original spec installation brought to site but could not be used.
| 03SR - Stations (RfL) | Cxxx-NCR-000285 | NCR | Kwikstrut Fixings for the Mile End drainage works - MCR not approved |  | Contr | SKC |  |  | 2015-06-29 | 2015-06-24 16:48 | -5 | 2015-03-06 16:44 | Civil - Drainage | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Other management problem | Completed |  | Kwikstrut fixings were installed on the drainage risers without an approved MCR
| 03SR - Stations (RfL) | Cxxx-NCR-000286 | NCR | Mile End Drainage Risers - Ring clamp not drilled into channels |  | Contr | SKC |  |  | 2015-08-10 | 2015-06-29 09:28 | -42 | 2015-03-06 17:09 | Civil - Drainage | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Drop rods are drilled into holorib decking soffit rather than into the channels as per design.
| 03SR - Stations (RfL) | Cxxx-NCR-000287 | NCR | Mile End - North Wing Wall |  | Contr | SKC |  |  | 2015-07-20 | 2015-06-10 15:21 | -40 | 2015-03-10 17:32 | Architectural - Walls | 3000 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | After striking the shutters on the North Wing wall pour 1, it was noticed that rebar is visible in a localised area and will require repair
| 03SR - Stations (RfL) | Cxxx-NCR-000288 | NCR | KF10.3206 : Curing Protection |  | Contr | SKC | ELS - Eleanor Street Shaft (Central) |  | 2015-04-22 | 2015-04-22 16:50 | 0 | 2015-04-08 15:41 | Tunnelling - Linings - In-situ Concrete | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Curing agent not applied on concrete surface upon striking of secondary lining shuttering 'KF10.3206 notes : Section d' curing should be applied immediately after the striking of the formwork has been completed. When the formwork from Section 2 - IA1 was removed, curing was not applied immediately. Section e) Method of curing shall prevent loss of moisture from the concrete.
| 03SR - Stations (RfL) | Cxxx-NCR-000289 | NCR | Damage to shaft secondary lining reinforcement bars |  | Contr | SKC | ELS - Eleanor Street Shaft (Central) |  | 2015-06-15 | 2015-06-10 08:45 | -5 | 2015-04-16 16:44 | Shafts - Linings | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During the construction of the shaft base reinforcement bars were installed as part of the shaft wall secondary lining. During continued SCL works, these bars were damaged/bent out of alignment.
| 03SR - Stations (RfL) | Cxxx-NCR-000290 | NCR | Early striking of secondary lining shutters |  | Contr | SKC | ELS - Eleanor Street Shaft (Central) |  | 2015-04-30 | 2015-04-20 11:43 | -10 | 2015-04-16 17:22 | Tunnelling - Linings - In-situ Concrete | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The secondary lining within adit IA2 was poured 14.04.15. Prior to striking the shutters a cube is crushed at 12hrs to confirm the strength and begin striking. The cube crushed from this pour at 12hrs was slightly below the requirement for striking. The supervisor misinterpreted a communication and began to strike the shutter once this strength was achieved. Only the small striking pieces were removed. Further striking was then immediately stopped. The remainder and integral part of the shutter was not removed until the required strength was achieved.
| 03SR - Stations (RfL) | Cxxx-NCR-000291 | NCR | Insitu concrete contact grouting pipes |  | Contr | SKC | ELS - Eleanor Street Shaft (Central) |  | 2015-05-04 | 2015-04-20 11:07 | -14 | 2015-04-20 09:10 | Tunnelling - Linings - In-situ Concrete | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During the pouring of the secondary lining within adit IA1 contact grouting pipes were installed at an avergae of more than 1.5m.
| 03SR - Stations (RfL) | Cxxx-NCR-000292 | NCR | Mile End Headhouse Screed |  | Contr | SKC |  |  | 2015-07-20 | 2015-07-16 10:21 | -4 | 2015-05-07 16:38 | Architectural - Flooring | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Floor Screed in Rooms LV 1 &2, HV1 &2 and TR1 &2 has been installed. It was identified that some of the material components of the screed were not in accordance with the corresponding MCRS. Floor screed has been installed to correct tolerance and all products are in accordance with specification.
| 03SR - Stations (RfL) | Cxxx-NCR-000295 | NCR | VE3 (WEST) Invert starter bars |  | Contr | SKC | ELS - Eleanor Street Shaft (Central) |  | 2015-06-10 | 2015-06-10 14:09 | 0 | 2015-05-13 14:49 | Tunnelling - Walkways | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | VE3 West Invert starter bars - waterproof membrane was damaged at starter bar locations.
| 03SR - Stations (RfL) | Cxxx-NCR-000296 | NCR | VE2 Invert Waterbar Damage |  | Contr | SKC | ELS - Eleanor Street Shaft (Central) |  | 2015-06-10 | 2015-06-10 14:10 | 0 | 2015-05-13 14:59 | Civil - Tunnelling | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Waterbar in VE2 invert has been torn/damaged.
| 03SR - Stations (RfL) | Cxxx-NCR-000297 | NCR | VE1 invert pour - missing flow tests. |  | Contr | SKC | ELS - Eleanor Street Shaft (Central) |  | 2015-06-10 | 2015-06-10 14:12 | 0 | 2015-05-13 15:13 | Civil - Tunnelling | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Only one flow test was conducted for the VE1 invert pour (44m3 total vol).
| 03SR - Stations (RfL) | Cxxx-NCR-000298 | NCR | VE1 invert pour - missing thermo couplers |  | Contr | SKC | ELS - Eleanor Street Shaft (Central) |  | 2015-06-10 | 2015-06-10 14:14 | 0 | 2015-05-13 15:21 | Civil - Tunnelling | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Thermo couplers were not installed to the insitu pour of VE1 invert. Therefore temperature was not monitored over time.
| 03SR - Stations (RfL) | Cxxx-NCR-000299 | NCR | Grout Box Installation in IA2 |  | Contr | SKC |  |  | 2015-06-02 | 2015-05-21 13:40 | -12 | 2015-05-19 10:54 | Tunnelling - Linings - In-situ Concrete | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | It was noted in a post pour check that at 1 section of Secondary Lining in IA2 the grout boxes in the attached photographs had moved slightly out of alignment.
| 03SR - Stations (RfL) | Cxxx-NCR-000300 | NCR | Damage to blockwork in Headhouse Corridor |  | Contr | SKC |  |  | 2015-07-21 | 2015-07-02 09:57 | -19 | 2015-05-21 16:41 | Architectural - Brickworks/Blockworks | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Improper preservation of material after installation | Completed |  | Minor damage has been caused to installed blockwork in the Mile End headhouse central corridor. See attached sketch and photograph. Wall has not been damaged structurally. Wall is currently constructed to Lintel height only.
| 03SR - Stations (RfL) | Cxxx-NCR-000301 | NCR | Debris in brick facade cavity |  | Contr | SKC |  |  | 2015-07-21 | 2015-07-17 10:32 | -4 | 2015-05-22 17:55 | Architectural - Brickworks/Blockworks | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | It has been identified that mortar has fallen onto the cavity wall ties in the brickwork cavity at Mile End Headhouse façade. A glove was also found in the cavity
| 03SR - Stations (RfL) | Cxxx-NCR-000302 | NCR | Secondary lining contraction joint between IE1 and the shaft |  | Contr | SKC | ELS - Eleanor Street Shaft (Central) |  | 2015-06-18 | 2015-06-17 01:07 | -1 | 2015-05-28 14:56 | Tunnelling - Linings - In-situ Concrete | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Upon completion of the crown secondary lining in IE1 Section 13, the crown lining was found to step out further than the cast invert slab causing a step between the invert and the crown. On the left hand side this step is 80mm and on the right hand side this step is 170mm.
| 03SR - Stations (RfL) | Cxxx-NCR-000303 | NCR | Radial cracks (joints) in adit secondary lining |  | Contr | SKC | ELS - Eleanor Street Shaft (Central) |  | 2015-07-17 | 2015-06-24 15:41 | -23 | 2015-06-16 17:21 | Tunnelling - Linings - In-situ Concrete | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | A number of what appear to be radial cracks have appeared in locations to be known construction joints as detailed on Cxxx drawings. These construction joints have been constructed inline with as detailed on Cxxx drawing general notes. When these cracks first appeared crack monitors were positioned and over the period of approximately 1 month no movement has been recorded.
| 03SR - Stations (RfL) | Cxxx-NCR-000304 | NCR | MEP suspended luminaires started without an accepted Code 1 ITP |  | Contr | SKC |  |  | 2015-07-03 | 2015-06-30 10:33 | -3 | 2015-06-19 11:37 | Electrical - Lighting | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Insufficient information made available to the worker. | Completed |  | MEP suspended luminaires started without an accepted Code 1 ITP, however this was not done intentionally and due to the fact that were seeking acceptance for the sample installation from CRL Project Manager. ITP eB document number Cxxx-SKC-E-ITP-CR094_WS109-50005 Mile End Park - Installation, Inspection and Testing of Second Fix Lighting and Small Power rev 1 has been signed by Crossrail at Code 3. An ITP workshop had previously taken place with all comments discussed, agreed and the ITP amended and approved in principle. These were sample units installed to demonstrate how luminaires will be installed across the project to seek the Project Manager’s acceptance.
| 03SR - Stations (RfL) | Cxxx-NCR-000305 | NCR | MEP mounted the VRF fan coil units on the wall without an accepted Code 1 ITP |  | Contr | SKC |  |  | 2015-07-03 | 2015-06-23 14:30 | -10 | 2015-06-19 11:44 | Mechanical - Heating Ventilation & Air Conditioning | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | MEP mounted the VRF fan coil units on the wall without an accepted Code 1 ITP, however this was not done intentionally and due to the fact that were seeking acceptance for the sample installation from CRL Project Manager. ITP eB document number Cxxx-SKC-M-ITP-CR094_WS109-50002 Mile End Park - Installation, Inspection, Testing and Commissioning of VRF DX Cooling System rev 1 has been signed by Crossrail at Code 3. An ITP workshop had previously taken place with all comments discussed, agreed and the ITP amended and approved in principle. These were sample units installed to demonstrate how the DX units will be installed across the project to seek the Project Manager’s acceptance.
| 03SR - Stations (RfL) | Cxxx-NCR-000306 | NCR | Joint Crack in Secondary Lining |  | Contr | SKC |  |  | 2015-07-06 | 2015-07-01 10:59 | -5 | 2015-06-22 15:26 | Tunnelling - Linings - In-situ Concrete | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | External Phenomenon - Other | Completed |  | A radial crack has appeared in IA2 in a construction joint location. These construction joints have been constructed inline with as detailed on Cxxx drawing general notes. Crack monitors have been positioned and over the period of approximately 1 week no movement has been recorded.
| 03SR - Stations (RfL) | Cxxx-NCR-000307 | NCR | MEP Fire Main installation started using a Preliminary (P0X) Status and not issued for Construction (IFC) drawings |  | Contr | SKC |  |  | 2015-09-30 | 2015-09-23 14:58 | -7 | 2015-06-24 10:29 | Mechanical - Piping | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Design Problem - Use of unapproved drawings | Completed |  | It was identified during the site visit that a number of drawings appropriate to the Fire Main installation were a Preliminary (P0X) Status and not Issued for Construction (IFC) and accepted by Crossrail on eB.
| 03SR - Stations (RfL) | Cxxx-NCR-000308 | NCR | Damage to galvanisation on hollorib decking soffit |  | Contr | SKC |  |  | 2016-02-01 | 2016-04-21 15:39 | 80 | 2015-06-26 12:24 | Architectural - Ceilings & Soffits | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | During the cleaning of the holorib decking in various locations throughout the shaft and headhouse, due to the use of a grinder the galvanisation has been potentially damaged. It is currently unknown whether or not the minimum thickness standard of the galvanisation has been breached. will compile a report summarizing the thickness of the galvanisation in each potentially damaged location and check if it meets the required standard. Evidence of an acceptable thickness will be provided from the manufacturer also.
| 03SR - Stations (RfL) | Cxxx-NCR-000309 | NCR | Shaft secondary lining - High level quadrant between IE1 and VA6 |  | Contr | SKC | ELS - Eleanor Street Shaft (Central) |  | 2015-08-27 | 2015-08-20 09:12 | -7 | 2015-07-09 15:43 | Shafts - Linings | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Shaft secondary lining (Quadrant 2) poured using high level EFCO with VA6 is out of tolerance by up to -11.8mm in localised areas. The finished surface must be within 0mm - > +35mm See attached photos and sketch.
| 03SR - Stations (RfL) | Cxxx-NCR-000310 | NCR | Potential Clearance Issue between Indoor AC Unit and CMS within the Mile End Head House LV A Room. |  | Contr | SKC |  |  | 2015-08-28 | 2015-08-25 07:02 | -3 | 2015-07-10 14:26 | Mechanical - Heating Ventilation & Air Conditioning | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Potential Clearance Issue between Indoor Fan Coil Unit and CMS within the Mile End Head House LV A Room, due to the installation MEP team not following the ITP (Cxxx-SKC-M-ITP-CR094_WS109-50002) for Installation, Inspection, Testing and Commissioning of VRF DX Cooling System section 3 - Construction Activities, items 3.1, 3.2 and 3.3 to identify and check location is available/cleared.
| 03SR - Stations (RfL) | Cxxx-NCR-000311 | NCR | Scratch to Door Frame - Level B1 |  | Contr | SKC |  |  | 2018-11-30 | 2018-11-15 19:18 | -15 | 2015-07-13 17:31 | Architectural - Doors | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Improper preservation of material after installation | Completed |  | A door frame on level B1 was noticed to have a scratch prior to installation. Update 28/07/2017 The Employer is referred to the Doors and Louvres handover records (last page of Cxxx-SKC-O4-LRC-CR094_WS109-50075) that details the joint inspection undertaken with the Employer in an effort to identified the doors to be repaired.
| 03SR - Stations (RfL) | Cxxx-NCR-000312 | NCR | Damage to the E/B Fire main - Level B2 |  | Contr | SKC |  |  | 2015-08-17 | 2015-08-05 14:02 | -12 | 2015-07-13 17:33 | Systems - Fire Detection systems and Mains | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | External Phenomenon - Other | Completed |  | Damage to the E/B Fire main on level B2.
| 03SR - Stations (RfL) | Cxxx-NCR-000313 | NCR | Eleanor Street Adits Drainage |  | Contr | SKC | ELS - Eleanor Street Shaft (Central) |  | 2015-10-30 | 2015-10-29 11:40 | -1 | 2015-08-04 16:06 | Civil - Drainage | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Cxxx-FCD-000348 refers to the drainage details shown on Cxxx-JUL-P-DDA-CR094_SH007-00534. These drainage details were not installed within the Cxxx designed in situ concrete works within the VE or VA adits. Based on the 'Typical Floor Channel to Adit' detail, of a 300mmx50mm channel, shown on Cxxx-JUL-P-DDA-CR094_SH007-00534 it was not feasible to install these drainage channels during construction of the adit secondary lining as the formwork system requires construction and anchorage on a flat level slab, at the point of the drainage channel. Formwork detail shown on Cxxx-SKC-C-CER-CR094_WS110-50037. Further to this mesh reinforcement has been installed on the top face of all invert concrete at a cover of 50mm, as detailed within Cxxx drawings. Cxxx-MMD-C4-DDD-CR094_SH007-06058, Cxxx-MMD-C4-DDD-CR094_SH007-06065. Both cases demonstrate that it was not feasible to install the proposed Cxxx drainage channels shown on Cxxx-JUL-P-DDA-CR094_SH007-00534.
| 03SR - Stations (RfL) | Cxxx-NCR-000314 | NCR | Secondary Lining - Concrete Drying Shrinkage Results |  | Contr | SKC | ELS - Eleanor Street Shaft (Central) |  | 2015-08-18 | 2015-08-03 14:36 | -15 | 2015-07-28 12:30 | Tunnelling - Linings - In-situ Concrete | 500 |  | Testing and Commissioning | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Secondary lining concrete drying shrinkage results, some individually are outside the requirements. However, taking an average of all the results the requirement is met (see attached summary of results).
| 03SR - Stations (RfL) | Cxxx-NCR-000315 | NCR | Secondary Lining - Concrete Drying Shrinakge Results |  | Contr | SKC |  |  | 2015-09-14 | 2015-08-03 14:09 | -42 | 2015-07-20 16:34 | Tunnelling - Linings - In-situ Concrete | 500 |  | Testing and Commissioning | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Secondary lining concrete drying shrinkage results, some individually are outside of the requirements. See attached summary of results.
| 03SR - Stations (RfL) | Cxxx-NCR-000316 | NCR | Excess Galvanisation on staircase landings |  | Contr | SKC |  |  | 2016-03-21 | 2016-03-09 09:14 | -12 | 2015-08-11 15:05 | Architectural - Finishes | 500 |  | Material | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Contamination | Completed |  | There is excess galvanisation pooled in the underside of some staircase landings, on the installed staircase at Mile End. Please see attached photographs and table of locations
| 03SR - Stations (RfL) | Cxxx-NCR-000317 | NCR | Exposed reinforcement in core hole |  | Contr | SKC |  |  | 2016-04-04 | 2016-04-04 22:08 | 0 | 2015-08-11 17:20 | Civil - Structural Engineering | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Due to the requirement for certain penetrations though the RC Concrete, core holes were drilled to accommodate this but in some instances reinforcement bars were exposed. Locations are as follows: • Location 1: 2no. 120mm Core holes through the concrete on the façade of the headhouse to allow for the temporary power cables (5no. 44mm diameter) to enter the headhouse. • Location 2: 40mm diameter penetrations to allow for conduit to come through the wall on B8 (This was in various locations on each floor of the shaft and due diligence was taken to avoid hitting reinforcement by the use of a scanner. It was found that on B8 in one location rebar was accidentally exposed) • Location 3: 2no. openings (100mm x 290mm) to allow for __’s MAP panel trunking and wiring on Level B00. See Sketches/drawings attached.
| 03SR - Stations (RfL) | Cxxx-NCR-000318 | NCR | North Wing Wall - Concrete Pour |  | Contr | SKC |  |  | 2015-09-10 | 2015-09-04 15:19 | -6 | 2015-08-14 15:08 | Civil - Civil Engineering General | 500 |  | Material | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Contamination | Completed |  | Whilst pouring the final section of the North wing wall, the 11m of concrete required to complete the works was split into two loads, one of 5.5m and one of 6m. The 5.5m concrete wagon's concrete was within the specification required, therefore the pour was accepted and concreting commenced. When the second wagon arrived with the 6m load, the concrete was tested and it fell outside of the required specification, therefore it was rejected and sent away. As the pour was late in the day, the concrete batching plant could not be contacted and therefore there was no way of getting more concrete to the site to finish the wing wall. It was subsequently left with only the 5.5m of concrete in the wall, as opposed the the 11.5 required.
| 03SR - Stations (RfL) | Cxxx-NCR-000319 | NCR | Cxxx Materials check (ventilation system) |  | Crossrail | XRL |  |  | 2015-11-26 | 2015-11-04 16:17 | -22 | 2015-09-14 17:12 | Mechanical - Heating Ventilation & Air Conditioning | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Design Problem - Error in equipment or material selection | Completed |  | Staircase Pressurisation fans ref. no. MES-PF-01A/B have been examined during the surveillance. These are circular cased axial fans with variable drive speed controllers and work in the duty/stand-by arrangement. They have been designed to work in horizontal orientation in a series configuration. The fans specified in the fan schedule provided by SKC (rev5.0 dated 17.03.15) shows the following __ fan model code: AXT125DL-4FA7+1J. The technical fan data sheet provided within the MCR (doc. ref. no. CRL-MCR-000339) and approved by CRL specifies the code as AXT125CX-4K3A71. The delivery note (supplier’s confirmation number 1603073) shows that the purchased fan was in line with the above fan schedule and different to what was approved by CRL within the MCR. There is no Project Manager Instruction or Communication to clarifying this matter.
| 03SR - Stations (RfL) | Cxxx-NCR-000320 | NCR | Internal noise level |  | Crossrail | XRL |  |  | 2017-07-31 | 2017-08-01 06:02 | 1 | 2015-09-14 17:17 | Mechanical - Heating Ventilation & Air Conditioning | 500 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | The employer’s Mechanical Services Specification doc. ref. no. Cxxx-JUL-M-RSP-CR094_SH006_Z-00001ver.2.0 states under clause JY41.1302 para b) that ‘The internal noise criterion for all plant rooms is 65dBA max’. In the Contractor’s Mechanical Services Specification doc. ref. no. Cxxx-SKC-M-RSP-CR094-50001rev5.0 this clause has been omitted and instead, for the acoustic requirements section, a reference is made to the ‘D25 Noise Demonstration Report’ doc. ref. no Cxxx-SKC-T1-RGN-CR094_WS109-50056rev2.0 decal1 and in turn to the D25 Fixed Plant Installations Options Report doc. ref. no. Cxxx-SKC-C-RGN-CR094_WS109-50007rev2.0. Neither of the documents refers to the maximum noise level within a plantroom. The industry standard guideline CIBSE Guide A states that: ‘The Noise at Work Regulations 2005(66) identify two levels of daily personal noise exposure (measured in a manner similar to LAeq,T) at which actions become necessary. These levels are 80 dBA for the lower level and 85 dBA for the higher level, corresponding to advisory and compulsory requirements’. As per the __ fan data sheet the staircase pressurisation fan mentioned above generates the breakout noise of 83dBA@3m in a hemi-spherical arrangement. This does not take into account the repatriation effect in in concrete finished plantroom.
| 03SR - Stations (RfL) | Cxxx-NCR-000321 | NCR | No testing certifiaces for attenuators |  | Crossrail | XRL |  |  | 2015-11-20 | 2015-11-05 16:09 | -15 | 2015-09-14 17:21 | Mechanical - Heating Ventilation & Air Conditioning | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | The technical data provided in the MCR do not specify the codes that the silencers have been tested to prior to delivery on site. NCR eB ref. no Cxxx-NCR-000321 has been raised for not specifying the testing procedures and codes that the acoustic attenuators are conducted to.
| 03SR - Stations (RfL) | Cxxx-NCR-000322 | NCR | Mile End park, Headhouse Louvre Lugs |  | Contr | SKC |  |  | 2016-02-22 | 2016-02-05 16:02 | -17 | 2015-09-15 17:57 | Architectural - Doors | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | In relation to the Louvre's to be installed to the Head-house at Mile End Park, to the external openings of the HRU Room and Fan Room. The connection detail is anchoring the Louvre's via a lug welded to the Louvre, into the RC headwall to the Head-house, with the Lug sitting flush to the RC wall. The brick fascia to the Head-house has been installed inline with the RC headwall, the frame has then been installed inside this opening, meaning the securing lugs to the Louvre's cannot sit flush to the RC wall in which it is anchored to. A cranked Lug would need to be manufactured to achieve a flush finish between RC wall and supporting Lug, which the installer will not certify. Update 27/10: Development has progressed with __ Engineering, they will not install their louvres using packers as previously discussed. Therefore Cranked Lugs have been detailed on Fabrication drawings submitted and reviewed by Cxxx and . A concession is being applied for to install non security rated certified Louvres on the following grounds; - Due to the Brick Façade protruding infront of the RC wall at Louvre openings, the connecting lugs from the frame of the Louvres have to be cranked in order to connect to the RC wall, to maintain a flush finish with the façade. This deviates from __ Engineering’s (CRL specified supplier) standard product and therefore the certification for security rating for this product is not valid. To achieve a certified security rating on the louvres each individual louvre would have to be tested with the exact dimensions of the cranked lugs, at an approximate cost of £100k per louvre for the testing body to carry out the certification, plus the tie frame of the certification process. -In light of the above, all suppliers of Louvres would have the same stance on security rating, unable to certify a non-standard product without carrying out further testing. -__ also have a rated blast protection on their louvres which our design team have informed us is also a project requirement and another reason why __ Louvres must be used. -To engage other suppliers to develop a product that could meet the project requirements and be fully certified, is not deemed practical for program and cost.
| 03SR - Stations (RfL) | Cxxx-NCR-000324 | NCR | Pile 11 - High steel cage |  | Contr | SKC | ELS - Eleanor Street Shaft (Central) |  | 2015-11-19 | 2015-11-10 16:56 | -9 | 2015-10-02 13:51 | Civil - Geotechnical Engineering | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Pile 11 was bored short by 345mm. The pile was initially dug to full depth and the steel reinforcement cage installed. Upon installing the cage, the pile measured 345mm short leaving the steel 310mm high. It is thought that a small amount of arising had fallen back in off the auger. The piling crane driver had left for the day and therefore the cage was unable to be removed. Rather than leave the dug pile open for the evening and creating a health and safety hazard, the decision was taken to concrete the pile to the designed level. Design pile toe level - 90.000mAOD (Actual pile toe level 90.345mm) Design top of steel - 109.815mAOD (Actual top of steel 110.125mAOD) This pile was installed using the Klemm 709 mini rig.
| 03SR - Stations (RfL) | Cxxx-NCR-000325 | NCR | Pile 1 - Concrete older than 2 hours |  | Contr | SKC | ELS - Eleanor Street Shaft (Central) |  | 2016-05-09 | 2016-04-28 13:28 | -11 | 2015-10-01 11:43 | Civil - Geotechnical Engineering | 500 |  | System Defect | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | For clarity: - This NCR is for Pile 1 only. Pile 5 was installed as per Piling Specification SPERW Clause B3.5.2.4 and cube results have confirmed it is of suitable concrete strength. Pile 5 is not an NCR. - Pile 1 concerns concrete which was installed 3 hours since batching. A concrete cube was taken of the concrete at the exact time of placing it into the pile and therefore represents the strength of the concrete at 3 hours. This cube result has been crushed by our UKAS accredited testing house, __, with a 34 day compressive strength of 42.5n/mm2, this is 2.5n/mm2 stronger than the design strength. The concrete had an approved MCR (Cxxx-SKC-C-LRC-CR094_WS110-50091). No additional water was added to this concrete as shown in the attached concrete delivery tickets. propose to close this NCR based on the sufficient concrete cube results of the pile as 'use as-is', a 1m core will not show any additional information that the concrete cube hasn't already shown. Integrity testing will be carried out as per the specification during the Zone 2 groundworks next month. Previous integrity test results across the site have all returned accepted. Cxxx do not anticipate any issues will arise from integrity testing of Pile 1, however if there is, a separate NCR will be raised.
| 03SR - Stations (RfL) | Cxxx-NCR-000329 | NCR | MCRs not in place prior to installation |  | Contr | SKC |  |  | 2015-12-21 | 2015-12-15 14:11 | -6 | 2015-10-01 10:04 | Civil - Drainage | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | has identified that some MCRs for the drainage installation were not in place before the installation occurred.
| 03SR - Stations (RfL) | Cxxx-NCR-000330 | NCR | Mile End Headhouse - Facade - Dummy Joint in Coping Stones |  | Contr | SKC |  |  | 2016-01-25 | 2016-01-15 16:06 | -10 | 2015-09-30 17:40 | Architectural - Brickworks/Blockworks | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Movement joints exist in the RC Headwall to the Mile End Head-house, the movement joints have been reflected in the Brickwork Façade to match, in 3 locations the Movement joints have not been properly extended in the coping stones at the top of the façade. a groove has been chased out of the top of the coping stone, and compressible filler pressed in to the groove to give the impression of a movement joint.
| 03SR - Stations (RfL) | Cxxx-NCR-000331 | NCR | Blocked reinjectable grout tubes |  | Contr | SKC | ELS - Eleanor Street Shaft (Central) |  | 2016-06-01 | 2016-05-05 09:47 | -27 | 2015-10-01 16:47 | Tunnelling - Grouting | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Waterproofing as-builts were complete in the adits, see Cxxx-SKC-C-DWG-CR094_WS110-50220. Following this, the reinjectable grout hoses were tested by __ and witnessed by Cxxx and . Each grout hose was testing in the following procedure 1. Water was pumped through the pipe using a pump 2. This was pumped for 1 minuet or until the water had come through the pipe and out the other side 3. Where water wasn't seen coming through to the other pipe, this pipe was also tested. The results which can be seen in the attached document: Open - The grouting pipe is clear , can grout from this side OK - Both sides are clear, can grout using this line and then flush to be used again Blocked - Both sides are clear but there is a blockage in the middle, can grout from each side once only Closed - The pipe is fully blocked, no grouting can be completed here Missing - The pipe was buried during the pour, no grouting can be completed here
| 03SR - Stations (RfL) | Cxxx-NCR-000332 | NCR | Mile End Shaft - Trench Covers to Adits - Support Angles, Countersunk holes |  | Contr | SKC |  |  | 2015-10-28 | 2015-10-26 08:32 | -2 | 2015-09-30 17:49 | Architectural - Finishes | 500 |  | Manufacturing Defect | Reject | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Support angles required to install trench covers in both Adits at B8 and B9 were required to have holes to allow securing anchors with a countersunk head. Upon inspection the angles didn't have the appropriate drilled hole to allow countersunk anchor to be installed giving a flush finish for covers to sit securely.
| 03SR - Stations (RfL) | Cxxx-NCR-000333 | NCR | Damaged junction boxes |  | Contr | SKC | ELS - Eleanor Street Shaft (Central) |  | 2016-05-30 | 2016-04-25 13:30 | -35 | 2015-10-02 14:06 | Tunnelling - Grouting | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | After review of the grouting system, it was highlighted than some of the adit and shaft junction boxes were misshapen or damaged. Because of this, some of the junction box lids don't fit onto the boxes securely.
| 03SR - Stations (RfL) | Cxxx-NCR-000334 | NCR | Missing cubes results for Test Pile 1 |  | Contr | SKC | ELS - Eleanor Street Shaft (Central) |  | 2015-10-29 | 2015-10-22 08:58 | -7 | 2015-10-05 17:34 | Geotechnical Engineering - Concrete - Bored Pile | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Test Pile 1 – Unable to locate test cube results for this pile to confirm minimum concrete strength of 25N/mm2 to allow pile test to commence. 1. TP1 is a non working pile and will be redundant upon completion of test. 2. The pile test system consists of a load cell and five displacement sensors (transducers), four monitoring the pile head displacement and a fifth (safety gauge) independently monitoring the reaction frame movement with reference to the pile head. This patented system has been developed to be fully capable of operating automatically unattended in a safe manner. The system checks constantly for any potential error conditions within the test and if any are encountered will fail safe without requiring user intervention. Experienced personnel will check all tests that are running remotely at regular intervals from the operations control centre.
| 03SR - Stations (RfL) | Cxxx-NCR-000336 | NCR | Mile End Park Shaft & Headhouse - Proceeding with Issued for information drawings instead of IFC drawings |  | Contr | SKC |  |  | 2016-06-13 | 2016-07-22 13:32 | 39 | 2015-10-19 16:42 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Identified during site surveillance that drawings were For Information status and not issued for construction (IFC).
| 03SR - Stations (RfL) | Cxxx-NCR-000337 | NCR | Eleanor Street Shaft Reinforcement Detailing Core Walls/ Base to B5 Proceeding with Issued for Preliminary (P0X) Status drawings instead of IFC (Issued for Construction) drawings |  | Contr | SKC | ELS - Eleanor Street Shaft (Central) |  | 2016-03-07 | 2016-03-07 16:50 | 0 | 2015-10-20 13:49 | Structural Engineering - Reinforcement | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Use of unapproved drawings | Completed |  | Identified during Joint /CRL site surveillance that drawings were a Preliminary (P0X) Status and not issued for Construction (IFC). Due to programme criticality, a number of meetings held by , __, CRL & Cxxx to address the comments, which took a long time to have the drawings accepted/issued on time for construction. PMI has been issued by Crossrail to which allowed us to proceed with the construction using a Preliminary (P0X) Status drawings.
| 03SR - Stations (RfL) | Cxxx-NCR-000338 | NCR | Mile End Shaft and Headhouse - Head Restraints to Blockwork Walls |  | Contr | SKC |  |  | 2015-11-25 | 2015-11-25 08:34 | 0 | 2015-10-28 07:25 | Architectural - Brickworks/Blockworks | 500 |  | Incomplete Works | Rework | 4 (0.5-3k) | Complete | Design Problem - Change to drawings not provided on time | Completed |  | During a surveillance inspection by it was noted that head restraints had not been installed to some Blockwork walls in Mile End Shaft and Headhouse.
| 03SR - Stations (RfL) | Cxxx-NCR-000339 | NCR | Mile End Shaft and Headhouse - Bearing of Installed Head restraints to Blockwork |  | Contr | SKC |  |  | 2016-10-31 | 2016-11-18 13:11 | 18 | 2015-10-28 08:01 | Architectural - Brickworks/Blockworks | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | During a surveillance inspection by of the Blockwork walls in the Mile End Shaft and Headhouse, it was noted that some of the installed head restraints to the Blockwork walls did not have full bearing on the Blockwork.
| 03SR - Stations (RfL) | Cxxx-NCR-000340 | NCR | Mile End Headhouse - Green Roof - Subsoil and subsequent layers |  | Contr | SKC |  |  | 2016-12-05 | 2016-12-06 10:56 | 1 | 2015-10-30 15:47 | Architectural - Landscape Architectural | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Construction of the Green Roof at Mile End Headhouse is currently underway, the documentation being used to construct is currently at "Issued for Contractor Design". The build up of the green roof layers are indicated on these drawings but the detail to be constructed requires documenting. As such the materials being used are not able to be submitted for MCR approval, due to the documentation not being in place to approve against, notably the subsoil being used.
| 03SR - Stations (RfL) | Cxxx-NCR-000341 | NCR | External Drainage - Manhole cover constructed without minimum requirement of 1 course of bricks |  | Contr | SKC |  |  | 2015-11-30 | 2015-11-25 14:57 | -5 | 2015-10-28 13:46 | Civil - Drainage | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Manhole 11 (MH11) on inspection it was noticed that the minimum requirement of 1 course of bricks was not adhered to as the manhole cover was placed directly on the biscuit.
| 03SR - Stations (RfL) | Cxxx-NCR-000342 | NCR | No Visibility of Foul Drainage in Man Hole 13 |  | Contr | SKC |  |  | 2015-12-18 | 2015-11-25 14:56 | -23 | 2015-11-09 15:02 | Civil - Drainage | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | No visibility of 'Y' junction between Headhouse foul drainage and Manhole 12 upstream. The cause of this was because to install the Non-return valve (NRV) in its designed location we had to have a complete pipe rather than one spur of the 'Y' junction meaning the visibility of the foul pipework was lost. When benching inside of manhole 13 this then covered in the one junction only the end of the 'Y' was visible.
| 03SR - Stations (RfL) | Cxxx-NCR-000343 | NCR | Mile End Shaft - IA2 - Ground Water Leakage in Adit Collar |  | Contr | SKC |  |  | 2016-05-16 | 2016-05-16 14:36 | 0 | 2015-11-17 18:07 | Civil - Tunnelling | 500 |  | System Defect | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | A leak is present in IA2 at the collar interfacing between the Adit and the running tunnel, coming from a hole in the crown the tunnel side of the temporary door in IA2.
| 03SR - Stations (RfL) | Cxxx-NCR-000344 | NCR | __ commenced UPS manufacture without a valid ITP. |  | Contr | SKC |  |  | 2016-07-18 | 2016-05-27 11:42 | -52 | 2015-11-18 09:22 | Electrical - LV Equipment | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Subcontractor Problems - Other | Completed |  | __ started to manufacture the UPS for Mile End Shaft following receiving an instruction to commence production from the CRL Project Manager (Cxxx-PMI-00440) to mitigate any potential impact to the relevant Mile End key dates. It was not clear whether the UPS is an off the shelf material or bespoke to Cxxx. This NCR has been raised as the ITP has not been issued formally via eB to Crossrail for acceptance prior manufacturing.
| 03SR - Stations (RfL) | Cxxx-NCR-000345 | NCR | Mile End Park Shaft - Earth Bars support is covered of uPVC |  | Contr | SKC |  |  | 2015-12-22 | 2015-12-16 13:39 | -6 | 2015-11-20 09:07 | Electrical - General | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | Earth Bars support installed at Mile End Shaft has the fixing base coated in PVC. Please note the Material (CRL-MCR-000541) was accepted at code 1 on the body of the document, with a reworked review comment rejected.
| 03SR - Stations (RfL) | Cxxx-NCR-000346 | NCR | Mile End Park Shaft - Fire Main A & B Thurst brackets and supports |  | Contr | SKC |  |  | 2016-06-30 | 2016-05-31 14:21 | -30 | 2015-11-20 09:23 | Mechanical - Piping | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Thrust calculations for fire mains has not been submitted for the supports/brackets. Thrust calculations for the restraint of dynamic stresses of the fire piping system has not been submitted.
| 03SR - Stations (RfL) | Cxxx-NCR-000347 | NCR | Stepney Green Shaft - Proceeding with Stage P Minigate Design Drawings instead of IFC (Issued for Construction) drawings |  | Contr | SKC |  |  | 2016-12-16 | 2016-12-08 08:40 | -8 | 2015-11-20 11:42 | Architectural - Brickworks/Blockworks | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Stepney Green Blockwork Gridline 6 to 10 Levels B1, B4, B5; Post Minigate Drawings are a Preliminary (P0X) Status and not issued for Construction (IFC). The design mini gate was agreed with CRL at the meeting held on 11/11/15, and was only subject to some conditions being meet, which will be closed out within two weeks (25/11/15). These conditions do not represent any risk to commencing the blockwork walls. Due to programme criticality, Cxxx have proceeded with construction on site on Levels B1, B4 & B5 based on Stage P agreed minigate drawings. Please refer to Cxxx-CCM-01653.
| 03SR - Stations (RfL) | Cxxx-NCR-000348 | NCR | Missing RESS Records from Eleanor Street Sub Constuction __ification Package Listing |  | Contr | SKC | ELS - Eleanor Street Shaft (Central) |  | 2016-01-29 | 2016-01-29 10:53 | 0 | 2015-12-01 09:19 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | RESS records missing from Eleanor St shaft SCL primary lining package listing (Cxxx-SKC-C-CER-CR094_WS110-50064)
| 03SR - Stations (RfL) | Cxxx-NCR-000354 | NCR | Eleanor Street Shaft core wall cast in plate welded connection |  | Contr | SKC | ELS - Eleanor Street Shaft (Central) |  | 2016-08-22 | 2016-08-22 19:57 | 0 | 2015-11-27 09:25 | Civil - Structural Engineering | 500 |  | Manufacturing Defect | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The reinforcement to cast in plate welded connection has failed during off site factory testing. Currently 18 plates have been cast in at Level B4 (lift 3). The plates for lift 4 at Level B3 has been taken back to the manufacturers for remedial action. A methodology to repair the already cast in items is currently underway.
| 03SR - Stations (RfL) | Cxxx-NCR-000355 | NCR | RC Structural openings for DBX-02 |  | Contr | SKC |  |  | 2016-01-21 | 2016-01-13 14:36 | -8 | 2015-11-27 11:32 | Architectural - Doors | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Whilst attempting to install Door02 on a number of floors in the shaft; B3, B4, B5, B7, B8, B9, it has come to our attention that there are discrepancies of between 5mm to 60mm in terms of height. According to the door schedule, the height of the opening for Door02 on each floor in the shaft should be 2300mm. See below for as built survey of the door opening: DB3-02 – 1200 x 2280 DB4-02 – 1195 x 2285 DB5-02 – 1185 x 2290 DB7-02 – 1170 x 2240 DB8-02 – 1445 x 2245 DB9-02 - 1195 x 2240 The current fabricated doors for these locations do not fit.
| 03SR - Stations (RfL) | Cxxx-NCR-000356 | NCR | Rate of rise exceedance |  | Contr | SKC | ELS - Eleanor Street Shaft (Central) |  | 2016-02-08 | 2016-01-04 14:38 | -35 | 2015-12-02 18:37 | Civil - Structural Engineering | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Information not detailed | Completed |  | The rate of rise for installing concrete was exceeded during the concrete pour of the perimeter wall for the sump as part of base plug stage 2 works at Eleanor Street Shaft. The concrete temperature was recorded at 17oC which has a designed rate of rise of 1.41m. The concrete was installed at circa 2.5m rate of rise.
| 03SR - Stations (RfL) | Cxxx-NCR-000357 | NCR | Construction drawings status and acceptance by CRL Project Manager |  | Crossrail | XRL |  |  | 2016-09-25 | 2016-09-08 19:45 | -17 | 2015-12-16 09:20 | Systems - Other | 500 |  | Documentation and Records | Repair | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | NCR has been raised to ensure that the drawings issued on site for installation are in ‘Issued for Construction’ status and have been received and accepted by the Project Manager as required in WIv2B part 7.7.8.2. For further information refer to surveillance report ref. no. Cxxx-XRL-O4-RGN-CR001-50023.
| 03SR - Stations (RfL) | Cxxx-NCR-000358 | NCR | Failure to provide evidence that the ATS equipment within the HRU Room was checked before installation |  | Crossrail | XRL |  |  | 2016-03-14 | 2016-03-14 16:04 | 0 | 2015-12-16 09:44 | Materials - General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | NCR has been raised as it was not possible to verify that the ATS equipment within the HRU Room was appropriately checked before installation and that it corresponds to the approved MCR (CRL-MCR-001686). The Contractor provided a packing note post surveillance - however this was not signed and the equipment could not be traced back to the approved MCR. For further details refer to section 5 of the surveillance report ref no. Cxxx-XRL-O4-RGN-CR001-50023.
| 03SR - Stations (RfL) | Cxxx-NCR-000360 | NCR | Missing Drainage Outlet Sleeves in IA1 |  | Contr | SKC |  |  | 2016-06-06 | 2016-06-03 11:09 | -3 | 2015-12-17 12:27 | Civil - Drainage | 500 |  | Incomplete Works | Repair | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | As per drawing Cxxx-OVE-C4-DDA-CR001_Z-50004 and Cxxx-OVE-C4-DDA-CR001_Z-50006, the drainge sleeves as outlined in the attached drawings were not installed during the concrete pour of the trenches in IA1. As a result, there is nowhere for the drainage channels in both trenches on IA1 to drain off.
| 03SR - Stations (RfL) | Cxxx-NCR-000362 | NCR | Missing __ around Doors |  | Contr | SKC |  |  | 2016-05-16 | 2016-03-29 07:07 | -48 | 2015-12-18 08:12 | Architectural - Doors | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | As per drawing Cxxx-SKC-A-DDD-CR094_SH006_S-00728, the packing between the intumescent mastic around the door frames was not installed.
| 03SR - Stations (RfL) | Cxxx-NCR-000363 | NCR | Pile 12 damaged during pile cropping |  | Contr | SKC | ELS - Eleanor Street Shaft (Central) |  | 2016-01-29 | 2016-01-29 19:57 | 0 | 2015-12-22 12:51 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During the cropping of Pile 12 a 300mm(w) x 200mm(h) x 50mm(d) section of concrete broke off below the designed cut off level. Annotated photo's attached.
| 03SR - Stations (RfL) | Cxxx-NCR-000364 | NCR | Cast iron pipe to clay pipe connection - Base drainage |  | Contr | SKC | ELS - Eleanor Street Shaft (Central) |  | 2016-02-29 | 2016-02-25 12:31 | -4 | 2015-12-22 12:28 | Civil - Drainage | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | Cxxx have cast within mass fill concrete a band seal connection at the base of the shaft. This has connected the running tunnel clay drainage pipe from the eastbound tunnel to the cast iron pipe connected to catch pit 1 between G/L C-D & 1A-2. The band seal does not have an approved MCR. All other materials within the drainage system has a CEG Code 1 approved MCR. The band seal is cast in within over 2m of mass fill concrete all around it. Please see attached photo of connection & sketch of location.
| 03SR - Stations (RfL) | Cxxx-NCR-000365 | NCR | Thickness of galvanizing to steel brackets installed as lintels to above/sides of openings in Mile End brick façade. |  | Contr | SKC |  |  | 2016-09-30 | 2016-08-26 09:30 | -35 | 2016-01-06 09:32 | Architectural - Finishes | 500 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Galvanised steel brackets have been installed as lintels to above/sides of openings in Mile End brick façade as per Stage F design, however concern raised by RfL that the thickness of galvanising in relation to exposure rating will not meet the design life requirement for 120years.
| 03SR - Stations (RfL) | Cxxx-NCR-000368 | NCR | Low 28 day strengh - Piles 19,20,22,26 |  | Contr | SKC | ELS - Eleanor Street Shaft (Central) |  | 2016-03-21 | 2016-01-25 10:36 | -56 | 2016-01-07 12:04 | Geotechnical Engineering - Concrete - Bored Pile | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | Piles 19, 20, 22, 26, TP1 5 no. piles at Eleanor Street Shaft have not met 28 day concrete strength (40N/mm2). All piles achieved required concrete strength after 56 days. Pile 19: 56 days strength = 42.5N/mm2 Pile 20: 56 days strength = 44.3N/mm2 Pile 22: 56 days strength = 41.3N/mm2 Pile 26: 56 days strength = 42.1N/mm2 TP1: 56 days strength = 44.0N/mm2
| 03SR - Stations (RfL) | Cxxx-NCR-000369 | NCR | Eleanor St - Below Head house drainage design - By Exception Technical Assurance Process |  | Contr | SKC | ELS - Eleanor Street Shaft (Central) |  | 2017-03-27 | 2017-03-27 15:59 | 0 | 2016-01-11 15:01 | Civil - Drainage | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | In order to meet the Eleanor Street construction programme the design technical assurance of the 2No. drainage drawings has been obtained through the CRL By Exception process (CRL1-XRL-O7-GPD-CR001-50023). Refer RiR ref Cxxx-SKC-C-LRC-CR094_WS110-50116 Rev 3 for drawing details/references. Refer completed Technical Assurance By Exception Gate Risk Assessment form (Cxxx-SKC-D-RGN_WS110-50001 Rev 1.0) appended to this NCR.
| 03SR - Stations (RfL) | Cxxx-NCR-000370 | NCR | Stepney Green - Blockwork between GL 6-10 - By Exception Technical Assurance Process |  | Contr | SKC |  |  | 2017-11-30 | 2017-11-16 14:35 | -14 | 2016-01-20 08:44 | Civil - Civil Engineering General | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | In order to meet the Stepney early access construction programme the design technical assurance of blockwork drawings between GL 6-10 has been obtained through the CRL By Exception process (CRL1-XRL-O7-GPD-CR001-50023). Refer RiR ref Cxxx-SKC-Z-LRG-CR094_WS108-50001 Rev 2.0 for drawing details/references. Refer completed Technical Assurance By Exception Gate Risk Assessment form (Cxxx-SKC-C-RGN-CR094_WS108-50008 Rev 1.0) appended to this NCR.
| 03SR - Stations (RfL) | Cxxx-NCR-000371 | NCR | Numerous PTRs had not been referenced on appropriate Redline Drawings or within the package listings as required by the ‘Management of Redlines’ procedure and Works Information. |  | Crossrail | XRL |  |  | 2016-06-06 | 2016-06-06 11:51 | 0 | 2016-01-20 09:46 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | During a planned Crossrail surveillance undertaken on 15th December 2015 and 11th January 2016 which looked at documentation surrounding Shaft and SCL package listings, it was identified that numerous PTRs had been missed from either the referenced Redline drawings or the detailing under package listing Section 4 ‘Construction/Installation Records’. A summary of the PTRs not marked up or referenced is detailed below: Package Listing - Cxxx-SKC-C-LST-CR094_WS109-50005 RFI *66 detailing had been marked up on drawing Cxxx-OVE-C4-DDD-CR001_Z- *23751 (X01) but the RFI number had been omitted. As the number had been omitted this provided no traceability to the PTR where the mark up had been agreed. Package Listing - Cxxx-SKC-C-CER-CR094_WS109-50019 FCD *94 was marked on drawing Cxxx-MMD-C4-DDB-CR094_SH006-02020 (X03) however was missing from the package listing, and NCRs *100 and *117 which relate to the design drawings had not been referenced on the relevant Redline drawing(s). Package Listing - Cxxx-SKC-C-CER-CR094_WS109-50032 The following PTRs which were referenced on the relevant Redline drawing(s) were missing from the package listing; NCRs *186, *208, *191 and RFI *164. Further more, the following PTRs had been referenced in the package listing but had been missed from the relevant Redline drawings; RFI *133, FCD *66 and *264. Package Listing - Cxxx-SKC-C-CER-CR094_WS110-50033 A number of PTRs had been referenced on Redline drawing Cxxx-OVE-C4-DDD-CR001_Z-23811 (X01) but were not recorded in the package listing. Following clarification, it was detailed that drawing *23811 is also applicable to package listing *50064, where the PTRs should be referenced, as such the package listings require revising. Additionally, RFI *227 which is noted on Redline drawing Cxxx-SKC-C-DWG-CR094_WS110-50125 (X02) was missing from the package listing. Package Listing - Cxxx-SKC-C-CER-CR094_WS110-50064 RFI *74 and FCD *246, had both been recorded in the package listing had not been referenced on the Redline drawing(s) where appropriate. It was also detailed that RFI *336 and FCD *236 required adding to the package listing as they had not been recorded. Works Information Vol 2B clause 13.3.6.1 states “The Contractor shall manage the Redline process in accordance with the Management of Redlines Procedure” and “The IFC drawings shall be marked up (i.e. Redlined)….”. Management of Redlines and As Builts Procedure clauses 3.9 states “The Redline must reference the appropriate full PTR document (RFI, NCR, FCD).” and 4.8 “The Contractor is responsible for ….. Maintaining an up to date full size working copy of IFC drawings, including annotating that copy up with any changes to the installed condition, including references to the relevant RFI/NCR/FCDs.” This NCR was raised resulting from the surveillance to ensure the reviewed listings, as detailed above, are revised accordingly, and that a review is undertaken on all other listing not covered by the surveillance to check for completeness, including the procedure and process for marking up Redline drawings.
| 03SR - Stations (RfL) | Cxxx-NCR-000372 | NCR | Submission of Factory Acceptance Test Procedure for LV panels not prior to commencement of Testing |  | Contr | SKC |  |  | 2016-02-25 | 2016-02-16 15:32 | -9 | 2016-01-26 11:52 | Electrical - LV Equipment | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | The Factory Acceptance tests for the main LV panels were carried out as per documents ref Cxxx-SKC-E-RGN-CR094_WS109-50005 (LV panel A) and Cxxx-SKC-E-RGN-CR094_WS109-50006 (LV panel B). However, the above tests were completed without a formal acceptance of the FAT procedures by CRL. The FAT procedures were not accepted by CRL prior to commence of the tests. The stage 1 of these tests were witnessed and signed by CEG representative Neville Leary.
| 03SR - Stations (RfL) | Cxxx-NCR-000373 | NCR | Installation of Tiles in WC |  | Contr | SKC |  |  | 2016-03-31 | 2016-03-14 16:15 | -17 | 2016-02-01 15:25 | Architectural - Sanitary Fittings | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Use of unapproved materials | Completed |  | Works commenced on the installation of the floor tiles in the W.C before the change in tile type was approved by Crossrail in Cxxx-FCD-000451.
| 03SR - Stations (RfL) | Cxxx-NCR-000374 | NCR | Sump house roof slab thickness |  | Contr | SKC | ELS - Eleanor Street Shaft (Central) |  | 2016-02-29 | 2016-02-26 10:37 | -3 | 2016-02-04 11:24 | Civil - Structural Engineering | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | F.A.O Cxxx Cxxx Sump Details II design intent (Cxxx-JUL-S-DDD-CR094_SH007-00427 Rev C01) details "250mm thk concrete slab + 50mm deep holorib decking" for the sump house roof slab. Cxxx reinforcement detail design Level B5 -Roof (Cxxx-SKC-C-DWG-CR094_WS110-50198 Rev 04) was given Code 1 on 03/12/15 and details a 200mm thick RC slab. Cxxx have already installed couplers for the 200mm thick slab and the accepted reinforcement is on site ready to be installed. Reinforcement is as per design intent, with a reduction of 50mm concrete only. Cxxx propose to keep the 200mm thick reinforced concrete roof slab as per the accepted detail design.
| 03SR - Stations (RfL) | Cxxx-NCR-000375 | NCR | Emergency Distribution Boards - 1 hour fire barrier |  | Contr | SKC |  |  | 2016-09-12 | 2016-08-10 12:39 | -33 | 2016-02-04 16:28 | Electrical - LV Equipment | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Potential not compliance with requirements JY71.1201 clause n of Mile End Park Shaft Electrical Systems Specification (Cxxx-SKC-E-RSP-CR094_WS109-50001 rev 5.0). As per above clause, “the emergency electrical cupboard shall be constructed to provide a 1 hour fire barrier from A and B electrical cupboards.” The current design states the requirement of the fire rated enclosure for EDB-2, EDB-3 & EDB-4. However, the installed emergency electrical cupboards does not provide 1 hour fire rating barrier for EDB-2, EDB-3 & EDB-4.
| 03SR - Stations (RfL) | Cxxx-NCR-000376 | NCR | Mile End Shaft - LV Submain Cables Installation |  | Contr | SKC |  |  | 2016-03-16 | 2016-02-16 15:35 | -29 | 2016-02-11 09:59 | Electrical - Power Distribution | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | A discrepancy between the Electrical Services Schedule Cxxx-SKC-E-RSP-CR094_WS109-50002 and the Cxxx Electrical LV Distribution Schematic (F2 Detail) Cxxx-SKC-E-DWG-CR094_WS109-50037 caused the A16/B16 and A17/B17 ATS cable pairs to be inverted: - A16/B16 should be terminated in the PFR ATS as per Cxxx-SKC-E-DWG-CR094_WS109-50037 . Instead they were terminated in the FAN ATS as shown on the attached marked up drawing. - A17/B17 should be terminated in the FAN ATS as per Cxxx-SKC-E-DWG-CR094_WS109-50037 . Instead they were termninated in the PFR ATS the attached marked up drawing.
| 03SR - Stations (RfL) | Cxxx-NCR-000377 | NCR | Shaft Base - Sump House Walls - Void in wall after concrete pour |  | Contr | SKC | ELS - Eleanor Street Shaft (Central) |  | 2016-03-23 | 2016-03-18 10:38 | -5 | 2016-02-10 08:51 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | After the removal of the sump wall shutters in the base of Eleanor street shaft, 1no large & 1no small void were found within the wall 5 (or wall 11 as per __'s design). The large void extends through the wall exposing the reinforcement. See attached photos. No voids were found within the other walls.
| 03SR - Stations (RfL) | Cxxx-NCR-000378 | NCR | MCR missed for Installation of Mastic Movement Joints on Brick Façade |  | Contr | SKC |  |  | 2016-03-01 | 2016-02-23 09:02 | -7 | 2016-02-16 11:41 | Architectural - Roofing & Exterior Treatment | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | Following the approval of Cxxx-FCD-000428, an MCR was not submitted before __Hyflex 250 Facade was installed.
| 03SR - Stations (RfL) | Cxxx-NCR-000379 | NCR | MCRs not in place before installation of the Balustrade |  | Contr | SKC |  |  | 2016-03-31 | 2016-02-24 16:45 | -36 | 2016-02-24 08:55 | Architectural - Balustrade | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | MCRs (Cxxx-SKC-C-LRC-CR094-50202, 50203, 50133) were submitted, and due to eB transmittal issues not accepted Code 1 prior to installation of the Balustrade at Mile End Park.
| 03SR - Stations (RfL) | Cxxx-NCR-000380 | NCR | PVC hose from condensate pump not compliant to LU 1-085 standard |  | Contr | SKC |  |  | 2016-04-28 | 2016-04-25 09:33 | -3 | 2016-03-02 16:34 | Mechanical - Mechanical Engineering General | 500 |  | Design | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Information not detailed | Completed |  | Braided PVC tube from condensate pump to condensate drain exceeds the plastic weights limits contained within 1-085 Standard over 500 mm linear lenght.
| 03SR - Stations (RfL) | Cxxx-NCR-000381 | NCR | Stepney Green Internal Shaft - Level B4 PR Riser Room Dimension |  | Contr | SKC |  |  | 2017-12-15 | 2017-12-08 08:33 | -7 | 2016-03-07 14:34 | Architectural - Brickworks/Blockworks | 1000 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Not Defined | Completed |  | To allow the blockwork to be laid around the edge of the constructed floor slab openings on B4 in the PR riser, wall 33 has been extended. This reduces the spacing between the PR Riser and Comms 1 Riser to 1050 mm, rather than 1215 mm, as stated by the drawings. This can be seen highlighted on the attachment. This affects the space available for passengers of reduced mobility which will not be large enough. 31/08/17 - Level B4 refuge area redesigned to accommodate asbuilt Cxxx and agreed penetrations for pipework, this also ensure minimum required dimensions for the PRM is achieved. Refer latest drawing which shows agreed arrangement/details, ref: Cxxx-SKC-A-DDD-CR094_SH005_Z-00758.
| 03SR - Stations (RfL) | Cxxx-NCR-000382 | NCR | Pouring B4 lobby slab without an approved design |  | Contr | SKC | ELS - Eleanor Street Shaft (Central) |  | 2016-05-23 | 2016-05-19 13:17 | -4 | 2016-03-08 18:04 | Civil - Structural Engineering | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | On 01/03/16 Cxxx poured B4 lobby slab. The works had an approved RAMS, ITP and temporary works design however the permanent reinforcement design was Code 3 not accepted. Rev 3 Code 3 received on 26/02/16 had no outstanding comments relating to the lobby slab area. Cxxx requested an instruction from CRL to pour the lobby slab without an approved permanent design. CRL sent email communication to on 01/03/16 at 16:14 stating that the lobby slab areas were OK to proceed based on Cxxx-SKC-C-DWG-CR094_WS110-50212 Rev 3 design and that a PMI was to follow.
| 03SR - Stations (RfL) | Cxxx-NCR-000383 | NCR | Eleanor Street Shaft cast-in galvanised plates as-built |  | Contr | SKC | ELS - Eleanor Street Shaft (Central) |  | 2016-08-22 | 2016-08-18 05:24 | -4 | 2016-03-24 17:28 | Structural Engineering - Steel Member | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | To form the structural floors within the shaft core and headhouse, cast-in plates were installed within the core walls. The orientation of some of the cast in plates on both the ventilation and intervention side are not vertically aligned. The attached sketches show the affected plates thus far and further information will follow once a full survey of all the plates is possible. This misalignment will result in the fin plates being inclined once welded and may potentially result in a misalignment with the steel beams. Also, the plate at B1 level on gridline C is out of position by 30mm at the top and 18mm at the bottom as shown on the attached picture. It is proposed to use as-is with the welded fin plates to be fabricated to a larger size than the design in order to compensate for the vertical misalignment. For example, if there is a deviation of 15mm from the bottom of the cast-in plate with respect to the top, the fin plate will be fabricated 15mm larger than the design. The fin plate will then be marked up on site to suit the inclination of the plate by the setting out engineer and trimmed by competent operatives, prior to welding. This will result in the plate being vertically aligned. Seeing as the floor beams will have holes post drilled into them for the bolts during the installation process, there will not be any misalignment issues between the fin plates and the beams. Please note that the plates will arrive on site pre-galvanised and only 20-30mm will be etched by the operatives as agreed between and CRL.
| 03SR - Stations (RfL) | Cxxx-NCR-000384 | NCR | 2no. cast-in plates not installed on lift no.9 |  | Contr | SKC | ELS - Eleanor Street Shaft (Central) |  | 2016-12-19 | 2016-12-19 12:35 | 0 | 2016-03-31 11:15 | Civil - Structural Engineering | 500 |  | Incomplete Works | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | 2no. cast-in galvanised plates have not been installed during the construction of the core wall at lift 9. These plates are to service steel beams B16 to connection 51 and beam B1 to connection 53. These plates will be installed at a later date. Further details for the repair will follow in due course.
| 03SR - Stations (RfL) | Cxxx-NCR-000385 | NCR | Fisher Street - B4 Cast-In PH - By Exception Technical Assurance Process |  | Contr | SKC |  |  | 2017-09-25 | 2017-08-17 08:54 | -39 | 2016-04-07 12:41 | Mechanical - Public Health Engineering | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | UPDATE - GATE PASS CERTIFICATE attached. In order to meet the Fisher Street construction programme the design technical assurance of B4 Cast-In Public Health has obtained through the CRL By Exception process (CRL1-XRL-O7-GPD-CR001-50023). Refer RiR ref Cxxx-SKC-Z-LRC-CR086_WS095-50001 Rev 1.0 for drawing details/references. Refer completed Technical Assurance By Exception Gate Risk Assessment form (Cxxx-SKC-P-__-CR086_WS095-50001 Rev 1.0) appended to this NCR.
| 03SR - Stations (RfL) | Cxxx-NCR-000386 | NCR | Wrong Type of Lock Installed on Door D00-29 |  | Contr | SKC |  |  | 2016-12-05 | 2016-12-06 14:54 | 1 | 2016-04-06 10:57 | Architectural - Doors | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | D00-29 was meant to be installed fitted with a Panic Bar as per Cxxx-SKC-A-DDD-CR094_SH006_Z-00722 Detail 'Door Type S2 - Single Louvred'. The door however has been installed with a auto deadlocking door handle. Cxxx-SKC-A-DDD-CR094_SH006_Z-00722 details that the louvered doors requires a stainless steel kick plate at the base, which has been omitted.
| 03SR - Stations (RfL) | Cxxx-NCR-000387 | NCR | Louvre Cill Not Installed |  | Contr | SKC |  |  | 2017-01-30 | 2016-12-21 07:32 | -40 | 2016-04-06 10:58 | Architectural - Doors | 500 |  | Incomplete Works | Rework | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | A louvre cill has been installed however, it is not as depicted in Cxxx-SKC-A-DDD-CR094_SH006_Z-00729.
| 03SR - Stations (RfL) | Cxxx-NCR-000388 | NCR | Mile End Shaft and Headhouse - Cxxx Penetrations |  | Contr | SKC |  |  | 2016-11-28 | 2016-10-16 12:25 | -43 | 2016-04-07 14:59 | Structural Engineering - Structural Engineering - General | 500 |  | Planning | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Other | Completed |  | received PMI to install core holes throughout shaft and headhouse to enable Cxxx works. Cxxx indicated verbally that they wish to review the locations for impact on RC walls. This was done via Cxxx-RFI-000543. Upon marking out the core holes on site by Cxxx, time wasn't allowed for Cxxx to review locations due to availability of Cxxx and the program requirements of Cxxx. Attached is the locations of the cores through the Reinforced concrete. It is noted that the as builts of the builders work schedules and the blockwork drawings will include these penetrations.
| 03SR - Stations (RfL) | Cxxx-NCR-000389 | NCR | Stepney Green - Blockwork GL 6-10 Phase 2 Levels B1-B4 - By Exception Technical Assurance Process |  | Contr | SKC |  |  | 2018-02-26 | 2017-11-03 00:07 | -115 | 2016-04-20 07:44 | Architectural - Brickworks/Blockworks | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Change to drawings not provided on time | Completed |  | In order to meet the Stepney Green early access construction programme the design technical assurance of the Blockwork drawings between GL 6-10 on Levels B1-B4 has been obtained through the CRL By Exception process (CRL1-XRL-O7-GPD-CR001-50023). Refer RiR ref RIR Cxxx-SKC-Z-LRG-CR094_WS108-50001 Rev 3.0 for drawing details/references. Refer completed Technical Assurance By Exception Gate Risk Assessment form (Cxxx-SKC-C-RGN-CR094_WS108-50011 Rev 1.0) appended to this NCR.
| 03SR - Stations (RfL) | Cxxx-NCR-000390 | NCR | Screed in Transformer rooms not extending to Louvres |  | Contr | SKC |  |  | 2016-11-21 | 2016-10-24 10:31 | -28 | 2016-04-21 07:35 | Architectural - Doors | 500 |  | Incomplete Works | Repair | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | The concrete screed in the transformer room has been left short of the Louvre.
| 03SR - Stations (RfL) | Cxxx-NCR-000391 | NCR | Out Of Specification concrete poured in Zone 2 Pile Caps |  | Contr | SKC | ELS - Eleanor Street Shaft (Central) |  | 2016-10-10 | 2016-07-06 14:41 | -96 | 2016-04-25 07:44 | Civil - Civil Engineering General | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | On the 20/04/2016 5 pile caps (PC1) along grid line 1 & grid line A ( 600mm x 600mm x 600mm each in size ) were poured with out of specification concrete. Please see attached sketch of poured pile caps
| 03SR - Stations (RfL) | Cxxx-NCR-000392 | NCR | Fisher Street - C12/15\2A 20mm CIIIA+SR Pump S3 DC-2 & C12/15\2A 20mm CIIIA S3 DC-1 (Mass fill plug) Exceeding allowable Alumina content within GGBS |  | Contr | SKC |  |  | 2016-05-13 | 2016-05-09 09:53 | -4 | 2016-04-29 07:13 | Civil - Civil Engineering General | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | Cxxx are currently placing concrete captured within MCR Cxxx-SKC-C-LRC-CR094-5219 which exceeds the allowable Alumina content stated in Cxxx-JUL-S-RSP-CR094_SH005_Z-50001 clause KF10.1403. Stated 10% vs Actual 11.6% The concrete poured was for the mass fill concrete which does not have any structural impact, and no structural pours will take place until this issue has been closed out.
| 03SR - Stations (RfL) | Cxxx-NCR-000393 | NCR | Fisher St - B4 Construction using P Status Drawings |  | Contr | SKC |  |  | 2016-08-27 | 2016-06-21 10:43 | -67 | 2016-04-29 09:44 | Civil - Structural Engineering | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Change to drawings not provided on time | Completed |  | Due to programme criticality, Cxxx have proceeded with construction on site on Level B4 based on Stage P agreed drawings.
| 03SR - Stations (RfL) | Cxxx-NCR-000394 | NCR | Fisher St - B4-B1 Walls & Slabs Construction using P Status Drawings |  | Contr | SKC |  |  | 2017-01-31 | 2016-12-07 08:28 | -55 | 2016-04-29 09:44 | Civil - Civil Engineering General | 3000 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Change to drawings not provided on time | Completed |  | Due to programme criticality, Cxxx have proceeded with construction on site on Level B4-B1 Walls & Slabs based on Stage P agreed drawings.
| 03SR - Stations (RfL) | Cxxx-NCR-000395 | NCR | Ommision of Rust Protection Paint whilst cutting 5m Fencing for Site Adjustments |  | Contr | SKC |  |  | 2016-06-20 | 2016-06-20 15:24 | 0 | 2016-05-06 07:09 | Civil - Street Furniture | 500 |  | Incomplete Works | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Whilst making site adaptions for the installation of the infill panel, installed to prevent footballs from falling in between the existing fencing and recently installed 5m fencing at the south side of the site, the operatives installing this did not apply rust protection measures. The area affected are shown in the attached photograph.
| 03SR - Stations (RfL) | Cxxx-NCR-000397 | NCR | Mile End External Balustrade installed without accepted Fabrication drawings. |  | Contr | SKC |  |  | 2017-04-24 | 2017-04-05 07:03 | -19 | 2016-05-07 08:59 | Architectural - Balustrade | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | Mile End External Balustrade installed with accepted Fabrication drawings. Design comments were still open on the balustrade when it was installed. External Balustrade Design Package Cxxx-SKC-C-DWG-CR094_WS109-50080 (Crossrail comments sheet document eB number Cxxx-SKC-C-XCS-CR094_WS109-50265) Rev 1 comments code 2, rev 2 comments code 3. 1/3/2017 Update Due to a number of revisions between Cxxx and the Contractor on the Balustrade design package (refer comments sheet No. Cxxx-SKC-C-XCS-CR094_WS109-50265) it has become apparent that Cxxx are concerned with the following: 1. The Contractors design departure from the Cxxx design intent. 2. The validity of the Contractors design with regards to compliance with the Building Regulations Document Part-K. 3. The robustness of the capping detail at the top of the RC wall. 4. The robustness of the waterproofing/mound interface detail. 5. The risk that balustrade support brackets presents to the public. This NCR is updated to capture Cxxx’s comments in order for Crossrail Cxxx to demonstrate that Cxxx’s comments have been adequately addressed and their comments are effectively closed and therefor allow Crossrail Cxxx to accept and close out the drawing package Code 1. Point No. 1 The Contractors design departure from the Cxxx design intent is due to the following: • The Cxxx design intent showed balustrade fixing hidden from view by both masonry cladding and the stainless steel capping plate making it difficult for maintenance i.e requires brick to be removed to replace/repair. The detail contradicted the Cxxx Architectural Specification Clause JA.6401 (i.e. to be capable of simple maintenance) and therefore the detail was amended. • The Cxxx design intent showed the end plate of the capping profile being adjacent to the ground level creating an easy target for vandalism. Again, the detail contradicted the Cxxx Architectural Specification Clause JA.6401 (i.e. to be capable of simple maintenance) and therefore the detail was amended. • The Contractor identified a number of weak points with the stainless steel capping detail of the Cxxx design intent making it susceptible to damage (i.e. water ingress and accelerated corrosion). The detail posed a risk to according to the 120 year design life as per Clause JL32.1212 of the Cxxx Architectural Specification and therefore was amended. • The Cxxx design intent shows the geometry of the balustrade and the stainless steel capping plate in vertical and horizontal curves which made the whole detail extremely complicated to fabricate. The balustrade and stainless steel capping plate would have to be fabricated sections, therefore requiring additional fixings within the capping plate. This was viewed to not accord Cxxx design intent. • Under structural review of the Cxxx design intent it was found inadequate to meet the loading requirement of Building Regulations/British Standard load tables (Table 4 of BS. 6399) and additionally Cxxx intent showed horizontal top rail which was identified as risk for climbing, skate boarder railing and public climbing around along from of balustrade which could lead to falls significant height. Furthermore: • The abovementioned issues were detailed to the Employer through Cxxx-RFI-000278 of which Cxxx confirmed that it had no objection to developing alternative balustrade fixings and coping details. • The Contractor had produced Stage F drawings of the balustrade detail (refer: Cxxx-SKC-A-DWG-CR094_WS109-50004 rev 4) of which the Crossrail Cxxx had approved the document Code 1. • The Cxxx architect inspected a sample mock up balustrade (refer Cxxx-CCM-01794) on 20 November 2015 and had no objection to the design and to proceed with fabrication and installation. Point No. 2 The Contractor confirms that it has complied with the Building Regulations Document Part-K on the basis of the following: • From the top of the parapet to the top of the balustrade there is 1208mm of edge protection. This is in excess of 1100mm required by the Building Regulations Document Part-K. • The balustrade fixings detail was as a result of Item No. 1. If a person were to balance on or climb up on the guardrail using the 15mm wide stanchion (or top of skirting or upper horizontal rail) as a climbing aide then this is not an issue with regards to heights required under the building regulations but of the guardrail and its supports as it has been designed to prevent further climbing. • While the risk of a person climbing the balustrade can never be fully designed out we note that the balustrade has already been redesigned from the stage E Works Information in order to address climbing issues by removing the continuous top rail from the Cxxx design intent and introducing vertical steel flat sections. • The balustrade fixings are only 15mm thick and as such not deemed to be considered an horizontal surface that is “climbable” such as the parapet. The current design exceeds the required 1200mm above the parapet, the highest horizontal surface adjacent to the balustrade, that someone could be reasonably considered to be able to stand next to the roof edge and thus present a risk of falling. • Someone trying to climb to the top of the stanchions (much like other parts of the balustrade) would fall under a different type of issue. This issue has already been addressed, or minimised, through re-design to prevent against climbing. • Again, someone climbing to the stanchions, like trying to climb the balustrade, would demonstrate an intent. The balustrade cannot be designed against these voluntary and intentional actions. As mentioned in the comment sheet, the risk of a person climbing the balustrade can never be fully designed out. • Risk of persons with intent to climb balustrade is noted in CDM register. Furthermore: • The Employer has instructed the installation of a 2.4m high secure fence at the bottom of the mound (refer Cxxx-PMI-00853). The introduction of the secure fence at the bottom of the mound will prevent public access to the mound. Point No. 3 • It should be noted that the capping detail is robust and incorporates a DPC detail (refer attachment ‘591-0040-SKE-118 - ME Coping ties.pdf’) the detail shows that the DPC layer has been installed in accordance with the Hyload-Design-Guide-April-2007 (attached, page 28). The copers have been dowel tied to the RC wall with resin at each joint, no penetration of the DPC has been undertaken. Point No. 4 • As discussed with Nick Lyons of Crossrail Cxxx an FCD will be raised for Crossrail Cxxx approval to address this concern. Point No. 5 • The Contractor has updated its CDM risk register in order to capture this point (refer Cxxx-SKC-O3-LRG-CR094_WS109-50001 Rev 6). It should be noted that the mitigation is that the Employer has instructed the installation of a 2.4m high secure fence at the bottom of the mound (refer Cxxx-PMI-00853). The introduction of the secure fence at the bottom of the mound will prevent public access to the mound.
| 03SR - Stations (RfL) | Cxxx-NCR-000398 | NCR | Slump Below requirements of Table B1 of BS 8500-1:2015 Consistence Target S3 C12/15\2A Pumpable |  | Contr | SKC |  |  | 2016-05-30 | 2016-05-17 13:33 | -13 | 2016-05-09 12:35 | Civil - Civil Engineering General | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Use of unapproved materials | Completed |  | __ carried out slump testing in line with BS EN 12350-2:2009. Recorded Slump was returned @ 75mm. After discussion with CRL it was decided to proceed due to the nature of the pour. { Mass fill in the Eastbound Addit }. Despite this, the workability of the concrete did appear to be satisfactory whilst it was being placed.
| 03SR - Stations (RfL) | Cxxx-NCR-000399 | NCR | Eleanor St - Level B5 CMS - By Exception Technical Assurance Process |  | Contr | SKC | ELS - Eleanor Street Shaft (Central) |  | 2016-07-29 | 2016-05-13 14:58 | -77 | 2016-05-13 08:56 | Electrical - Cable Management | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | In order to meet the Eleanor Street construction programme the design technical assurance of the 8No. Electrical drawings has been obtained through the CRL By Exception process (CRL1-XRL-O7-GPD-CR001-50023). Refer completed Technical Assurance By Exception Gate Risk Assessment form (Cxxx-SKC-E-RGN-CR094_WS110-50010 Rev 1.0) appended to this NCR for details of the drawings and scope.
| 03SR - Stations (RfL) | Cxxx-NCR-000400 | NCR | Limmo - Level B1 Blockwork - By Exception Technical Assurance Process |  | Contr | SKC |  |  | 2016-05-25 | 2016-05-12 10:04 | -13 | 2016-05-11 22:00 | Architectural - Brickworks/Blockworks | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | In order to meet the Limmo construction programme the design technical assurance of the blockword drawings has been obtained through the CRL By Exception process (CRL1-XRL-O7-GPD-CR001-50023). Refer completed Technical Assurance By Exception Gate Risk Assessment form (Cxxx-SKC-C-RGN-CR144_WS155-50009 Rev 1.0) appended to this NCR for details of the drawings and scope.
| 03SR - Stations (RfL) | Cxxx-NCR-000401 | NCR | Mile End - WC Threshold Detail |  | Contr | SKC |  |  | 2017-01-23 | 2017-01-12 10:50 | -11 | 2016-05-12 08:21 | Architectural - Flooring | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The floor tiles in the Mile End WC finish short of the door threshold as detailed in Cxxx-SKC-A-DDD_CR094_SH005_Z-00730 (C01, detail 3). There is a 50mm gap of concrete between the finished floor tile line and the door threshold, the tiles are therefore not able to be finished as per the detail on the drawing. 15/09/2016 The door has not been moved far enough back, door to be moved to ensure grout line is hidden. It is noted the the ecxternal trim for the tiles has not been installed. to use Johnston or similar ceramic bath-trim to close this issue.
| 03SR - Stations (RfL) | Cxxx-NCR-000402 | NCR | ESS - Smaller diameter downpipes installed at zone 3 |  | Contr | SKC | ELS - Eleanor Street Shaft (Central) |  | 2016-09-26 | 2016-08-31 07:15 | -26 | 2016-05-19 12:00 | Civil - Drainage | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Two no. 100mm diameter downpipes were installed into the blinding only of the groundworks area zone 3 at GL 1/E. The required diameter is 150mm as shown on the attached drawing Cxxx-SKC-D-DDA-CR094_SH007_1-00001, therefore the 2no 100mm pipes will be replaced with 2no 150mm pipes.
| 03SR - Stations (RfL) | Cxxx-NCR-000403 | NCR | Mile End - Ommission of Certificate of Conformity within __ Commissioning prior to PCC Certificate |  | Contr | SKC |  |  | 2016-10-14 | 2016-10-05 08:22 | -9 | 2016-05-24 09:02 | Mechanical - Mechanical Engineering General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Other | Completed |  | As part of the activities prior to PCC of VRF system, the ITP requires to the MELSmart Certificate of Conformity to be provided. However, due to the not completion of final connection of ductwork to the louver, the foregoing certificate cannot be provided by the specialist, __.
| 03SR - Stations (RfL) | Cxxx-NCR-000405 | NCR | Additional steelwork to B4 |  | Contr | SKC | ELS - Eleanor Street Shaft (Central) |  | 2016-08-22 | 2016-08-22 20:00 | 0 | 2016-06-02 12:28 | Structural Engineering - Structural Engineering - General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | B4 additional steel has been installed and the concrete floor slab will be poured before design acceptance of B4 additional steel design. Following review of the B4 steel design calculations, it was agreed between CRL, Cxxx, __ and at a further design workshop on 31/05/16 that final design close out could follow on from B4 floor slab concrete pour as any further work on the connections will be carried out on site. All connections are detailed in a single design pack of calculations. The majority of these connections have been accepted with some queries outstanding on a few connections. This provides the best programme to achieve SLD dates without compromising quality of completed connections. This includes continuing the steelwork erections and associated concrete slab pours. RCA & __ are happy with the calculations and design and will take on comments raised by Cxxx/CRL. Any further change if required can follow post pour as all relevant connections are fully accessible underneath the slabs. This NCR must be completed and closed out before the temporary support to B4 slab is removed.
| 03SR - Stations (RfL) | Cxxx-NCR-000406 | NCR | Stepney Green Headhouse Piling - Added Water to Concrete for Load Test Pile |  | Contr | SKC |  |  | 2016-11-30 | 2016-11-24 16:13 | -6 | 2016-06-08 12:34 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | During sample concrete spot checks (slump test) for the Stepney Green Headhouse piling installation works on 6th June 2016, specifically the construction and concreting of the load test pile. Initial slump test was taken from the supplied C32/40 S4 strength mix and achieved a slump of 130mm resulting in a failure. contacted to deem the allowable water to be added within the water cement ratio and they advised 27L could be added to stay well within the water cement ratio for the approved mix. Secondary spot check slump test was taken after the added water, concrete achieved a slump test of 180mm (within the S4 slump range for spot sample checks of 140-230mm).
| 03SR - Stations (RfL) | Cxxx-NCR-000407 | NCR | Incomplete pour for Level B4 slab |  | Contr | SKC |  |  | 2016-09-12 | 2016-07-27 15:04 | -47 | 2016-06-15 07:32 | Civil - Civil Engineering General | 500 |  | Incomplete Works | Repair | 4 (0.5-3k) | Complete | Personnel Error - Other human error | Completed |  | Whilst nearing completion of pouring the final segment of the B4 infill slab under the Lahyer stairs, it become apparent that the team had under-estimated the amount of concrete required. As it was too late to order some more concrete as the concrete had started to set when the error was realised. After discussion on site with the CRL Field engineer the decided action was to place a stop-end on the surface, and moving the concrete below the top mat of reinforcement (see attached photo).
| 03SR - Stations (RfL) | Cxxx-NCR-000408 | NCR | Welding Documentation for Mile End Balustrade |  | Contr | SKC |  |  | 2016-11-14 | 2016-11-11 09:54 | -3 | 2016-06-20 09:40 | Architectural - Balustrade | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | Revision 2 of the Welding Submission was significantly different from revision 1. This was due to some material in revision 1 not being relevant and as such was removed from revision 2 following Sandburg review. Therefore it is difficult to gauge the quality of the finished product which has already been installed on site.
| 03SR - Stations (RfL) | Cxxx-NCR-000409 | NCR | Stepney Green - Blockwork between GL 5-10 at Level B5 - By Exception Technical Assurance Process |  | Contr | SKC |  |  | 2017-08-31 | 2017-10-26 08:33 | 56 | 2016-06-23 08:38 | Civil - Civil Engineering General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Change to drawings not provided on time | Completed |  | In order to meet the Stepney early access construction programme the design technical assurance of blockwork drawings between GL 5-10 at Level B5 has been obtained through the CRL By Exception process (CRL1-XRL-O7-GPD-CR001-50023). Refer completed Technical Assurance By Exception Gate Risk Assessment form (Cxxx-SKC-C-RGN-CR094_WS108-50012 Rev 1.0) appended to this NCR.
| 03SR - Stations (RfL) | Cxxx-NCR-000411 | NCR | NCR - Eleanor St - Installation of CMS based on F1 drawings |  | Contr | SKC | ELS - Eleanor Street Shaft (Central) |  | 2016-10-24 | 2016-10-24 16:36 | 0 | 2016-07-04 08:26 | Electrical - Cable Management | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Due to program criticality, construction team proceeded with installation of CMS in B5 without clarifying an ambiguity in the drawings.
| 03SR - Stations (RfL) | Cxxx-NCR-000412 | NCR | Mile End Shaft Mastic Sealant around Doors |  | Contr | SKC |  |  | 2016-10-31 | 2016-10-26 14:40 | -5 | 2016-06-30 07:52 | Architectural - Doors | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Post completion of the installation external doors, identified that there is a significantly larger gap between the external door frame head and the existing structural openings (i.e. greater than the nominal 15mm at locations). As such, the current approved mastic sealant cannot be used (i.e. gaps up to 15mm width).
| 03SR - Stations (RfL) | Cxxx-NCR-000413 | NCR | Fire stopping Mastic used without approved MCR |  | Contr | SKC |  |  | 2016-11-07 | 2016-11-08 07:51 | 1 | 2016-06-30 07:48 | Architectural - Partitions | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Use of unapproved materials | Completed |  | “The subcontractor has used __ Acoustic Intumescent Sealant (MCR Cxxx-SKC-C-LRC-CR094_WS109-50100) and a sister product __ High Expansion Intumescent Sealant which does not have an MCR. __ High Expansion Intumescent Sealant is very similar to the MCR’d product and meets all parts of the specification. Similarly, when installing the __ walls the subcontractor has used a __ product, __ In tumescent Acrylic Sealant as this was part of __’s __ system. This product, however, was not included in the __ MCR”
| 03SR - Stations (RfL) | Cxxx-NCR-000414 | NCR | ESS - Starter bars not installed on groundfloor slab for the 300mm wall at GL 4/C |  | Contr | SKC | ELS - Eleanor Street Shaft (Central) |  | 2016-10-04 | 2016-09-13 14:43 | -21 | 2016-07-06 12:00 | Structural Engineering - Reinforcement | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Starter bars for the 300mm wall on GL C not installed within the groundslab. As it can be seen on the attached photo, the slab has been poured approximately 475mm from the kicker at GL 4 and no stater bars have been installed for the 300mm headhouse walls at GL C. Further to that, 3no. starter bars have been cast into the 200mm kicker at GL 4 while they should have been installed for a 300mm wall.
| 03SR - Stations (RfL) | Cxxx-NCR-000415 | NCR | Eleanor St - Intervention Staircase - By Exception Technical Assurance Process |  | Contr | SKC | ELS - Eleanor Street Shaft (Central) |  | 2017-02-20 | 2017-02-22 14:45 | 2 | 2016-07-13 12:19 | Civil - Structural Engineering | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | In order to meet the Eleanor Street construction programme the design technical assurance of the 8No. Sturctural Intervention Staircase drawings has been obtained through the CRL By Exception process (CRL1-XRL-O7-GPD-CR001-50023). Refer completed Technical Assurance By Exception Gate Risk Assessment form (Cxxx-SKC-S-RGN-CR094_WS110-50001 Rev 1.0) appended to this NCR for details of the drawings and scope.
| 03SR - Stations (RfL) | Cxxx-NCR-000416 | NCR | Stepney Green - B5 Drainage upstand GL 10 |  | Contr | SKC |  |  | 2016-09-16 | 2016-08-17 10:31 | -30 | 2016-07-13 15:26 | Civil - Drainage | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Improper handling of material | Completed |  | After casting the drainage channel upstand on B5 (GL10) the shutters were struck and it could be seen that the concrete was not compacted properly. There was a large area of 'honeycombing' to the face of the upstand. Photos attached DSCF0674 and DSCF0675.
| 03SR - Stations (RfL) | Cxxx-NCR-000417 | NCR | Stepney green - Installation of CMS based on F1 drawings |  | Contr | SKC |  |  | 2017-07-24 | 2017-07-03 15:53 | -21 | 2016-07-11 13:10 | Electrical - Cable Management | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | s MEP Subcontractor has commenced preliminary setting out at Stepney without accepted F1 design for the following drawings. A. Stepney (plan) • Cxxx-SKC-E-DDA-CR094_SH005_2-00242 (P02) • Cxxx-SKC-M-DDA-CR094_SH005_2-00124 (P03) • Cxxx-SKC-M-DDA-CR094_SH005_2-00224 (P02) B. Stepney (sections) • Cxxx-SKC-E-DDB-CR094_SH005-00332 (P02) • Cxxx-SKC-E-DDB-CR094_SH005-00333 (P02) • Cxxx-SKC-M-DDD-CR094_SH005_Z-00622 (P01) • Cxxx-SKC-M-DDD-CR094_SH005_Z-00623 (P01) • Cxxx-SKC-M-DDD-CR094_SH005_Z-00624 (P01) C. Stepney (coordinated) • Cxxx-SKC-E-DDL-CR094_SH005_2-00323 (P01) These drawings are related to CMS work in risers. Due to the above F1 design being not formally accepted by CRL and gate not being achieved for Stepney, are applying for by exception status for these drawing prior to GATE certificate.
| 03SR - Stations (RfL) | Cxxx-NCR-000422 | NCR | Slip Resistance Testing |  | Contr | SKC |  |  | 2016-10-23 | 2016-08-22 22:21 | -62 | 2016-07-15 08:34 | Architectural - Flooring | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | Only 1 reading was taken at each location. This does not comply with the requirement for an average of 10 readings at each location to be reported and the results are therefore invalid.
| 03SR - Stations (RfL) | Cxxx-NCR-000423 | NCR | Piling - Pile position out of tolerance |  | Contr | SKC |  |  | 2016-12-09 | 2016-11-28 13:32 | -11 | 2016-07-25 11:02 | Structural Engineering - Concrete Member | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | During preliminary as-built survey of 17no of the 18no piles in the head house structure it was discovered that 1no pile is outside of horizontal tolerances. Pile 10 has a discrepancy from design coordinates of 0.135mE and 0.061mN. See attached sketch for approximate location relative to ground beam and table of asbuilt coordinates. Asbuilt positions are pending final survey following pile break down. NCR to be updated once final survey is complete. It is possible that the pile will fall marginally outside the ground beam. Update: Please see attached drawing number Cxxx-SKC-S-DWG-CR094_WS108_50007 Rev C02 which incorporates the out of position pile 10 by increasing the east-west dimension of Pile Cap 1B and associated steel.
| 03SR - Stations (RfL) | Cxxx-NCR-000424 | NCR | Mile End - Sump Pumps Paintwork |  | Contr | SKC |  |  | 2016-10-31 | 2016-10-28 05:45 | -3 | 2016-07-21 16:25 | Mechanical - Public Health Engineering | 500 |  | Material | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | The paintwork on the sump pumps at level B9 had several imperfections causing slight rusting of the pumps. Punchwork Cxxx-PWK-00118 was raised at IRN stage to highlight this issue. The paint used to touch up the defects on the pumps was not fit for purpose and will need to be entirely removed.
| 03SR - Stations (RfL) | Cxxx-NCR-000425 | NCR | Limmo Shaft - B1 Blockwork - By Exception Technical Assurance Process |  | Contr | SKC |  |  | 2017-04-28 | 2017-04-05 12:11 | -23 | 2016-07-25 15:00 | Architectural - Masonary | 500 |  | Planning | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | In order to meet the Limmo construction programme the design technical assurance of B1 Blockwork has obtained through the CRL By Exception process (CRL1-XRL-O7-GPD-CR001-50023). Refer RiR ref Cxxx-SKC-Z-LRC-CR144_WS155-50002 Rev 1.0 for drawing details/references. Refer completed Technical Assurance By Exception Gate Risk Assessment form (Cxxx-SKC-C-__-CR144_WS155-50001 Rev 1.0) appended to this NCR.
| 03SR - Stations (RfL) | Cxxx-NCR-000426 | NCR | Limmo Shaft - Blockwork - By Exception Technical Assurance Process |  | Contr | SKC |  |  | 2017-04-28 | 2017-04-05 12:12 | -23 | 2016-07-25 15:33 | Architectural - Masonary | 500 |  | Planning | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | In order to meet the Limmo construction programme the design technical assurance of Blockwork (All Levels excluding B1) has obtained through the CRL By Exception process (CRL1-XRL-O7-GPD-CR001-50023). Refer RiR ref Cxxx-SKC-Z-LRC-CR144_WS155-50002 Rev 2.0 for drawing details/references. Refer completed Technical Assurance By Exception Gate Risk Assessment form (Cxxx-SKC-C-__-CR144_WS155-50003 Rev 1.0) appended to this NCR.
| 03SR - Stations (RfL) | Cxxx-NCR-000427 | NCR | Eleanor St - B1-B5 CMS - By Exception Technical Assurance Process |  | Contr | SKC | ELS - Eleanor Street Shaft (Central) |  | 2017-03-27 | 2017-03-06 20:30 | -21 | 2016-07-29 10:58 | Electrical - Cable Management | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | In order to meet the Eleanor Street construction programme the design technical assurance of the shaft levels B1-B5 CMS design has been obtained through the CRL By Exception process (CRL1-XRL-O7-GPD-CR001-50023). Refer RiR ref Cxxx-SKC-Z-LRC-CR094_WS110-50001 Rev 2.0 for drawing details/references and completed Technical Assurance By Exception Gate Risk Assessment form (Cxxx-SKC-E-RGN-CR094_WS110-50011 Rev 1.0) appended to this NCR.
| 03SR - Stations (RfL) | Cxxx-NCR-000435 | NCR | LMP - Inherited Cxxx Works |  | Contr | SKC |  |  | 2017-07-31 | 2017-06-15 06:07 | -46 | 2016-08-01 09:38 | Civil - Structural Engineering | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | *The full agreed resolution is critical to allow Cxxx to meet Project Critical Path dates for the Transformer Rooms as per email from to Cxxx and CRL on 29/07* NCR's 428-434 have been combined to reduce admin. 00428 -Issues with couplers for the transformer wingwalls (10,11,12,13) and for security corridor (6,8): - Couplers have insufficient cover. - Missing couplers in two sections of wall. - Spacings incorrect for couplers. Proposed Disposition: Rework NCR Classification: Incorrect Installation 000429 - LMP - Cxxx Concrete poured about SSL The concrete walls are poured above SSL on: Wall 4 GL3-4 Wall 7 Wall on GL4 Wall 3 GL6-7 Wall 2 Wall 9 GL6-7 Proposed Disposition: Repair NCR Classification: Incorrect Installation 000430 - LMP - Cxxx Insufficient cover for Starter Bars for Transformer rooms There is insufficient cover for starter bars for the transformer room wing walls. Proposed Disposition: Rework NCR Classification: Incorrect Installation 000431 - LMP - Cxxx - Insufficient lap lengths of rebar at top of RC walls Sections of reinforcement specifically on Gridline 4 and around Lift Core have been cut to level of concrete, therefore there is insufficient lap length. Proposed Disposition: Rework NCR Classification: Incorrect Installation 000432 - LMP - Cxxx Existing cast-in jacks from slip form There are cast in jacks left in the RC from the slip form at high level around the top of the RC walls. Proposed Disposition: Rework NCR Classification: Incorrect Installation 000433 - LMP - Cxxx Concrete splashed onto exposed reinforcement There is concrete splashed onto the exposed reinforcement at the top of the RC walls. Proposed Disposition: Use As-Is NCR Classification: Workmanship 000434 - LMP - Cxxx Cracked concrete on Wall 9 Cracked concrete and poor quality finish at the top of Wall 9. Proposed Disposition: Repair NCR Classification: Workmanship As detailed in inherited RC Works Report (attached by Kadar)
| 03SR - Stations (RfL) | Cxxx-NCR-000437 | NCR | Damage to Balustrade |  | Contr | SKC |  |  | 2016-10-31 | 2016-10-13 13:16 | -18 | 2016-08-01 10:14 | Civil - Civil Engineering General | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | A single infill bar on Panel No. 47 has been damaged (i.e. broken off).
| 03SR - Stations (RfL) | Cxxx-NCR-000438 | NCR | Mile End - Aspirating System Interface with Ductwork |  | Contr | SKC |  |  | 2016-08-24 | 2016-08-25 06:01 | 1 | 2016-08-04 12:35 | Mechanical - Mechanical Engineering General | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | Aspirating system installed in the FAN room has an interface with Pressurisation System. Installation is shown on Cxxx-SKC-E-DWG-CR094_WS109-50114 X02. The drawing does not give any details on the interface between ductwork and pipework.
| 03SR - Stations (RfL) | Cxxx-NCR-000439 | NCR | Limmo Peninsula - Laying saturated blockwork to B4 Eastern Wall |  | Contr | COS |  |  | 2016-09-30 | 2016-09-22 14:05 | -8 | 2016-08-05 10:14 | Architectural - Brickworks/Blockworks | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | During the construction of the Eastern Wall 2nd Lift on access level B4, operatives lowered a saturated/wet pallet of blocks in preparation for Blockwork installation. Operatives were seen laying a handful of wet blocks to the eastern wall; they were immediately asked to stop, and advised to use an alternative (dry) pallet of blocks, as opposed to saturated blocks.
| 03SR - Stations (RfL) | Cxxx-NCR-000440 | NCR | Stepeny Green - CMS in Comms 1 Riser Level B1 to B4 - By Exception Assurance Process |  | Contr | SKC |  |  | 2017-11-30 | 2017-11-16 14:36 | -14 | 2016-08-05 15:41 | Electrical - Cable Management | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | In order to meet the Stepney Green construction programme the design technical assurance of the CMS drawings between Levels B1-B4 in Comms Riser 1 has been obtained through the CRL By Exception process (CRL1-XRL-O7-GPD-CR001-50023). Refer RiR ref RIR Cxxx-SKC-Z-LRC-CR094_WS108-50001 Rev 1.0 for drawing details/references. Refer completed Technical Assurance By Exception Gate Risk Assessment form (Cxxx-SKC-C-RGN-CR094_WS108-50013 Rev 1.0) appended to this NCR.
| 03SR - Stations (RfL) | Cxxx-NCR-000441 | NCR | Door Contacts - Mechanical Fixing into Doors |  | Contr | SKC |  |  | 2016-10-31 | 2016-10-18 06:14 | -13 | 2016-08-05 16:22 | Architectural - Doors | 500 |  | Incomplete Works | Repair | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | As per Cxxx-RFI-000561 and Cxxx-PMI-00580 has installed the specified door contacts (ABUS MK4200) however, they have been in adequately fixed.
| 03SR - Stations (RfL) | Cxxx-NCR-000442 | NCR | Limmo - Escape and Intervention Staircase - By Exception Assurance Process |  | Contr | SKC |  |  | 2017-06-30 | 2017-04-03 09:01 | -88 | 2016-08-08 08:03 | Civil - Civil Engineering General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | In order to meet the Limmo Peninsula construction programme the design technical assurance of the Escape and Intervention staircase drawings has been obtained through the CRL By Exception process (CRL1-XRL-O7-GPD-CR001-50023). Refer RiR ref RIR Cxxx-SKC-Z-LRC-CR144_WS155-50002 Rev 3.0 for drawing details/references. Refer completed Technical Assurance By Exception Gate Risk Assessment form (Cxxx-SKC-C-RGN-CR144_WS155-50011 Rev 1.0) appended to this NCR.
| 03SR - Stations (RfL) | Cxxx-NCR-000443 | NCR | Mile End - NCR - FAN room temperature sensor |  | Contr | SKC |  |  | 2016-09-26 | 2016-09-28 06:26 | 2 | 2016-08-09 11:05 | Mechanical - Mechanical Engineering General | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Temperature sensor in FAN room not accessible due to ductwork lagging isntallation.
| 03SR - Stations (RfL) | Cxxx-NCR-000444 | NCR | Mile End - NCR - FAN room ATS |  | Contr | SKC |  |  | 2016-10-15 | 2016-10-11 00:06 | -4 | 2016-08-16 13:57 | Electrical - LV Equipment | 500 |  | Supervision/Management | Repair | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Access to ATS panel in FAN room limited by lagging to pressurisation ductwork installation.
| 03SR - Stations (RfL) | Cxxx-NCR-000445 | NCR | Stepeny Green - Sub surface drainage in ATX transformer bund area - By Exception Assurance Process |  | Contr | SKC |  |  | 2017-11-30 | 2017-11-16 14:37 | -14 | 2016-08-09 12:00 | Civil - Drainage | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | In order to meet the Stepney Green construction programme the design technical assurance of the drainage drawings for area of transformer bunds at ground level has been obtained through the CRL By Exception process (CRL1-XRL-O7-GPD-CR001-50023). Refer RiR ref RIR Cxxx-SKC-Z-LRC-CR094_WS108-50001 Rev 2.0 for drawing details/references. Refer completed Technical Assurance By Exception Gate Risk Assessment form (Cxxx-SKC-C-RGN-CR094_WS108-50014 Rev 1.0) appended to this NCR.
| 03SR - Stations (RfL) | Cxxx-NCR-000446 | NCR | ESS - Pouring concrete without full welding of splice plates at B2 level |  | Contr | SKC | ELS - Eleanor Street Shaft (Central) |  | 2017-01-23 | 2016-12-13 07:21 | -41 | 2016-09-12 07:31 | Structural Engineering - Steel Member | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | During the installation of the structural steel at B2 level, it was identified that the splice connection detail could not be welded on site as per the approved design. A 6mm full profile weld was detailed in the approved design but this was not constructible due to lack of access between the edge of the splice plate and web of the column. This affected 7no. C2 to C1 column connections on level B2. Sketches and pictures of this connection have been attached. Cxxx designers were consulted and provided a new 8mm and 12mm weld design for the splice connection. Details of this design is shown in the attached sketches and structural calculations will be provided soon. The splice connection was welded according to the new design and the first floor slab was poured.
| 03SR - Stations (RfL) | Cxxx-NCR-000447 | NCR | __ - Escape and Intervention Staircase - By Exception Assurance Process |  | Contr | SKC |  |  | 2017-09-25 | 2017-10-26 08:36 | 31 | 2016-08-11 10:15 | Civil - Civil Engineering General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | In order to meet the Stepney Green Shaft construction programme, the design technical assurance of the Escape and Intervention Staircase drawings has been obtained through the CRL By Exception process (CRL1-XRL-O7-GPD-CR001-50023). Refer RiR ref number Cxxx-SKC-Z-LRC-CR094_WS108-50001 Rev 3.0 for drawing details/references. Refer completed Technical Assurance By Exception Gate Risk Assessment form (Cxxx-SKC-C-__-CR094_WS108-50007 Rev 1.0) appended to this NCR.
| 03SR - Stations (RfL) | Cxxx-NCR-000448 | NCR | Mile End - NCR - Touch Potential within Earth Gapping |  | Contr | SKC |  |  | 2016-10-31 | 2016-11-28 14:39 | 28 | 2016-08-11 07:57 | Electrical - Electrical Engineering General | 500 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Touch Potential clearance within Earth Gapping zone potentially not achieved in B8 and B9 adits at Mile End.
| 03SR - Stations (RfL) | Cxxx-NCR-000449 | NCR | Limmo Peninsula – Installation of Standard Blocks (Colour variations) |  | Contr | COS |  |  | 2016-09-30 | 2016-08-17 14:18 | -44 | 2016-08-12 08:24 | Architectural - Brickworks/Blockworks | 500 |  | Manufacturing Defect | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | It has been identified that the Blockwork installed on access level B1, is variant in colour, due to the units from different packs and deliveries.
| 03SR - Stations (RfL) | Cxxx-NCR-000450 | NCR | Mile End - NCR - Sump Pump compliance with SCADA spec |  | Contr | SKC |  |  | 2016-10-29 | 2016-10-28 06:03 | -1 | 2016-08-20 14:40 | Communications and Control Systems - SCADA/Central Management System | 500 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | The local control SUmp Pump Panel at Mile End has been provided with volt free contacts for monitoring purposes as per Work Information at the time (MCR-001356).
| 03SR - Stations (RfL) | Cxxx-NCR-000451 | NCR | MES - Open/Closed signal from Main LV Switchboard to SCADA |  | Contr | SKC |  |  | 2017-01-23 | 2017-01-24 07:18 | 1 | 2016-08-20 14:52 | Communications and Control Systems - SCADA/Central Management System | 500 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | The Modbus interface of the LV panel provide the open/close/tripped signals from the same register as follows. Register: 562 Close: Bit 0 Status 1 Open: Bit 0 Status 0 Trip: Bit 1 Status 1 This arrangement does not align potentially with section 6.5 of CRL1-XRL-R3-RSP-CR001-50003 regarding Main LV Switchboards. This document states that open/close/tripped outputs must be provided, however our units provide open/close output from the same bit. However, there is not explicit requirement in the SCADA spec to provide indivudial signals for each status.
| 03SR - Stations (RfL) | Cxxx-NCR-000452 | NCR | Mile End - NCR - __ sockets' fire survivability |  | Contr | SKC |  |  | 2016-12-20 | 2016-10-28 10:53 | -53 | 2016-08-20 16:31 | Electrical - Lighting | 0 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | __ socket's may not be able to maintain circuit integrity and fire survivability for emergency lighting. __ sockets specified in Electrical Specification and have been approved through the MCR process for Normal Lighting. Additionally __ sockets are used widely in LU for emergency lighting.
| 03SR - Stations (RfL) | Cxxx-NCR-000453 | NCR | Mile End - NCR - Benching (Spare) |  | Contr | SKC |  |  | 2016-10-31 | 2016-10-18 06:35 | -13 | 2016-08-17 17:40 | Mechanical - Public Health Engineering | 500 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Benching in the sump pump pit not installed due to the interference with the sump pumps ( limited space on either side of the pumps). Cxxx-SKC-P-DWG-CR094_WS109-50008 does not provide enough information for the long side of the sump pump pit, where the interference occurs. Additionally, benching requirements are not captured in the Mechanical or the Civil specification.
| 03SR - Stations (RfL) | Cxxx-NCR-000454 | NCR | Mile End - NCR - Earthing to Doors |  | Contr | SKC |  |  | 2016-12-19 | 2016-12-02 09:52 | -17 | 2016-08-17 16:55 | Electrical - Electrical Engineering General | 500 |  | Incomplete Works | Repair | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Doors have been provided without an Earthing Facility.
| 03SR - Stations (RfL) | Cxxx-NCR-000455 | NCR | Mile End - NCR - Aspirating System Compliance with FENG 19 |  | Contr | SKC |  |  | 2016-11-28 | 2016-09-09 13:09 | -80 | 2016-08-20 14:57 | Fire - Detection | 500 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | The requirement for isolation valves on the aspirating system copper pipework has been identified. The requirement for the valves arises from FENG 19 ( fire engineering guidance note) which is not part of Cxxx specification or W.I.
| 03SR - Stations (RfL) | Cxxx-NCR-000456 | NCR | Mile End - NCR - Missing Pressurisation Ductwork Access Hatch |  | Contr | SKC |  |  | 2016-10-24 | 2016-10-20 21:57 | -4 | 2016-08-15 12:19 | Mechanical - Mechanical Engineering General | 500 |  | Supervision/Management | Repair | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | The pressurisation plenum in the FAN room has not been provided with an access hatch for maintenance.
| 03SR - Stations (RfL) | Cxxx-NCR-000458 | NCR | Mile End - NCR - Location of Aspirating System with respect to damper in FAN room |  | Contr | SKC |  |  | 2016-09-22 | 2016-09-09 13:06 | -13 | 2016-08-17 18:40 | Mechanical - Mechanical Engineering General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Due to program criticality the aspirating System Pipework was not installed in the correct location.
| 03SR - Stations (RfL) | Cxxx-NCR-000459 | NCR | Fisher Street B4 Jump { Area of uncompacted Concrete } |  | Contr | SKC |  |  | 2016-10-31 | 2016-10-31 15:42 | 0 | 2016-08-18 12:51 | Civil - Civil Engineering General | 2000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | After the removal of the Jump Form shutters in the base of Fisher street shaft, 1no small void were found within the wall 6. The small void extends through the wall exposing the reinforcement. See photos titled before.
| 03SR - Stations (RfL) | Cxxx-NCR-000460 | NCR | Fisher Street B4 Jump Wall { Possible Localised Cold Joint } |  | Contr | SKC |  |  | 2017-01-31 | 2016-12-16 13:29 | -46 | 2016-08-18 13:28 | Civil - Civil Engineering General | 5000 |  | Workmanship | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | After the removal of the wall shutters in the base of Fisher street shaft, 2 No areas of poor compaction found within the wall 6. It is suspected that there may be a cold joint in the area shown.
| 03SR - Stations (RfL) | Cxxx-NCR-000461 | NCR | Stepney Green - TR2 Floor Penetrations |  | Contr | SKC |  |  | 2016-11-25 | 2016-11-24 14:23 | -1 | 2016-08-25 14:11 | Electrical - Cable Management | 500 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | The TR2 room at level B1 is designed with 2no floor penetrations rising from level B2. This configuration can be seen in the B1 containment layout drawing: Cxxx-SKC-E-DDA-CR094_SH005_2-00242. The penetration located at the top right corner of the room allows the HV cable tray to rise from the HV switch room at B2 level to the transformer at B1 level. Attachment 1 is a photo of the floor penetration. The hole size is too small to allow for the size of the cable ladder to go through. The second penetration located in the lower half of the TR2 Room allows for the LV busbar to drop to level B2. Attachment 2 depicts the LV busbar floor penetration. Which is also too small to allow the LV busbar to drop down. The floor slab is 450mm thick reinforced concrete.
| 03SR - Stations (RfL) | Cxxx-NCR-000463 | NCR | Grout Cubes required on Steel Staircase ITP |  | Contr | SKC |  |  | 2016-09-14 | 2016-08-31 13:03 | -14 | 2016-08-31 11:08 | Architectural - Flooring | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Other | Completed |  | As per Cxxx-SKC-C-ITP-CR094-50021 check sheet 50021-A , operation 6 originally stated that cubes will be taken of the grout installed around the base plate on B9. Upon review has deemed that this is not requirement of the works information and also not required due to the grout being installed only for aesthetics and is not structural and therefore strength testing has been deemed overkill.
| 03SR - Stations (RfL) | Cxxx-NCR-000464 | NCR | Public Health Arrangement B8 and B9 |  | Contr | SKC |  |  | 2017-05-15 | 2017-04-27 08:20 | -18 | 2016-08-31 15:32 | Mechanical - Public Health Engineering | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | The drainage details on Cxxx-SKC-P-DDA-CR094_SH006_10-00101, Cxxx-SKC-P-DDB-CR094_SH006_Z-00200 and Cxxx-SKC-P-DDA-CR094_SH006_9-00101 at the end of IA1 and IA2 has not been constructed to. The details missed are the half channel, and associated work, and the Aco drain. However the drainage details as per Cxxx-OVE-C4-DDB-CR001_Z-50006, Cxxx-OVE-C4-DDB-CR001_Z-50013, Cxxx-OVE-C4-DDB-CR001_Z-50016, Cxxx-OVE-C4-DDB-CR001_Z-50003, Cxxx-OVE-C4-DDA-CR001_Z-50004 and Cxxx-OVE-C4-DDA-CR001_Z-50014 have been installed. This drawings were instructed to in Cxxx-PMI-00295.
| 03SR - Stations (RfL) | Cxxx-NCR-000465 | NCR | FIS - B3 Jump - Placing of Concrete |  | Contr | SKC |  |  | 2016-09-19 | 2016-09-14 14:47 | -5 | 2016-09-05 14:27 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | During the B3 Jump section concrete pour on the 31/08/16, the tremie lines that were in place for the concrete pour were deemed ineffective as the concrete would not flow through them properly without clogging up. The tremie lines were taken out and as the concrete pour had already commenced, were left with no alternative but to continue with the pour. The issue that occurred due to the ineffective tremie lines was that the hose extension on the concrete pump was approximately only 3m in length. This meant that in the early stages of the concrete pour, the placing of concrete was from approximately 3m in height as the overall concrete pour height was just shy of 6m. Clause KF10.3210 of the Civil/Structural Spec states 'Unless otherwise agreed, concrete shall not be discharged vertically through a height greater than 2 metres or more than 1 metre from a chute.' Once 1m in height of concrete pour was completed there was no issue with regard to not adhering to the spec as the max vertical drop of the concrete discharge would have been within 2m.
| 03SR - Stations (RfL) | Cxxx-NCR-000466 | NCR | Limmo Shaft - B1 CMS - By Exception Technical Assurance Process |  | Contr | SKC |  |  | 2017-04-28 | 2017-04-05 12:12 | -23 | 2016-09-06 08:15 | Electrical - Cable Management | 500 |  | Planning | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | In order to meet the Limmo construction programme the design technical assurance of CMS Level B1 has obtained through the CRL By Exception process (CRL1-XRL-O7-GPD-CR001-50023). Refer RiR ref Cxxx-SKC-Z-LRC-CR144_WS155-50002 Rev 4.0 for drawing details/references. Refer completed Technical Assurance By Exception Gate Risk Assessment form (Cxxx-SKC-E-__-CR144_WS155-50001 Rev 1.0) appended to this NCR.
| 03SR - Stations (RfL) | Cxxx-NCR-000467 | NCR | ESS - Insufficient thread on holding down bolts at ground floor level |  | Contr | SKC | ELS - Eleanor Street Shaft (Central) |  | 2016-11-06 | 2016-10-28 06:35 | -9 | 2016-09-07 15:32 | Structural Engineering - Steel Member | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | During the installation of the structural steel at ground floor slab, it has been identified that a few of the holding down bolts have insufficient thread. The check sheet on the ITP for the installation of structural steel states that the bolts must have a minimum of 3 complete threads. There are some instances where the nuts have either one tread or where the head of the bolt is flush with the top of the nut as shown on the attached pictures. Cxxx notes that currently only two C4 columns located at GL G do not meet the requirement for 3 threads on each bolt. The holding down bolts of the C4 column at GL 2/G have maximum 1no. thread (See attached photo C4 column - GL 2-G). The second C4 column, has only one holding down bolt that does not meet the minimum of three thread requirement (see attached photo C4 column - GL 3-G).
| 03SR - Stations (RfL) | Cxxx-NCR-000469 | NCR | FIS - B3 Jump Form Wall 4 (Area of uncompacted Concrete) |  | Contr | SKC |  |  | 2017-01-31 | 2016-12-13 14:17 | -49 | 2016-09-13 09:22 | Civil - Civil Engineering General | 5000 |  | Workmanship | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Inadequate/insufficient tooling. | Completed |  | After the removal of the Jump form shutters for the B3 level walls, an area of uncompacted concrete was discovered on Wall 4 next to the lift entrance doorway (See attached Location Sketch and photos). There was also some honeycombing above the uncompacted concrete that can be seen in Photo P9092231.
| 03SR - Stations (RfL) | Cxxx-NCR-000470 | NCR | Mile End Headhouse |  | Contr | SKC |  |  | 2016-12-12 | 2016-11-25 13:09 | -17 | 2016-09-14 07:35 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Changes to the Cxxx asset were communicate from to CRL via CCM 1028. No PTR was raised. FCD 583 was raised to track these changes for the purpose of as builts, however Cxxx noted that the procedure was not correctly followed, thus this should be a NCR.
| 03SR - Stations (RfL) | Cxxx-NCR-000471 | NCR | ESS - Differences between as built shear studs to Cxxx design intent |  | Contr | SKC | ELS - Eleanor Street Shaft (Central) |  | 2016-10-28 | 2016-10-26 14:03 | -2 | 2016-09-16 12:36 | Structural Engineering - Steel Member | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Cxxx design intent for the installation of the shear studs on the structural steel beams supporting the slabs is specifying 100mm x 19mm studs. Due to the fact that recesses had to be created around the access hatches at GL C-D/3-4 (see attached Cxxx-RFI-000597 ), shorter studs were required to achieve the 25mm cover as stated on the response provided from Cxxx on Cxxx-RFI-000597. However, it was agreed in the design meetings that 100mm studs where accepted if 25mm cover was maintained. Therefore, at levels B4-B1, Cxxx installed 100mm studs. Cxxx notes that at levels B4-B1 all the studs were checked and there was no requirement to cut the studs. At ground floor level, in order to maintain the 25mm cover and have 55mm shear studs installed as detailed on the attached sketch provided by Cxxx on the above mentioned RFI, Cxxx had to cut off the shear stud head. Please refer to the attached sketches for clarity regarding the areas that 100mm and 55mm studs were installed and where the stud head was cut. Cxxx notes that this NCR has been discussed in various design meetings between , Cxxx & CRL.
| 03SR - Stations (RfL) | Cxxx-NCR-000472 | NCR | Stepeny Green - CMS in critical risers/rooms, Level B1 to B5 - By Exception Assurance Process |  | Contr | SKC |  |  | 2017-08-31 | 2017-10-26 08:34 | 56 | 2016-09-15 19:06 | Electrical - Cable Management | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | In order to meet the Stepney Green construction programme the design technical assurance of the CMS drawings between Levels B1-B5 in critical risers/rooms (namely: HV/LV risers in Levels B2-B5, R2 riser in Level B1, R2A riser in Level B2, LV2 switch room in level B2 and 25kV switch rooms in level B3) has been obtained through the CRL By Exception process (CRL1-XRL-O7-GPD-CR001-50023). Refer to By Exception RiR ref RIR Cxxx-SKC-Z-LRC-CR094_WS108-50001 Rev 4.0 for drawing details/references. Refer to completed Technical Assurance By Exception Gate Risk Assessment form (Cxxx-SKC-C-RGN-CR094_WS108-50018 Rev 1.0) appended to this NCR.
| 03SR - Stations (RfL) | Cxxx-NCR-000473 | NCR | FIS - Possible Cold Joints in Walls on B3 |  | Contr | SKC |  |  | 2017-01-31 | 2017-01-23 09:03 | -8 | 2016-09-19 15:55 | Civil - Civil Engineering General | 1000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During post pour inspections of walls on B3 (see exact locations on 'Location Sketch - B3' attached), it was identified along with the CRL Field Engineer that there were 2no. locations of possible cold joints in the walls (see attached 2no. photos).
| 03SR - Stations (RfL) | Cxxx-NCR-000474 | NCR | Fisher - Intervention Staircase - By Exception Assurance Process |  | Contr | SKC |  |  | 2017-05-30 | 2017-05-31 08:37 | 1 | 2016-09-20 08:33 | Architectural - General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Use of unapproved drawings | Completed |  | In order to meet the Fisher Street Shaft construction programme the design technical assurance of the Intervention staircase drawings has been obtained through the CRL By Exception process (CRL1-XRL-O7-GPD- CR001-50023). Refer RiR ref RIR Cxxx-SKC-Z-LRC-CR086_WS095-50002 Rev 1.0 for drawing details/references. Refer completed Technical Assurance By Exception Gate Risk Assessment form (Cxxx-SKC-C-RGN- CR086_WS095-50010 Rev 1.0) appended to this NCR.
| 03SR - Stations (RfL) | Cxxx-NCR-000475 | NCR | FIS - Concrete Compaction on Wall 6 - Level B3 |  | Contr | SKC |  |  | 2017-01-31 | 2017-01-11 08:31 | -20 | 2016-09-21 17:16 | Civil - Civil Engineering General | 6000 |  | Workmanship | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | After the removal of the Jump Form shutters in the Fisher street shaft on Wall 6 at Level B3, 4no. voids were found. See attached photos 1. , 2. (x2) , 3. and attached Location sketch (NCR Wall 6). Reinforcement can be seen in 2no. voids in Photo 2.
| 03SR - Stations (RfL) | Cxxx-NCR-000477 | NCR | Fisher St { Abandoned B1 to GL Jump Form Pour } |  | Contr | SKC |  |  | 2017-07-14 | 2017-07-10 11:27 | -4 | 2016-09-27 12:28 | Civil - Civil Engineering General | 20000 |  | Incomplete Works | Use As-Is | 2 (6-60k) | Complete | External Phenomenon - Other | Completed |  | The jump form Pour was set to commence at 11am on the 26.09.2016. The first truck that was batched via tarmac was refused as they had batched from an unapproved batching plant. Subsequently the next truck was batched from Kings Cross with the Approved 10mm mix. Load 1 Time Batched was 12.01 Time received was 12.20 Slumping commenced and 140mm was recorded. Discharge commenced at 12.25. Temperature of mix was 23.3 degrees c. Discharge was complete by 13.10 Load 2 Time Batched was 12.56 Time received was 13.28 The gap between Delivery & Discharge was due to an unscheduled truck for the movie studio blocking the road between 13.23 and 13.43. This inadvertently had no detrimental effect due to the slump. Time backed up for Discharge 13.47 Slumping commenced and 300mm was recorded. Discharge did not commence. Driver directed to dump .5m3 in the a bund and a re slump was taken. Slumping commenced and circa 270mm was recorded. Discharge did not commence. Temperature of mix was 23.5 degrees c. At 14.10 the pump driver advised the line was blocked due to the delays in discharges and the slump being on the low end in the first load. The team attempted to clear the line up until 14.20 until at that point the decision was taken to stop the pour as the concrete on the previously laid layer was gone off in areas. *************************************************************** Cxxx Response 09/03/2017 Added up revved report actioning comments, proposed resolutions still are still the contractors preference. 1. Wall 6/2/7/4 no further action required other than cosmetic tidy up using approved method NCR 460. 2. Wall 8 Corrective actions as per attachment. *********************************************************************** Cxxx Response 04/05/2017 Based on the __ Consulting Engineers report attached 58550J SR 02 imh gdt jc.pdf Dated confirmed on 26th April 2017 upon a re-visit to site once close inspection and access to all walls could be achieved. Cxxx propose to carry out the recommended corrective actions shown on Page 3 part 4. This corrective action will be applied to the common stair core area also for aesthetics. Cxxx will utilize all components for the repair that were previously agreed as part of Cxxx-NCR-000460. This proposed resolution supersedes any of previous proposed remediation's indicated currently in " Evidence for Correction and Corrective Action area " as more intimate clarity on joint condition has been attained. *************************************************************************
| 03SR - Stations (RfL) | Cxxx-NCR-000478 | NCR | Fisher St { Concrete poured with out of Spec GGBS Content } |  | Contr | SKC |  |  | 2017-02-24 | 2017-03-07 10:24 | 11 | 2016-09-27 15:10 | Civil - Civil Engineering General | 2000 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Clause KF10.1402 iv) of the Civil & Structural spec for Fisher Street (Cxxx-JUL-S-RSP-CR094_SH005_Z-50001 Rev 3.0), states that the amount of GGBS a concrete mix should contain is between 50-90%. Concrete was placed in line with Cxxx-SKC-C-LRC-CR094-50219 whose mixes complied with relevant British standards & at the time what was believed to be compliant with Cxxx-JUL-S-RSP-CR094_SH005_Z-50001 Rev 3.0. After the event it was noted that these mixes did not comply with Clause KF10.1402 iv. Structures effected by this non compliant mix are : All B4 base structural elements. B4 / B3 Jump form walls. Once realised Cxxx reverted back to a mix which complied with the British Standards and site specific structural spec. ****************************************** Cxxx Response 07/12/2016 : After further review of information held within Cxxx-JUL-S-RSP-CR094_SH005_Z-50001 & BS 8500-2 It is Cxxx’s belief that as the mix in question complies with KF10.1401 a) “Constituent materials shall comply with Section 5 of BS EN206-1 and Section 4 of BS 8500-2. “ BS-8500-2 See section 4.2 “Where cements and combinations have been specified using a broad designation, the producer shall select one of the cements or combinations from Table 1 for the specified designation. Where neither a DC-class nor a specific cement or combination type is specified, the producer shall use one of the cements or combinations from Table 1. “ KF10.1402 p) “ Where agreed by the Project Manager the concrete mix may contain the following cementitious additions, in the proportions allowable by the exposure class as defined in BS 8500: i) Ground granulated blast furnace slag (GGBS) in accordance with BS EN 15167. ii) Fly Ash in accordance with BS EN 450-1. iii) Silica fume in accordance with BS EN 13263.” The extract from BS 8500-2 Table 1 General purpose cements and combinations (1 of 2) states. “CEM I cement conforming to BS EN 197-1 with a mass fraction of 6% to 20% of combination of GGBS conforming to BS EN 15167-1 “this is applicable to CIIA-S. The mix in question is CIIA-S with a GGBS content of 20%. BS 8500 allows for GGBS to be as low as 6% of the combination (for CIIA-S type concrete). In the previous response received it was noted that “Cxxx has previously objected to mixes with less than 50% GGBS at Fisher St (see Cxxx-FCD-000601 - FIS - Allowable GGBS Content in Concrete) and also other shafts (see Cxxx-RFI-000669 STG).” But KF10.1402 a) seems to contravene these RFI responses, reason being: “ Cement to BS EN 197-1, from manufacturers who are BSI registered firms of assessed capability in accordance with ISO 9000- Quality Assurance “ It is noted that from BS 8500-2 Table 1 General purpose cements and combinations (1 of 2) states. “CEMI can be used with 0% GGBS “ As this clause allows for a mix to be designed with 100% cement and no GGBS Content. It is Cxxx’s view that the current mix in question is superior to a 100% cement mix as it provides greater durability complying with KF10.1303). If a 100% cement mix allowed by the spec can offer 120 years, durability is not an issue with a mix containing 20% GGBS { which is primarily used to provide protection against both sulphate attack and chloride attack and furthermore to limit the temperature rise in large concrete pours} as it offers increased durability. Thermal cracking is primarily a worry in deeper pours (generally greater than 500mm deep in plan) that required to limit the temperature rise, this generates both lower peak and less total overall heat. The Walls are Max 300mm wide and the slabs are 250mm deep structurally. Cxxx have carried out a visual inspection of all structures poured and there are no signs of cracking. In relation to KF10.1402 a) iv) “ A mixture of BS EN 197-1 and BS EN 15167-1 and 2 (Specification for ground granulated blast furnace slag for use with cement) provided that the amount of GGBS is not less than 50% nor more than 90% by weight of total cement. “ Cxxx are in the belief that this clause applies more to protect against chloride attack, GGBS is used at a replacement level of 50% in concrete. This level of Chloride attack relates to marine environments / road bridges & Abutments. The reinforced concrete poured inside the footprint of the shaft are not as susceptible to this as the mentioned structures. Cxxx responded to the NCR by stating that they were concerned about the “durability requirements and crack widths due to early age thermal cracking”, Cxxx would question the validity of this concern when concrete poured has 20% more than the spec contemplates. Cxxx Note “Apart from the concrete’s constituent materials and strength the works documents require the concrete to fulfil and satisfy many other requirements including durability requirements (e.g. Structural Spec Cxxx-JUL-S-RSP-CR094_SH005_Z-50001 Rev 3.0 KF10.1303). “ Cxxx believe in relation to this requirement that we have fulfilled the requirement as the Mix through complying with BS 8500-2 Table 1 / KF10.1401 a) & KF10.1303 as the benchmark is BS8500-2. Cxxx Note “The concrete at B4 level includes sumps to collect water” this is noted but with the omission of shaft drainage the water now collected by this sump is negligible, and will only be in contact with excessive water in the event of a firefighting situation. Furthermore this Sump will not be exposed to sitting water as the sump pump is an automatic discharge. Cxxx Note “The core from B4-B3 level is subject to compression.” this is again noted but please refer to previous statement in relation to KF10.1402 a) that the installed concrete is more durable than the spec suggests is allowable “CEMI can be used with 0% GGBS “ Cxxx note “that measures could be adopted to enhance the long term durability of the affected concrete (such as surface applications), but the appropriateness and implications (e.g. ongoing maintenance) of these would need to be discussed and agreed with CRL”. Cxxx believe in relation to this requirement that we have fulfilled the requirement as the Mix is in line with BS 8500-2 Table 1 / KF10.1401 a) & KF10.1303, therefore no action is required on this unless directed by PM. In conclusion it is Cxxx’s view that in complying with all of the above that this is no longer an NCR and propose cancelling. ****************************************** Cxxx Response 27/02/2017 : Further to discussion and subsequent site visit by Cxxx / CRL representatives on 18/01/2017, Cxxx note the following in relation to the durability of the concrete poured at Level B4/B3: Cxxx have complied with the requirements of Crossrail CEDS: • CR-STD-303-1 Introduction and general requirements • Cl. 1.15 – Design Life • Cl. 1.17 Durability • CR-STD-303-2 Tunnels and shafts • Cl. 2.2.2 Durability The Cxxx Stage E Architectural Specification Cxxx-JUL-A-RSP-CR086_SH003_Z-50001 Rev 3.0 cl JA.5801 e) defines the Environment Category of the shaft (internal) as C4. Based on further design development and risk assessment, Cxxx have reclassified the Environment Category of the shaft (internal) as C2. This C2 classification has now been accepted at the Cxxx Stage F Gate 3 and therefore the expected environmental conditions within the shaft can be considered to impose far less detrimental impact on the long term durability of the concrete than the previous C4 classification. It is also noted that Cxxx have designed the waterproof membrane for the SCL section of the shaft to provide an internal ‘dry’ environment such that there is negligible seepage within the shaft. In reality the location of the concrete poured at B4/B3 level is within an internal environment which is less onerous than CEDS non location specific requirements. Cxxx note that the B4/B3 concrete was poured several months ago. At the wall sections, cracking / micro-cracking in vertical alignment should not be of great concern due to compressive forces. Horizontally, as the wall lengths are not excessive it is considered that the stresses developed will be low. Based on the site visit on 18/01/17, Cxxx note that CRL/Cxxx did not notice any visible cracks of any concern. Even at localised zones where stresses may be concentrated, such as around door openings, CRL/Cxxx only noted a single visible crack between two openings but this was not raised as a specific concern to Cxxx. In terms of early age heat of hydration shrinkage cracking, this should not be of concern due to relatively thin sections of concrete. Again, based on the site visit on 18/01/17, CRL/Cxxx did note any visible cracks of concern to Cxxx. Cxxx therefore propose to use as is.
| 03SR - Stations (RfL) | Cxxx-NCR-000479 | NCR | R2 Riser - High Level CMS Aperture |  | Contr | SKC |  |  | 2016-11-27 | 2016-11-24 16:14 | -3 | 2016-09-28 12:57 | Electrical - Cable Management | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Design Problem - Conflicting information on drawings | Completed |  | At Stepney Green Shaft the R2 riser at B1 level accommodates the 25kV traction cable route. At Level B1 the 900mm traction cable tray exits out of the R2 riser at high level. The height of the aperture provided is of 300mm, it should be lowered/enlarged by approx 150mm to allow for fire stopping and the size of the 25kV cables. Please refer to electrical drawing Cxxx-SKC-E-DDA-CR094_SH005_2-00242 for the 25kV CMS route at B1 level. Please see attached photograph for current aperture configuration.
| 03SR - Stations (RfL) | Cxxx-NCR-000480 | NCR | ESS - Incorrect position of 1no. cast in plate at first floor level |  | Contr | SKC | ELS - Eleanor Street Shaft (Central) |  | 2016-12-27 | 2016-12-02 13:49 | -25 | 2016-09-28 15:03 | Architectural - Balustrade | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | The cast in plate at the first floor level shown on the attached marked up sketch, has been installed as per drawing Cxxx-JUL-S-DDA-CR094_SH007-00207 C06 and not as per the updated revision C07.
| 03SR - Stations (RfL) | Cxxx-NCR-000481 | NCR | Windpost fabrication and installation |  | Contr | SKC |  |  | 2017-01-16 | 2017-01-12 08:35 | -4 | 2016-09-30 14:54 | Architectural - Brickworks/Blockworks | 500 |  | Documentation and Records | Repair | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | __ have engaged __ to manufacture windposts for blockwork walls to meet programme prior to having the required documentation in place. The welding statement, MCR and ITP have been submitted to Crossrail but have not yet been approved.
| 03SR - Stations (RfL) | Cxxx-NCR-000482 | NCR | HV and LV CMS Routing |  | Contr | SKC |  |  | 2016-11-24 | 2016-11-24 14:27 | 0 | 2016-10-10 14:21 | Electrical - Cable Management | 500 |  | Incomplete Works | Repair | 4 (0.5-3k) | Complete | Previous Construction - Interfacing issues | Completed |  | 1. The link between SRHV1 at level B2 and TR1 at level B1 is done via 450mm cable tray. The design intent is for the HV cable link between TR1 and SRHV1 to drop from level B1 to Level B2 via a floor penetration, however this floor penetration is non-existent. 2. Similarly the link between SRLV1 at level B2 and TR1 at level B1 is done via an interconnecting busbar. The design intent is for the busbar link between TR1 and SRLV1 to drop from level B1 to Level B2 via a floor penetration, however this floor penetration is non-existent. The floor slab at this location is 400mm thick reinforced concrete. Please refer to drawing number Cxxx-SKC-E-DDA-CR094_SH005_2-00242 and attached sketch for details on the CMS routing.
| 03SR - Stations (RfL) | Cxxx-NCR-000483 | NCR | Damaged FCU front panel |  | Contr | SKC |  |  | 2017-05-31 | 2017-03-31 12:46 | -61 | 2016-10-13 10:28 | Mechanical - Heating Ventilation & Air Conditioning | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Improper preservation of material after installation | Completed |  | Front panel of an FCU panel has been damaged in CER 1 - B1
| 03SR - Stations (RfL) | Cxxx-NCR-000484 | NCR | Damaged Earth Cable Sheathing |  | Contr | SKC |  |  | 2017-05-15 | 2017-05-19 14:45 | 4 | 2016-10-13 15:07 | Electrical - Cable Management | 500 |  | Material | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Improper preservation of material after installation | Completed |  | The sheathing of the earth cable in SR 22Kv HV1 has been damaged when the screed was laid.
| 03SR - Stations (RfL) | Cxxx-NCR-000485 | NCR | Stepney Green - Intervention Stairs - Galvanised Coating |  | Contr | SKC |  |  | 2017-06-30 | 2017-05-08 14:32 | -53 | 2017-02-17 07:22 | Architectural - General | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Subcontractor Problems - Other | Completed |  | There was a localised build up of galvanising in an area and so it was sanded down. Too much was taken off and exposed the metal work. This was carried out in the factory prior to delivery to site. It was picked up once the stairs were off loaded.
| 03SR - Stations (RfL) | Cxxx-NCR-000486 | NCR | Stepney Green - Intervention Stairs - Acid Weep from Welded Angle |  | Contr | SKC |  |  | 2017-06-30 | 2017-05-09 10:07 | -52 | 2017-02-17 07:16 | Architectural - General | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Verification Problems - Other | Completed |  | Acid weep from welded angle has discoloured the top of the finished box section. The angle which is completely welded on three sides only and intermittent welded on the top side to allow moisture to escape and prevent any explosion during the galvanising process, is showing some weeping from the joint.
| 03SR - Stations (RfL) | Cxxx-NCR-000489 | NCR | Limmo Shaft - B1 CMS (excluding Level B1) - By Exception Technical Assurance Process |  | Contr | SKC |  |  | 2017-04-28 | 2017-04-05 12:10 | -23 | 2016-10-17 | Electrical - Cable Management | 500 |  | Planning | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | In order to meet the Limmo construction programme the design technical assurance of CMS has obtained through the CRL By Exception process (CRL1-XRL-O7-GPD-CR001-50023). Refer RiR ref Cxxx-SKC-Z-LRC-CR144_WS155-50002 Rev 5.0 for drawing details/references. Refer completed Technical Assurance By Exception Gate Risk Assessment form (Cxxx-SKC-E-__-CR144_WS155-50002 Rev 1.0) appended to this NCR.
| 03SR - Stations (RfL) | Cxxx-NCR-000491 | NCR | Mile End Shaft Lintels B0 Lift Lobby and B9 Riser Room |  | Contr | SKC |  |  | 2017-04-28 | 2017-03-30 21:51 | -29 | 2016-10-25 18:33 | Architectural - Brickworks/Blockworks | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | As per the attached photos, minor cracking has been identified by Crossrail within the Mile End Shaft Lintels B0 Lift Lobby and B9 Riser Room. 15/12/2016 has reviewed this further with its designers and proposes the below the way forward. 01/12/2016 has reviewed the cracking with its designers comments as per the following: Level 00: The loadings on the top of the lintel have been reviewed and found to be conservative against the lintel suppliers maximum loading restriction, however it is noted that the crack (approx. 0.2mm) continues to the underside suggesting that it could be caused from bending. At the moment, it is noted that the crack is relatively small. Level B9: The cracks appearing only on one side of the lintels, not propagating to the underside and the crack width of 0.1mm suggests that these cracks are superficial.
| 03SR - Stations (RfL) | Cxxx-NCR-000492 | NCR | __ - Blockwork GL 5-14 at Levels B1-B4 - By Exception Technical Assurance Process |  | Contr | SKC |  |  | 2017-08-31 | 2017-10-26 08:35 | 56 | 2016-11-02 18:17 | Architectural - Brickworks/Blockworks | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Use of unapproved drawings | Completed |  | In order to meet the Stepney Green early access construction programme, the design technical assurance of the Blockwork drawings between grid lines 6-14 on Levels B1-B4 has been obtained through the CRL By Exception process (CRL1-XRL-O7-GPD-CR001-50023). Refer to RiR (Cxxx-SKC-Z-LRC-CR094_WS108-50001) Rev 5.0 for drawing details/references. Refer to completed Technical Assurance By Exception Gate Risk Assessment form (Cxxx-SKC-C-RGN-CR094_WS108-50017 Rev 1.0) appended to this NCR.
| 03SR - Stations (RfL) | Cxxx-NCR-000494 | NCR | ESS - Construction of blockwork walls using P status drawings |  | Contr | SKC | ELS - Eleanor Street Shaft (Central) |  | 2017-05-05 | 2017-04-26 14:40 | -9 | 2016-11-01 13:00 | Architectural - Brickworks/Blockworks | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | In order to meet the Eleanor Street Shaft construction programme, the construction of the blockwork walls has commenced using P status drawings as the stage F design has not been finalized yet. Cxxx and CRL is currently working through by exception review process.
| 03SR - Stations (RfL) | Cxxx-NCR-000495 | NCR | ESS - 2no. cast in plates not installed on core wall lift 10 |  | Contr | SKC | ELS - Eleanor Street Shaft (Central) |  | 2017-03-31 | 2017-03-29 10:00 | -2 | 2016-10-31 16:09 | Structural Engineering - Steel Member | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | 2no. cast in galvanised plates have not been installed during the construction of the core wall at lift 10. Please see attached marked up sketches showing the missing cast in plates.
| 03SR - Stations (RfL) | Cxxx-NCR-000496 | NCR | Mile End Shaft - In situ slip resistance test for Steel Staircase |  | Contr | SKC |  |  | 2017-05-22 | 2017-04-30 15:43 | -22 | 2016-11-04 09:08 | Architectural - General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | In situ slip resistance test results (PTV) for Mile End Shaft stairs pass for normal exposure dry conditions (PTV greater than 36), however in wet condition potentially do not meet the Contract specification. 5/12/2016 have consulted with its designer to respond to this NCR. confirms that it has undertaken the design in accordance with the regulations and standards specified and complied with the works information. The details are as follows: • notes that slip testing on the stairs were undertaken using Slider 55 and Slider 96 in accordance with UKSRG for a profiled surface. It is noted that Slider 55 achieved moderate slip potential result in wet conditions (i.e. average of PTV 29.8) and Slider 96 achieved a low slip potential result in wet conditions (i.e. average of PTV 40.2). • It is and its designers opinion that if the stairs are expected to meet the slip resistance requirements in wet conditions, these should be assessed by obtaining readings to achieve a minimum PTV of 36 (low slip potential) to BS 7976. The tests should be carried out by using the 4S Slider with a Rubber Hardness IRHD 96 (i.e. Slider 96) as this is the best representation of everyday pedestrian shoes and thus meets the requirement of BS 5395-1 Section 7. It is noted that TRL Slider – IRHD 55 (Slider 55) represents barefoot floor conditions and therefore is not applicable in this situation. Furthermore: • It is noted that the architectural specification Cxxx-SKC-A-RSP-CR094¬_WS109-50001 rev 3.0 in Section JM10, specifies that the floor should be evaluated in both dry and wet conditions and that samples should be tested at the stages of approval, production and post-installation (in situ). note that it has complied with this Clause. • BS 5395-1 in Section 7, indicates that the “PTV should be measured in the conditions to which the stair is likely to be exposed.” note that this response interprets this requirement correctly. • It is noted that due to the shaft construction, with a double concrete wall with a waterproof membrane in between, the shaft is designed to remain dry, safe from water ingress during its lifetime. • It is and its designers understanding that under normal circumstances the staff accessing the below ground levels of the shaft will have the lift available. If the fire alarm is activated, the lift is to return to ground floor level to be available to be used by the emergency fire brigade services. Any maintenance staff in the below ground levels should evacuate by using the stairs. It is noted that this scenario represents the most likely event to which the stair is likely to be exposed. • Notwithstanding the above, and its designers cannot rule out maintenance staff using the stair instead of the lift during normal access and maintenance activities, albeit less likely. • It is noted that in both these scenarios the stair is more than likely to be dry, however it should be noted that some staff may be wearing shoes with wet soles when using the stairs. This could be due to having worked on any pipe leak for example. • It is also noted that the fire brigade could use the stairs, although the firefighting lift has been designed so they don’t have to. If elements of the fire brigade using the stairs when tackling an emergency is considered likely, than it is expectable they will be wearing shoes with wet soles. • In both cases, note that the rubber slider best represents these scenarios is Slider 96 which achieved a low slip potential result (i.e. average of PTV 40.2). In view of these notes, and its designers considers very improbable that the stair could be used in any likely scenario other than a dry environment, thus meeting the prescribed in BS 5395-1. therefore confirms that it has undertaken the design in accordance with the regulations and standards specified and complied with the works information. 28/02/2017 Further to the above, the meeting between and Crossrail Cxxx on 5 January 2017 and Cxxx-EWN-01792, adds on the following additional comments: • JL30.1206 (The Employers Spec) calls for galvanised mild steel chequer plate to form the treads and risers as well as all exposed metal surfaces shall have galvanised steel finish – accords with this. • JL30.2203 (The Employers Spec) calls for testing in wet and dry conditions to obtain the PTV specified – works info does not specify PTV values, BS 5395-1 specifies PTV value for chequer plate on Page 18 Table 3 – accords with this. • Notwithstanding the BS 5395-1 Clause 7 (B) NOTE 2 “Any flooring material providing sufficient slip resistance for use on the level, typically with a PTV greater than 36, is suitable for use on stairs.” It is noted that that the selected material, steel chequer plate, is part of the Employer Design in our Works Information. If this material was ever to achieve the most stringent compliance with BS 5395-1 PTV values in wet conditions with both sliders, then this requirement contradicts directly with the standard (i.e. BS 5395-1 specifies PTV value for chequer plate on Page 18 Table 3). The value on the right of the table is the wet PTV value and it’s only 30 (moderate slip potential). Even if these values are only indicative, it would appear from the aforementioned Table that the full stringent compliance in both dry and wet conditions was never realistically probable for to be able to achieve.” • It was discussed at the meeting between and Crossrail Cxxx on 5 January 2017 to look into a treatment to the chequer plate. note that The Employers Spec does not state to apply a treatment to the chequer plate. Should Crossrail Cxxx require the chequer plate to meet PTV 36 in wet and dry conditions for both slider 55 and slider 96 then an instruction is warranted. • It should be noted that initial investigations of coatings from a range of suppliers do not appear to have been previously tested on a profiled surface in wet conditions with Slider 55.
| 03SR - Stations (RfL) | Cxxx-NCR-000497 | NCR | Mile End - NCR - Damaged Cxxx Cable |  | Contr | SKC |  |  | 2017-01-06 | 2016-12-19 16:50 | -18 | 2016-11-07 11:29 | Communications and Control Systems | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Improper preservation of material after installation | Completed |  | Cxxx installed one of their cables in the COMMS riser at Mile End Shaft earlier this year. The cable has been left coiled at B8 adit pending final connection with the tunnel COMMS services. In the time between installation and present time works have been ongoing in the B8 adit. While works were ongoing the cable has been damaged, see pictures attached.
| 03SR - Stations (RfL) | Cxxx-NCR-000498 | NCR | Firestopping - Exceeding Manufacturers Guidelines |  | Contr | SKC |  |  | 2017-07-31 | 2017-06-28 13:52 | -33 | 2016-11-08 17:34 | Fire - Compartmentation | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Not Defined | Completed |  | The __ Intumescent Sealant has been installed to the movement joints in the block work throughout the shaft incorrectly into gaps up to 50mm. Exceeding the manufacturers guidelines of 30mm.
| 03SR - Stations (RfL) | Cxxx-NCR-000499 | NCR | Firestopping - Installation Of Mastic |  | Contr | SKC |  |  | 2017-07-31 | 2017-06-29 13:09 | -32 | 2016-11-09 10:01 | Fire - Compartmentation | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | The intumescent sealant installed in areas is starting to de-bond and peel away from the blockwork where the surface hasn't been correctly prepared by the contractor prior to installation.
| 03SR - Stations (RfL) | Cxxx-NCR-000500 | NCR | Firestopping - Installation Of __ |  | Contr | SKC |  |  | 2017-08-31 | 2017-06-29 14:52 | -63 | 2016-11-09 10:52 | Fire - Compartmentation | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | In areas the __ packing that is placed between the blockwork movement joints has not been packed/installed tightly enough to achieve a compact finish and provide the correct backing for the fire stop sealant.
| 03SR - Stations (RfL) | Cxxx-NCR-000501 | NCR | Pile 11A out of position |  | Contr | SKC |  |  | 2017-01-31 | 2017-01-17 10:33 | -14 | 2016-11-16 11:09 | Civil - Structural Engineering | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Upon fixing reinforcement for the ground beams, it was found that pile 11A was out of position by 340mm in one direction (northing). Therefore pile 11A exceeds the 75mm tolerance by 265mm (see attachment ‘Pile 11A as-built survey’). This error was not captured in ’s original as-built survey of the pile. This is because the as-built survey compared against ’s design coordinates for the piles. Upon investigation, it was found that the design coordinates for pile 11A were incorrect, hence no error originally being apparent. The design co-ordinates were incorrect due to error in plotting to obtain the co-ordinates in AutoCAD. This was necessary as at the point of installation no setting out information for the piles had been provided. A new as-built survey using the correct design co-ordinates for the pile revealed the error.
| 03SR - Stations (RfL) | Cxxx-NCR-000502 | NCR | Fisher St { Couplers in incorrect position for Beam type B1 on B3 Slab Level } Room LVR room GL 4B |  | Contr | SKC |  |  | 2016-11-30 | 2016-11-28 13:38 | -2 | 2016-11-16 11:20 | Civil - Civil Engineering General | 3000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | On exposing couplers for the B1 beam it has become apparent that there is a misalignment and Incorrect positioning of couplers in Wall 6 and Wall 2. There is no issue on the vertical height of the couplers said issue is in the horizontal plane.
| 03SR - Stations (RfL) | Cxxx-NCR-000503 | NCR | Piles 14 & 15 out of tolerance |  | Contr | SKC |  |  | 2017-01-21 | 2017-01-17 10:24 | -4 | 2016-11-22 15:59 | Civil - Structural Engineering | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Upon fixing reinforcement for the ground beams, it was found that piles 14 and 15 are out of position (similar to previously raised Cxxx-NCR-000501 and Cxxx-RFI-000853 for pile 11A). The as-built coordinates are over the allowable 0.075m : Pile 14 (GL11) – 1.36m from GL A to centre of pile rather than 0.965m (320mm out) 0.68m from GL 11 to centre of pile rather than 0.760m (5mm out) Pile 15 (GL 12)- 1.33m from GL A to centre of pile rather than 0.965m (290mm out) 1.01m from GL 12 to centre of pile rather than 1.110m (25mm out) As-built results are illustrated in the attachment ‘pile 14 & 15 as-built’. This error was not captured in ’s original as-built survey of the pile. This is because the as-built survey compared against ’s design coordinates for the piles. Upon investigation, it was found that the design coordinates for pile 11A were incorrect, hence no error originally being apparent. The design co-ordinates were incorrect due to error in plotting to obtain the co-ordinates in AutoCAD. This was necessary as at the point of installation no setting out information for the piles had been provided. A new as-built survey using the correct design co-ordinates for the pile revealed the error.
| 03SR - Stations (RfL) | Cxxx-NCR-000504 | NCR | Limmo Shaft CER Room B1 - Firestopping condensate pipe |  | Contr | SKC |  |  | 2016-12-16 | 2016-12-16 12:22 | 0 | 2016-12-02 08:29 | Mechanical - Heating Ventilation & Air Conditioning | 500 |  | Incomplete Works | Rework | 4 (0.5-3k) | Complete | Design Problem - Not Defined | Completed |  | The condensate pipework serving the 2 Fan Coil Units (FCU) in CER, discharges into the cavity between the block work wall and the D-wall. Rubber foam insulation was installed around the pipework across its length. The NCR raised at the point where pipework traverses through the wall, where the rubber foam was maintained going through the wall. This installation method does not allow firestopping to be installed.
| 03SR - Stations (RfL) | Cxxx-NCR-000507 | NCR | Infill Slabs Surface Defects |  | Contr | SKC |  |  | 2017-08-31 | 2017-09-25 07:55 | 25 | 2016-12-06 10:47 | Civil - Civil Engineering General | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Uncontrollable water dripping down the wailer beams, as depicted in the attached picture at B1 Grid line 6, onto the freshly poured concrete has led to grout loss and concrete finish impairment. propose to scabble back this area locally to expose a suitably roughened surface to receive a __ HB45 (MCR number, Cxxx-SKC-C-LRC-CR094-50237) finish, to provide a smooth surface. The repair will follow the procedure as indicated in the Concrete Repairs ITP for Stepney Green (document number Cxxx-SKC-C-ITP-CR094_WS108-50010). This has occurred in numerous areas, on the infill slabs and it is proposed this NCR covers all areas for the infill slabs and exact locations will be marked up on the asbuilts.’ HI comment 24/05/2017 In response to Cxxxs comment regarding material can Cxxx please assess the attached __ __ S. Should Cxxx accept this material in principle Cxxx will raise the MCR as necessary.
| 03SR - Stations (RfL) | Cxxx-NCR-000509 | NCR | Limmo Peninsula - Shaft - Intervention Staircase/COM2 - Incorrect setting out |  | Contr | SKC |  |  | 2017-07-31 | 2017-06-15 12:27 | -46 | 2016-12-07 19:18 | Architectural - Brickworks/Blockworks | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Between access levels B5 to B2 the a single blockwork wall has been set out incorrectly due to the subcontractor installing lintels which are longer than stated in the lintel schedule and thus overhangs by more than 150mm of the door opening. Please see attachment for the floors effected. This also resulted in the intervention staircase not fitting in (durbar landings were now too long)
| 03SR - Stations (RfL) | Cxxx-NCR-000510 | NCR | Mile End - NCR- LUX levels at Mile End Headhouse |  | Contr | SKC |  |  | 2017-01-30 | 2017-01-31 07:12 | 1 | 2016-12-05 19:06 | Electrical - Lighting | 500 |  | Testing and Commissioning | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Following from the Lighting Levels testing at Mile End on the 18/10/2016, it was found that the lighting levels at the following areas were lower than the Average Lighting Level (150 lux) value deeming them non-compliant. These areas were: -FAN room lobby -PFR/LCR room lobby - WC room All these lights have the 650 mm long, "A" type luminaire fitting installed.
| 03SR - Stations (RfL) | Cxxx-NCR-000511 | NCR | Insufficient Moment Capacity in Steel Beam Connections |  | Contr | SKC |  |  | 2017-03-31 | 2017-02-17 08:55 | -42 | 2016-12-06 14:23 | Structural Engineering - Welding | 500 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | As per Cxxx-PMI-810 and Cxxx-PMI-824, Cxxx installed structural steelwork before the detailed design review by Cxxx. The detailed design review by Cxxx showed that there was insufficient moment capacity within the connection plates on the steelwork. The design showed that an increase in the fillet weld from 8mm to 10mm shown in the documentation listed below would provide the required moment capacity through the plate. All the beams that had not been installed within the shaft were taken back to the fabrication yard and the weld were increased to 10 mm fillet welds. However the beams that had already been installed, required structural stiffeners to increase the moment capacity. Drawing packs Cxxx-SKC-S-XCL-CR094_WS108-50005 Stepney Green Shaft – Basement Roof to Level B2 Structural Steel Connection Designs between Gridlines 2-6 and Cxxx-SKC-S-XCL-CR094_WS108-50006 Stepney Green Shaft – Basement Roof to Level B2 Structural Steel Connection Designs between Gridlines 10-14 contain this information and this NCR can be considered closed once this documentation is code 1. Some space proofing works will be required once the structural stiffeners are installed, however this will be captured in separate PTRs.
| 03SR - Stations (RfL) | Cxxx-NCR-000512 | NCR | ESS - Inaccessible grout injection tubes |  | Contr | SKC | ELS - Eleanor Street Shaft (Central) |  | 2017-04-28 | 2017-04-03 18:04 | -25 | 2016-12-06 15:39 | Civil - Tunnelling | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | 8 Grout tubes boxes within the shaft secondary lining are inaccessible as they clash with the B1 structural steel members and B1 concrete floor slab. the sketches below show the location of the missing grout tubes. Please see attached dwg (ZONE 10 (B1) - J589-Cxxx-RR-124) which shows tubes are inaccessible. Update 27/03/17 Cxxx can confirm that: - In total 6 boxes are blocked / encased at the below locations, not 8, this was a typo error upon PTR submission. - R8T06,B06,T07,B07,T08,B08,T09,B09 are encased within the B1 floor slab, although stated on the attachment as behind a beam this comment will be amended prior to any document submission. ( 4nos boxes ) - R810,B10,T11,B11 are blocked behind a steel beam ( 2nos boxes ). Zone 9 attachment is replaced with relevant zone 8 sketch. This will match the plan level of previous attachment zone 8. Zone 9 did not correspond with the plan sketch therefore should be ignored. To avoid confusion, the name of zone 10 sketch has been changed to zone 8 to match the zone referenced on the sketch itself.
| 03SR - Stations (RfL) | Cxxx-NCR-000513 | NCR | Spaceproofing Structural Stiffeners Grid Line 2-4 |  | Contr | SKC |  |  | 2017-07-28 | 2017-04-24 07:56 | -95 | 2016-12-06 16:32 | Structural Engineering - Welding | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | As per Cxxx-SKC-S-XCL-CR094_WS108-50005 Stepney Green Shaft – Basement Roof to Level B2 Structural Steel Connection Designs between Gridlines 2-6 structural stiffeners are required in the locations as shown in ‘Sketch of Plinth Extension’. These stiffeners will protrude the finished floor level by approximately 100mm. To avoid a trip hazard in these areas Cxxx propose increasing the size of the plinths as per the attached sketches. Can Cxxx/CRL please confirm this proposal is acceptable. HI Comment 15/12/2016 As per the Cxxx/Cxxx/Cxxx Coordination meeting on 14/12/2016 it is noted that no parties have any issues with the increase of these plinths. Comment 22/03/2017 As discussed and agreed between __ and __ see attached mark up showing the original size of the plinths as well as the larger size as-builted plinths on B2 grid line 2-4.
| 03SR - Stations (RfL) | Cxxx-NCR-000514 | NCR | HRU Pentrations |  | Contr | SKC |  |  | 2018-03-26 | 2018-01-12 16:57 | -73 | 2016-12-08 17:21 | Structural Engineering - Structural Engineering - General | 1500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | 1) confirm the size of the cores do not meet the agreed design 150mm and 50mm, instead the contactor on site cored the at 127mm and 93mm respectively. As a Consequence of this the Roxtec seal transit system may potentially not achieve a water tight seal. 2) confirm when the contractor undertook the coring and subsequently a section of vertical reinforcement was also cored in the process.
| 03SR - Stations (RfL) | Cxxx-NCR-000515 | NCR | Lack of fusion in structural stiffener weld. |  | Contr | SKC |  |  | 2017-03-31 | 2016-12-15 16:34 | -106 | 2016-12-12 11:16 | Structural Engineering - Welding | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Upon the N__ (Non Destructive Test) ultrasound for the butt weld on B2 (see attached mark up for exact location) it became apparent that there was a lack of fusion approximately 3 mm thick running along the direction of the weld.
| 03SR - Stations (RfL) | Cxxx-NCR-000516 | NCR | ESS - Grillage door at IE1 adit |  | Contr | SKC | ELS - Eleanor Street Shaft (Central) |  | 2017-01-30 | 2017-01-24 07:16 | -6 | 2016-12-13 14:54 | Civil - Civil Engineering General | 500 |  | Design | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Cxxx manufactured and delivered on site the grillage door at IE1 adit RfL storage area with a clear opening of 1920mm and not 2000mm as specified on 591-0040-SKE-206 sketch attached on Cxxx-RFI-000579.
| 03SR - Stations (RfL) | Cxxx-NCR-000517 | NCR | Water seepage to fire boards within shaft and headhouse |  | Contr | COS | ELS - Eleanor Street Shaft (Central) |  | 2017-04-28 | 2017-04-12 12:00 | -16 | 2017-01-18 15:10 | Fire - Compartmentation | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | Rainwater ingress into the shaft has seeped into the __ fire boards at B4 and B3 soffit level as shown on the attached sketches and pictures. This occurred whilst the shaft was not watertight, i.e. when the roof had not been installed. The rainwater has left behind a slight discolouration of the __ boarding locally upon drying. Cxxx have contacted the manufacturer of the product, __, to determine if this water seepage will cause any detrimental impact to the usability of the affected boards. They replied by saying that the boards will only temporarily lose some strength in its wet state, however they will regain full strength upon drying - please refer to attached __ email. Cxxx are therefore satisfied that the boards can be left in their current state and will not need replacing. Can CRL confirm that this is acceptable?
| 03SR - Stations (RfL) | Cxxx-NCR-000518 | NCR | Stepney Green - Escape Stair Temporary Voids |  | Contr | SKC |  |  | 2017-03-27 | 2017-02-07 11:09 | -48 | 2016-12-15 17:45 | Structural Engineering - Reinforcement | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | installed temporary box outs to the escape stair north and south core walls. Following receipt of response to RFI "Cxxx-RFI-000857 Stepney Green - Cast Voids in Escape Stair Walls" it was identified that installed H10 bars and not H12s as required. Picture attached.
| 03SR - Stations (RfL) | Cxxx-NCR-000519 | NCR | Stepney Green - Lintels in Blockwork walls |  | Contr | SKC |  |  | 2017-02-28 | 2017-01-03 10:28 | -56 | 2016-12-16 14:39 | Architectural - Brickworks/Blockworks | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | 25kv room existing opening lintel was left within the blockwork without removal due to design changes. Removing lintels takes extra 3 more days to build the wall up back again.
| 03SR - Stations (RfL) | Cxxx-NCR-000520 | NCR | Spaceproofing Structural Stiffener B2 Grid Line 4.5 |  | Contr | SKC |  |  | 2017-07-28 | 2017-06-13 14:48 | -45 | 2016-12-18 15:35 | Structural Engineering - Steel Member | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | As per Cxxx/Cxxx/Cxxx/CRL coordination meeting on 15/12/2016 Cxxx intend to encase the structural stiffener on B2 grid line 4.5 in concrete. Some general notes as below. 1) C32/40 concrete. 2) 50 mm cover all around stiffener. 3) Plinth to be delineated by yellow paint. It is noted that no party had any major issue with this in the meeting on 15/12/2016, however can CRL please confirm this proposal is acceptable. HI comment 05/05/2017 please see attached correspondence raising the issue with Cxxx.
| 03SR - Stations (RfL) | Cxxx-NCR-000522 | NCR | LPS - Shaft - Benchmark |  | Contr | SKC |  |  | 2017-02-27 | 2017-02-20 09:36 | -7 | 2016-12-21 13:46 | Architectural - Brickworks/Blockworks | 500 |  | Incomplete Works | Rework | 4 (0.5-3k) | Complete | Procedure Problem - Lack of procedure | Completed |  | There is no benchmark at Limmo Peninsula for blockwork, Cxxx Architectural Specification Cxxx-SKC-A-RSP-CR144_WS155-50001 Cl JA.4011. Instead a blockwork test panel was presented to Crossrail for acceptance, this was completed for mortar colour finish validation for the Limmo/Fisher shafts.
| 03SR - Stations (RfL) | Cxxx-NCR-000523 | NCR | B1 and B2 RC walls |  | Contr | SKC |  |  | 2016-03-31 | 2017-01-03 15:32 | 278 | 2016-12-20 16:48 | Structural Engineering - Structural Engineering - General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Cxxx note that the walls on B2/B1 and B1/B0 have been constructed as per Cxxx-JUL-S-DDL-CR094_SH005-02679. This drawing was not part of the original works information, but as per Cxxx-PMI-00944 the building of the wall to this drawing has been accepted. Cxxx-PMI-00919, however, has also issued Cxxx-JUL-S-DDL-CR094_SH005-50661 to Cxxx. As part of Cxxx-PMI-00919, Cxxx were required to raise this NCR to allow a cross check of the two drawings to ensure the that the dimensions of as built openings are acceptable for MEP and A requirements.
| 03SR - Stations (RfL) | Cxxx-NCR-000524 | NCR | B1 Cxxx Opening Hatch |  | Contr | SKC |  |  | 2018-05-01 | 2018-03-09 15:39 | -53 | 2016-12-21 08:50 | Structural Engineering - Structural Engineering - General | 1000 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | As per Cxxx-PMI-00863, Cxxx were instructed to build the B1 level access hatch to Cxxx-JUL-S-DDA-CR094_SH005-50211 P04 (dimension sizes of 4.341 m x 4.114 m) on 27/09/2016. However as per Cxxx-PMI-000810 had already fabricated and galvanised the steel beams to be installed in this area prior to receiving this instruction and as such the hatch has been constructed to Cxxx-JUL-S-DDA-CR094_SH005-50211 P03 (dimension size 4.0 m x 4.0 m). The decision was made to proceed as this slab was critical to meet single line diagram dates, namely the CER room on B01 which would have been delayed further if the beam needed to go through fabrication again for adjustments to be carried out and then re-galvanising.
| 03SR - Stations (RfL) | Cxxx-NCR-000526 | NCR | MCC Room Doorway - B2 |  | Contr | SKC |  |  | 2017-02-28 | 2017-01-27 11:48 | -32 | 2017-01-09 11:04 | Architectural - Brickworks/Blockworks | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Due to the B2 structural beam weld failure a stiffener bracket was welded to the beam at GL D-E, 5.5. This resulted in a concrete plinth being created above the FSL at GL D-E, 5.5 in the wall of the MCC room. The plinth also protruded into the MCC doorway. After discussions with Cxxx (the owner of the MCC room) it was agreed that the doorway could be reduced in width to 1850mm. The doorway was also shifted across to be closer to the RC wall. To facilitate this reduced block width block brackets were installed on the RC wall. Due to program constraints the works were carried out once agreed via email with Cxxx. See attached correspondence
| 03SR - Stations (RfL) | Cxxx-NCR-000528 | NCR | Blocked Reinjectable grout tubes |  | Contr | SKC | ELS - Eleanor Street Shaft (Central) |  | 2017-03-27 | 2017-03-02 14:30 | -25 | 2017-01-17 13:55 | Civil - Tunnelling | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Waterproofing as-builts were complete in the Shaft, see Package Cxxx-SKC-C-DWG-CR094_WS110-50223. Following this, the reinjectable grout hoses were tested by __ and witnessed by Cxxx and . Each grout hose was testing in the following procedure 1. Water was pumped through the pipe using a pump 2. This was pumped for 1 minute or until the water had come through the pipe and out the other side 3. Where water wasn't seen coming through to the other pipe, this pipe was also tested. The results which can be seen in the attached documents: Open - The grouting pipe is clear , can grout from this side OK - Both sides are clear, can grout using this line and then flush to be used again Blocked - Both sides are clear but there is a blockage in the middle, can grout from each side once only Closed - The pipe is fully blocked, no grouting can be completed here Missing - The pipe was buried during the pour, no grouting can be completed here
| 03SR - Stations (RfL) | Cxxx-NCR-000530 | NCR | Windpost-Steel beam install |  | Contr | SKC |  |  | 2017-05-25 | 2017-02-16 13:54 | -98 | 2017-01-17 15:46 | Architectural - Roofing & Exterior Treatment | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Holes have been drilled into Steel beam for Wind post fixing prior to detail being accepted by Cxxx.
| 03SR - Stations (RfL) | Cxxx-NCR-000531 | NCR | COM-R2 B3 Riser out of Position |  | Contr | SKC |  |  | 2017-02-28 | 2017-02-08 08:45 | -20 | 2017-01-17 12:51 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | COM-R2 has been cast out of position by 50mm due to incorrect setting out. See attached Mark up for Clarity. A review has been carried out of the Stage F containment, this shows that there is enough capacity within the riser to allow for the out of position formed riser. The block wall will be set in its correct position not to interfere with room sizing's for the adjacent ESR room & B4 blocks are completed. There will be an overhang on one face of 50mm for 1550mm which has been confirmed acceptable with contractors designers for block work. Please note the wall is 215mm wide.
| 03SR - Stations (RfL) | Cxxx-NCR-000532 | NCR | ESS - Overstressed steel to concrete connections in shaft intervention side |  | Contr | SKC | ELS - Eleanor Street Shaft (Central) |  | 2017-08-28 | 2017-07-19 12:54 | -40 | 2017-01-18 09:28 | Civil - Structural Engineering | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Upon review of the General Arrangement drawings for the Eleanor Street Shaft – Shaft Steelwork - Upper Attenuator Level B3 Drawing Pack Cxxx-SKC-S-DWG-CR094_WS110-50019 it has been identified that connection 21 (referenced as connection H on Cxxx drawings) is overstressed. In particular, the connection specifies 2 no. M20 bolts, both of which have been found to be 50% overstressed when considering the final design loads. Cxxx notes that the floor slab above has been cast on 21/06/16 and the blockwork walls have been built on the 21/10/16. Cxxx are currently in the process of reviewing the design and a solution will be provided in due course.
| 03SR - Stations (RfL) | Cxxx-NCR-000533 | NCR | B1 Cable Rooms 2 & 3 layout change |  | Contr | SKC |  |  | 2017-02-28 | 2017-02-01 11:29 | -27 | 2017-01-24 16:09 | Architectural - Brickworks/Blockworks | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Single dividing wall between Cable Room 2 and Cable Room 3 has not been constructed as per the drawings. This has occurred due to the TTVS being located at the original design location of the dividing wall. Subsequently, individual walls were built to enclose each of the Cable Rooms - see attached mark-up. In-turn this results in the reduction of available space in each of these rooms
| 03SR - Stations (RfL) | Cxxx-NCR-000535 | NCR | Sec.Lobby 2 slab GL4/FH finish |  | Contr | SKC |  |  | 2017-05-19 | 2017-05-19 14:02 | 0 | 2017-01-30 08:17 | Structural Engineering - Finishes | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Management Problem - Improper resource allocation | Completed |  | The slab finish in the security room 2 is below the specified quality. This was due to restricted access & rapid dropping temperatures at the time of casting, leading to the application of frost blankets over the surface.
| 03SR - Stations (RfL) | Cxxx-NCR-000536 | NCR | CMS into SR 11kV HV1 - compound depth not acheived |  | Contr | SKC |  |  | 2017-06-30 | 2017-06-07 07:54 | -23 | 2017-01-30 10:23 | Fire - Compartmentation | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | Where 2no cable trunkings enter SR 11kV HV1 from South Corridor, minimum installation of 50mm of firestopping compound between CMS and edge of penetration has not been achieved. On the Switchroom side of the penetration, 35mm has been achieved and on the corridor side 45mm has been achieved. All other dimensions are conform ant.
| 03SR - Stations (RfL) | Cxxx-NCR-000537 | NCR | Fisher Street - Blockwork B4, B3 B1 - By Exception Process |  | Contr | SKC |  |  | 2017-05-29 | 2017-05-16 06:58 | -13 | 2017-02-01 08:35 | Architectural - Walls | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | In order to meet the Fisher Street Shaft construction programme the design technical assurance of the blockwork masonry drawings has been obtained through the CRL By Exception process (CRL1-XRL-O7-GPD-CR001-50023). Refer RiR ref RIR Cxxx-SKC-Z-LRC-CR086_WS095-50002 Rev 2.0 for drawing details/references. Refer completed Technical Assurance By Exception Gate Risk Assessment form (Cxxx-SKC-C-RGN-CR086_WS095-50011 Rev 1.0) appended to this NCR.
| 03SR - Stations (RfL) | Cxxx-NCR-000538 | NCR | Limmo - HV Route between Shaft and BSP - By Exception |  | Contr | SKC |  |  | 2017-07-28 | 2017-07-18 12:43 | -10 | 2017-02-01 16:32 | Civil - Civil Engineering General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | In order to meet the Limmo Shaft construction programme the design technical assurance of the HV route between Shaft and BSP drawings has been obtained through the CRL By Exception process (CRL1-XRL-O7-GPD-CR001-50023). Refer RiR ref RIR Cxxx-SKC-Z-LRC-CR144_WS155-50002 Rev 6.0 for drawing details/references. Refer completed Technical Assurance By Exception Gate Risk Assessment form (Cxxx-SKC-S-RGN-CR144_WS155-50003) appended to this NCR.
| 03SR - Stations (RfL) | Cxxx-NCR-000540 | NCR | Limmo Firestopping - No Approved F1 |  | Contr | SKC |  |  | 2017-02-27 | 2017-02-23 09:46 | -4 | 2017-02-13 18:05 | Fire - Compartmentation | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Not Defined | Completed |  | The two drawings (Cxxx-SKC-E-DDD-CR144_SH011-00610, Cxxx-SKC-E-DDD-CR144_SH011-00611) contain the F1 firestopping design of MEP services through walls. These drawings were mistakenly not included in the Limmo blockwork By Exception. Construction of the firestopping commenced onsite before it was realised the two firsstopping drawings were not part of the blockwork By Exception. The equivalent firestopping drawings for Fisher Street shaft were included in the Fisher Street blockwork By Exception and passed through the By Exception with no comments. Therefore we do not anticipate any risks with the Limmo firestoping installed to date.
| 03SR - Stations (RfL) | Cxxx-NCR-000541 | NCR | Eleanor Street - Blockwork Levels B5-B1 - By Exception Process |  | Contr | SKC | ELS - Eleanor Street Shaft (Central) |  | 2017-04-28 | 2017-04-19 13:14 | -9 | 2017-02-07 22:28 | Civil - Civil Engineering General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | In order to meet the Eleanor Street Shaft construction programme the design technical assurance of the blockwork masonry drawings has been obtained through the CRL By Exception process (CRL1-XRL-O7-GPD-CR001-50023). Refer RiR ref RIR Cxxx-SKC-Z-LRG-CR094_WS110-50001 Rev 3.0 for drawing details/references. Refer completed Technical Assurance By Exception Gate Risk Assessment form (Cxxx-SKC-C-RGN-CR094_WS110-50220 Rev 1.0) appended to this NCR.
| 03SR - Stations (RfL) | Cxxx-NCR-000542 | NCR | Fisher Street { B4 Slab Concrete Levels } |  | Contr | SKC |  |  | 2017-05-26 | 2017-05-16 07:42 | -10 | 2017-02-08 13:04 | Civil - Civil Engineering General | 5000 |  | Workmanship | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The design level of the B4 slab is 102.220 , however localised areas have been identified to be up to a maximum of +10mm to - 8mm. This exceeds the specified tolerance of within 5mm of design level. In line with Cxxx-NCR-000277 Mile End { Top of Ground Floor Slab Concrete Level } Corrective action - It is proposed to make up the low areas to the correct level using a thin bed levelling screed. Option A : ARDEX A 55 for the low spots & Scabble down the high spots. Option B : Low spots will be brought up to design level via Flow screed Industrial Top { Approved for use as part of resin flooring } & Scabble down the high spots.
| 03SR - Stations (RfL) | Cxxx-NCR-000543 | NCR | Fisher Street { B3 Slab Concrete Levels } |  | Contr | SKC |  |  | 2017-05-26 | 2017-05-16 07:43 | -10 | 2017-02-09 12:10 | Civil - Civil Engineering General | 5000 |  | Workmanship | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The design level of the B3 slab is 108.000 , however localised areas have been identified to be up to a maximum of +10mm to - 8mm. This exceeds the specified tolerance of within 5mm of design level. In line with Cxxx-NCR-000277 Mile End { Top of Ground Floor Slab Concrete Level } Corrective action - It is proposed to make up the low areas to the correct level using a thin bed levelling screed. Option A : ARDEX A 55 for the low spots & Scabble down the high spots. Option B : Low spots will be brought up to design level via Flow screed Industrial Top as part of resin flooring activity & Scabble down the high spots.
| 03SR - Stations (RfL) | Cxxx-NCR-000544 | NCR | Fisher Street { Wall 6 Error in Detailing } |  | Contr | SKC |  |  | 2017-07-31 | 2017-04-27 07:00 | -95 | 2017-02-14 07:40 | Civil - Civil Engineering General | 2000 |  | Documentation and Records | Repair | 4 (0.5-3k) | Complete | Design Problem - Error in equipment or material selection | Completed |  | On completion of a review of Cxxx-SKC-S-DWG-CR086_WS095-50029 Rev 3 by Cxxx. Cxxx Notes " Cxxx between grid 1 and 2 Ground floor “25-H12-ST08-200 startabox” Cxxx intent is H16-200. Cxxx notes the walls has been cast (part of the jump form). " Shown in the attached : Cxxx-SKC-C-DWG-CR086_WS095-50009 are the incorrect bars. This wall was poured as part of the Jump form on the 13th of October under Cxxx-SKC-S-DWG-CR086_WS095-50029 Rev 2 { Code 1 }. Cxxx Note that it is the same on the other side of the Wall 6 GL also. ************************************************** Cxxx Response : Cxxx will install : 1-H16-200 (drill and chemical grout to centreline of the wall) = 2135mm2/m & use __ HIT-RE 500 mortar to install said reinforcement.
| 03SR - Stations (RfL) | Cxxx-NCR-000545 | NCR | Limmo Firestopping - Installation of LUFF coating without approved MCR |  | Contr | SKC |  |  | 2017-02-23 | 2017-02-20 11:02 | -3 | 2017-02-09 15:26 | Fire - Compartmentation | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Procedure Problem - Other | Completed |  | submitted Cxxx-SKC-C-LRC-CR094-50300 -Material Compliance Record - Sitewide - Luff Coating __ on 12/12/2016 in order to meet construction programme for Limmo shaft. This MCR has not been returned to . As a result have applied LUFF Coating in order to meet construction programme. The application of LUFF Coating has been undertaken in instances where headjoints between blockwork and concrete have been greater than 30mm and thus the intumescent mastic is not suitable. The joints which are wider than 30mm are as a result of variance in floor level of concrete works installed by Cxxx. The compartmentation requirement in these areas is for two-hour separation which is achieved by 100mm of PFC __ C144 which is installed within the joint to the manufacturer’s instructions , to which LUFF coating is applied as a sealant. This is an LU approved product and method under the APR system. Material was verified verbally via CRL/CEG prior the application, and is deemed to comply with CRL specification.
| 03SR - Stations (RfL) | Cxxx-NCR-000547 | NCR | Flexcell- impregnated fibreboard filler used without approved MCR |  | Contr | SKC |  |  | 2017-03-10 | 2017-03-02 12:16 | -8 | 2017-02-10 07:16 | Civil - Drainage | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Subcontractor Problems - Insufficient work planning by the subcontractors | Completed |  | The subcontractor has installed Flexcell, which is a bitumen impregnated fibreboard joint filler around the joints of the clay drainage pipes as per the drawing, listed below. This product meets all of the drawing requirements (Cxxx-SKC-D-DDD-CR144_SH011_Z-00003) but was installed without an approved MCR.
| 03SR - Stations (RfL) | Cxxx-NCR-000548 | NCR | Stepney Green - Stepney Green Cores Grid Line 9 |  | Contr | SKC |  |  | 2017-12-15 | 2017-10-12 08:54 | -64 | 2017-02-09 17:45 | Structural Engineering - Structural Engineering - General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | As per PMI 00900 have proceeded with coring additional holes through the slab as raised per Cxxx-FCD-000594 and PMI-00900, however the cores have not been reviewed from a structural perspective by Cxxx. The mark up of the cores, incuding position is attached as well as a picture showing the cores. Cxxx oversized the cores by 25 mm in all direction to ensure sufficient renderoc could be applied to the exposed reinforcement to ensure adequate cover was maintained. This remedial work was undertaken shortly after the cores were taken. Can Cxxx confirm acceptance of these cores through the structure. Please see attached photos of the cores which confirm no damage to the bar mark (76) in question. Cxxx (STL) Response to Cxxx Rev 2.0 Comments below. 22/09/2017 1) On Page SG/B1/03 the blockwork walls are calculated as applying a slab load of 17.2kN/m. Using a 2kN/m2 allowance requires an 8.6m width of slab to achieve an equivalent total load. This is not considered realistic and the blockwork walls should be considered as line loads in the assessment of the slab. This produces a more onerous condition particularly in the beam strip A8. STL have revised the calculations for the worst cases loading found previously, replacing the 2kN/m2 UDL with a 17.2kN/m Line load (please find STL Calcs SG-B1-29 to 42 – RevP01 attached). The slab has been found to be satisfactory under this loading. 2) Cxxx understand the rebar as indicated on Pages SG/B1/12 and SG/B1/12-1 has been confirmed on site as cut by the Cxxx site team. Cxxx to confirm this is the case. The number of cut bars has been based on the rebar centres and size of core formed. 3) Cxxx note the fire resistance for the slabs stated in the analysis is 60mins. The fire rating for structural elements in the shaft is 90mins. Cxxx note this has no impact on these calculations. Amended in revised calculations attached. 4) Cxxx note the span steel as noted on Page SG/B1/23 is B25 @ 125 and the support steel is noted as B25 @ 200. Cxxx note the actual as-built span steel and support steel is B25@200 and B12@200 respectively. As per the attached mark-up, the as built drawing indicates 12No. B25 bars (3 of which will have been cut) in the span and 5No. B25 at the supports in this zone. This is equivalent to B25 @ 125c/c and B25 @ 200 c/c respectively to input into the software used previously – however this has been replaced with a hand calculation using the number of bars shown on the as-built in the revised calculations. 5) Check of Strip A6 (Page SG/B1/14) – Cxxx considers that for checking bending the span should be taken from the edge of the prop beam to the centre of slab strip A7. Amended in revised calculations attached. 6) Cxxx note distance applied to area A1 on Page SG/B1/32 is incorrect and should be 0.15m. This affects the rest of the calculation on this page. Cxxx to revise. Amended in revised calculations attached.
| 03SR - Stations (RfL) | Cxxx-NCR-000549 | NCR | Stepney Green - C50/60 Concrete |  | Contr | SKC |  |  | 2017-04-28 | 2017-03-30 13:39 | -29 | 2017-02-09 16:34 | Structural Engineering - Structural Engineering - General | 500 |  | Manufacturing Defect | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | Cxxx wish to note that the compressive strength of the concrete pour for B1 Grid Line 5 wall did not reach the intended compressive strength of 60 N/mm2 for the strength concrete used C50/60. The cube reached 58 N/mm2, however the design of this wall was for C32/40 and therefore the design strength was met after 28 days (40 N/mm2). Cxxx used C50/60 concrete under the mitigation PMI to ensure that the SLD dates for the CER room was maintained. Please refer to the attached cube data results.
| 03SR - Stations (RfL) | Cxxx-NCR-000550 | NCR | Limmo Firestopping - Water damage to head joints on B1 |  | Contr | SKC |  |  | 2017-07-21 | 2017-06-15 06:11 | -36 | 2017-02-13 17:52 | Fire - Compartmentation | 5000 |  | Damaged | Repair | 3 (3-6k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | After completion of firestopping to headjoints in Limmo peninsula shaft, water ingress has caused damage to PFC __ Intumescent Mastic and PFC __ C144 strips and under clause JP10.3201 i) this must be considered not to be incorporated into final works.
| 03SR - Stations (RfL) | Cxxx-NCR-000551 | NCR | Limmo Firestopping - Incorrect installation of intumescent mastic to holorib soffit |  | Contr | SKC |  |  | 2017-06-19 | 2017-06-14 13:34 | -5 | 2017-02-13 18:02 | Fire - Compartmentation | 5000 |  | Incorrect Installation | Repair | 3 (3-6k) | Complete | Design Problem - Other | Completed |  | Where masonry walls meet concrete slab with a holorib soffit, intumescent mastic has been used to seal not only the joint between masonry and soffit but also the dovetail sections of holorib decking. At these points the overall joints height is 80mm which exceeds the 30mm maximum specified by PFC __.
| 03SR - Stations (RfL) | Cxxx-NCR-000552 | NCR | Fisher Street { Incorrect Startabox on Wall 2 ground floor } |  | Contr | SKC |  |  | 2017-03-31 | 2017-03-17 09:41 | -14 | 2017-02-14 07:48 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Repair | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | On review of Cxxx-SKC-S-DWG-CR086_WS095-50029 Rev 3, Cxxx noted that Cxxx note “15 H12-ST02-150NF startabox” into the ground floor slab near grid B, the width W of the box appears to be incorrect, the bars will be in the wrong layer and hence will clash with the bar layering in the slab. Cxxx notes the walls has been cast (part of the jump form). Hence this will impact the slab reinforcement. This wall was poured in Oct 2016 under Cxxx-SKC-S-DWG-CR086_WS095-50029 Rev 2 , Code 1.
| 03SR - Stations (RfL) | Cxxx-NCR-000553 | NCR | Fisher Street - Level B3/B4 CMS, Lighting and Small power - By Exception Process |  | Contr | SKC |  |  | 2017-05-22 | 2017-05-14 10:55 | -8 | 2017-02-14 17:24 | Electrical - General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | In order to meet the Fisher Street Shaft construction programme the design technical assurance of the Level B3/B4 CMS, lighting and small power drawings has been obtained through the CRL By Exception process (CRL1-XRL-O7-GPD-CR001-50023). Refer RiR ref RIR Cxxx-SKC-Z-LRC-CR086_WS095-50002 Rev 4.0 for drawing details/references. Refer completed Technical Assurance By Exception Gate Risk Assessment form (Cxxx-SKC-E-RGN-CR086_WS095-50010 Rev 1.0) appended to this NCR.
| 03SR - Stations (RfL) | Cxxx-NCR-000554 | NCR | Material Samples for Acceptance |  | Crossrail | XRL |  |  | 2017-06-30 | 2017-06-15 06:40 | -15 | 2017-02-15 11:08 | Fire - Compartmentation | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | A planned Crossrail surveillance was undertaken on 14th February 2017 to look at fire stopping in the Limmo Shaft, carried out by __. During a review of the Materials Compliance Records (MCR) for the fire stopping, it was found that the Contractor has not supplied samples of the materials for acceptance by CRL, as per the Architectural Specification Cxxx-SKC-A-RSP-CR144_WS155-50001 rev 1 Clause JP10.2103.
| 03SR - Stations (RfL) | Cxxx-NCR-000555 | NCR | Limmo - Floor Finishes and Firestopping - By Exception |  | Contr | SKC |  |  | 2017-06-12 | 2017-05-31 08:38 | -12 | 2017-02-15 12:01 | Architectural - General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | In order to meet the Limmo Shaft construction programme the design technical assurance of the Floor Finishes and Firestopping drawings has been obtained through the CRL By Exception process (CRL1-XRL-O7-GPD-CR001-50023). Refer RiR ref RIR Cxxx-SKC-Z-LRC-CR144_WS155-50002 Rev 6.0 for drawing details/references. Refer completed Technical Assurance By Exception Gate Risk Assessment form (Cxxx-SKC-A-RGN-CR144_WS155-50002) appended to this NCR.
| 03SR - Stations (RfL) | Cxxx-NCR-000556 | NCR | Fisher St { Wall 6 Incorrect Startabox Alignment } |  | Contr | SKC |  |  | 2017-03-17 | 2017-03-17 09:40 | 0 | 2017-02-15 14:24 | Civil - Civil Engineering General | 2000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Cxxx set the false work for the ramp between gridline 5 & 4, it has become apparent that the startabox may have floated in the pour on the southern end. As a result the bars are above the SSL for the pour the area effected is circa 2m long. Propose the resolution as shown in the attached. 1. Cut off effected bars ensuring 25mm cover is maintained & Remove all startabox that would encroach in the cover zone once the slab is poured. 2. Replace each bar with a drill and fix through the wall. Diameter of hole 16mm hole. 3. Blow out the hole and ensure all surfaces are clear of dust. 4. Fill holes with __ RE-200. 5. Insert the H12 bars to replace the ones removed in Step one to the correct level with the development as per Cxxx drawings into both pours. 6. Install the U Bars where it has an opening on the Quadrant side of Wall 6, achieve cover off the box out and develop as per Cxxx drawings in to the corridor. 7. Tie Steel 8. Pour Slab. 9. Repair the remaining step left due to original startabox using previously approved method & materials in line with Cxxx-NCR-000460 using __ & Nitrobond. ********************************************************************************************** Cxxx Response to Engineering Rework . 1. At the worst location, can Cxxx measure how much higher the startabox bars are from where the intent position is? 40mm Higher on the bottom Layer 2. Are the startabox bars that are in the wrong position aligned in a straight line? No there is a fall on it , just not enough 3. Cxxx propose a H10-U bar beside the slab penetration. Will a H12 bar fit? Yes it will work , Minimum bend in a 12mm U bar is 110mm. 4. In this area on Wall Elevation 5 on RC drawing Cxxx-SKC-C-DWG-CR086_WS095-50009 calls up H12-ST02-150 Startabox. In this drawing in the startabox schedule it gives code 00/2/2, which is a continuous bar through the wall. Therefore will the bottom bars from the startabox projecting into the adjacent room be below the slab in places and have inadequate cover in others? Attached is a photo showing the works in progress so what was done on Site is 2 U bar boxes, The correct Startabox was installed further back. This NCR will capture the use of The U Bar Startabox in these locations in Lieu of the ST02 bar mark along with the misalignment.
| 03SR - Stations (RfL) | Cxxx-NCR-000557 | NCR | Split pour on B2 Grid Line 4-6 due to Equipment Procurement |  | Contr | SKC |  |  | 2017-06-30 | 2017-04-20 16:21 | -71 | 2017-02-20 10:26 | Structural Engineering - Finishes | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | For the pour for B2 grid line 4-6, due to the procurement of the wrong equipment to install the couplers on B2, a split pour was required as the coupler bolts had not been sheared early enough to allow a continuous pour. Around a 0.5 meter by 2 m strip was left as a stop end and scabbled and jet washed before the infill was poured the following day, following shearing of the bolts. HI Comment 27/03/2017 Please see attached marked up drawing Cxxx-JUL-S-DDL-CR094_SH005-50621 indicating the sketch as requested as well as results of a cover survey indicating minimum cover of 30 mm which is sufficient for minimum cover for slabs as stated by note 4 on drawing Cxxx-JUL-S-DDL-CR094_SH005-50621.
| 03SR - Stations (RfL) | Cxxx-NCR-000558 | NCR | Stepney Green B00 Cxxx Access Hatch |  | Contr | SKC |  |  | 2017-08-31 | 2017-05-10 16:21 | -113 | 2017-04-12 15:21 | Structural Engineering - Structural Engineering - General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | The B00 Cxxx access hatch is 70 mm narrower than it should be in one direction as per the attached marked up drawing. Also as shown in the attached photograph and as built section there are 'shoulders' that limit the size of the opening. These shoulders have been formed when the base plates of the steelwork had been grouted and has encroached onto the clear opening of the access hatch. HI Comment 05/05/2017 Please see attached correspondence with Cxxx accepting the change
| 03SR - Stations (RfL) | Cxxx-NCR-000559 | NCR | Pull test calculations have not been produced for CMS Installation (supports and hangers) |  | Crossrail | XRL | ELS - Eleanor Street Shaft (Central) |  | 2018-03-26 | 2018-02-06 08:25 | -48 | 2017-02-24 13:54 | Electrical - Cable Management | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | A planned Crossrail surveillance was undertaken on 25.01.17 to look at Containment Installation at ESS. Pull testing is being undertaken to 0.9kN for resin anchors and 1.8kN for mechanical anchors as detailed in the Pull Testing check sheet associated with the CMS Installation ITP. __ provided calculations from __ as evidence to meet the requirements of M&W Specification JY63 which states under clause JY63.1302; “Load calculations and proposed support systems shall be submitted for approval before installation commences”. However __, who were present at a post meeting (20/02/17), confirmed that they would not be responsible for such calculations. It was also noted that the calculations presented, only accounted for loads associated with a unistrut bracket fixed to a certain substrate, with no mention of shear and tensile loads based on the cable types being supported in both concrete and blockwork fabrics. It was agreed that the calculations should have been produced by the F2 designer and none had been done. As no calculations have been produced prior to installation, it is unclear whether the proof load testing completed to date for containment installation is correct. ITP to be updated to reflect the load parameters.
| 03SR - Stations (RfL) | Cxxx-NCR-000560 | NCR | __ not torqueing __ resin anchors fixed into Blockwork as per the manufacturers data sheet |  | Crossrail | XRL | ELS - Eleanor Street Shaft (Central) |  | 2017-07-28 | 2017-07-27 07:59 | -1 | 2017-02-24 13:47 | Electrical - Cable Management | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Other | Completed |  | A planned Crossrail surveillance was undertaken on 25.01.17 to look at Containment Installation at ESS. During the surveillance it was identified that __ had been tightening the __ resin anchors fixed into the blockwork by the use of spanners. Post surveillance __ was requested to provide information on whether torqueing was required. In a post Exit meeting it was confirmed by __ that the resin anchors should be tightened with a torque wrench set at 8Nm as per their manufacturer’s details. As the resin anchors had been spanner tightened the contractor should investigate whether the force applied is either in excess or not to the desired torque of 8Nm. If it is identified that the force is greater than 8Nm then according to the manufacturer the fixing/resin contact becomes void. In addition the ITP should be updated to include the torque parameters.
| 03SR - Stations (RfL) | Cxxx-NCR-000561 | NCR | Firestopping - Late completion of benchmarking |  | Contr | SKC |  |  | 2017-05-08 | 2017-04-30 11:24 | -8 | 2017-02-23 13:17 | Fire - Compartmentation | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Limmo Peninsula Architectural Specification (Cxxx-SKC-A-RSP-CR144_WS155-50001) Clause JP10.2106 States that "quality benchmarks shall be provided in locations to be agreed with the Project Manager, in accordance with Section JA.4000: a) First of each type installed." At Limmo Peninsula this was not complied with as the nominated benchmarks were not the first of each type installed. Instead chose locations of exemplary installation that will be easily accessible as works progress for inspection.
| 03SR - Stations (RfL) | Cxxx-NCR-000562 | NCR | Stepney Green: Use of C50/60 Concrete |  | Contr | SKC |  |  | 2017-05-31 | 2017-03-30 11:59 | -62 | 2017-02-22 12:11 | Structural Engineering - Structural Engineering - General | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Other | Completed |  | To achieve early strike time to meet the single line diagrams associated with the handover of the CER room, Cxxx used C50/60 for areas where C32/40 was specified.
| 03SR - Stations (RfL) | Cxxx-NCR-000563 | NCR | Floor Finishes (all floors) and Blockwork (floors B2 & GF only) - By Exception |  | Contr | SKC |  |  | 2017-07-01 | 2017-05-29 02:34 | -33 | 2017-02-24 14:10 | Architectural - General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | In order to meet the Fisher Shaft construction programme the design technical assurance of the 'Floor Finishes (all floors) and Blockwork (floors B2 & GF only) drawings has been obtained through the CRL By Exception process (CRL1-XRL-O7- GPD-CR001-50023). Refer RiR ref RIR Cxxx-SKC-Z-LRC-CR086_WS095-50002 Rev 4.0 for drawing details/references. Refer completed Technical Assurance By Exception Gate Risk Assessment form (Cxxx-SKC-A-RGN-CR086_WS095-50006).
| 03SR - Stations (RfL) | Cxxx-NCR-000564 | NCR | Fisher Street Shaft – By Exception – HV CMS |  | Contr | SKC |  |  | 2017-06-26 | 2017-05-29 02:31 | -28 | 2017-02-24 14:43 | Electrical - General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | In order to meet the Fisher Shaft construction programme the design technical assurance of the 'HV CMS drawings has been obtained through the CRL By Exception process (CRL1-XRL-O7-GPD-CR001-50023). Refer RiR ref RIR Cxxx-SKC-Z-LRC-CR086_WS095-50002 Rev 3.0 for drawing details/references. Refer completed Technical Assurance By Exception Gate Risk Assessment form (Cxxx-SKC-E-RGN-CR086_WS095-50002).
| 03SR - Stations (RfL) | Cxxx-NCR-000565 | NCR | Louvre Door Closers and Kick Plate |  | Contr | SKC |  |  | 2017-04-24 | 2017-03-07 10:38 | -48 | 2017-02-27 11:10 | Architectural - Doors | 500 |  | Incomplete Works | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Louvre Doors installed appear to not accord with Cxxx-SKC-A-DDD-CR094_SH006_Z-00722. Please refer to Cxxx-FCD-000661.
| 03SR - Stations (RfL) | Cxxx-NCR-000566 | NCR | VRF Pipework Insulation |  | Contr | SKC |  |  | 2017-04-17 | 2017-04-09 20:45 | -8 | 2017-03-09 08:14 | Materials - General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | CRL-MCR-000415 was previously raised to capture Refrigerant Pipework and refrigerant pipework insulation. However, as requested by CEG refrigerant pipework insulation was removed from CRL-MCR-000415 to be issued under separate MCR. Installation of refrigerant pipework proceeded without a separate MCR being issued for the material. It should be noted that the material has already been given a Code 1 F1 on another CRL project. An MCR has been raised to capture the refrigerant pipework insulation under: CRL-MCR-004571 Armaflex Insulation for Pipework
| 03SR - Stations (RfL) | Cxxx-NCR-000567 | NCR | Fisher St { Over pour of B1 jump form straddling SCL } |  | Contr | SKC |  |  | 2017-04-28 | 2017-04-05 10:57 | -23 | 2017-02-28 09:47 | Civil - Civil Engineering General | 2000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Worker not correctly instructed | Completed |  | The B1 jump form has been poured straddling over the SCL at the locations.
| 03SR - Stations (RfL) | Cxxx-NCR-000568 | NCR | Fisher St { B4 & B3 Blockwork } |  | Contr | SKC |  |  | 2017-04-28 | 2017-03-24 12:35 | -35 | 2017-02-28 13:08 | Civil - Civil Engineering General | 1000 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Fisher St Floor heights are not relative to block work coursing. { B4 & B3 Block work } Floor Heights 5.780m - Depth of Slab 300mm { Inc Comflor } - 30mm for Fireproofing Joint. This leaves 5.450m = 36.3 courses of block the .3 of a course remains circa 45mm. Block work on B4 & B3 out of Gauge by 46mm, Due to the allowable tolerances on the blocks during manufacture, it has created a bigger joint in some cases. From a site survey Carried out the joints are Nominally 15mm at its worst. Designer has advised that they are happy with the arrangement as long as joints do not exceed 15mm. ******************************************************************************************* Cxxx Response 01.03.2017 Please see attached extract from BS EN 1996-1-1:2005 Clause 8.1.5 Mortar Joints. Limmo approved RFI stating that 15mm joints are acceptable: " We are generally happy with this arrangement, provided the max thickness of the mortar joints is not more than 15mm. It should also be noted that the overlapping of blocks should be not less than 0.4 times the thickness of the 100mm bespoke blocks, as per cl. 8.1.4.1 of BS EN 1996-1-1. The minimum class of mortar for this wall as per the specifications. " ******************************************************************************* Cxxx Response : 21/03/2017 Cxxx Note that evidence for this NCR has been provided via Cxxx--RFI-WW-465 response to my Query which was 1: What is the maximum permissible joint size you previously confirmed 15mm (according to BS EN 1996-1-1)? Can you confirm this is the case for Fisher St? Response : 1. Agreed, the requirements under EN 1996 1-1 should apply for Fisher Street as well. Bed joints and perpend joints made with general purpose and lightweight mortar joints shall be in between 6 – 15mm as per EN 1996 1-1. Cxxx will review all other works to ensure compliance with all WI. If there are any departures found we will raise a separate NCR. Cxxx suggest that this NCR can now be closed as evidence has been supplied in relation to joint sizes.
| 03SR - Stations (RfL) | Cxxx-NCR-000569 | NCR | Metal in eastbound penetration |  | Contr | SKC |  |  | 2017-03-14 | 2017-03-15 09:59 | 1 | 2017-02-28 14:54 | Electrical - Cable Management | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Previous Construction - Improper As Built | Completed |  | investigation has found what appears to be a piece of cast in steel temporary works in the middle of the penetration leading to east bound tunnel on B6 from the escape stairs.
| 03SR - Stations (RfL) | Cxxx-NCR-000570 | NCR | ESS - Mortar on drip ties within brickwork cavity |  | Contr | SKC | ELS - Eleanor Street Shaft (Central) |  | 2017-05-26 | 2017-05-31 08:34 | 5 | 2017-03-02 12:07 | Architectural - Brickworks/Blockworks | 1000 |  | Incomplete Works | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | During construction of the brickwork cavity mortar has fallen into the cavity and onto the brickwork ties causing a bridge for water to traverse over the drip in the tie.
| 03SR - Stations (RfL) | Cxxx-NCR-000571 | NCR | Limmo - By Exception - F1 __ and HV Duct Backfill |  | Contr | SKC |  |  | 2017-06-26 | 2017-05-29 02:33 | -28 | 2017-03-03 15:14 | Civil - Civil Engineering General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | In order to meet the Limmo Shaft construction programme the design technical assurance of the 'F1 __ and HV Duct Backfill' drawings has been obtained through the CRL By Exception process (CRL1-XRL-O7-GPD-CR001-50023). Refer RiR ref RIR Cxxx-SKC-Z-LRC-CR144_WS155-50002 Rev 7.0 for drawing details/references. Refer completed Technical Assurance By Exception Gate Risk Assessment form (Cxxx-SKC-S-RGN-CR144_WS155-50004) appended to this NCR.
| 03SR - Stations (RfL) | Cxxx-NCR-000572 | NCR | Limmo Peninsula - Screed Flooring - Installation of incorrect screed angles |  | Contr | COS |  |  | 2017-07-24 | 2017-06-29 07:06 | -25 | 2017-03-08 17:57 | Architectural - Flooring | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | The subcontractor has installed non-galvanised mild steel angles have been installed in the location detailed on drawing Cxxx-SKC-A-DDA-CR144_SH011_2-00242 (namely SR 11kv HV1, SR 11kv HV2, SR 22kv HV1 and SR 22kv HV2), which should have been a galvanised finished mild steel restraint (as per clause JM10.1204 of Limmo Architectural Specification) but was installed without an approved MCR.
| 03SR - Stations (RfL) | Cxxx-NCR-000573 | NCR | Water damage to head of wall movement joint firestopping at soffit of B1 Intervention stairs due to rain |  | Contr | SKC |  |  | 2017-04-28 | 2017-04-27 14:03 | -1 | 2017-03-13 13:56 | Fire - Compartmentation | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | External Phenomenon - Weather or ambient condition | Completed |  | Where the head of wall joint at B1 soffit lies underneath the entrance to the intervention stairs at Limmo, firestopping has become water damaged due to ingress of rain water.
| 03SR - Stations (RfL) | Cxxx-NCR-000574 | NCR | Mastic leaks onto blockwork and RC due to rain ingress |  | Contr | SKC |  |  | 2017-04-28 | 2017-04-27 14:14 | -1 | 2017-03-13 15:56 | Fire - Compartmentation | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | External Phenomenon - Weather or ambient condition | Completed |  | Further to Cxxx-NCR-000574, where rainwater has damaged firestopping to head of wall movement joints, intumescent mastic has leaked down walls as it is water miscible.
| 03SR - Stations (RfL) | Cxxx-NCR-000575 | NCR | Leak of mastic onto Intervention stairs steelwork |  | Contr | SKC |  |  | 2017-05-08 | 2017-04-28 15:05 | -10 | 2017-03-13 17:34 | Fire - Compartmentation | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | External Phenomenon - Weather or ambient condition | Completed |  | Further to Cxxx-NCR-000573, mastic which has leaked from the damaged joint has flowed onto the steelwork of the intervention stairs
| 03SR - Stations (RfL) | Cxxx-NCR-000576 | NCR | Fisher Street { Missed Beam Starters Head house roof } |  | Contr | SKC |  |  | 2017-04-30 | 2017-04-27 06:58 | -3 | 2017-03-17 10:24 | Civil - Civil Engineering General | 1000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | Cxxx poured the Jump form in Oct 16. The starter bars for the head house beams were not included in the pack, and subsequently missed out of Wall 2 Internal. Highlighted in the attached scan. Drawing number Cxxx-SKC-S-DWG-CR086_WS095-50031.
| 03SR - Stations (RfL) | Cxxx-NCR-000577 | NCR | ESS - Roof bracings offset from intersection points |  | Contr | SKC | ELS - Eleanor Street Shaft (Central) |  | 2018-01-29 | 2017-10-03 09:04 | -118 | 2017-03-31 08:20 | Structural Engineering - Steel Member | 5000 |  | Incorrect Installation | Use As-Is | 3 (3-6k) | Complete | Management Problem - Inadequate supervision | Completed |  | Roof bracings shown on the attached marked up sketch are offset from the design intent. In particular, rather than the bracings all coming together in one centralised node, a number of the braces are offset from the primary connection. Cxxx notes that this NCR is raised following CRL/Cxxx response on Cxxx-FCD-000724.
| 03SR - Stations (RfL) | Cxxx-NCR-000578 | NCR | ELS - Construction Starting Without Documentaion in Place |  | Crossrail | XRL | ELS - Eleanor Street Shaft (Central) |  | 2017-04-14 | 2017-04-06 14:35 | -8 | 2017-03-20 12:56 | Materials - General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Personnel Error - Violation of requirement or procedure | Completed |  | Construction works to the Bilco roof access hatch were completed without the acceptance of the necessary documentation. Crossrail were only receipt of the of the MCR after the works had been completed (document Cxxx-SKC-C-LRC-CR094-50459 rev 1).
| 03SR - Stations (RfL) | Cxxx-NCR-000579 | NCR | ESS - __ Louver Doors installed without accepted MCR |  | Contr | SKC | ELS - Eleanor Street Shaft (Central) |  | 2017-04-03 | 2017-03-24 12:02 | -10 | 2017-03-20 17:05 | Architectural - Doors | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | __ louvre doors were installed prior to the acceptance of the MCR and ITP. The MCR Cxxx-SKC-C-LRC-CR094-50409 was submitted on 28.02.17 and was returned code 1 on 17.03.17 The ITP Cxxx-SKC-C-ITP-CR094_WS110-50058 was submitted 01.03.17 and is currently with CRL. Cxxx notes that this product is specifically called out in the Architectural Specification Cxxx-SKC-A-RSP-CR094_WS110-50005, clause JL13.1209, and was approved for use at Mile End.
| 03SR - Stations (RfL) | Cxxx-NCR-000580 | NCR | ESS - Installation of fireproofing to blockwork headjoint to holorib soffit without an approved design |  | Contr | COS | ELS - Eleanor Street Shaft (Central) |  | 2017-06-30 | 2017-06-16 14:55 | -14 | 2017-03-21 18:14 | Fire - Compartmentation | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Cxxx have installed the detail on the attached sketch to the blockwork headjoint – holorib soffit, without an approved design. In essence, 100mm corofil C144 dovetail shape strips have been inserted within the dovetail section and straight sections of C144 have been installed to the horizontal blockwork headjoint gap. Where the headjoint gap is less than 30mm, PFC __ intumescent mastic was applied to the face of the corofil strips. Where the gap was greater than 30mm, LUFF coating was applied to the corofil strips. LUFF coating was also applied to the dovetail section. It is noted that there was no detail within the works information for the blockwork/holorib joint and therefore Cxxx specialist sub-contractor came up with the proposal described above. This was agreed with CRL and CEG on site as part of IRF 679. This detail has been installed on the ground floor level only. Therefore Cxxx would like formal confirmation that the detail is still acceptable.
| 03SR - Stations (RfL) | Cxxx-NCR-000581 | NCR | ESS - Blockwork workmanship - cut blocks under lintels |  | Contr | SKC | ELS - Eleanor Street Shaft (Central) |  | 2017-05-08 | 2017-03-30 21:28 | -39 | 2017-03-22 12:22 | Architectural - Brickworks/Blockworks | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | During the construction of the blockwork walls, cut blocks have been used due to the door and M&E design. The cut blocks vary in height between 35mm - Full block. This is a non compliance with the architectural specification, Cxxx-SKC-A-RSP-CR094_WS110-50005 clause: JF10.3214. In response to Cxxx-EWN-01821 see attached Cxxx--RFI-WW-489, statement from Cxxx's designers stating all blocks greater than 20mm thickness are acceptable to be used in all areas. Test results from samples taken of 20mm, 35mm and 50mm are included in the RFI.
| 03SR - Stations (RfL) | Cxxx-NCR-000582 | NCR | ESS - __ installed without accepted MCR |  | Contr | SKC | ELS - Eleanor Street Shaft (Central) |  | 2017-04-06 | 2017-03-30 21:44 | -7 | 2017-03-23 14:44 | Architectural - Brickworks/Blockworks | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | __ 1, a polyethylene filler for expansion and movement joints, was installed within the external brickwork before an accepted MCR was in place.
| 03SR - Stations (RfL) | Cxxx-NCR-000583 | NCR | Fisher Street Shaft – By Exception – GF cast-in PH & Foul |  | Contr | SKC |  |  | 2017-10-01 | 2017-05-29 02:38 | -125 | 2017-03-24 09:34 | Mechanical - Public Health Engineering | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | In order to meet the Fisher Shaft construction programme the design technical assurance of the 'GF cast-in PH & Foul' drawings has been obtained through the CRL By Exception process (CRL1-XRL-O7-GPD-CR001-50023). Refer RiR ref RIR Cxxx-SKC-Z-LRC-CR086_WS095-50002 Rev 4.0 for drawing details/references. Refer completed Technical Assurance By Exception Gate Risk Assessment form (Cxxx-SKC-P-RGN- CR086_WS095-50003).
| 03SR - Stations (RfL) | Cxxx-NCR-000585 | NCR | Damaged __ Board installed to B3 Corridor windposts |  | Contr | SKC |  |  | 2017-06-30 | 2017-06-28 14:03 | -2 | 2017-03-28 16:00 | Fire - Compartmentation | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | __ fire-board installed to B3 corridor blockwork wall windposts have been damaged during installation or post installation - see attached mark-up with pictures
| 03SR - Stations (RfL) | Cxxx-NCR-000586 | NCR | Windpost __ installed using incorrect screws |  | Contr | SKC |  |  | 2017-06-30 | 2017-06-28 14:05 | -2 | 2017-03-30 16:03 | Fire - Compartmentation | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | __ board fixed to corridor windpost outside SRLV2 using incorrect fixings
| 03SR - Stations (RfL) | Cxxx-NCR-000587 | NCR | ESS - Panic Bar to Transformer Room Louvre Doors not Installed |  | Contr | SKC | ELS - Eleanor Street Shaft (Central) |  | 2017-06-02 | 2017-04-06 05:45 | -57 | 2017-04-03 13:07 | Architectural - Doors | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Panic Bar to Transformer Room Louvre Doors D00.27 and D00.28 not Installed as specified on Cxxx-SKC-A-DDD-CR094_SH007_Z-06100 as it would entail that the doors would not be security rated. Cxxx has installed the Surelock McGill Slimline SL311, three point manual deadlocking and autobolting locking system which allows for D00.27 and D00.28 doors to be security rated.
| 03SR - Stations (RfL) | Cxxx-NCR-000588 | NCR | Blockwork cuts below 65mm |  | Contr | SKC |  |  | 2017-07-24 | 2017-06-15 12:18 | -39 | 2017-04-20 11:52 | Architectural - Brickworks/Blockworks | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | In a number of instances the blockwork has had to be cut to below 70mm (typically the height is 140mm). The smallest size block we have cut at Limmo Peninsula is 35mm.
| 03SR - Stations (RfL) | Cxxx-NCR-000589 | NCR | Installation of incorrect screed angles |  | Contr | SKC |  |  | 2017-07-31 | 2017-07-07 11:59 | -24 | 2017-04-06 15:57 | Architectural - Flooring | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | At the door openings of rooms with screed, non-galvanised mild steel angles have been installed to the exposed edge. Architectural specifications require galvanised mild steel restraint angles to be installed.
| 03SR - Stations (RfL) | Cxxx-NCR-000590 | NCR | Damaged floor resin in HVLV risers |  | Contr | SKC |  |  | 2017-08-07 | 2017-07-11 15:35 | -27 | 2017-04-07 15:14 | Architectural - Flooring | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Floor resin has been damage upon removal of temporary timber covers installed over openings as fall protection
| 03SR - Stations (RfL) | Cxxx-NCR-000591 | NCR | Blockwork Chipped |  | Contr | SKC |  |  | 2017-06-15 | 2017-05-15 18:36 | -31 | 2017-04-20 10:10 | Architectural - Brickworks/Blockworks | 500 |  | Damaged | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Improper preservation of material after installation | Completed |  | Blockwork has been chipped accidentally due to subcontractor interface with completed blockwork wall.
| 03SR - Stations (RfL) | Cxxx-NCR-000592 | NCR | Exposed U-Bar reinforcement at top of Wall 2 |  | Contr | SKC |  |  | 2017-06-26 | 2017-05-19 14:46 | -38 | 2017-04-10 07:55 | Structural Engineering - Reinforcement | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Exposed/insufficient cover of steel reinforcement at top of Wall 2 (Gridline 7+1212) between E and E+1000 (approx.). Six U-bars are visible as they protrude out of the concrete. Along this wall there are also three exposed slip form tubes which will need to be locally scabbled down and cut off 50mm below FL. The tubes will be filled with grout prior to being covered. This wall was constructed by Cxxx.
| 03SR - Stations (RfL) | Cxxx-NCR-000593 | NCR | Slip joints seperated by single block |  | Contr | SKC |  |  | 2017-06-26 | 2017-05-19 14:51 | -38 | 2017-04-20 10:18 | Architectural - Brickworks/Blockworks | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | An additional movement joint has been added between wall 40 and 55.
| 03SR - Stations (RfL) | Cxxx-NCR-000594 | NCR | Crack in mass pour concrete inbetween shaft and BSP |  | Contr | SKC |  |  | 2017-07-24 | 2017-05-20 09:50 | -65 | 2017-05-08 16:06 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Improper preservation of material after installation | Completed |  | During on site inspections on 10/04/2017 it was observed that there is a crack in the mass fill concrete which was poured on 06/04/2017. The crack is located GL 4-5 from the edge of the filter drain around drawpit A to the edge of the mass fill (approximately 2.5M in length). The crack is 1mm in width. The depth of the mass fill is 550mm and made up of C32/40 concrete.
| 03SR - Stations (RfL) | Cxxx-NCR-000595 | NCR | Damaged Fire-stopping in Intervention Stairs from Rain Event |  | Contr | SKC |  |  | 2017-06-26 | 2017-06-22 12:34 | -4 | 2017-04-10 13:05 | Fire - Compartmentation | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | PFC __ Intumescent Mastic located in the north-east corner of the Intervention stairs has been damaged from rain. Photos attached
| 03SR - Stations (RfL) | Cxxx-NCR-000596 | NCR | Corner concrete crack at NE corner of Headhouse |  | Contr | SKC |  |  | 2017-07-31 | 2017-07-07 14:40 | -24 | 2017-04-10 14:29 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Previous Construction - Other | Completed |  | A crack on the North-eastern corner of the head house (intersection of walls 2 and 3) on the northern face starts 100mm off the corner at the top end with a thickness of approximately 3-4mm and reduces in thickness as it travels down towards ground level. This wall was constructed by Cxxx.
| 03SR - Stations (RfL) | Cxxx-NCR-000597 | NCR | Cracks in spine wall |  | Contr | SKC |  |  | 2017-08-31 | 2017-07-18 13:32 | -44 | 2017-04-10 14:43 | Civil - Civil Engineering General | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | 3 hairline cracks on the northern face spine wall have been identified at the following locations: 1. Gridline 6+1.2m approx. 3.3m in length 2. Gridline 5+3.3m approx. 2.0m in length 3. Gridline 5+1.9m approx. 3.3m in length All cracks are less than 1mm in width
| 03SR - Stations (RfL) | Cxxx-NCR-000598 | NCR | Stepney Green - Surface Cracking in Infill Slabs |  | Contr | SKC |  |  | 2017-08-31 | 2017-11-01 15:20 | 62 | 2017-04-13 09:16 | Structural Engineering - Structural Engineering - General | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | During a joint site visit between CRL, Cxxx and Cxxx two minor surface cracks were observed in the infill slabs, one or B01 and one on B00. Please see attached mark ups and photos for location. These surface cracks will need remediation to ensure a moisture path is not created. Cxxx propose to chase to chase these out by 10 mm by 10 mm and reinstate with five star grout as per MCR Cxxx-SKC-C-LRC-CR094-50224, to prevent a moisture pathway developing. Can Cxxx please approve this methodology. HI comment 24/05/2017 In response to Cxxxs comment regarding material can Cxxx please assess the attached __ __ S. Should Cxxx accept this material in principle Cxxx will raise the MCR as necessary.
| 03SR - Stations (RfL) | Cxxx-NCR-000599 | NCR | ESS - Lintel with insufficient bearing on blockwork wall |  | Contr | SKC | ELS - Eleanor Street Shaft (Central) |  | 2017-05-26 | 2017-05-24 06:56 | -2 | 2017-04-18 12:01 | Architectural - Brickworks/Blockworks | 2000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | Following on from Cxxx-EWN-01821, Cxxx-CCM-02432 and Cxxx-PMC-02187. During construction of a blockwork wall at Eleanor Street a lintel has been installed with insufficient bearing see attached photo S3701178.JPG
| 03SR - Stations (RfL) | Cxxx-NCR-000600 | NCR | ESS - Cut to proprietary blockwork lintel |  | Contr | SKC | ELS - Eleanor Street Shaft (Central) |  | 2017-05-18 | 2017-05-24 06:56 | 6 | 2017-04-18 13:11 | Architectural - Brickworks/Blockworks | 2000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Following on from Cxxx-EWN-01821, Cxxx-CCM-02432 and Cxxx-PMC-02187. During construction of a blockwork wall at Eleanor Street a lintel has been cut to avoid ingress into a builder's work hole, see attached photo S3701164.JPG
| 03SR - Stations (RfL) | Cxxx-NCR-000601 | NCR | NCR - Wiring of lighting circuits while CMS checksheets are not available |  | Contr | SKC | ELS - Eleanor Street Shaft (Central) |  | 2017-08-21 | 2017-08-17 12:16 | -4 | 2017-04-24 12:25 | Electrical - Cable Management | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | Lighting circuits have been wired through CMS (trunking and conduit) at Eleanor and Limmo Shafts to meet SLD dates. CMS in the Systewide areas and throughout the shaft was signed off as part of the SLD dates. Installation has been ongoing since then in non-systemwide areas. On a recent site visit by CRL, the relevant checksheets for signing off the CMS prior to wiring were not available. It should be noted that recent VAP audits at Eleanor did not raise any detrimental issues with the installation.
| 03SR - Stations (RfL) | Cxxx-NCR-000602 | NCR | STG Fire-stopping - Proceeding with Issued for Preliminary (P0X) Status drawings instead of IFC (Issued for Construction) drawings |  | Contr | SKC |  |  | 2017-08-31 | 2017-11-16 09:02 | 77 | 2017-04-24 18:13 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate resources | Completed |  | Fire-stopping works have been undertaken using Issued for Preliminary Status drawings instead of Issued for Construction drawings
| 03SR - Stations (RfL) | Cxxx-NCR-000603 | NCR | Fisher Street { Replacement of Incorrectly detailed U-Bars Wall 3 } |  | Contr | SKC |  |  | 2017-06-11 | 2017-05-16 07:36 | -26 | 2017-04-27 13:12 | Civil - Civil Engineering General | 2000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Information not detailed | Completed |  | Incorrect detailing in the area highlighted on RM Mark up for incorrect cover to U Bars for OSD interface Inset & Attached Sketches.
| 03SR - Stations (RfL) | Cxxx-NCR-000604 | NCR | Wall movement joint remediation works on level B5 - wall 24 to 08 |  | Contr | SKC |  |  | 2017-09-29 | 2017-08-07 09:56 | -53 | 2017-04-27 18:21 | Architectural - Walls | 500 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | Level B5, Wall 24-08 movement joint built not continuous due to meet 150mm lintel bearing.
| 03SR - Stations (RfL) | Cxxx-NCR-000606 | NCR | ESS - Roofing - Installation of Mansafe System Without Approved Code 1 MCR |  | Contr | SKC | ELS - Eleanor Street Shaft (Central) |  | 2017-05-29 | 2017-05-16 06:50 | -13 | 2017-05-04 12:07 | Architectural - Roofing & Exterior Treatment | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Procedure Problem - Other | Completed |  | Mansafe system installed prior to MCR being Code 1 approved.
| 03SR - Stations (RfL) | Cxxx-NCR-000607 | NCR | ESS - Roofing - Roofing Works Commenced Without 'C' Status Drawings |  | Contr | SKC | ELS - Eleanor Street Shaft (Central) |  | 2017-07-28 | 2017-07-19 08:29 | -9 | 2017-05-04 12:26 | Architectural - Roofing & Exterior Treatment | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Roofing works commenced without Code 1 approved C status drawings. The risk to carry out work on P status drawings was minimal. The comments that needed amending had no impact on the construction of the roof at that stage
| 03SR - Stations (RfL) | Cxxx-NCR-000608 | NCR | Cxxx inherited works: Exposed Reinforcement at the doorway of Secure Lobby toward Escape Stairs |  | Contr | SKC |  |  | 2017-09-25 | 2017-10-09 13:41 | 14 | 2017-05-12 14:01 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | External Phenomenon - Other | Completed |  | The bottom of the doorway between the Security Lobby and the Escape Stairs has been poured higher than SSL the design level of +108.140 (works undertaken by Cxxx). When this area was scabbled back to tie into the slab level in the security Lobby, the reinforcement became visible. Upon further inspection and survey, it has been noted that 5 U-Bars are sitting at a height of up to +108.152, 12mm above SSL. It should be noted that a previous NCR (Cxxx-NCR-535) had been raised for __ pouring the Security Lobby slab adjacent to the doorway too high. During the rectification scabbling back of this work, it was discovered that the doorway was also too high, and was scabbled at the same time to not cause a step.
| 03SR - Stations (RfL) | Cxxx-NCR-000609 | NCR | __ - Traction HV CMS, level B3 |  | Contr | SKC |  |  | 2017-08-24 | 2017-08-17 13:00 | -7 | 2017-05-10 12:44 | Electrical - Cable Management | 5000 |  | Design | Rework | 3 (3-6k) | Complete | Design Problem - Other | Completed |  | At Stepney Green the traction HV CMS installation on level B3 was installed through the "by exception" process. The "by exception" C status drawing used to proceed with the works was issued by the F1 designer as fit for construction. Following the completion of the works the design was further developed and as a result there is a deviation between the on site installation and the current revision of the F1 design. This was not captured as part of an FCD and Cxxx have raised this as a concern. Containment Layout dwg, level B3: Cxxx-SKC-E-DDA-CR094_SH005_4-00244
| 03SR - Stations (RfL) | Cxxx-NCR-000610 | NCR | Fisher Street - __ not ferro-scanning RC prior to drilling fixings |  | Contr | SKC |  |  | 2017-06-30 | 2017-06-27 07:22 | -3 | 2017-05-12 11:54 | Electrical - General | 2000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | Hole Drilled for CMS Bracket without Ferro scanning prior to commencement. Operative drilled a number of holes to install Support brackets subsequently coming in contact with reinforcement.
| 03SR - Stations (RfL) | Cxxx-NCR-000611 | NCR | B5 Welfare missed floor penetrations |  | Contr | SKC |  |  | 2017-07-31 | 2017-07-26 15:54 | -5 | 2017-05-15 17:30 | Civil - Civil Engineering General | 500 |  | Planning | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | 3 no. floor penetrations (inc. stiffener plates) have not been installed in the raised block and beam floor of the B5 Welfare room - see attached mark-up. These penetrations are required for 2 no. floor traps and 1 no. drainage pipe.
| 03SR - Stations (RfL) | Cxxx-NCR-000612 | NCR | B5 Wet Closet screed installed to incorrect thinkness |  | Contr | SKC |  |  | 2017-12-25 | 2018-09-03 16:25 | 252 | 2017-05-15 17:58 | Civil - Civil Engineering General | 1000 |  | Supervision/Management | Repair | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Within the B5 Wet Closet Room the screed has been installed 50mm thick. As per the latest design drawing for the floor finish on this level, the thickness of the screed should only be 30mm thick.
| 03SR - Stations (RfL) | Cxxx-NCR-000613 | NCR | STG TR1, TR2, SRHV1, & SRLV2 Door openings built small than design |  | Contr | SKC |  |  | 2017-08-31 | 2017-05-23 16:30 | -100 | 2017-05-15 18:35 | Civil - Civil Engineering General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Supervision - Other | Completed |  | The structural opening heights into the following rooms have been constructed smaller than the design specifications. -TR1, design height 2500mm, as-built height 2440mm, proposed clear opening 2370mm -TR2, design height 2500mm, as-built height 2440mm, proposed clear opening 2370mm -SRHV1, design height 2500mm, as-built height 2480mm, proposed clear opening 2410mm -SRLV1, design height 2500mm, as-built height 2420mm, proposed clear opening 2350mm -SRLV2, design height 2500mm, as-built height 2400mm, proposed clear opening 2330mm
| 03SR - Stations (RfL) | Cxxx-NCR-000614 | NCR | Stepney Green - Breaking Back D-Wall on B4 to install Intervention Stairs (ST1) |  | Contr | SKC |  |  | 2017-08-31 | 2017-06-01 08:33 | -91 | 2017-05-17 13:06 | Structural Engineering - Diaphragm Walls | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Due to the undulating surface of the Cxxx diaphragm wall, Cxxx were required to break back the diaphragm wall provide a relatively even face free from bulges to install the intervention stairs landing brackets. As part of this breaking back some of the reinforcement was exposed. Please see attached photos for extent of reinforcement exposed.
| 03SR - Stations (RfL) | Cxxx-NCR-000615 | NCR | Gap due to lintel schedule error |  | Contr | SKC |  |  | 2017-08-31 | 2017-08-17 05:35 | -14 | 2017-05-17 12:56 | Architectural - Brickworks/Blockworks | 500 |  | Design | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | The lintel schedule gives a lintel which doesnt end flush with the blockwork wall resulting in a small 20-30mm gap which a block cannot fit into. Please see photo attachment.
| 03SR - Stations (RfL) | Cxxx-NCR-000616 | NCR | Stepney Green - Late submission of ST1 and ST2 F2 Drawings |  | Contr | SKC |  |  | 2017-09-30 | 2017-07-13 14:45 | -79 | 2017-05-17 13:12 | Architectural - General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | did not submit the F2 detailing packs to CRL before installation works commenced on site for ST1 Intervention and ST2 Escape stair cases issued by Stair Fabricator, Environmental Fabrications Ltd.
| 03SR - Stations (RfL) | Cxxx-NCR-000617 | NCR | Stepney Green - 25 x 25 mm Chamfer on Escape Stair Doors |  | Contr | SKC |  |  | 2017-07-28 | 2017-06-02 15:21 | -56 | 2017-05-18 11:33 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | As per the attached mark up the drawing the door ways into the escape stairs have been cast with 25 x 25 chamfer. As per Cxxx-JUL-S-DDJ-CR094_SH005-01010; heading Structural concrete Subject 3 All arises 90 degrees or less shall have 25x25 chamfers except door openings unless noted otherwise. Thus the doors should have been cast without the 25 x 25 chamfer. HI Comment 31/05/2017 The kicker is proposed to be cut to match the angle fillet on the doorway.
| 03SR - Stations (RfL) | Cxxx-NCR-000618 | NCR | FIS - Headhouse External Wall 5 - Cube Results |  | Contr | SKC |  |  | 2017-09-29 | 2017-08-17 11:02 | -43 | 2017-05-19 08:17 | Civil - Civil Engineering General | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | Whilst reviewing the Post-Pour Check Sheets for some recent concrete pours, it was noticed that for the headhouse external wall 5 pour on 27/03/17 that the cube results for the 28 days strength has failed to reach the required 60 N/mm2 strength (C50/60 Concrete). ************************************************************************************* Cxxx - update as of 29/06/17 1. i) See attached 'Fibre Mix' for details on concrete mix ordered from supplier ii) See attached 'Failed Cubes Dockets' for details on mix supplied iii) See attached 'Failed Cubes Dockets' for details on mix delivered 2. The concrete supplier did sample one of the three deliveries of the C50/60 on the date in question (ticket number 357503) and the cube results comply with the specified characteristic strength at 28 days. - See attached 'Test Certificate 357503'. 3. The batching plant have stated the following: "There are a number of factors that can affect the strength of concrete cube results. In this instance, we are of the opinion that deficiencies in sampling and cube manufacture have potentially contributed to the lower than anticipated results obtained at site. This opinion is based upon the reported hardened densities of the site cubes and __’s satisfactory production records, consistence records and compliant cube results. Therefore we would believe that the results obtained at site do not represent the quality of the delivered concrete." The latest cube results obtained from site (tested at 91 days) now comply with the specified characteristic strength, and the contractor suggests 'Use as is'. See attachment __ Results - 90 days, which had a compressive strength of 61.1 N/mm2. Furthermore, see attached letter from __ in relation to the failed cube test (__ Letter NCR 618). With all the above information in mind, the route cause of the failed results seems to be from the incorrect compaction of the cube at manufacture stage, resulting in lower than anticipated results.
| 03SR - Stations (RfL) | Cxxx-NCR-000619 | NCR | FIS - Headhouse External Walls 2,3,4,5 and 7 - Cube Results |  | Contr | SKC |  |  | 2017-07-31 | 2017-06-28 06:57 | -33 | 2017-05-19 08:37 | Civil - Civil Engineering General | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | Whilst reviewing the Post-Pour Check Sheets for some recent concrete pours, it was noticed that the pour for the headhouse external walls 2,3,4,5 and 7 (Wall 7 kicker section) on 13/04/17 that the cube results for the 28 days strength has failed to reach the required 60 N/mm2 strength (C50/60 Concrete).
| 03SR - Stations (RfL) | Cxxx-NCR-000620 | NCR | Stepney Green - ST1 and ST2 Threshold Plates |  | Contr | SKC |  |  | 2017-10-02 | 2017-07-04 08:33 | -90 | 2017-05-19 16:30 | Architectural - Finishes | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | have installed a 3mm steel plates with chamfered edges to the Intervention (ST1) and Escape (ST2) landings at slab level (as shown on drawing attached). The approved F1 drawings showed a flat plate across the slab and stair landing. The F2 installed plate has a slight chamfer to accommodate the as-built level difference.
| 03SR - Stations (RfL) | Cxxx-NCR-000621 | NCR | NCR - Ductwork Installation |  | Contr | SKC |  |  | 2018-01-22 | 2018-02-06 07:08 | 15 | 2017-05-23 07:47 | Mechanical - Mechanical Engineering General | 500 |  | Planning | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Sections of Ductwork at Limmo have been installed in close proximity of the electrical services' CMS. This includes the installation of drop rods in close proximity of the HV services. As a result the services within the CMS will not be accessible once the ductwork installation is completed. The current installation does not take into consideration the fact that the ductwork will need to be lagged.
| 03SR - Stations (RfL) | Cxxx-NCR-000622 | NCR | NCR - STG/LIP - Cable trays installed in risers with no allowance for cleating cables |  | Contr | SKC |  |  | 2017-08-25 | 2017-08-18 22:03 | -7 | 2017-05-23 15:32 | Electrical - Cable Management | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | During site inspections it has been identified that the cable trays installed in the main risers at both Limmo Peninsula & Stepney Green have been installed in such a way that severely hinders future installation of cable cleats. Current design does not require cleats to be used and CMS has been sized to accommodate current installation.
| 03SR - Stations (RfL) | Cxxx-NCR-000623 | NCR | Stepney Green - Intervention and Escape Stair Horizontal Packing |  | Contr | SKC |  |  | 2017-09-08 | 2017-07-03 08:35 | -67 | 2017-05-30 13:37 | Civil - Structural Engineering | 500 |  | Design | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Packers were used to install the landing brackets of the escape and intervention stairs. The packers that have been used are metal shims. queried the maximum horizontal distance with the Cxxx Stage F designers and the response received said max 150mm (RFI-184). However the response also stated that a grout mortar should be used. When __ (Cxxx Structural engineers) were on a site visit, they highlighted that the metal shims used nor the __ bolt installed can resist shear and the size of the shims significantly reduces the amount of grout used. Therefore additional steel angles are required where the packing exceeds 12mm (RFI-542). Please find attached the 2no. RFI responses.
| 03SR - Stations (RfL) | Cxxx-NCR-000624 | NCR | FIS Firestopping – Incorrect Mastic Installation (Joint width exceeding 30mm) |  | Contr | SKC |  |  | 2017-06-13 | 2017-06-05 09:14 | -8 | 2017-05-30 11:03 | Fire - Compartmentation | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | In the HV LV R1, on B4, where the curved masonry wall meets the concrete adit ceiling - see attached Supporting Location Sketch and photograph 'Excessive Width Mastic Joint', the width of the intumescent mastic joint exceeds the 30mm maximum specified by PFC __ (being inferior to 40mm).
| 03SR - Stations (RfL) | Cxxx-NCR-000625 | NCR | Resin leak within lift shaft |  | Contr | SKC | ELS - Eleanor Street Shaft (Central) |  | 2017-09-29 | 2017-09-08 14:54 | -21 | 2017-06-01 13:52 | Mechanical - Lifts | 1000 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During the resin application of the shaft lobby floors at Eleanor Street, resin has leaked under the __ lift door threshold on Level B2 into the inside of the lift core. Some of the resin has leaked onto the __ lift door on the level below (B3) and a small amount of resin has gone onto the __ lift inside the shaft. Levels B2-B3 only areas to be affected.
| 03SR - Stations (RfL) | Cxxx-NCR-000626 | NCR | ESS - Doors - |  | Contr | SKC | ELS - Eleanor Street Shaft (Central) |  | 2017-09-29 | 2017-12-06 10:15 | 68 | 2017-06-01 15:37 | Architectural - Doors | 3000 |  | Manufacturing Defect | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Doors frames belonging to doors DB4.02, DB5.04, D00.01 and D00.01 have been fabricated too big. scabbling of structural openings to suit already fabricated frame sizes
| 03SR - Stations (RfL) | Cxxx-NCR-000627 | NCR | ESS - Drilling close to the edge of blockwork |  | Contr | SKC | ELS - Eleanor Street Shaft (Central) |  | 2017-10-31 | 2017-11-09 10:50 | 9 | 2017-06-02 10:18 | Electrical - Cable Management | 2000 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During the installation of uni-strut for use as part of the cable management system at Eleanor Street fixings have been installed close to the edge of blockwork. See attached photos. The manufacturers guidance for installing these fixings recommends a distance of 50 mm from the edge of block to prevent damage. due to the design and space proofing requirements of the M&E works in some places it has been required to install a fixing within this 50mm distance. For all the fixings installed there is no visible signs of damage to the blocks or the mortar. __ data sheet attached.
| 03SR - Stations (RfL) | Cxxx-NCR-000628 | NCR | External Drainage |  | Contr | SKC |  |  | 2017-09-29 | 2017-09-08 07:40 | -21 | 2017-06-05 17:20 | Civil - Drainage | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Procedure Problem - Other | Completed |  | The Mile End External CCTV Report Rev 2 (refer Cxxx-SKC-D-RGN-CR094_WS109-50001) has been returned Code 3 on the basis that there are displaced joints within the run (refer Cxxx-SKC-D-XCS-CR094_WS109-50005). It should be noted that the comments sheet refer to the following locations: MH10 - MH 11 - Displacement approx. at 6.2m and 7.4m from MH 11 MH12 - MH13 - Displacement approx. 100mm from MH 13 MH13 - MH 20 - Displacement approx. 9m from MH 13 MH10 - B - Displacement approx. 300mm from MH 10 28 June 2016 Update. It is noted that repair solution has been discussed with CRL and CEG. As such the proposed solution is as per the attached email and subsequent attachment. For the avoidance of doubt, out of the locations listed above and taking into account the attached email, the following is to be undertaken: MH10 - B - Displacement approx. 300mm from MH 10 - Air Test Only MH12 - MH13 - Displacement approx. 100mm from MH 13 - Air Test Only Noted the attached mark up states water testing, it is noted that this is applicable to the manholes in this application only which is covered under Cxxx-PWK-00270.
| 03SR - Stations (RfL) | Cxxx-NCR-000629 | NCR | Oversized lintel above opening reaches edge of wall |  | Contr | SKC |  |  | 2017-07-24 | 2017-06-15 12:59 | -39 | 2017-06-06 15:49 | Architectural - Brickworks/Blockworks | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | In the lintel schedule Lintel LB1.78.02 should have a 715mm lintel instead a longer lintel was installed which extends all the way to edge of the blockwork wall B1.78 (SR11kV HV2). Please see photo attached
| 03SR - Stations (RfL) | Cxxx-NCR-000630 | NCR | Fisher St { KF10.1210 Homogeneity of Fibre Distribution results In-conclusive } |  | Contr | SKC |  |  | 2017-07-31 | 2017-06-23 11:56 | -38 | 2017-06-07 10:12 | Civil - Civil Engineering General | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Defective or inadequate procedure | Completed |  | All tests taken to comply with KF10.1210 Homogeneity of Fibre Distribution returned results indicating less than design requirements for walls mentioned as part of Cxxx-JUL-S-DDJ-CR086_SH003-02100 Note 9. __ have confirmed that the Mix attached was as per approved MCR attached. Attached also is the results and example dockets from Pours tested. ************************************************************************************************************************************** Further Cxxx Response 16.06.2017 Attached is a Statement from __ “British Standard Requirements There is unfortunately no standard test method in the United Kingdom for determining the content of class 1a and 1b polymer fibres in fresh concrete. There is therefore no associated repeatability or reproducibility data or defined limits for determining conformity. In-house test methods reviewed by ourselves have provided significantly variable results. This is simply due to the inherent difficulties that can be experienced in accurately extracting and drying a very small volume of lightweight material. BS 8500-2 and BS EN 206 reflect the lack of standard test procedures and require that where fibres are added at the concrete batching plant ‘Where the fibre content of fresh concrete is to be determined, it shall be taken either as recorded on the print-out of the batch recorder or where recording equipment is not used, from the production record in connection with the batching instruction. __ Production Procedures Our production procedures reflect the requirements of BS 8500-2 and BS EN 206. Where fibre additions are used the number of bags are annotated on the delivery ticket and recorded on a manual additions sheet. After reviewing our production records we can confirm that the correct amount of fibre was added to all of the concrete delivered. “ Attached is __’s statement “ We carried out the sampling and testing in accordance with BS EN 14488-7 Method B Fresh fibre wash out. The only change from the standard is to use a 10L pot (as stated in KF10.12.10 Crossrail specification) where BS EN 14488-7 states each sample should be between 1 to 2 L. BS EN 14488-7 is for sprayed concrete and is used as to the best of our knowledge the only standard that has provisions for a synthetic fibre. As these fibres are so fine and adoption of procedure that no one cannot be wholly confident that this has captured all of the fibres. We had also tried to extract the fibres through the hardened concrete cubes however due to the fineness this was unsuccessful. We undertake many tests for fibres in concrete but this is the first time we have ever been requested for such fine synthetic fibre, as generally testing relates to Steel fibre Contents, so very unusual. “ Attached is the Propex statement from the companies director of Engineering “It is not common practice to undertake washout tests for micro pp fibres. Typically "wash out" tests are completed for "structural fibres" - these are typically either steel or macro synthetic fibre which have a diameter up to 1mm where it is important to verify the consistency of fibre reinforce concrete as the fibres are providing a load bearing or flexural capacity to the concrete. In comparison, the FM150 fibres you are trying to test have a diameter of just 0.032mm - so are very difficult to measure using a standard washout tests as typically specified in the "codes", as very careful sieving of the material would be required to capture the fibres to give any chance of a realistic measurement. For example if you were to take a standard sample of 8 litres of fibre reinforced concrete, you would expect to weigh just 16g of fibres ( this equates to 1.6 million individual fibres). However, we do know of instances where this has been completed successfully - but it just takes time and a lot of care! “ And with Further correspondence stated “It is possible to do and has been done successfully despite the it being very difficult. However, it is very unusual to undertake the test, and I can only recall a very small number of tests ever being completed in all the projects we supply around the world.” Can you please review and advise the best way forward in order to close out this NCR as it has been indicated by a number of specialists that this test is next to impossible in its current format and the BS standard referenced is used for sprayed concrete, therefore not applicable in this instance. With all the above taken in to account are in the belief “ Use as Is “ is the best Disposition as numerous parties question the Validity of the test in this situation.
| 03SR - Stations (RfL) | Cxxx-NCR-000631 | NCR | ST3 Handrail too short |  | Contr | SKC |  |  | 2017-07-28 | 2017-07-03 18:18 | -25 | 2017-06-27 11:07 | Structural Engineering - Steel Member | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The handrail for ST3 at the plenum level was too short to span the width of the plenum corridor approximately 200mm short. Therefore __ added an additional "sleeve" to span across.
| 03SR - Stations (RfL) | Cxxx-NCR-000632 | NCR | ESS - Roof - Flashing Colour Mis-match |  | Contr | SKC | ELS - Eleanor Street Shaft (Central) |  | 2017-07-27 | 2017-07-06 14:04 | -21 | 2017-06-09 12:22 | Architectural - Roofing & Exterior Treatment | 2000 |  | Manufacturing Defect | Rework | 4 (0.5-3k) | Complete | Personnel Error - Inattention to detail | Completed |  | Section of flashing installed between GL C-F along GL 1 is a different colour (black) than the rest of the flashing and guttering (pale blue/grey). Please see attached photo.
| 03SR - Stations (RfL) | Cxxx-NCR-000633 | NCR | Cracks in Adit Service Trenche Shoulders |  | Crossrail | XRL | ELS - Eleanor Street Shaft (Central) |  | 2017-09-29 | 2017-09-06 07:22 | -23 | 2017-06-09 14:14 | Civil - Civil Engineering General | 5000 |  | Supervision/Management | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Further to RFI956: Mass fill concrete forming the shoulders of the service trenches in the intervention adits have cracked considerably. There are several cracks (approximately 20No) which are 2-3mm wide running the full extend of the shoulder structure. No reinforcement was included during construction. The cracks run all the way through the shoulders (part of which is a drainage channel) and into the service trench. Furthermore, despite this issue being known about since Nov 2016, the same excessive lengths of mass fill concrete bays have now been cast in the ventilation side of the shaft. These are likely to crack in the same way. were given several opportunities to raise this NCR but declined.
| 03SR - Stations (RfL) | Cxxx-NCR-000634 | NCR | ESS - MCR not in place for curing agent on the secondary lining |  | Contr | SKC | ELS - Eleanor Street Shaft (Central) |  | 2017-08-08 | 2017-06-19 11:02 | -50 | 2017-06-09 16:15 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | During the construction of the shaft secondary lining (completed around 08/15), Cxxx did not have an approved MCR in place for the curing agent that was applied on the concrete surface upon striking of secondary lining shuttering. In order to comply with KF10 a water based sprayed curing agent was applied on the secondary lining pours, in particular the material used was Adocure. Cxxx notes that Adocure has been used by a different subcontractor at a later stage during the construction of the concrete walls and the MCR was in place (see attached MCR).
| 03SR - Stations (RfL) | Cxxx-NCR-000635 | NCR | Adaptable Boxes for fire detection cabling |  | Contr | SKC |  |  | 2017-10-30 | 2017-10-19 13:17 | -11 | 2017-06-13 14:30 | Electrical - Cable Management | 500 |  | Incomplete Works | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | In several locations in the Limmo Peninsula shaft, 50mm deep adaptable boxes have been installed for the fire detection cabling.
| 03SR - Stations (RfL) | Cxxx-NCR-000636 | NCR | Cube results of LM-008 not reaching required strength of 40MPa |  | Contr | SKC |  |  | 2018-02-26 | 2017-12-19 13:53 | -69 | 2017-06-17 09:25 | Civil - Civil Engineering General | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | The cube results corresponding to the concrete pour for LM-008 were crushed at 35MPa, below the required 40MPa. The pour took place over the eastern inverted turret, and will have a secondary 210mm RC placed directly on top.
| 03SR - Stations (RfL) | Cxxx-NCR-000637 | NCR | Fire main vertical fixings |  | Contr | SKC |  |  | 2017-08-28 | 2017-07-19 12:21 | -40 | 2017-06-15 11:48 | Mechanical - Piping | 500 |  | Incomplete Works | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | To affix the fire main support bracketry, resin anchors have been fixed vertically to the soffit in the 00 security lobby and lobby area. Whereas the fire main services typical support details (Cxxx-SKC-P-DWG-CR144_WS155-50001) shows where the fire main are hung vertically the support channel are to be held by __ M10 HUS5 screw anchors
| 03SR - Stations (RfL) | Cxxx-NCR-000638 | NCR | Stepney Green - Vertical Packing ST1 and ST2 |  | Contr | SKC |  |  | 2017-09-29 | 2017-09-14 09:38 | -15 | 2017-07-10 08:29 | Civil - Structural Engineering | 500 |  | Material | Repair | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | During installation of the Stairs at each slab landing, the brackets are fixed to the face of the DSJV waler beams. Each outside bracket, has 2no. fixings and the middle brackets 3no. fixings. All required a minimum embedment depth of 170mm. A ferroscanner was used to avoid reinforcement however it could only read up to a depth of 120mm. When the stair installers (__) drilled, they hit reinforcement at a depth approximately 130-150mm. Cxxx discussed the issue with __ (Cxxx Structural Engineers) who then assessed a number of options to keep the use of the same hole, including a change to the fixing types. See emails attached from __ engineers.
| 03SR - Stations (RfL) | Cxxx-NCR-000639 | NCR | Punctures in waterproofing membrane due to protection fixing |  | Contr | SKC |  |  | 2018-01-02 | 2018-01-30 08:27 | 28 | 2017-07-06 11:08 | Civil - Civil Engineering General | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | As per datasheet for __ 800PA (Cxxx-SKC-C-LRC-CR094-50180), waterproofed surfaces cannot remain exposed for longer than 30 days. Temporary protection is therefore required on all vertical surfaces (horizontal surfaces to be protected by permanent screed). The permanent vertical protection, __ protection board, cannot be installed until as the mound is backfilled, as it is fixed in place by the fill. A layer of black polythene is the most suitable means of this temporary protection. The polythene must be mechanically fixed to the external headhouse walls, as trying to sandbag them in places poses a major safety risk of getting blown away, particularly due to the potential length of time the protection will be in place. Chemically fixing the polythene was not considered as 1) it is only a temporary measure and the difficulty in removing it and 2) the effect an adhesive may have on the overall life of the __.
| 03SR - Stations (RfL) | Cxxx-NCR-000640 | NCR | Firestopping fixings metal nail anchor installed without accepted MCR |  | Contr | SKC | ELS - Eleanor Street Shaft (Central) |  | 2017-09-29 | 2017-10-30 13:23 | 31 | 2017-06-23 07:31 | Fire - Compartmentation | 1000 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | JCP Metal Nail Anchors have been installed on site without an accepted MCR. They were missed out of the fire stopping fixings MCR: Cxxx-SKC-C-LRC-CR094-50420.
| 03SR - Stations (RfL) | Cxxx-NCR-000641 | NCR | ESS – Deformed Washers in installation of Secondary Steelwork for Cladding |  | Contr | SKC | ELS - Eleanor Street Shaft (Central) |  | 2017-09-05 15:11 | 2017-10-30 15:39 | 55 | 2017-06-27 12:30 | Architectural - General | 3000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Washers have deformed in over tightening the PFC to RSA bolted connection on gridlines 1 and 4. In some areas this has affected the bearing of the washer on the bracket. See attached photos
| 03SR - Stations (RfL) | Cxxx-NCR-000642 | NCR | Non-MCR'd Item Installed |  | Contr | SKC |  |  | 2017-11-27 | 2017-09-29 13:10 | -59 | 2017-06-27 16:25 | Mechanical - Public Health Engineering | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Use of unapproved materials | Completed |  | There is no MCR for the victaulic clamp bolts used on the fire main
| 03SR - Stations (RfL) | Cxxx-NCR-000643 | NCR | No Installation of Fire Collars |  | Contr | SKC |  |  | 2017-11-27 | 2017-10-03 07:44 | -55 | 2017-06-27 16:18 | Fire - Compartmentation | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | As per the Fire stopping Detail "JNP/7692PR/F024/01" from "The Fire Systems Reference Manual Part 1", where a pipe passes through a concrete slab it is to be sleeved and compound is to be applied from the sleeve to the penetration and rockwool is to be used between the sleeve and the pipe. At Limmo Peninsula the fire main pipes are currently being installed but no sleeves have been installed.
| 03SR - Stations (RfL) | Cxxx-NCR-000645 | NCR | Site made CMS bends - Back to back trunking |  | Crossrail | XRL |  |  | 2017-09-04 | 2017-08-11 05:59 | -24 | 2017-07-07 08:04 | Electrical - Cable Management | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Use of unapproved materials | Completed |  | Surveillance on Electrical Installation was carried out at Cxxx Limmo Shaft. It was agreed to check Corridor B1 and associated rooms. Whilst in the Corridor it was noticed that inverted sections of trunking was being installed to the main run of multi-compartment trunking. The Contractor had fabricated site made ‘TEE’ sections by installing trunking back to back and joining them with bushes and lock rings. Installing bushes and lock rings has resulted in a loss of cable capacity in the trunking past this point.
| 03SR - Stations (RfL) | Cxxx-NCR-000646 | NCR | Trunking screws protruding through captive nuts |  | Crossrail | XRL |  |  | 2017-09-04 | 2017-09-12 13:27 | 8 | 2017-07-07 08:12 | Electrical - Cable Management | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Surveillance on Electrical Installation was carried out at Cxxx Limmo Shaft. It was agreed to check Corridor B1 and associated rooms. Whilst inside the Battery Room a section of installed trunking was checked at a manufactured bend. Upon checking the joining screws protruded through the captive nuts.
| 03SR - Stations (RfL) | Cxxx-NCR-000647 | NCR | Emergency lighting not segregated from other services. DALI Lighting Control wiring |  | Crossrail | XRL |  |  | 2017-09-04 | 2017-09-12 13:22 | 8 | 2017-07-07 08:22 | Electrical - Lighting | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Surveillance on Electrical Installation was carried out at Cxxx Limmo Shaft. It was agreed to check Corridor B1 and associated rooms. Whilst inside the CER it was noticed that conduit had been installed linking two different compartments of the multi-compartment trunking. The Contractor stated that this was to connect DALI control cables to the lighting in the room. The Contractor explained that they were told they could run the control cables in either the normal or Emergency compartment of the trunking and that the cables had been installed in the Emergency Lighting compartment.
| 03SR - Stations (RfL) | Cxxx-NCR-000648 | NCR | Installation of Non-MCR'd Stainless Steel Pipe |  | Contr | SKC |  |  | 2017-11-27 | 2017-11-13 08:31 | -14 | 2017-07-19 10:33 | Mechanical - Public Health Engineering | 1000 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Use of unapproved materials | Completed |  | The stainless steel pipework under the HRU room on level 00 in the limmo peninsula shaft has been installed, welded and covered by Denso tape prior to the MCR acceptance. (CRL-MCR-004957)
| 03SR - Stations (RfL) | Cxxx-NCR-000649 | NCR | LPS - Firemain MCR did not cover the diameter of pipe used on site |  | Contr | SKC |  |  | 2017-11-27 | 2017-10-04 06:35 | -54 | 2017-07-19 16:34 | Mechanical - Mechanical Engineering General | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Lack or improper material identification and traceability | Completed |  | The 200mm firemain that is partially installed through the shaft and head house does not have an MCR that covers the product, as the MCR that it was assumed it was under, has a maximum size of 150mm.
| 03SR - Stations (RfL) | Cxxx-NCR-000650 | NCR | ESS - Incorrect fireproofing installation below D158 roof decking |  | Contr | COS | ELS - Eleanor Street Shaft (Central) |  | 2017-10-19 | 2017-10-20 11:45 | 1 | 2017-07-21 12:30 | Fire - Compartmentation | 1000 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Lack or improper material identification and traceability | Completed |  | Cxxx-RFI-1054 specified the use of Firepro Soft Seal Batt to be installed between the D158 decking void and the blockwork/steel beams underneath. Upon a site inspection, it was found that Firepro Ablative Coated Batt and mastic was installed instead of Firepro Soft Seal Batt and mastic.